## Test Conditions
DESIREE-FIRE Test Number 12 - Circuit Simulator Data Only
Test Date: | 2009-08-12
DCSim DAQ Start Time | 18:14
DCSim Time for Synchronization | 18:47
Heat Source Synchronization | 1:46 | minutes:seconds
Heat Source DAQ Start Time | 18:44
Fire Time | 18:47
Offset | 0:33 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1965 | seconds
Heat Source Offset | 0:03 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 151 | seconds
Heat Source Stop Time | 19:27
Test Duration | 0:40 | minutes:seconds
| 2400 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
MOV 2 | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.51562 | 123.3948 | -60.1273 | 63.1348 | -0.027161 | 0.0014163 | 0.063993 | 0.065399 | -0.0015103 | -0.0012112 | 0.0013971 | -0.041534 | 0.0016043 | 0.068772 | 0.06285 | -0.0017432 | -0.00016658 | -0.0046035 | -0.1236 | 63.1897 | -60.3882 | 62.883 | -60.1181 | -60.466 | -0.11444 | -0.15106 | 63.1577 | -60.2371 | 63.089 | -60.054 | -60.2554 | -59.8801 | -0.26093 | 0.054931 | -0.25177 | 0.009155 | 60.0128 | -0.33875 | 60.2737 | -0.077819 | -0.10986 | 0.022888 | -0.045777 | 0.073242 | 0.24719 | -0.12817 | 0.35706 | -0.01831 | 0.27008 | 123.2712 | 0.18311 | 123.3261 | 123.5779 | 123.3948 | 123.317 | 123.2849 | -123.523 | -123.3719 | 123.0103 | 123.2162 | 60.0037 | 59.9762
0.54688 | 123.4268 | -60.1044 | 63.1485 | -0.050049 | -0.00050633 | 0.065275 | 0.065612 | -0.00086946 | -0.0020658 | 0.0011835 | -0.023224 | 0.0020315 | 0.066849 | 0.069686 | -0.000675 | 0.00026062 | -0.0011855 | 0.004578 | 63.2034 | -60.3287 | 62.9517 | -59.9991 | -60.3561 | 0.018311 | 0.054932 | 63.208 | -60.1639 | 63.1622 | -60.1135 | -60.2234 | -59.816 | -0.2243 | 0.054931 | -0.19684 | 0.10529 | 60.1227 | -0.25177 | 60.347 | -0.027466 | -0.059509 | 0.059509 | 0.013732 | -0.009155 | 0.28839 | -0.11902 | 0.3479 | -0.05951 | 0.32959 | 123.2803 | 0.050354 | 123.3261 | 123.5321 | 123.3719 | 123.3078 | 123.3124 | -123.4772 | -123.3124 | 123.056 | 123.2666 | 60.1089 | 60.1593
1.4844 | 123.3765 | -60.1364 | 63.1073 | -0.011902 | 0.0012027 | 0.065702 | 0.065612 | 0.0023349 | 0.00028418 | 0.00075627 | -0.029327 | -0.00095912 | 0.068131 | 0.066909 | -3.4196e-05 | -0.0018756 | -0.00097194 | -0.13275 | 63.1851 | -60.3928 | 62.8876 | -60.1227 | -60.4889 | -0.13733 | -0.16937 | 63.1622 | -60.2234 | 63.1073 | -60.2097 | -60.3287 | -59.8526 | -0.25635 | 0.07782 | -0.21973 | 0.013733 | 59.9991 | -0.35248 | 60.2554 | -0.096131 | -0.086975 | 0.054931 | 0 | -0.073242 | 0.28381 | -0.19226 | 0.37079 | -0.10529 | 0.27008 | 123.2803 | 0.013733 | 123.3307 | 123.5779 | 123.3856 | 123.3215 | 123.2986 | -123.5001 | -123.3307 | 123.024 | 123.2437 | 60.0037 | 59.967
2.5469 | 123.4406 | -60.0906 | 63.1073 | -0.027161 | 0.0014163 | 0.064847 | 0.06369 | 0.00019874 | 0.0015658 | -9.8328e-05 | 0.086639 | -0.00053192 | 0.067704 | 0.064559 | 0.001034 | -0.0027302 | 0.00095066 | 0.027466 | 63.1943 | -60.2875 | 63.0386 | -59.9075 | -60.26 | 0.10986 | 0.12817 | 63.1851 | -60.1318 | 63.2309 | -60.0494 | -60.1273 | -59.7427 | -0.19684 | 0.086975 | -0.068665 | 0.1831 | 60.2005 | -0.16937 | 60.3973 | 0.027466 | -0.041199 | 0.07782 | 0.1236 | 0.041199 | 0.3479 | -0.036621 | 0.3891 | 0.004578 | 0.37994 | 123.3261 | 0.082398 | 123.3627 | 123.4818 | 123.317 | 123.2849 | 123.2758 | -123.3948 | -123.2391 | 123.1293 | 123.3215 | 60.1181 | 60.2188
3.4844 | 123.3856 | -60.141 | 63.1073 | -0.019531 | 0.0020573 | 0.065488 | 0.065612 | -0.00065586 | 0.00092498 | -0.00095273 | -0.044586 | 0.0016043 | 0.067063 | 0.062209 | -0.0008886 | -0.0020892 | -0.0028945 | -0.11444 | 63.1943 | -60.3928 | 62.8738 | -60.1089 | -60.4477 | -0.10986 | -0.14648 | 63.1668 | -60.2142 | 63.1393 | -60.1868 | -60.2783 | -59.8526 | -0.25177 | 0.086975 | -0.23346 | 0.032043 | 60.0311 | -0.3067 | 60.2829 | -0.054932 | -0.073242 | 0.059509 | 0.032043 | -0.045777 | 0.28839 | -0.13733 | 0.36163 | -0.064087 | 0.28381 | 123.2666 | 0.027465 | 123.3536 | 123.587 | 123.381 | 123.3353 | 123.3078 | -123.5001 | -123.3215 | 123.0148 | 123.2803 | 60.0266 | 59.9945
4.4844 | 123.3444 | -60.1227 | 63.1119 | -0.042419 | 0.0014163 | 0.066984 | 0.065185 | 0.00062594 | -0.00078402 | -0.00095273 | -0.041534 | -0.00074552 | 0.067704 | 0.065414 | 0.0012476 | -0.00016658 | 0.0013779 | -0.059509 | 63.1668 | -60.3516 | 62.8922 | -60.0632 | -60.4019 | -0.10071 | -0.068665 | 63.1851 | -60.1868 | 63.1348 | -60.1868 | -60.2921 | -59.8572 | -0.22888 | 0.054932 | -0.21973 | 0.05951 | 60.022 | -0.27924 | 60.2509 | -0.050355 | -0.064087 | 0.073243 | 0.022889 | -0.064087 | 0.2655 | -0.16937 | 0.32959 | -0.10529 | 0.28839 | 123.2437 | 0 | 123.3215 | 123.5184 | 123.3719 | 123.2895 | 123.3078 | -123.4634 | -123.2986 | 123.0148 | 123.2574 | 60.0632 | 60.054
5.5469 | 123.3719 | -60.1181 | 63.1714 | -0.065308 | -0.00071993 | 0.064207 | 0.061553 | -0.00065586 | 0.00071138 | 0.0016107 | 0.046967 | 0.0018179 | 0.067704 | 0.0605 | 0.0008204 | -0.0012348 | -0.00054474 | -0.013733 | 63.208 | -60.3287 | 62.9288 | -60.0357 | -60.3745 | 0.041199 | 0.027466 | 63.1989 | -60.173 | 63.1302 | -60.1318 | -60.2325 | -59.8297 | -0.21057 | 0.036621 | -0.24262 | 0.082397 | 60.1593 | -0.25635 | 60.3699 | -0.045777 | -0.054932 | 0.027466 | -0.041199 | -0.013733 | 0.28839 | -0.11444 | 0.34332 | -0.059509 | 0.29297 | 123.2574 | 0.041199 | 123.3032 | 123.5367 | 123.3719 | 123.3261 | 123.317 | -123.5001 | -123.3444 | 123.0469 | 123.2483 | 60.1044 | 60.1456
6.4844 | 123.3673 | -60.1181 | 63.1302 | -0.027161 | 0.0031253 | 0.065061 | 0.065399 | -0.00065586 | 0.00092498 | 0.0013971 | -0.041534 | -0.00095912 | 0.067063 | 0.071181 | 0.0006066 | -0.00080758 | -0.00075834 | -0.050354 | 63.176 | -60.3561 | 62.9059 | -60.054 | -60.4294 | -0.068665 | -0.054932 | 63.1851 | -60.1776 | 63.1348 | -60.1685 | -60.2921 | -59.8526 | -0.23804 | 0.045776 | -0.2243 | 0.064087 | 60.0494 | -0.31128 | 60.2875 | -0.073242 | -0.059509 | 0.054932 | 0.004578 | -0.050354 | 0.2655 | -0.17395 | 0.32501 | -0.11444 | 0.30212 | 123.262 | 0.009155 | 123.3124 | 123.5321 | 123.3627 | 123.2941 | 123.3032 | -123.4863 | -123.3078 | 123.024 | 123.2529 | 60.0677 | 60.0632
7.5469 | 123.3215 | -60.1135 | 63.1393 | 0.0033567 | -0.00029273 | 0.065275 | 0.063476 | 0.00019874 | 0.00028418 | -0.0013799 | 0.016449 | 0.0011771 | 0.069199 | 0.070113 | -0.0017432 | 0.00047422 | -0.0011855 | -0.022888 | 63.2126 | -60.3424 | 62.9333 | -60.054 | -60.3561 | 0 | 0 | 63.2217 | -60.1959 | 63.1622 | -60.1181 | -60.1913 | -59.9121 | -0.22888 | 0.073242 | -0.20599 | 0.059509 | 60.1135 | -0.24262 | 60.3424 | -0.013733 | -0.082398 | 0.082398 | 0.022888 | -0.004578 | 0.20142 | -0.07782 | 0.28381 | 0.004578 | 0.28839 | 123.2758 | 0.07782 | 123.3582 | 123.555 | 123.4177 | 123.3261 | 123.3353 | -123.4818 | -123.3353 | 123.0469 | 123.2758 | 60.0906 | 60.1135
8.4844 | 123.4131 | -60.0998 | 63.1439 | -0.019531 | 0.00077547 | 0.066556 | 0.063262 | 0.0010531 | -0.0027066 | 0.00075627 | -0.053741 | 0.0026725 | 0.06514 | 0.064773 | -0.0002478 | -0.0010212 | -0.0011855 | -0.013733 | 63.1897 | -60.3149 | 62.9608 | -60.0037 | -60.3561 | -0.009155 | 0.041199 | 63.1805 | -60.173 | 63.1897 | -60.1273 | -60.2371 | -59.8068 | -0.21515 | 0.045776 | -0.18311 | 0.09613 | 60.0906 | -0.25635 | 60.3058 | -0.041199 | -0.073243 | 0.036621 | 0.045776 | -0.027466 | 0.29297 | -0.13733 | 0.36621 | -0.064087 | 0.31128 | 123.2758 | 0.045777 | 123.3627 | 123.5046 | 123.3536 | 123.2895 | 123.2803 | -123.4589 | -123.317 | 123.0606 | 123.2895 | 60.0861 | 60.141
9.4844 | 123.3582 | -60.1181 | 63.1165 | -0.050049 | -0.00029273 | 0.063138 | 0.065185 | 0.0021213 | 0.0024204 | 0.0018243 | -0.026276 | 0.0011771 | 0.068344 | 0.0652 | -0.0008886 | -0.0018756 | 0.0013779 | -0.064087 | 63.1851 | -60.3928 | 62.9059 | -60.0677 | -60.4385 | -0.11444 | -0.13733 | 63.1668 | -60.2097 | 63.1165 | -60.2051 | -60.3058 | -59.8572 | -0.27466 | 0.068665 | -0.21057 | 0.050354 | 60.0037 | -0.32044 | 60.2783 | -0.045777 | -0.091553 | 0.050354 | 0 | -0.086975 | 0.26093 | -0.18768 | 0.35248 | -0.09613 | 0.32501 | 123.2986 | 0.004578 | 123.3261 | 123.5779 | 123.3765 | 123.3032 | 123.2849 | -123.5092 | -123.3261 | 123.024 | 123.2346 | 60.054 | 59.9808
10.5469 | 123.3856 | -60.1044 | 63.1485 | -0.027161 | -0.00050633 | 0.062284 | 0.061126 | 0.0021213 | -0.00078402 | -0.0026617 | 0.010345 | 0.0018179 | 0.068772 | 0.067123 | 0.0001794 | -0.0035846 | -0.0024673 | -0.018311 | 63.2446 | -60.3149 | 62.9288 | -60.0403 | -60.3607 | 0.036621 | 0.009155 | 63.2217 | -60.2005 | 63.121 | -60.1501 | -60.2234 | -59.8206 | -0.21057 | 0.09613 | -0.21973 | 0.064087 | 60.141 | -0.25635 | 60.3516 | -0.045777 | -0.09613 | 0.073242 | -0.027466 | -0.045776 | 0.28381 | -0.11902 | 0.37994 | -0.022889 | 0.27466 | 123.2437 | 0.050354 | 123.3215 | 123.5596 | 123.4222 | 123.349 | 123.3261 | -123.4634 | -123.349 | 123.0331 | 123.2254 | 60.0861 | 60.1135
11.4844 | 123.3719 | -60.141 | 63.0844 | -0.072937 | 0.00056187 | 0.06677 | 0.066253 | 0.0038303 | -0.00078402 | -0.0013799 | -0.038483 | 0.00074988 | 0.06749 | 0.064773 | -0.000675 | -0.0020892 | 0.00052346 | -0.11444 | 63.1714 | -60.379 | 62.8784 | -60.0998 | -60.4523 | -0.13733 | -0.16937 | 63.1577 | -60.2142 | 63.1256 | -60.1868 | -60.2966 | -59.8572 | -0.23804 | 0.086975 | -0.20599 | 0.041199 | 60.0037 | -0.31128 | 60.2417 | -0.073243 | -0.073242 | 0.073242 | 0.041198 | -0.045777 | 0.28381 | -0.15564 | 0.35706 | -0.082398 | 0.27924 | 123.2574 | 0.027465 | 123.3398 | 123.5504 | 123.3719 | 123.3124 | 123.2986 | -123.4634 | -123.2986 | 123.0194 | 123.2666 | 60.0266 | 59.9716
12.4844 | 123.381 | -60.1044 | 63.1348 | -0.057678 | 0.00098907 | 0.064634 | 0.063903 | -0.00065586 | 0.0011386 | 0.00054267 | -0.05069 | 0.0026725 | 0.067276 | 0.068831 | -0.001316 | -0.0023028 | -0.0026809 | -0.036621 | 63.2172 | -60.3653 | 62.9288 | -60.0449 | -60.3973 | -0.064087 | -0.064087 | 63.1851 | -60.1685 | 63.1256 | -60.1868 | -60.2463 | -59.848 | -0.26093 | 0.082397 | -0.20599 | 0.059509 | 60.0403 | -0.29297 | 60.3012 | -0.032044 | -0.064087 | 0.050354 | -0.009156 | -0.082398 | 0.25635 | -0.14191 | 0.32043 | -0.07782 | 0.32043 | 123.2941 | -0.018311 | 123.2941 | 123.5825 | 123.3536 | 123.3215 | 123.2895 | -123.5001 | -123.3032 | 123.0331 | 123.23 | 60.0677 | 60.0403
13.4844 | 123.4039 | -60.1364 | 63.1165 | -0.050049 | 0.00077547 | 0.063138 | 0.065612 | -0.0010831 | 0.00071138 | 0.0011835 | -0.035431 | 0.0011771 | 0.067063 | 0.066695 | -0.0011022 | 0.00090142 | 0.0028733 | -0.11444 | 63.1668 | -60.3882 | 62.8693 | -60.1181 | -60.4706 | -0.10986 | -0.16479 | 63.1714 | -60.2051 | 63.1119 | -60.2051 | -60.3012 | -59.8572 | -0.25177 | 0.050354 | -0.24719 | 0.018311 | 60.0266 | -0.33417 | 60.2783 | -0.082397 | -0.068664 | 0.054932 | -0.004578 | -0.068664 | 0.27924 | -0.16479 | 0.3479 | -0.09613 | 0.27008 | 123.2574 | 0 | 123.317 | 123.555 | 123.3765 | 123.3032 | 123.3078 | -123.5046 | -123.3215 | 123.0057 | 123.2483 | 60.022 | 59.9716
14.4844 | 123.3856 | -60.1181 | 63.1256 | -0.027161 | -0.00093353 | 0.063566 | 0.062622 | -0.0051419 | -0.00057042 | -9.8328e-05 | -0.035431 | 0.0011771 | 0.066422 | 0.063064 | -0.0002478 | -0.00038018 | 0.0011643 | -0.027466 | 63.1897 | -60.3653 | 62.9379 | -60.022 | -60.379 | -0.041199 | -0.022888 | 63.1851 | -60.1913 | 63.1439 | -60.1685 | -60.2692 | -59.8434 | -0.24719 | 0.064087 | -0.18768 | 0.09613 | 60.0769 | -0.26093 | 60.3241 | -0.013733 | -0.073242 | 0.05951 | 0.018311 | -0.050354 | 0.27466 | -0.15106 | 0.3479 | -0.07782 | 0.34332 | 123.3032 | 0.022888 | 123.3353 | 123.555 | 123.3765 | 123.3078 | 123.3032 | -123.4909 | -123.317 | 123.056 | 123.262 | 60.0906 | 60.0952
15.4844 | 123.349 | -60.1318 | 63.1027 | -0.03479 | -0.00071993 | 0.066556 | 0.064758 | 0.0021213 | 0.0015658 | 0.0033197 | -0.05069 | -0.0011727 | 0.069199 | 0.064345 | -0.0038794 | 0.001115 | -0.0022537 | -0.10986 | 63.1897 | -60.3928 | 62.8418 | -60.1501 | -60.4889 | -0.11902 | -0.15564 | 63.1714 | -60.2371 | 63.1027 | -60.2051 | -60.3241 | -59.8434 | -0.26093 | 0.086975 | -0.26093 | -0.01831 | 60.0128 | -0.35706 | 60.2737 | -0.096131 | -0.10529 | 0.068665 | 0 | -0.073242 | 0.28839 | -0.19226 | 0.39368 | -0.086975 | 0.24262 | 123.2346 | 0.032044 | 123.3398 | 123.5825 | 123.4085 | 123.3215 | 123.3032 | -123.4955 | -123.3398 | 122.9736 | 123.2346 | 60.022 | 59.9762
16.5469 | 123.4177 | -60.0861 | 63.1393 | -0.042419 | 0.00098907 | 0.065061 | 0.063903 | 0.00083954 | 0.0011386 | -9.8328e-05 | -0.041534 | -0.00053192 | 0.065995 | 0.06755 | 0.000393 | -0.0012348 | 0.00052346 | -0.018311 | 63.2263 | -60.3333 | 62.9425 | -60.0266 | -60.3607 | -0.018311 | 0.1236 | 63.1989 | -60.1685 | 63.176 | -60.0952 | -60.2142 | -59.7794 | -0.24719 | 0.086975 | -0.19684 | 0.05951 | 60.0677 | -0.27466 | 60.3149 | -0.027466 | -0.082397 | 0.05951 | 0.036621 | -0.009155 | 0.3067 | -0.12817 | 0.3891 | -0.045776 | 0.3067 | 123.2758 | 0.073242 | 123.3444 | 123.5596 | 123.3673 | 123.3124 | 123.2849 | -123.4726 | -123.3078 | 123.0286 | 123.262 | 60.0677 | 60.2097
17.4844 | 123.3719 | -60.1318 | 63.1165 | -0.095825 | 0.0022709 | 0.065061 | 0.063262 | 0.0016939 | -0.00014322 | -0.00052553 | -0.029327 | -0.00010472 | 0.065995 | 0.069045 | -0.0017432 | -0.00038018 | 0.0039413 | -0.1236 | 63.1668 | -60.3653 | 62.8738 | -60.1044 | -60.4523 | -0.12817 | -0.14648 | 63.1302 | -60.2325 | 63.0981 | -60.1822 | -60.2966 | -59.848 | -0.23346 | 0.050354 | -0.24262 | 0.027466 | 60.0037 | -0.32044 | 60.2371 | -0.086976 | -0.10071 | 0.013733 | -0.01831 | -0.050354 | 0.28381 | -0.16479 | 0.38452 | -0.064087 | 0.26093 | 123.2391 | 0.050354 | 123.3307 | 123.5321 | 123.3627 | 123.2986 | 123.262 | -123.4818 | -123.349 | 123.0057 | 123.23 | 60.0082 | 59.9854
18.4844 | 123.3444 | -60.1044 | 63.1302 | -0.027161 | 0.00077547 | 0.063993 | 0.063903 | -0.00044226 | 0.0032748 | -0.0022345 | -0.029327 | 0.0028861 | 0.066208 | 0.062636 | 0.0001794 | 0.0015424 | 0.0015915 | -0.045776 | 63.1943 | -60.347 | 62.9333 | -60.0266 | -60.3882 | -0.045776 | -0.041199 | 63.2126 | -60.1959 | 63.1302 | -60.1593 | -60.2875 | -59.8297 | -0.24261 | 0.064087 | -0.19684 | 0.07782 | 60.0586 | -0.28381 | 60.3012 | -0.041199 | -0.091553 | 0.082397 | 0 | -0.054932 | 0.27466 | -0.18311 | 0.36621 | -0.091553 | 0.32043 | 123.2803 | 0.036621 | 123.3261 | 123.5413 | 123.4085 | 123.2986 | 123.317 | -123.4772 | -123.3261 | 123.0377 | 123.2346 | 60.0586 | 60.0632
19.5625 | 123.3673 | -60.1364 | 63.0936 | -0.080566 | -0.00093353 | 0.065916 | 0.064117 | -0.0017239 | 0.00049778 | 0.0039607 | -0.038483 | 0.00032248 | 0.06514 | 0.065414 | -0.0011022 | 0.00090142 | 0.00095066 | -0.10986 | 63.2126 | -60.3699 | 62.883 | -60.1135 | -60.4523 | -0.11902 | -0.16937 | 63.1439 | -60.2097 | 63.1073 | -60.2051 | -60.3058 | -59.8618 | -0.23346 | 0.11902 | -0.21057 | 0.022889 | 60.0174 | -0.31586 | 60.2509 | -0.082398 | -0.073242 | 0.050354 | 0.013733 | -0.068664 | 0.27466 | -0.16937 | 0.3479 | -0.09613 | 0.25635 | 123.2529 | 0.004578 | 123.317 | 123.5825 | 123.3536 | 123.349 | 123.2803 | -123.4634 | -123.3032 | 123.0194 | 123.2437 | 60.0266 | 59.967
20.4844 | 123.3444 | -60.1318 | 63.1439 | 0.018616 | 0.0014163 | 0.066343 | 0.064544 | -0.0017239 | -0.0014248 | 0.0024653 | -0.041534 | 0.0011771 | 0.067704 | 0.06755 | -0.0011022 | 0.0015424 | 0.0022323 | -0.082397 | 63.1897 | -60.3836 | 62.9013 | -60.0586 | -60.4248 | -0.064087 | -0.086975 | 63.1851 | -60.1639 | 63.1165 | -60.2051 | -60.2921 | -59.8526 | -0.25177 | 0.045776 | -0.24262 | 0.073242 | 60.0677 | -0.29297 | 60.3195 | -0.041199 | -0.032043 | 0.041199 | -0.027466 | -0.073242 | 0.27924 | -0.16022 | 0.31128 | -0.12817 | 0.32501 | 123.2849 | -0.041199 | 123.2803 | 123.5733 | 123.349 | 123.3215 | 123.317 | -123.5275 | -123.3078 | 123.0331 | 123.2483 | 60.0494 | 60.0449
21.5469 | 123.3856 | -60.1135 | 63.1256 | -0.042419 | 0.0026981 | 0.066129 | 0.060485 | 0.00041234 | 0.00071138 | -0.00073913 | -0.038483 | 0.0011771 | 0.065354 | 0.061141 | -0.0017432 | 4.7018e-05 | 0.00073706 | -0.045776 | 63.1943 | -60.347 | 62.9425 | -60.0082 | -60.3561 | -0.027466 | 0.013733 | 63.1714 | -60.1868 | 63.1577 | -60.1456 | -60.2509 | -59.8206 | -0.23346 | 0.068665 | -0.18311 | 0.10529 | 60.0861 | -0.24262 | 60.3195 | -0.009155 | -0.073243 | 0.045777 | 0.032044 | -0.032044 | 0.29297 | -0.13733 | 0.36621 | -0.064086 | 0.33874 | 123.2895 | 0.041199 | 123.3444 | 123.5413 | 123.3582 | 123.3078 | 123.2849 | -123.4726 | -123.3124 | 123.056 | 123.2712 | 60.0677 | 60.1273
22.4844 | 123.4222 | -60.1227 | 63.1485 | 0.018616 | 0.0014163 | 0.063993 | 0.060913 | -0.0017239 | 0.00092498 | -0.0013799 | 0.004242 | 0.0033133 | 0.067917 | 0.068404 | -0.0015296 | -0.00059378 | -0.0022537 | -0.013733 | 63.2217 | -60.3287 | 62.9471 | -59.9625 | -60.3287 | 0.022888 | 0.041199 | 63.1851 | -60.1593 | 63.1668 | -60.1135 | -60.2097 | -59.7839 | -0.20599 | 0.073242 | -0.20142 | 0.16022 | 60.1456 | -0.20599 | 60.3516 | 0 | -0.036621 | 0.036621 | 0.01831 | 0.009156 | 0.33875 | -0.086975 | 0.37537 | -0.050354 | 0.36621 | 123.2758 | 0.045777 | 123.3261 | 123.5504 | 123.3444 | 123.3444 | 123.3078 | -123.4772 | -123.3078 | 123.0698 | 123.2895 | 60.1089 | 60.1639
23.4844 | 123.381 | -60.1227 | 63.1302 | -0.10345 | 0.00013467 | 0.065916 | 0.066253 | 0.0023349 | 0.00071138 | 0.00011527 | -0.035431 | 0.00096348 | 0.06749 | 0.063491 | 0.0012476 | 0.00047422 | -0.00097194 | -0.032043 | 63.176 | -60.3561 | 62.9333 | -60.0266 | -60.3745 | -0.022888 | -0.018311 | 63.1989 | -60.1913 | 63.1348 | -60.1593 | -60.2692 | -59.8343 | -0.23346 | 0.045776 | -0.19684 | 0.096131 | 60.0998 | -0.25177 | 60.3333 | -0.018311 | -0.068664 | 0.068665 | 0.004578 | -0.036621 | 0.28839 | -0.14648 | 0.35705 | -0.07782 | 0.32959 | 123.2895 | 0.032043 | 123.3261 | 123.5321 | 123.3902 | 123.2986 | 123.3215 | -123.4863 | -123.3215 | 123.056 | 123.2574 | 60.0906 | 60.1044
24.4844 | 123.3261 | -60.1273 | 63.1302 | -0.050049 | 0.0022709 | 0.066129 | 0.064544 | 0.0014803 | 7.0582e-05 | 0.00075627 | -0.023224 | -0.0016001 | 0.067276 | 0.06285 | -0.002384 | 4.7018e-05 | 0.00030966 | -0.09613 | 63.2034 | -60.3699 | 62.9013 | -60.0357 | -60.4019 | -0.086975 | -0.07782 | 63.1897 | -60.2005 | 63.1119 | -60.2051 | -60.3012 | -59.8526 | -0.24262 | 0.073242 | -0.22888 | 0.091552 | 60.0403 | -0.27466 | 60.2829 | -0.032044 | -0.073242 | 0.059509 | -0.018311 | -0.07782 | 0.27466 | -0.17395 | 0.3479 | -0.10071 | 0.33417 | 123.2712 | -0.004578 | 123.3124 | 123.5733 | 123.3902 | 123.3307 | 123.317 | -123.5001 | -123.3307 | 123.0286 | 123.2391 | 60.0311 | 60.0494
25.4844 | 123.3627 | -60.1273 | 63.1165 | -0.027161 | -0.00029273 | 0.064634 | 0.063262 | -0.0012967 | -0.00014322 | 0.00011527 | -0.047638 | 0.00010888 | 0.065995 | 0.072036 | 0.0008204 | -0.00016658 | -0.00075834 | -0.11444 | 63.1943 | -60.3882 | 62.8693 | -60.1273 | -60.4568 | -0.13275 | -0.17853 | 63.1485 | -60.2325 | 63.1073 | -60.2051 | -60.3241 | -59.8618 | -0.26093 | 0.07782 | -0.24719 | 0 | 59.9945 | -0.32959 | 60.2554 | -0.068664 | -0.10529 | 0.032044 | -0.009155 | -0.07782 | 0.2655 | -0.19684 | 0.37079 | -0.091553 | 0.26093 | 123.2574 | 0.027466 | 123.3398 | 123.5825 | 123.381 | 123.3215 | 123.2758 | -123.5046 | -123.349 | 122.9965 | 123.2346 | 60.0128 | 59.9487
26.5469 | 123.3765 | -60.1135 | 63.1531 | -0.027161 | 0.00034827 | 0.062284 | 0.064544 | -0.0036465 | -0.0037746 | -0.00073913 | 0.040863 | 0.0011771 | 0.069626 | 0.062423 | -0.0011022 | -0.00016658 | 0.00095066 | -0.041199 | 63.2355 | -60.3561 | 62.9013 | -60.0357 | -60.3745 | 0.027466 | 0.018311 | 63.2217 | -60.1868 | 63.1165 | -60.1318 | -60.2371 | -59.8251 | -0.24262 | 0.082398 | -0.25177 | 0.077819 | 60.141 | -0.26093 | 60.3836 | -0.018311 | -0.073243 | 0.068665 | -0.036621 | -0.018311 | 0.28839 | -0.1236 | 0.36163 | -0.050354 | 0.32043 | 123.2574 | 0.054932 | 123.3032 | 123.5916 | 123.4085 | 123.349 | 123.3353 | -123.5092 | -123.3398 | 123.0148 | 123.23 | 60.0723 | 60.1318
27.4844 | 123.3627 | -60.1501 | 63.1348 | -0.057678 | -0.00093353 | 0.063138 | 0.062194 | -0.0010831 | -0.00014322 | -0.0028753 | -0.029327 | 0.0018179 | 0.070481 | 0.066054 | 0.0018884 | 0.00026062 | -0.00033114 | -0.1236 | 63.1851 | -60.3745 | 62.8555 | -60.1135 | -60.4431 | -0.14648 | -0.16479 | 63.1668 | -60.2417 | 63.0936 | -60.1913 | -60.3149 | -59.8526 | -0.22431 | 0.050354 | -0.27924 | 0.036621 | 60.0037 | -0.29297 | 60.228 | -0.068664 | -0.091553 | 0.032043 | -0.041199 | -0.041199 | 0.29755 | -0.16479 | 0.3891 | -0.073242 | 0.26093 | 123.23 | 0.050354 | 123.3353 | 123.5596 | 123.4085 | 123.3353 | 123.317 | -123.5092 | -123.3765 | 123.0057 | 123.2437 | 60.0266 | 59.9854
28.5469 | 123.4726 | -60.0906 | 63.121 | -0.042419 | 0.0022709 | 0.061857 | 0.062835 | -0.00065586 | 0.0017794 | -0.0020209 | 0.080536 | -0.00010472 | 0.067276 | 0.062209 | -0.000675 | -0.0027302 | 0.0026597 | 0.018311 | 63.1897 | -60.2875 | 63.0341 | -59.8984 | -60.2463 | 0.10071 | 0.13275 | 63.1622 | -60.141 | 63.2263 | -60.0311 | -60.1135 | -59.7336 | -0.19684 | 0.068664 | -0.086975 | 0.19226 | 60.1913 | -0.15564 | 60.3882 | 0.041199 | -0.050354 | 0.041198 | 0.10529 | 0.059509 | 0.35706 | -0.022888 | 0.40741 | 0.027466 | 0.3891 | 123.3215 | 0.10986 | 123.3673 | 123.4772 | 123.3032 | 123.2803 | 123.2529 | -123.4085 | -123.262 | 123.1247 | 123.317 | 60.1089 | 60.2234
29.4844 | 123.3902 | -60.1227 | 63.1348 | -0.0042723 | -7.913e-05 | 0.063993 | 0.065826 | -0.0015103 | -0.0012112 | -0.00073913 | -0.041534 | 0.0020315 | 0.066849 | 0.06285 | -0.0004614 | 0.00026062 | 0.0011643 | -0.018311 | 63.2034 | -60.3561 | 62.9425 | -60.0037 | -60.3607 | -0.022888 | 0.018311 | 63.1805 | -60.173 | 63.1531 | -60.141 | -60.2325 | -59.8022 | -0.23346 | 0.068664 | -0.19226 | 0.11902 | 60.0998 | -0.23804 | 60.3333 | -0.004578 | -0.050354 | 0.045776 | 0.01831 | -0.01831 | 0.32044 | -0.10986 | 0.37079 | -0.059509 | 0.35248 | 123.2986 | 0.032044 | 123.3261 | 123.5596 | 123.3536 | 123.3261 | 123.3032 | -123.4909 | -123.3078 | 123.0652 | 123.2758 | 60.1044 | 60.141
30.5469 | 123.4909 | -60.0632 | 63.1302 | -0.10345 | 0.0016299 | 0.063138 | 0.061553 | 0.0025485 | -0.0022794 | 0.00011527 | 0.046967 | 0.00074988 | 0.067276 | 0.06285 | 0.0001794 | -0.0040118 | 0.0011643 | -0.050354 | 63.1805 | -60.3333 | 62.9791 | -59.9762 | -60.3149 | 0.045776 | 0.009155 | 63.1668 | -60.1685 | 63.2126 | -60.054 | -60.1318 | -59.7336 | -0.27008 | 0.050354 | -0.15106 | 0.086975 | 60.1089 | -0.25177 | 60.379 | 0.018311 | -0.10529 | 0.036621 | 0.082397 | 0.009155 | 0.32959 | -0.068665 | 0.43487 | 0.036621 | 0.35706 | 123.3124 | 0.11444 | 123.381 | 123.5138 | 123.3353 | 123.2437 | 123.23 | -123.4634 | -123.2986 | 123.0423 | 123.2758 | 60.0128 | 60.0723
31.4844 | 123.3215 | -60.1181 | 63.1256 | -0.065308 | 0.0012027 | 0.063779 | 0.064971 | 0.0046847 | -0.0029202 | 0.0022517 | -0.05069 | 0.00053628 | 0.066422 | 0.064773 | 0.001034 | -0.00080758 | 0.00073706 | -0.10071 | 63.1714 | -60.3882 | 62.8922 | -60.1089 | -60.4614 | -0.1236 | -0.13733 | 63.1805 | -60.2051 | 63.089 | -60.2325 | -60.3287 | -59.8526 | -0.27008 | 0.045777 | -0.23346 | 0.009155 | 59.9945 | -0.34332 | 60.2646 | -0.073242 | -0.086975 | 0.054932 | -0.036621 | -0.11444 | 0.2655 | -0.21057 | 0.35248 | -0.1236 | 0.27924 | 123.2803 | -0.027466 | 123.2941 | 123.5596 | 123.3856 | 123.2895 | 123.2986 | -123.5138 | -123.3307 | 123.0103 | 123.2071 | 60.0174 | 59.9808
32.5469 | 123.4818 | -60.0494 | 63.0844 | -0.027161 | 0.0018435 | 0.062498 | 0.062835 | -0.0023649 | 0.00049778 | -0.00073913 | 0.046967 | -0.0011727 | 0.067917 | 0.062423 | -0.0004614 | -0.0029438 | 0.0011643 | -0.022888 | 63.1989 | -60.3149 | 63.002 | -59.967 | -60.2829 | 0.059509 | 0.07782 | 63.1577 | -60.1547 | 63.2263 | -60.0357 | -60.1135 | -59.729 | -0.2655 | 0.11444 | -0.082398 | 0.082397 | 60.1089 | -0.23346 | 60.3744 | 0.032043 | -0.10529 | 0.073242 | 0.14191 | 0.013732 | 0.32043 | -0.064087 | 0.42572 | 0.041199 | 0.3479 | 123.317 | 0.11902 | 123.381 | 123.5138 | 123.3124 | 123.2483 | 123.2071 | -123.3994 | -123.2391 | 123.0515 | 123.2758 | 60.0266 | 60.1273
33.4844 | 123.3444 | -60.1501 | 63.1073 | -0.011902 | -0.00093353 | 0.065916 | 0.065399 | 0.0031893 | -0.0022794 | -0.00073913 | -0.065949 | 0.0018179 | 0.067704 | 0.067977 | -0.000675 | 0.0013288 | 0.0024461 | -0.11444 | 63.1897 | -60.4019 | 62.8555 | -60.1501 | -60.4843 | -0.13275 | -0.15564 | 63.1668 | -60.2188 | 63.1165 | -60.2188 | -60.3149 | -59.8663 | -0.25177 | 0.082397 | -0.25177 | 0 | 60.0174 | -0.33417 | 60.2692 | -0.082397 | -0.068665 | 0.059509 | 0.009155 | -0.068665 | 0.28381 | -0.16479 | 0.35248 | -0.09613 | 0.25177 | 123.2574 | 0 | 123.3353 | 123.5916 | 123.3856 | 123.3398 | 123.317 | -123.5092 | -123.3261 | 123.0057 | 123.2666 | 60.0357 | 59.9945
34.4844 | 123.4085 | -60.1089 | 63.1393 | -0.042419 | 0.00098907 | 0.063993 | 0.065185 | 0.0021213 | 0.0011386 | 0.0011835 | -0.035431 | 0.00053628 | 0.067704 | 0.068831 | -0.0021704 | -0.0023028 | -0.0013991 | 0.013733 | 63.2172 | -60.3241 | 62.9608 | -59.9899 | -60.347 | 0.013733 | 0.059509 | 63.1897 | -60.1685 | 63.1989 | -60.1181 | -60.2142 | -59.7748 | -0.21515 | 0.07782 | -0.17853 | 0.11902 | 60.1227 | -0.23804 | 60.3378 | -0.022888 | -0.059509 | 0.050354 | 0.05951 | -0.009155 | 0.33417 | -0.10529 | 0.39368 | -0.045776 | 0.33417 | 123.2849 | 0.050354 | 123.3673 | 123.5413 | 123.3582 | 123.3261 | 123.2986 | -123.4634 | -123.3078 | 123.0698 | 123.3078 | 60.1227 | 60.1685
35.5469 | 123.4772 | -60.0311 | 63.1119 | -0.065308 | 0.00077547 | 0.062925 | 0.062408 | -0.00022866 | 0.0011386 | -0.00052553 | 0.059174 | -0.00053192 | 0.068772 | 0.066695 | -0.000675 | -0.0027302 | -0.0022537 | 0.027466 | 63.1805 | -60.2875 | 63.0249 | -59.8801 | -60.2417 | 0.11902 | 0.15564 | 63.1302 | -60.141 | 63.2401 | -60.0082 | -60.0952 | -59.7107 | -0.25635 | 0.068665 | -0.086975 | 0.15106 | 60.1501 | -0.21057 | 60.4065 | 0.045777 | -0.10986 | 0.018311 | 0.12817 | 0.022888 | 0.32044 | -0.064087 | 0.4303 | 0.045776 | 0.40741 | 123.3124 | 0.13275 | 123.381 | 123.468 | 123.2712 | 123.2117 | 123.1613 | -123.3994 | -123.2529 | 123.056 | 123.2712 | 60.0586 | 60.1868
36.4844 | 123.3902 | -60.0861 | 63.1485 | -0.03479 | 0.00013467 | 0.063352 | 0.065826 | 0.0025485 | 0.00071138 | 0.0024653 | 0.0011902 | 0.0016043 | 0.066422 | 0.066054 | -0.000675 | -0.0018756 | -0.0018265 | -0.018311 | 63.2446 | -60.347 | 62.9242 | -60.0449 | -60.3699 | 0.009155 | 0.013733 | 63.2126 | -60.1822 | 63.1256 | -60.1181 | -60.228 | -59.8251 | -0.26092 | 0.09613 | -0.22431 | 0.041199 | 60.0952 | -0.28381 | 60.3561 | -0.022888 | -0.09613 | 0.064086 | -0.022889 | -0.032043 | 0.26093 | -0.14191 | 0.35706 | -0.045776 | 0.30212 | 123.2712 | 0.064087 | 123.3078 | 123.5916 | 123.3948 | 123.3307 | 123.2986 | -123.4955 | -123.3307 | 123.0103 | 123.2117 | 60.0677 | 60.0998
37.5469 | 123.3948 | -60.1044 | 63.1622 | -0.03479 | 0.00077547 | 0.065061 | 0.061126 | -0.0023649 | -0.0020658 | -0.00073913 | -0.014069 | -0.0011727 | 0.06749 | 0.061782 | -0.0017432 | -0.0023028 | -0.0018265 | 0 | 63.2126 | -60.3424 | 62.9379 | -59.9579 | -60.3149 | 0.009155 | 0.068665 | 63.1943 | -60.1776 | 63.1714 | -60.1089 | -60.2234 | -59.7794 | -0.23804 | 0.050354 | -0.2243 | 0.14648 | 60.1135 | -0.21057 | 60.3516 | 0.027466 | -0.073242 | 0.032044 | 0.009156 | -0.004578 | 0.32501 | -0.11902 | 0.39825 | -0.045777 | 0.38452 | 123.2803 | 0.068664 | 123.349 | 123.555 | 123.3719 | 123.317 | 123.2986 | -123.5046 | -123.3398 | 123.0423 | 123.2758 | 60.1044 | 60.173
38.4844 | 123.381 | -60.0952 | 63.1348 | -0.027161 | 0.00056187 | 0.063566 | 0.065612 | 0.0016939 | -0.00099762 | -0.00052553 | -0.044586 | 0.0018179 | 0.066635 | 0.066482 | -0.000675 | -0.0010212 | -0.00033114 | -0.013733 | 63.2034 | -60.347 | 62.9791 | -60.0037 | -60.3378 | 0.013733 | 0.054932 | 63.1897 | -60.2051 | 63.1851 | -60.1135 | -60.228 | -59.7931 | -0.25177 | 0.068664 | -0.15564 | 0.091553 | 60.1089 | -0.24261 | 60.3607 | 0.009155 | -0.10986 | 0.054931 | 0.050354 | -0.01831 | 0.30212 | -0.13275 | 0.41199 | -0.022888 | 0.34332 | 123.3261 | 0.091553 | 123.3902 | 123.5504 | 123.3948 | 123.2986 | 123.2849 | -123.4818 | -123.3398 | 123.0743 | 123.2803 | 60.0815 | 60.1501
39.4844 | 123.4543 | -60.0861 | 63.0798 | -0.011902 | 0.00098907 | 0.065488 | 0.064117 | -1.486e-05 | 0.00028418 | 0.00032907 | 0.0072936 | -0.0011727 | 0.067276 | 0.0699 | -0.0008886 | 4.7018e-05 | -0.00011754 | -0.11444 | 63.1622 | -60.4019 | 62.9242 | -60.0357 | -60.4111 | -0.07782 | -0.20142 | 63.1531 | -60.1868 | 63.1851 | -60.1089 | -60.2005 | -59.7702 | -0.31586 | 0.082397 | -0.15564 | 0.050354 | 60.0082 | -0.32501 | 60.3241 | -0.009155 | -0.10071 | 0.073242 | 0.10529 | -0.022888 | 0.31586 | -0.11444 | 0.41656 | -0.013732 | 0.36621 | 123.3261 | 0.07782 | 123.3719 | 123.5641 | 123.3398 | 123.2483 | 123.2391 | -123.4818 | -123.2666 | 123.0103 | 123.2712 | 59.9716 | 59.8846
40.5469 | 123.4314 | -60.0632 | 63.1348 | -0.042419 | 0.0014163 | 0.065916 | 0.064544 | -0.0038603 | 7.0582e-05 | -0.00095273 | 0.050018 | -0.0011727 | 0.067704 | 0.063064 | -0.0015296 | 0.00090142 | -0.0016129 | 0.027466 | 63.1805 | -60.3058 | 63.0112 | -59.9213 | -60.2783 | 0.11902 | 0.11444 | 63.1851 | -60.1547 | 63.2172 | -60.0494 | -60.141 | -59.761 | -0.24262 | 0.045776 | -0.1236 | 0.14191 | 60.1822 | -0.21515 | 60.4248 | 0.027466 | -0.091553 | 0.050354 | 0.082397 | 0.013733 | 0.30212 | -0.07782 | 0.39368 | 0.013733 | 0.38452 | 123.317 | 0.10529 | 123.3719 | 123.4863 | 123.3398 | 123.2437 | 123.2483 | -123.4406 | -123.2895 | 123.0743 | 123.2803 | 60.0906 | 60.1776
41.5 | 123.4497 | -60.0723 | 63.1165 | 0.010986 | 0.0035525 | 0.068052 | 0.060913 | -0.0010831 | 0.00028418 | -0.0020209 | 0.043915 | -0.0018137 | 0.067917 | 0.063491 | 0.0001794 | -0.00038018 | -0.0013991 | -0.064087 | 63.176 | -60.3104 | 62.9608 | -59.9991 | -60.3195 | 0.004578 | -0.013733 | 63.1348 | -60.173 | 63.1989 | -60.0769 | -60.1318 | -59.7519 | -0.23804 | 0.059509 | -0.15564 | 0.073243 | 60.0769 | -0.24719 | 60.3149 | -0.009155 | -0.10071 | 0.018311 | 0.082398 | -0.004577 | 0.32044 | -0.059509 | 0.42114 | 0.041199 | 0.31128 | 123.2712 | 0.096131 | 123.3719 | 123.4863 | 123.3078 | 123.2483 | 123.2071 | -123.4268 | -123.2895 | 123.0331 | 123.2712 | 60.0082 | 60.0586
42.5469 | 123.4818 | -60.0677 | 63.1256 | -0.019531 | -0.0022153 | 0.063993 | 0.063049 | -0.00086946 | -0.00014322 | 0.00011527 | 0.05307 | -0.00010472 | 0.066208 | 0.062209 | -0.0019568 | -0.0014484 | -0.0043899 | 0.032043 | 63.176 | -60.3012 | 63.0615 | -59.8801 | -60.2417 | 0.10071 | 0.15564 | 63.1714 | -60.1273 | 63.2584 | -59.9991 | -60.0952 | -59.7015 | -0.23346 | 0.050354 | -0.064087 | 0.18768 | 60.1685 | -0.17395 | 60.4019 | 0.059509 | -0.059509 | 0.045777 | 0.13275 | 0.068665 | 0.36621 | -0.027466 | 0.42572 | 0.032043 | 0.42114 | 123.3627 | 0.12817 | 123.3856 | 123.4772 | 123.2986 | 123.2437 | 123.2391 | -123.4268 | -123.2529 | 123.1293 | 123.3261 | 60.0998 | 60.2234
43.4844 | 123.349 | -60.1181 | 63.1256 | -0.11871 | 0.0012027 | 0.065061 | 0.066467 | 0.0019077 | 0.0017794 | 0.0016107 | -0.087311 | 0.00074988 | 0.065781 | 0.066054 | -0.0025976 | 0.0015424 | 0.0030869 | -0.054932 | 63.1897 | -60.3607 | 62.9242 | -60.0815 | -60.4019 | -0.07782 | -0.091553 | 63.1943 | -60.1959 | 63.1165 | -60.173 | -60.3241 | -59.8663 | -0.24262 | 0.064087 | -0.20142 | 0.036621 | 60.0403 | -0.28381 | 60.2829 | -0.041199 | -0.07782 | 0.068665 | -0.009155 | -0.054932 | 0.25177 | -0.20599 | 0.32959 | -0.12817 | 0.27924 | 123.2849 | 0.022888 | 123.3124 | 123.5504 | 123.3902 | 123.3078 | 123.3124 | -123.4863 | -123.3215 | 123.0423 | 123.2346 | 60.0632 | 60.0266
44.5469 | 123.3582 | -60.0769 | 63.1805 | -0.011902 | 0.00098907 | 0.063352 | 0.064758 | 0.0029757 | 0.0013522 | 0.00011527 | -0.0018616 | -0.00074552 | 0.06749 | 0.066482 | -0.0017432 | 0.00090142 | -0.0024673 | -0.032043 | 63.208 | -60.3378 | 62.9379 | -60.0311 | -60.3607 | 0.013733 | 0.036621 | 63.2172 | -60.1776 | 63.1393 | -60.1273 | -60.228 | -59.8297 | -0.26093 | 0.027466 | -0.24262 | 0.045776 | 60.0906 | -0.28381 | 60.3516 | -0.022888 | -0.10071 | 0.036621 | -0.041199 | -0.050354 | 0.24719 | -0.15106 | 0.3479 | -0.050354 | 0.3067 | 123.2758 | 0.050354 | 123.317 | 123.5458 | 123.3948 | 123.2849 | 123.2941 | -123.5184 | -123.3582 | 123.0148 | 123.2162 | 60.0449 | 60.1135
45.4844 | 123.3536 | -60.1044 | 63.1165 | -0.12634 | 0.0020573 | 0.065916 | 0.064758 | 0.0034029 | 7.0582e-05 | 0.0016107 | -0.059845 | 0.00074988 | 0.069199 | 0.064345 | -0.0011022 | -0.00080758 | 0.0011643 | -0.050354 | 63.1989 | -60.3882 | 62.915 | -60.0632 | -60.4248 | -0.07782 | -0.068665 | 63.1714 | -60.1913 | 63.1348 | -60.1868 | -60.2966 | -59.8526 | -0.28381 | 0.082398 | -0.20142 | 0.041199 | 60.0266 | -0.32043 | 60.3104 | -0.036621 | -0.086975 | 0.054932 | 0.018311 | -0.082398 | 0.25177 | -0.19226 | 0.33874 | -0.10529 | 0.32501 | 123.3032 | 0.004577 | 123.3261 | 123.587 | 123.3627 | 123.3032 | 123.2758 | -123.5046 | -123.3078 | 123.0194 | 123.2391 | 60.054 | 60.0357
46.5625 | 123.3536 | -60.1364 | 63.121 | -0.050049 | 0.0016299 | 0.064207 | 0.065185 | 0.0027621 | 0.0011386 | -0.0015935 | -0.062897 | 0.00074988 | 0.065567 | 0.066482 | -3.4196e-05 | -0.00038018 | -0.00033114 | -0.07782 | 63.176 | -60.3973 | 62.9013 | -60.054 | -60.4248 | -0.064087 | -0.091553 | 63.1897 | -60.2005 | 63.1165 | -60.1776 | -60.2875 | -59.8709 | -0.26093 | 0.054931 | -0.21973 | 0.082398 | 60.0723 | -0.28839 | 60.3333 | -0.027466 | -0.064086 | 0.068664 | -0.004578 | -0.041198 | 0.2655 | -0.15106 | 0.32959 | -0.086976 | 0.34332 | 123.2986 | 0.022888 | 123.317 | 123.5733 | 123.3902 | 123.3124 | 123.3261 | -123.5184 | -123.3215 | 123.0377 | 123.2529 | 60.0586 | 60.0449
47.4844 | 123.349 | -60.1318 | 63.121 | -0.11108 | 0.00098907 | 0.065275 | 0.062835 | 0.0019077 | -0.0016384 | 0.00054267 | -0.056793 | 0.0011771 | 0.067917 | 0.070113 | -0.001316 | -0.0023028 | -0.00097194 | -0.045776 | 63.1668 | -60.3561 | 62.915 | -60.0403 | -60.4065 | -0.073242 | -0.064087 | 63.1989 | -60.2097 | 63.1165 | -60.1639 | -60.2737 | -59.8572 | -0.2243 | 0.045776 | -0.20599 | 0.091553 | 60.0586 | -0.27466 | 60.2829 | -0.050354 | -0.07782 | 0.07782 | -0.004578 | -0.032043 | 0.27466 | -0.14191 | 0.35248 | -0.064087 | 0.31586 | 123.2712 | 0.045777 | 123.3261 | 123.5229 | 123.4085 | 123.2986 | 123.3307 | -123.4772 | -123.3307 | 123.0469 | 123.2483 | 60.0861 | 60.0677
48.4844 | 123.3719 | -60.1044 | 63.1393 | -0.065308 | -7.913e-05 | 0.065275 | 0.062408 | 0.0040439 | -0.00057042 | -0.00052553 | -0.032379 | 0.0013907 | 0.067063 | 0.067336 | 0.0014612 | -0.00016658 | 0.0030869 | 0.082397 | 63.2355 | -60.3333 | 62.9929 | -59.9945 | -60.347 | 0.013733 | 0.064087 | 63.2034 | -60.1913 | 63.1714 | -60.0906 | -60.2097 | -59.7885 | -0.22888 | 0.096131 | -0.14648 | 0.10986 | 60.1181 | -0.24261 | 60.347 | -0.013733 | -0.086975 | 0.064087 | 0.032044 | 0.013733 | 0.31586 | -0.10529 | 0.40283 | -0.018311 | 0.33875 | 123.3261 | 0.10071 | 123.3627 | 123.5687 | 123.3948 | 123.3398 | 123.3078 | -123.4726 | -123.3307 | 123.0972 | 123.2758 | 60.1868 | 60.1685
49.5469 | 123.3582 | -60.1044 | 63.1622 | -0.0042723 | 0.00098907 | 0.06442 | 0.062835 | -0.0015103 | -0.00099762 | 0.00011527 | 0.004242 | 0.0026725 | 0.068985 | 0.068618 | -0.0011022 | -0.0025164 | -0.00075834 | -0.036621 | 63.2492 | -60.3378 | 62.9288 | -60.0449 | -60.3699 | 0.022888 | 0.022888 | 63.1989 | -60.1868 | 63.1302 | -60.1227 | -60.2234 | -59.8389 | -0.23346 | 0.086976 | -0.23346 | 0.059509 | 60.1273 | -0.2655 | 60.3607 | -0.032043 | -0.082398 | 0.036622 | -0.032043 | -0.018311 | 0.2655 | -0.11902 | 0.3479 | -0.036621 | 0.29297 | 123.2666 | 0.064087 | 123.317 | 123.587 | 123.3856 | 123.3536 | 123.3032 | -123.5001 | -123.349 | 123.0331 | 123.2346 | 60.0677 | 60.1273
50.4844 | 123.3536 | -60.0952 | 63.1714 | -0.050049 | 0.0012027 | 0.061643 | 0.062194 | -0.0038603 | -0.00014322 | -0.00073913 | -0.020172 | 0.0022453 | 0.068344 | 0.068191 | -0.0011022 | -0.00059378 | -0.0018265 | -0.022888 | 63.2172 | -60.3287 | 62.9196 | -60.0357 | -60.3516 | 0.004578 | 0.013733 | 63.2355 | -60.1822 | 63.1302 | -60.1227 | -60.2417 | -59.816 | -0.23346 | 0.045776 | -0.25177 | 0.059509 | 60.0998 | -0.25635 | 60.3333 | -0.022888 | -0.086975 | 0.064087 | -0.041199 | -0.027466 | 0.27924 | -0.14648 | 0.36621 | -0.059509 | 0.29297 | 123.2483 | 0.059509 | 123.3124 | 123.5458 | 123.4177 | 123.3124 | 123.3307 | -123.5001 | -123.3536 | 123.0148 | 123.2254 | 60.0723 | 60.1089
51.5 | 123.468 | -60.1089 | 63.089 | -0.072937 | 0.0031253 | 0.063779 | 0.062835 | 0.00041234 | -0.001852 | -0.00095273 | -0.026276 | -0.00074552 | 0.067704 | 0.068831 | -0.0011022 | -0.0010212 | -0.0020401 | -0.11902 | 63.1439 | -60.379 | 62.9654 | -60.0082 | -60.3561 | -0.027466 | -0.082397 | 63.1073 | -60.1868 | 63.2126 | -60.0769 | -60.1639 | -59.7382 | -0.27008 | 0.054932 | -0.1236 | 0.10071 | 60.0815 | -0.24719 | 60.3516 | 0.022888 | -0.07782 | 0.018311 | 0.1236 | 0.032044 | 0.37079 | -0.054931 | 0.44861 | 0.022889 | 0.37079 | 123.3444 | 0.10986 | 123.3994 | 123.5229 | 123.2941 | 123.2529 | 123.2162 | -123.468 | -123.2758 | 123.0743 | 123.3215 | 59.9899 | 60.0266
52.4844 | 123.4039 | -60.1044 | 63.1439 | -0.042419 | 0.0026981 | 0.063566 | 0.065826 | -0.0012967 | 0.0013522 | 0.0024653 | -0.032379 | -0.0020273 | 0.068131 | 0.067977 | 0.0018884 | 0.0015424 | -0.0018265 | 0.009155 | 63.1943 | -60.3516 | 62.9562 | -60.0128 | -60.3378 | 0.022888 | 0.036621 | 63.176 | -60.1868 | 63.1805 | -60.0952 | -60.2097 | -59.7839 | -0.24719 | 0.050354 | -0.18768 | 0.091553 | 60.1273 | -0.23346 | 60.3745 | 0.013732 | -0.082398 | 0.032043 | 0.036621 | 0.009155 | 0.32043 | -0.10529 | 0.40283 | -0.022888 | 0.33875 | 123.3078 | 0.091553 | 123.3673 | 123.5458 | 123.3627 | 123.2986 | 123.2803 | -123.4955 | -123.3307 | 123.0606 | 123.2849 | 60.1135 | 60.141
53.4844 | 123.3261 | -60.141 | 63.1073 | -0.019531 | 0.00034827 | 0.066343 | 0.064971 | 0.00083954 | 7.0582e-05 | -0.00095273 | -0.072052 | 0.0018179 | 0.06749 | 0.063705 | 0.0006066 | 0.00026062 | -0.0028945 | -0.10986 | 63.2034 | -60.3882 | 62.851 | -60.1227 | -60.4797 | -0.10986 | -0.16479 | 63.1805 | -60.2005 | 63.1073 | -60.2005 | -60.3012 | -59.8572 | -0.24719 | 0.09613 | -0.25635 | 0.01831 | 60.0311 | -0.33875 | 60.2783 | -0.091552 | -0.059509 | 0.073242 | 0 | -0.059509 | 0.28381 | -0.16022 | 0.34332 | -0.10071 | 0.2655 | 123.2391 | 0 | 123.3078 | 123.5916 | 123.381 | 123.3444 | 123.3215 | -123.4955 | -123.3078 | 122.9919 | 123.2483 | 60.0311 | 59.9762
54.5469 | 123.4955 | -60.054 | 63.0936 | -0.050049 | -7.913e-05 | 0.062925 | 0.063262 | 0.00041234 | -0.00057042 | -0.0020209 | 0.077484 | 0.00010888 | 0.068558 | 0.06285 | -3.4196e-05 | -0.0023028 | -0.0011855 | -0.009155 | 63.1668 | -60.2966 | 63.0112 | -59.8846 | -60.26 | 0.10071 | 0.13733 | 63.1393 | -60.1547 | 63.2584 | -59.9854 | -60.0723 | -59.6786 | -0.24262 | 0.073242 | -0.082398 | 0.16937 | 60.1547 | -0.20599 | 60.3973 | 0.036621 | -0.10071 | 0.045776 | 0.16479 | 0.068664 | 0.37537 | -0.018311 | 0.47607 | 0.082397 | 0.41199 | 123.3078 | 0.16937 | 123.4131 | 123.4634 | 123.2941 | 123.2208 | 123.1934 | -123.3902 | -123.2483 | 123.0652 | 123.3124 | 60.0449 | 60.1913
55.4844 | 123.3994 | -60.1135 | 63.0936 | -0.065308 | 0.0018435 | 0.063779 | 0.064331 | -0.00086946 | 0.00049778 | 0.0035333 | -0.05069 | 0.00074988 | 0.065781 | 0.06285 | -0.001316 | -0.0027302 | -0.0016129 | -0.11444 | 63.1668 | -60.3882 | 62.883 | -60.1089 | -60.434 | -0.1236 | -0.14648 | 63.1577 | -60.2188 | 63.1119 | -60.1868 | -60.2875 | -59.848 | -0.27466 | 0.073242 | -0.21057 | 0.004577 | 59.9899 | -0.32043 | 60.2646 | -0.045776 | -0.10529 | 0.064087 | 0.01831 | -0.073243 | 0.2655 | -0.17395 | 0.37079 | -0.068665 | 0.27924 | 123.2712 | 0.032043 | 123.3307 | 123.555 | 123.3765 | 123.2803 | 123.2712 | -123.4818 | -123.3124 | 122.9965 | 123.2254 | 59.9991 | 59.967
56.5625 | 123.3856 | -60.1181 | 63.0844 | -0.057678 | -0.00071993 | 0.065275 | 0.064117 | -0.00044226 | -0.001852 | 0.0026789 | -0.05069 | 0.00032248 | 0.066849 | 0.068404 | -3.4196e-05 | 0.00047422 | 0.00052346 | -0.11444 | 63.1805 | -60.3699 | 62.883 | -60.0861 | -60.4523 | -0.12817 | -0.16022 | 63.1577 | -60.2142 | 63.1393 | -60.1639 | -60.2783 | -59.816 | -0.25177 | 0.09613 | -0.20142 | 0.032043 | 59.9899 | -0.33417 | 60.2417 | -0.082398 | -0.09613 | 0.073242 | 0.054931 | -0.045776 | 0.30212 | -0.16022 | 0.39825 | -0.064087 | 0.28381 | 123.2529 | 0.050354 | 123.3536 | 123.5504 | 123.3719 | 123.2986 | 123.2758 | -123.4543 | -123.2986 | 123.0011 | 123.2574 | 60.0037 | 59.9579
57.4844 | 123.3902 | -60.1089 | 63.1302 | -0.072937 | 0.0012027 | 0.065275 | 0.064544 | 0.0010531 | 0.0017794 | 0.0033197 | -0.062897 | 0.00096348 | 0.068558 | 0.067336 | -0.0032386 | 0.00090142 | -0.00054474 | -0.027466 | 63.2034 | -60.3561 | 62.9333 | -60.0037 | -60.347 | -0.018311 | 0.022888 | 63.1943 | -60.1639 | 63.1531 | -60.1273 | -60.2234 | -59.8114 | -0.24719 | 0.073242 | -0.19684 | 0.10529 | 60.0906 | -0.23804 | 60.3378 | 0.009155 | -0.054931 | 0.064087 | 0.022888 | -0.01831 | 0.29755 | -0.11444 | 0.35248 | -0.05951 | 0.35248 | 123.2895 | 0.036621 | 123.317 | 123.5596 | 123.3582 | 123.3124 | 123.3032 | -123.4863 | -123.2941 | 123.0423 | 123.262 | 60.0815 | 60.1318
58.5469 | 123.4589 | -60.0494 | 63.1027 | -0.065308 | 0.0022709 | 0.06442 | 0.061553 | -1.486e-05 | 0.0032748 | 0.0028925 | 0.065277 | -0.00074552 | 0.068772 | 0.063918 | -0.0019568 | -0.0018756 | 0.0015915 | 0.009155 | 63.2034 | -60.3149 | 63.0203 | -59.8938 | -60.2509 | 0.10986 | 0.14191 | 63.1622 | -60.1364 | 63.2263 | -60.0037 | -60.0861 | -59.697 | -0.2655 | 0.10071 | -0.082397 | 0.15564 | 60.1593 | -0.20142 | 60.4248 | 0.064087 | -0.086976 | 0.059509 | 0.1236 | 0.045776 | 0.35248 | -0.036622 | 0.43945 | 0.050354 | 0.42114 | 123.3353 | 0.13275 | 123.3627 | 123.5184 | 123.2986 | 123.2529 | 123.2117 | -123.4177 | -123.2391 | 123.0698 | 123.2758 | 60.0586 | 60.1913
59.4844 | 123.3673 | -60.1364 | 63.1073 | -0.057678 | 0.00013467 | 0.064207 | 0.066253 | -0.00022866 | 0.00028418 | -0.00052553 | -0.047638 | 0.0026725 | 0.067704 | 0.067763 | -0.0004614 | -0.00059378 | -0.0037491 | -0.11902 | 63.1943 | -60.3745 | 62.883 | -60.1044 | -60.4248 | -0.1236 | -0.15106 | 63.176 | -60.2005 | 63.1165 | -60.2005 | -60.3012 | -59.8343 | -0.23804 | 0.086975 | -0.2243 | 0.032044 | 60.0128 | -0.28839 | 60.2509 | -0.050354 | -0.064086 | 0.068664 | 0.009155 | -0.064086 | 0.30212 | -0.16479 | 0.36621 | -0.10071 | 0.27008 | 123.2574 | 0 | 123.317 | 123.5687 | 123.3765 | 123.3307 | 123.3124 | -123.4818 | -123.3078 | 123.0194 | 123.2529 | 60.0174 | 59.9854
60.4844 | 123.3856 | -60.1273 | 63.1165 | -0.080566 | -0.00050633 | 0.065061 | 0.061126 | 0.0014803 | -0.0020658 | 0.0024653 | -0.026276 | -0.00010472 | 0.069626 | 0.069472 | -0.0002478 | -0.0014484 | -0.0039627 | -0.036621 | 63.1989 | -60.3424 | 62.9379 | -59.9991 | -60.3058 | -0.018311 | 0.027466 | 63.208 | -60.2051 | 63.1714 | -60.1181 | -60.2371 | -59.7885 | -0.21515 | 0.082398 | -0.17853 | 0.12817 | 60.1089 | -0.17853 | 60.3241 | 0.036621 | -0.07782 | 0.091553 | 0.054932 | 0.009155 | 0.33874 | -0.10986 | 0.41656 | -0.032044 | 0.34332 | 123.2803 | 0.086975 | 123.3765 | 123.5413 | 123.4131 | 123.3261 | 123.3353 | -123.4589 | -123.3215 | 123.0652 | 123.2986 | 60.0906 | 60.1547
61.5469 | 123.3856 | -60.0906 | 63.1302 | -0.03479 | -0.00050633 | 0.065488 | 0.062622 | 0.0046847 | -0.00099762 | -0.0020209 | -0.041534 | 0.0026725 | 0.067276 | 0.066054 | -0.001316 | 0.0013288 | 0.0033005 | -0.022888 | 63.2034 | -60.3241 | 62.9471 | -59.9899 | -60.3287 | -0.004578 | 0.064087 | 63.1943 | -60.173 | 63.1714 | -60.1089 | -60.2142 | -59.7977 | -0.23346 | 0.073242 | -0.1831 | 0.10071 | 60.0861 | -0.23804 | 60.3195 | -0.004577 | -0.082398 | 0.064087 | 0.041199 | -0.018311 | 0.29297 | -0.1236 | 0.37537 | -0.041198 | 0.33417 | 123.2712 | 0.064087 | 123.3444 | 123.5275 | 123.3673 | 123.2941 | 123.2849 | -123.4543 | -123.3032 | 123.0377 | 123.262 | 60.0677 | 60.1547
62.4844 | 123.3856 | -60.1044 | 63.1073 | -0.11871 | 0.00056187 | 0.062711 | 0.062835 | 0.0025485 | 0.0011386 | 0.0046015 | -0.038483 | 0.00074988 | 0.069626 | 0.076308 | 0.0001794 | -0.00016658 | 0.0039413 | -0.022888 | 63.1897 | -60.3516 | 62.9517 | -60.0082 | -60.3607 | -0.004578 | 0.018311 | 63.1805 | -60.1685 | 63.1851 | -60.1181 | -60.2188 | -59.7794 | -0.24719 | 0.082397 | -0.15564 | 0.09613 | 60.0998 | -0.25635 | 60.347 | -0.009156 | -0.064087 | 0.073242 | 0.07782 | -0.013733 | 0.32501 | -0.11444 | 0.3891 | -0.050354 | 0.34332 | 123.3032 | 0.050354 | 123.3536 | 123.5413 | 123.349 | 123.2941 | 123.2849 | -123.4589 | -123.2758 | 123.056 | 123.2895 | 60.0815 | 60.1227
63.5469 | 123.381 | -60.1044 | 63.1393 | -0.072937 | 0.0014163 | 0.065916 | 0.064544 | -0.00065586 | 7.0582e-05 | -9.8328e-05 | -0.053741 | -0.0033089 | 0.065995 | 0.063277 | -0.0002478 | 0.001115 | 0.0015915 | -0.018311 | 63.1851 | -60.3699 | 62.9425 | -60.0037 | -60.3653 | 0.004578 | -0.068665 | 63.1851 | -60.2005 | 63.1439 | -60.1364 | -60.2234 | -59.7977 | -0.2655 | 0.045777 | -0.19684 | 0.10071 | 60.1089 | -0.26093 | 60.3745 | 0.004578 | -0.09613 | 0.045777 | 0.004578 | -0.032044 | 0.3067 | -0.11902 | 0.40283 | -0.022889 | 0.36621 | 123.3124 | 0.064086 | 123.3444 | 123.555 | 123.3856 | 123.2895 | 123.2895 | -123.5092 | -123.3398 | 123.0469 | 123.2483 | 60.0861 | 60.0357
64.4844 | 123.3765 | -60.1044 | 63.1256 | -0.011902 | 0.0016299 | 0.063993 | 0.063476 | 0.0012667 | -0.0016384 | -0.0015935 | -0.026276 | 0.0028861 | 0.069626 | 0.070113 | 0.0001794 | 0.00090142 | 9.6064e-05 | -0.013733 | 63.1897 | -60.3561 | 62.9425 | -59.9899 | -60.3424 | 0 | 0.009155 | 63.1668 | -60.1822 | 63.1668 | -60.1318 | -60.2005 | -59.7977 | -0.25177 | 0.064087 | -0.18311 | 0.11444 | 60.1044 | -0.23804 | 60.3561 | 0.013733 | -0.07782 | 0.041199 | 0.041199 | -0.027466 | 0.3067 | -0.09613 | 0.38452 | -0.01831 | 0.36621 | 123.2986 | 0.050354 | 123.349 | 123.5458 | 123.349 | 123.2941 | 123.2712 | -123.4818 | -123.3078 | 123.0469 | 123.2712 | 60.0906 | 60.1135
65.5469 | 123.3398 | -60.1044 | 63.1439 | -0.042419 | -0.00050633 | 0.062498 | 0.063049 | -0.0036465 | -0.00035682 | 0.00032907 | 0.059174 | -0.0011727 | 0.068772 | 0.061996 | -0.0004614 | -0.00059378 | 0.0028733 | -0.009155 | 63.1851 | -60.3241 | 62.9333 | -60.0174 | -60.3836 | 0.050354 | -0.004578 | 63.2217 | -60.1501 | 63.1119 | -60.1181 | -60.2097 | -59.816 | -0.21973 | 0.041199 | -0.21057 | 0.086975 | 60.1547 | -0.27924 | 60.3745 | -0.059509 | -0.045776 | 0.07782 | -0.032044 | -0.013733 | 0.28839 | -0.10529 | 0.33417 | -0.05951 | 0.3067 | 123.2574 | 0.032043 | 123.262 | 123.5092 | 123.3719 | 123.2895 | 123.3261 | -123.468 | -123.2941 | 123.0377 | 123.2162 | 60.0952 | 60.0998
66.4844 | 123.3856 | -60.1273 | 63.1165 | -0.072937 | 0.0016299 | 0.064634 | 0.062408 | -0.00044226 | 0.00049778 | 0.00075627 | -0.035431 | 0.0013907 | 0.070053 | 0.072036 | -0.0002478 | -0.00016658 | -0.00011754 | -0.11902 | 63.1897 | -60.3973 | 62.8693 | -60.1089 | -60.4523 | -0.1236 | -0.15564 | 63.1531 | -60.173 | 63.1073 | -60.1868 | -60.3149 | -59.8526 | -0.27008 | 0.073242 | -0.24719 | 0.01831 | 60.0037 | -0.32501 | 60.2737 | -0.054932 | -0.045777 | 0.036621 | -0.009155 | -0.05951 | 0.27466 | -0.18768 | 0.32043 | -0.14191 | 0.28839 | 123.2666 | -0.013733 | 123.2803 | 123.587 | 123.3261 | 123.317 | 123.2803 | -123.5138 | -123.2895 | 122.9965 | 123.2346 | 60.0082 | 59.9716
67.5469 | 123.3353 | -60.0861 | 63.1302 | -0.042419 | 0.00077547 | 0.064207 | 0.064331 | 0.0010531 | 0.00028418 | 0.00032907 | -0.029327 | 0.00032248 | 0.067917 | 0.064986 | -0.000675 | -0.00080758 | 0.00052346 | -0.018311 | 63.1805 | -60.3561 | 62.9379 | -60.0037 | -60.3561 | -0.018311 | -0.004578 | 63.1622 | -60.1868 | 63.1668 | -60.1364 | -60.2509 | -59.8206 | -0.27008 | 0.050354 | -0.19226 | 0.082398 | 60.0677 | -0.27008 | 60.3378 | 0 | -0.10071 | 0.032043 | 0.036621 | -0.050354 | 0.2655 | -0.16479 | 0.36621 | -0.064086 | 0.35248 | 123.2941 | 0.050354 | 123.3536 | 123.5367 | 123.349 | 123.2666 | 123.2483 | -123.4863 | -123.317 | 123.024 | 123.2529 | 60.0677 | 60.0815
68.4844 | 123.3215 | -60.1181 | 63.1119 | -0.019531 | 0.00056187 | 0.065916 | 0.064331 | -0.0021513 | 0.0011386 | 0.0022517 | -0.032379 | 0.00096348 | 0.068344 | 0.065414 | -0.0011022 | 0.00090142 | 0.0013779 | -0.082397 | 63.2217 | -60.3653 | 62.8418 | -60.1273 | -60.4385 | -0.13275 | -0.16479 | 63.176 | -60.2188 | 63.0798 | -60.1868 | -60.3149 | -59.8663 | -0.24719 | 0.10986 | -0.27008 | -0.009155 | 59.9854 | -0.32044 | 60.2325 | -0.073243 | -0.10071 | 0.064087 | -0.032043 | -0.068665 | 0.25177 | -0.19684 | 0.35248 | -0.09613 | 0.23804 | 123.2071 | 0.032043 | 123.2986 | 123.587 | 123.3948 | 123.3398 | 123.2941 | -123.4772 | -123.3307 | 122.9599 | 123.1979 | 60.0357 | 59.9533
69.4844 | 123.3948 | -60.1318 | 63.0569 | -0.095825 | -7.913e-05 | 0.064847 | 0.062194 | 0.0044711 | -0.00057042 | -0.00095273 | -0.035431 | 0.0011771 | 0.068344 | 0.0652 | -0.0017432 | -0.00038018 | 0.00073706 | -0.1236 | 63.1897 | -60.3882 | 62.8647 | -60.0906 | -60.4431 | -0.1236 | -0.16479 | 63.1668 | -60.2188 | 63.0936 | -60.1822 | -60.2829 | -59.8434 | -0.25635 | 0.13275 | -0.19226 | 0.041199 | 60.0082 | -0.31128 | 60.2646 | -0.054931 | -0.086975 | 0.10986 | 0.036621 | -0.050354 | 0.28839 | -0.15106 | 0.37537 | -0.064087 | 0.29755 | 123.2529 | 0.036621 | 123.3124 | 123.5779 | 123.3856 | 123.3215 | 123.2986 | -123.4451 | -123.2758 | 122.9965 | 123.2254 | 60.0082 | 59.967
70.5469 | 123.3765 | -60.0952 | 63.1393 | -0.072937 | 0.00098907 | 0.06207 | 0.063049 | -0.00065586 | -0.00099762 | 0.00032907 | 0.004242 | 0.0016043 | 0.068985 | 0.067123 | -0.0015296 | 0.0013288 | -0.0011855 | -0.022888 | 63.2126 | -60.3333 | 62.9974 | -60.0677 | -60.434 | 0.027466 | 0.032043 | 63.1989 | -60.2051 | 63.1714 | -60.1089 | -60.2142 | -59.7885 | -0.23804 | 0.073242 | -0.14191 | 0.027466 | 60.1227 | -0.33874 | 60.3607 | -0.10071 | -0.10986 | 0.05951 | 0.032044 | -0.013733 | 0.3067 | -0.11902 | 0.41656 | -0.009155 | 0.2655 | 123.3307 | 0.09613 | 123.3765 | 123.5458 | 123.4039 | 123.3078 | 123.2941 | -123.4726 | -123.3444 | 123.0927 | 123.2666 | 60.0723 | 60.1273
71.4844 | 123.349 | -60.1227 | 63.1348 | -0.072937 | 0.0024845 | 0.065488 | 0.062622 | 0.00041234 | 0.0034884 | 0.00075627 | -0.023224 | 0.0013907 | 0.068558 | 0.067336 | 0.001034 | 0.00068782 | 0.0011643 | -0.10529 | 63.2126 | -60.3973 | 62.8418 | -60.1273 | -60.4752 | -0.15106 | -0.15564 | 63.1714 | -60.2097 | 63.089 | -60.2051 | -60.3104 | -59.8526 | -0.27466 | 0.077819 | -0.29297 | -0.004577 | 59.9716 | -0.35248 | 60.2463 | -0.07782 | -0.086975 | 0.036621 | -0.045777 | -0.082397 | 0.27008 | -0.18768 | 0.35706 | -0.10071 | 0.27008 | 123.2391 | 0.004578 | 123.2986 | 123.6099 | 123.381 | 123.3353 | 123.2941 | -123.5321 | -123.3444 | 122.9645 | 123.2117 | 60.0174 | 59.967
72.5469 | 123.5001 | -60.0723 | 63.121 | -0.080566 | -0.0026425 | 0.062498 | 0.061981 | -0.0025785 | 7.0582e-05 | -0.0024481 | 0.068329 | 0.00074988 | 0.065995 | 0.067123 | -3.4196e-05 | -0.0014484 | 0.0028733 | -0.022888 | 63.176 | -60.3149 | 63.0295 | -59.8755 | -60.2371 | 0.1236 | 0.16479 | 63.1302 | -60.1318 | 63.2584 | -59.9945 | -60.0769 | -59.6786 | -0.24261 | 0.054931 | -0.091553 | 0.19684 | 60.1959 | -0.16479 | 60.4385 | 0.077819 | -0.059509 | 0.009155 | 0.13733 | 0.07782 | 0.39368 | -0.004577 | 0.45319 | 0.054932 | 0.43945 | 123.3444 | 0.13733 | 123.3902 | 123.4909 | 123.262 | 123.2483 | 123.2025 | -123.436 | -123.2529 | 123.1018 | 123.3307 | 60.0494 | 60.2371
73.4844 | 123.4131 | -60.1044 | 63.089 | -0.072937 | 0.00098907 | 0.063993 | 0.062622 | 0.0019077 | -0.00035682 | -0.0013799 | 0.016449 | 0.0013907 | 0.068131 | 0.065627 | -0.002384 | -0.00016658 | 0.0026597 | -0.059509 | 63.1348 | -60.3378 | 62.9837 | -59.9533 | -60.3378 | -0.027466 | -0.009155 | 63.121 | -60.173 | 63.1989 | -60.0723 | -60.1868 | -59.7061 | -0.23346 | 0.045777 | -0.10528 | 0.15106 | 60.0769 | -0.23346 | 60.3104 | 0 | -0.068665 | 0.032044 | 0.10986 | 0.032043 | 0.39825 | -0.082398 | 0.46692 | -0.013733 | 0.38452 | 123.3215 | 0.10071 | 123.3719 | 123.4726 | 123.2941 | 123.2391 | 123.2254 | -123.4268 | -123.262 | 123.0881 | 123.3032 | 60.0449 | 60.0952
74.5469 | 123.3627 | -60.1227 | 63.1165 | 0.026245 | -7.913e-05 | 0.065275 | 0.06369 | 0.0036165 | -0.0014248 | 0.00011527 | -0.053741 | 0.0022453 | 0.066635 | 0.066695 | -0.0011022 | 0.00068782 | 0.0039413 | -0.027466 | 63.1989 | -60.3561 | 62.9333 | -60.0311 | -60.3928 | -0.054932 | -0.041199 | 63.1851 | -60.1822 | 63.1485 | -60.173 | -60.2829 | -59.848 | -0.23346 | 0.082398 | -0.18311 | 0.091553 | 60.0677 | -0.27008 | 60.3012 | -0.036621 | -0.059509 | 0.068665 | 0.032044 | -0.050354 | 0.27466 | -0.16022 | 0.33417 | -0.10071 | 0.32501 | 123.2895 | 0.009155 | 123.3307 | 123.555 | 123.3673 | 123.3215 | 123.3078 | -123.4726 | -123.2986 | 123.056 | 123.2712 | 60.0952 | 60.0815
75.4844 | 123.4772 | -60.1089 | 63.0524 | -0.03479 | -0.0015743 | 0.065702 | 0.063476 | 0.00041234 | 0.0011386 | -0.0013799 | -0.020172 | -0.00095912 | 0.067704 | 0.069045 | 0.000393 | -0.00038018 | -0.00097194 | -0.09613 | 63.1577 | -60.347 | 62.9379 | -60.0037 | -60.3424 | -0.059509 | -0.082397 | 63.1302 | -60.1776 | 63.2126 | -60.0861 | -60.1913 | -59.7382 | -0.23804 | 0.10529 | -0.11444 | 0.10529 | 60.0494 | -0.23346 | 60.2875 | 0.004578 | -0.068664 | 0.07782 | 0.16022 | 0.022888 | 0.37079 | -0.082397 | 0.43945 | -0.013733 | 0.34332 | 123.2849 | 0.091552 | 123.3902 | 123.5046 | 123.3078 | 123.2666 | 123.2391 | -123.3994 | -123.23 | 123.0469 | 123.3215 | 60.0128 | 60.0266
76.5469 | 123.3856 | -60.0815 | 63.1165 | -0.0042723 | 0.0012027 | 0.063779 | 0.063262 | -0.00044226 | 0.00071138 | -9.8328e-05 | -0.026276 | 0.00010888 | 0.069626 | 0.064986 | -0.0015296 | -0.0025164 | -0.0011855 | -0.073242 | 63.2172 | -60.3378 | 62.9288 | -59.9899 | -60.3333 | 0.009155 | 0.036621 | 63.2401 | -60.1913 | 63.1805 | -60.0998 | -60.2142 | -59.7794 | -0.25635 | 0.10071 | -0.18768 | 0.091553 | 60.0906 | -0.25177 | 60.347 | 0.004578 | -0.10986 | 0.1236 | 0.064087 | -0.01831 | 0.30212 | -0.13275 | 0.41199 | -0.022888 | 0.3479 | 123.2666 | 0.091553 | 123.3719 | 123.555 | 123.4314 | 123.2986 | 123.3215 | -123.4543 | -123.3078 | 123.0103 | 123.262 | 60.0082 | 60.1181
77.4844 | 123.3765 | -60.1181 | 63.0524 | -0.011902 | 0.0026981 | 0.066556 | 0.065185 | -0.00065586 | 0.00028418 | -9.8328e-05 | -0.035431 | -0.00074552 | 0.067917 | 0.0652 | -0.0008886 | -0.00038018 | 0.0026597 | -0.1236 | 63.1851 | -60.379 | 62.8784 | -60.0861 | -60.4248 | -0.13275 | -0.15106 | 63.1577 | -60.2234 | 63.1393 | -60.1593 | -60.2646 | -59.697 | -0.26093 | 0.13275 | -0.17395 | 0.032043 | 59.9854 | -0.3067 | 60.2463 | -0.045777 | -0.10529 | 0.10529 | 0.086975 | -0.041199 | 0.42114 | -0.14648 | 0.52643 | -0.041198 | 0.29297 | 123.2574 | 0.064087 | 123.3627 | 123.5641 | 123.381 | 123.3032 | 123.2758 | -123.4314 | -123.2758 | 122.9965 | 123.2574 | 59.9945 | 59.967
78.4844 | 123.3719 | -60.1273 | 63.0981 | -0.050049 | 0.0016299 | 0.065275 | 0.062194 | 0.0031893 | 0.00071138 | -0.00073913 | -0.065949 | 0.0013907 | 0.067917 | 0.07524 | 0.0014612 | 0.001115 | 9.6064e-05 | -0.13733 | 63.1805 | -60.379 | 62.8601 | -60.1044 | -60.466 | -0.11444 | -0.1831 | 63.1577 | -60.2142 | 63.1165 | -60.1776 | -60.3012 | -59.848 | -0.25177 | 0.082397 | -0.23804 | 0.022888 | 60.0128 | -0.33875 | 60.2646 | -0.086975 | -0.086975 | 0.059509 | 0.01831 | -0.050354 | 0.27924 | -0.17395 | 0.36621 | -0.086975 | 0.27466 | 123.2391 | 0.036621 | 123.3307 | 123.5596 | 123.3719 | 123.3078 | 123.2849 | -123.4772 | -123.3124 | 122.9874 | 123.2437 | 59.9899 | 59.9442
79.5469 | 123.349 | -60.1273 | 63.1119 | -0.019531 | -0.00029273 | 0.064847 | 0.063476 | 0.0034029 | 7.0582e-05 | 0.0024653 | -0.062897 | 0.00053628 | 0.066849 | 0.067336 | 0.0012476 | -0.0010212 | 0.0030869 | -0.12817 | 63.1897 | -60.3973 | 62.8784 | -60.0998 | -60.4431 | -0.11444 | -0.16479 | 63.1668 | -60.2005 | 63.1119 | -60.1868 | -60.3104 | -59.8526 | -0.27008 | 0.07782 | -0.23346 | 0.027466 | 60.0128 | -0.31586 | 60.2829 | -0.045776 | -0.073242 | 0.054932 | 0 | -0.05951 | 0.27466 | -0.18311 | 0.3479 | -0.10986 | 0.29755 | 123.2758 | 0.013732 | 123.3124 | 123.587 | 123.3673 | 123.317 | 123.2941 | -123.5092 | -123.3124 | 123.0057 | 123.2391 | 59.9991 | 59.9625
80.4844 | 123.436 | -60.0998 | 63.0707 | -0.057678 | 0.00056187 | 0.063779 | 0.061981 | 0.0010531 | 0.00092498 | -0.00031193 | -0.047638 | -0.0020273 | 0.067063 | 0.064345 | 0.0001794 | -0.001662 | -0.0016129 | -0.10529 | 63.1668 | -60.3561 | 62.9425 | -59.9899 | -60.3653 | -0.032043 | -0.064087 | 63.1119 | -60.1959 | 63.2034 | -60.0815 | -60.1822 | -59.7336 | -0.25635 | 0.09613 | -0.12817 | 0.10986 | 60.0677 | -0.2655 | 60.3241 | -0.009155 | -0.096131 | 0.041198 | 0.13275 | 0.01831 | 0.36621 | -0.082398 | 0.46234 | 0.013733 | 0.36621 | 123.2986 | 0.11444 | 123.3994 | 123.5229 | 123.3078 | 123.2666 | 123.2117 | -123.4268 | -123.2666 | 123.0423 | 123.3032 | 59.9945 | 60.0357
81.5469 | 123.2986 | -60.1089 | 63.1027 | -0.027161 | -7.913e-05 | 0.063352 | 0.064117 | 0.0016939 | -0.00057042 | 0.00096987 | -0.072052 | 0.0035269 | 0.06749 | 0.071181 | 0.001034 | -0.00080758 | -0.00033114 | -0.09613 | 63.1943 | -60.3653 | 62.9105 | -60.1273 | -60.4797 | -0.10986 | -0.16479 | 63.1943 | -60.2234 | 63.0844 | -60.2142 | -60.3333 | -59.8663 | -0.25635 | 0.091553 | -0.19226 | -0.01831 | 59.9991 | -0.37079 | 60.2554 | -0.11444 | -0.11444 | 0.091553 | -0.01831 | -0.10529 | 0.24262 | -0.2243 | 0.35706 | -0.10986 | 0.23804 | 123.2758 | 0.009156 | 123.3078 | 123.5596 | 123.4177 | 123.3032 | 123.3032 | -123.468 | -123.3261 | 123.0194 | 123.1934 | 60.0128 | 59.9442
82.4844 | 123.3902 | -60.1227 | 63.0753 | -0.027161 | 0.0024845 | 0.065275 | 0.064331 | 0.0012667 | -0.00099762 | 0.0018243 | -0.062897 | 0.00074988 | 0.066635 | 0.069472 | -0.0004614 | -0.0012348 | 0.0030869 | -0.12817 | 63.1622 | -60.3973 | 62.8647 | -60.0815 | -60.4385 | -0.1236 | -0.14648 | 63.1531 | -60.2051 | 63.1485 | -60.2646 | -60.1318 | -59.7244 | -0.27466 | 0.086975 | -0.21057 | 0.041199 | 59.9991 | -0.31586 | 60.2737 | -0.041199 | -0.082397 | 0.07782 | 0.073243 | -0.14191 | 0.39825 | -0.009155 | 0.48065 | 0.073242 | 0.31586 | 123.262 | -0.059509 | 123.3536 | 123.5596 | 123.3582 | 123.2849 | 123.2758 | -123.4726 | -123.2803 | 122.9874 | 123.2712 | 59.9945 | 59.9762
83.4844 | 123.4543 | -60.0723 | 63.0798 | -0.065308 | 0.0012027 | 0.062711 | 0.060485 | -0.0021513 | -0.00035682 | -0.00095273 | -0.01712 | 0.00010888 | 0.067276 | 0.067336 | -0.0004614 | -0.0010212 | -0.0020401 | -0.064087 | 63.1485 | -60.3287 | 62.9562 | -59.9533 | -60.3241 | -0.013733 | 0.022888 | 63.1073 | -60.1685 | 63.176 | -60.0677 | -60.173 | -59.7473 | -0.25635 | 0.068665 | -0.1236 | 0.11902 | 60.0586 | -0.25177 | 60.3149 | 0.004577 | -0.09613 | 0.027466 | 0.09613 | 0.004578 | 0.32501 | -0.10071 | 0.42114 | -0.004578 | 0.37537 | 123.2849 | 0.10071 | 123.3444 | 123.4772 | 123.2758 | 123.2208 | 123.1796 | -123.4085 | -123.2483 | 123.0286 | 123.2483 | 60.0082 | 60.0952
84.4844 | 123.3582 | -60.1135 | 63.1073 | -0.088196 | 0.0014163 | 0.066984 | 0.06604 | -0.0015103 | 0.00092498 | 0.00032907 | -0.053741 | -0.00010472 | 0.067704 | 0.072677 | -0.001316 | -0.00059378 | -0.0035355 | -0.12817 | 63.1805 | -60.3607 | 62.8784 | -60.1273 | -60.4431 | -0.12817 | -0.17853 | 63.1897 | -60.2234 | 63.1073 | -60.2051 | -60.2966 | -59.8526 | -0.24719 | 0.073242 | -0.22888 | -0.013733 | 59.9854 | -0.32959 | 60.2325 | -0.082397 | -0.10986 | 0.082397 | 0 | -0.091553 | 0.26093 | -0.18311 | 0.37079 | -0.073242 | 0.23346 | 123.2391 | 0.018311 | 123.3307 | 123.5413 | 123.4131 | 123.2941 | 123.3032 | -123.468 | -123.3307 | 122.9919 | 123.2208 | 59.9854 | 59.935
85.4844 | 123.4863 | -60.0861 | 63.0524 | -0.080566 | 0.00034827 | 0.06442 | 0.062835 | -0.0015103 | 0.0032748 | 0.00032907 | -0.014069 | 0.00053628 | 0.066208 | 0.066054 | -3.4196e-05 | -0.0014484 | 0.00030966 | -0.091553 | 63.1485 | -60.3699 | 62.9288 | -60.0586 | -60.3104 | -0.045776 | -0.054932 | 63.1165 | -60.1822 | 63.2126 | -60.0586 | -60.1822 | -59.729 | -0.28381 | 0.096131 | -0.1236 | 0.027466 | 60.0403 | -0.2243 | 60.3241 | 0.059509 | -0.09613 | 0.064087 | 0.16022 | 0.027466 | 0.35706 | -0.09613 | 0.45319 | 0 | 0.31128 | 123.2986 | 0.1236 | 123.3948 | 123.5184 | 123.2986 | 123.2346 | 123.2025 | -123.4222 | -123.2346 | 123.0148 | 123.2986 | 59.9945 | 60.0311
86.5469 | 123.3353 | -60.1135 | 63.1119 | 0.018616 | 0.00034827 | 0.064847 | 0.064544 | -0.0019377 | -0.00078402 | -0.0013799 | -0.065949 | 0.0011771 | 0.067063 | 0.064986 | -0.000675 | 0.001115 | 9.6064e-05 | -0.059509 | 63.1943 | -60.3516 | 62.8967 | -60.0632 | -60.3653 | -0.07782 | -0.07782 | 63.1897 | -60.1913 | 63.1027 | -60.1593 | -60.2829 | -59.8251 | -0.23804 | 0.082398 | -0.21515 | 0.050354 | 60.0357 | -0.25177 | 60.2737 | -0.013733 | -0.07782 | 0.07782 | -0.009155 | -0.045777 | 0.28839 | -0.16937 | 0.36621 | -0.091553 | 0.28839 | 123.2483 | 0.032043 | 123.2941 | 123.5458 | 123.381 | 123.3078 | 123.3032 | -123.4634 | -123.3032 | 123.0103 | 123.2162 | 60.054 | 60.0357
87.4844 | 123.468 | -60.0677 | 63.0753 | -0.088196 | 0.0012027 | 0.063993 | 0.062622 | -0.00065586 | 0.0011386 | -0.0030889 | 0.05307 | 0.00010888 | 0.069199 | 0.061141 | -0.0011022 | -0.0027302 | 0.0039413 | -0.068665 | 63.1897 | -60.3104 | 62.9608 | -59.9899 | -60.3287 | 0.018311 | -0.013733 | 63.1165 | -60.1822 | 63.2629 | -59.9487 | -60.1959 | -59.7794 | -0.24262 | 0.11444 | -0.11444 | 0.07782 | 60.0861 | -0.26093 | 60.3287 | -0.01831 | -0.11444 | 0.041199 | 0.18768 | 0.11902 | 0.28839 | -0.12817 | 0.40283 | -0.013733 | 0.32044 | 123.2712 | 0.23346 | 123.4451 | 123.5001 | 123.2986 | 123.2574 | 123.1842 | -123.3856 | -123.2574 | 123.0286 | 123.3307 | 59.9991 | 60.054
88.5469 | 123.381 | -60.0815 | 63.1348 | 0.033875 | -0.0022153 | 0.064847 | 0.064117 | -0.00022866 | -0.00035682 | -0.00073913 | -0.035431 | 0.00096348 | 0.068985 | 0.067977 | 0.0006066 | -0.00016658 | -0.0024673 | 0.091553 | 63.2584 | -60.3287 | 62.9471 | -60.0403 | -60.3333 | 0 | 0.009155 | 63.1805 | -60.173 | 63.1622 | -60.0952 | -60.2142 | -59.7656 | -0.24719 | 0.1236 | -0.18768 | 0.041199 | 60.0815 | -0.25177 | 60.3287 | -0.004578 | -0.091553 | 0.045776 | 0.027465 | -0.013733 | 0.31586 | -0.13275 | 0.40741 | -0.041198 | 0.28839 | 123.2758 | 0.07782 | 123.3353 | 123.587 | 123.3536 | 123.3398 | 123.262 | -123.4634 | -123.3078 | 123.0286 | 123.2437 | 60.173 | 60.0906
89.4844 | 123.4177 | -60.1089 | 63.0798 | -0.057678 | 0.0022709 | 0.06442 | 0.062835 | -0.0021513 | -0.00035682 | -0.0033025 | 0.025604 | -0.00010472 | 0.068344 | 0.06285 | -0.0021704 | -0.0023028 | 0.00030966 | -0.086975 | 63.1256 | -60.3241 | 62.9471 | -59.9945 | -60.379 | -0.036621 | -0.068665 | 63.1256 | -60.1959 | 63.1531 | -60.0998 | -60.173 | -59.7702 | -0.21515 | 0.045776 | -0.13275 | 0.11444 | 60.0723 | -0.27008 | 60.2875 | -0.054931 | -0.086975 | 0.045776 | 0.073242 | 0.009156 | 0.33874 | -0.064087 | 0.42572 | 0.022888 | 0.32959 | 123.2712 | 0.096131 | 123.349 | 123.4497 | 123.3215 | 123.2346 | 123.2346 | -123.4039 | -123.2758 | 123.056 | 123.262 | 60.022 | 60.0403
90.4844 | 123.4726 | -60.0677 | 63.0569 | -0.03479 | -0.00029273 | 0.06442 | 0.062408 | 0.0014803 | 7.0582e-05 | 0.0013971 | -0.01712 | -0.0013863 | 0.068131 | 0.072463 | -0.0002478 | -0.0018756 | 9.6064e-05 | -0.059509 | 63.1165 | -60.3653 | 62.9791 | -59.9579 | -60.3333 | -0.045776 | -0.041199 | 63.089 | -60.1822 | 63.2217 | -60.0677 | -60.173 | -59.7382 | -0.29755 | 0.059509 | -0.07782 | 0.10986 | 60.022 | -0.2655 | 60.3195 | 0.032043 | -0.11444 | 0.032043 | 0.16479 | 0 | 0.32959 | -0.10529 | 0.44403 | 0.009155 | 0.40741 | 123.3444 | 0.11444 | 123.4039 | 123.4818 | 123.2712 | 123.1842 | 123.1567 | -123.4222 | -123.2391 | 123.0469 | 123.2895 | 60.0082 | 60.0266
91.5469 | 123.4085 | -60.1135 | 63.1073 | 0.08728 | -0.00050633 | 0.063779 | 0.065185 | 0.0040439 | 0.00028418 | -9.8328e-05 | -0.026276 | 0.00010888 | 0.067063 | 0.067977 | -0.0004614 | -0.00038018 | 0.0022323 | -0.12817 | 63.1622 | -60.3836 | 62.8738 | -60.0723 | -60.3973 | -0.086975 | -0.13733 | 63.1439 | -60.2005 | 63.176 | -60.1318 | -60.2509 | -59.8022 | -0.27008 | 0.054931 | -0.23346 | 0.041198 | 60.0266 | -0.28381 | 60.2966 | -0.013733 | -0.086975 | 0.036621 | 0.068664 | -0.018311 | 0.31128 | -0.13733 | 0.39825 | -0.050354 | 0.31128 | 123.2574 | 0.068664 | 123.3765 | 123.5458 | 123.3444 | 123.2758 | 123.2574 | -123.4909 | -123.3078 | 122.9874 | 123.2895 | 59.9854 | 59.9762
92.4844 | 123.5275 | -60.0861 | 63.0432 | -0.10345 | -0.00071993 | 0.063779 | 0.06134 | -0.0045011 | 0.0037022 | 0.0024653 | -0.014069 | 0.00010888 | 0.065995 | 0.068191 | -0.0015296 | 0.001115 | -0.0018265 | -0.059509 | 63.1256 | -60.3058 | 62.9883 | -59.9533 | -60.3149 | -0.045776 | -0.032043 | 63.1119 | -60.173 | 63.2126 | -60.0586 | -60.1639 | -59.7336 | -0.21973 | 0.082397 | -0.054932 | 0.13275 | 60.0403 | -0.22888 | 60.26 | -0.009155 | -0.086975 | 0.068664 | 0.16937 | 0.027466 | 0.35248 | -0.077819 | 0.43945 | 0.009156 | 0.35248 | 123.2941 | 0.11444 | 123.3856 | 123.4314 | 123.2849 | 123.2117 | 123.1979 | -123.349 | -123.2162 | 123.0743 | 123.2986 | 60.0266 | 60.054
93.4844 | 123.468 | -60.054 | 63.1027 | -0.072937 | -0.00050633 | 0.063138 | 0.062835 | -0.0015103 | 0.00028418 | -0.0022345 | 0.031708 | -0.00031832 | 0.066422 | 0.060287 | 0.001034 | -0.00016658 | -0.0022537 | 0.032043 | 63.1622 | -60.2783 | 63.0524 | -59.8709 | -60.2371 | 0.10071 | 0.13733 | 63.1485 | -60.1501 | 63.2446 | -59.9899 | -60.0861 | -59.7015 | -0.2243 | 0.059509 | -0.050354 | 0.1831 | 60.1547 | -0.18311 | 60.379 | 0.041198 | -0.09613 | 0.045777 | 0.14191 | 0.064087 | 0.35248 | -0.032044 | 0.44861 | 0.064086 | 0.40741 | 123.3307 | 0.16022 | 123.3948 | 123.4406 | 123.2986 | 123.2162 | 123.2025 | -123.381 | -123.2529 | 123.1064 | 123.2986 | 60.0861 | 60.1913
94.5469 | 123.3765 | -60.141 | 63.1073 | -0.065308 | 0.0029117 | 0.063993 | 0.062622 | 0.0021213 | 0.0034884 | -0.0015935 | -0.041534 | -0.00031832 | 0.06514 | 0.064986 | -0.001316 | -0.0020892 | -0.0022537 | -0.11902 | 63.176 | -60.3653 | 62.709 | -60.0632 | -60.1685 | -0.082397 | -0.1236 | 63.1714 | -60.1685 | 63.1393 | -60.173 | -60.3104 | -59.8389 | -0.2243 | 0.068664 | -0.39825 | 0.07782 | 60.0586 | -0.027466 | 60.2829 | 0.19684 | -0.027466 | 0.064087 | 0.032043 | -0.032044 | 0.30212 | -0.16937 | 0.32959 | -0.14191 | 0.30212 | 123.0743 | -0.004578 | 123.3078 | 123.5413 | 123.3398 | 123.317 | 123.3124 | -123.4726 | -123.2758 | 122.85 | 123.2803 | 60.022 | 60.0174
95.4844 | 123.4955 | -60.0494 | 63.0936 | -0.080566 | 0.00013467 | 0.063993 | 0.061553 | -0.0027921 | 0.0015658 | -9.8328e-05 | 0.031708 | -0.00031832 | 0.068344 | 0.067336 | -3.4196e-05 | -0.0012348 | 0.0020187 | -0.018311 | 63.1439 | -60.3149 | 63.0249 | -59.8938 | -60.2554 | 0.11444 | 0.12817 | 63.1531 | -60.1685 | 63.2492 | -59.9762 | -60.0769 | -59.6603 | -0.2655 | 0.050354 | -0.068665 | 0.15564 | 60.1639 | -0.20599 | 60.4294 | 0.059509 | -0.11902 | 0.059509 | 0.15564 | 0.073242 | 0.3891 | -0.027466 | 0.50812 | 0.091553 | 0.42114 | 123.3398 | 0.19226 | 123.4177 | 123.4589 | 123.3215 | 123.1934 | 123.2025 | -123.4085 | -123.262 | 123.0743 | 123.2986 | 60.0311 | 60.1776
96.4844 | 123.4039 | -60.1044 | 63.089 | -0.027161 | 0.00056187 | 0.062711 | 0.06369 | -0.0019377 | -0.00099762 | -0.00073913 | 0.004242 | 0.00074988 | 0.068985 | 0.068404 | -0.0008886 | -0.001662 | 0.00030966 | -0.09613 | 63.1577 | -60.3287 | 62.97 | -60.0037 | -60.3699 | -0.041199 | -0.064087 | 63.1256 | -60.1959 | 63.1714 | -60.0815 | -60.1822 | -59.7656 | -0.2243 | 0.068665 | -0.11902 | 0.10071 | 60.0632 | -0.2655 | 60.2875 | -0.041199 | -0.091553 | 0.036621 | 0.082398 | 0.022888 | 0.33875 | -0.07782 | 0.4303 | 0.013733 | 0.32501 | 123.2986 | 0.11444 | 123.3673 | 123.4863 | 123.3215 | 123.262 | 123.23 | -123.4177 | -123.2849 | 123.0743 | 123.2758 | 60.0082 | 60.0403
97.4844 | 123.4909 | -60.0861 | 63.1073 | -0.027161 | 0.0016299 | 0.065061 | 0.062408 | -0.0010831 | 0.00071138 | -0.00073913 | 0.031708 | 0.00032248 | 0.068344 | 0.060073 | -0.0008886 | -0.0027302 | 0.00052346 | -0.054932 | 63.176 | -60.3195 | 62.9929 | -59.9533 | -60.2921 | 0.054932 | 0.032043 | 63.1897 | -60.1456 | 63.2172 | -60.0128 | -60.1089 | -59.7107 | -0.23346 | 0.068664 | -0.11444 | 0.13275 | 60.141 | -0.20599 | 60.3745 | 0.027466 | -0.059509 | 0.082397 | 0.10986 | 0.073243 | 0.37537 | -0.022888 | 0.43488 | 0.036621 | 0.36621 | 123.3124 | 0.13275 | 123.3627 | 123.4955 | 123.3353 | 123.262 | 123.2758 | -123.4268 | -123.2529 | 123.0789 | 123.3032 | 60.0311 | 60.1181
98.5469 | 123.4589 | -60.0586 | 63.0707 | -0.11108 | 0.0029117 | 0.066129 | 0.065185 | -0.0021513 | -0.0020658 | 0.0024653 | -0.059845 | -0.00010472 | 0.066849 | 0.072249 | -0.0008886 | -0.00016658 | 0.0030869 | -0.086975 | 63.1165 | -60.3745 | 62.9791 | -59.967 | -60.3333 | -0.041199 | -0.045776 | 63.1256 | -60.1776 | 63.2355 | -60.0677 | -60.1547 | -59.7198 | -0.31586 | 0.045776 | -0.091553 | 0.091553 | 60.0174 | -0.27466 | 60.3333 | 0.041199 | -0.11902 | 0.054931 | 0.1648 | -0.009155 | 0.33874 | -0.09613 | 0.45776 | 0.022888 | 0.40741 | 123.3536 | 0.10986 | 123.4131 | 123.4909 | 123.3032 | 123.175 | 123.1842 | -123.4451 | -123.2483 | 123.0377 | 123.2941 | 59.9716 | 60.0128
99.4844 | 123.468 | -60.0998 | 63.0753 | -0.065308 | -0.00050633 | 0.062498 | 0.064117 | -0.00065586 | -0.0014248 | -0.0037299 | 0.034759 | 0.00010888 | 0.064713 | 0.061141 | 0.000393 | -0.0027302 | -0.00097194 | -0.027466 | 63.1577 | -60.3195 | 62.9929 | -59.9304 | -60.2783 | 0.064087 | 0.073242 | 63.1622 | -60.141 | 63.2492 | -60.022 | -60.1227 | -59.7107 | -0.21973 | 0.082398 | -0.082397 | 0.16937 | 60.1639 | -0.17853 | 60.3836 | 0.041199 | -0.041199 | 0.086975 | 0.17395 | 0.077819 | 0.3891 | -0.022889 | 0.4303 | 0.01831 | 0.3891 | 123.3124 | 0.11902 | 123.3902 | 123.4772 | 123.3032 | 123.2574 | 123.262 | -123.3948 | -123.2162 | 123.0927 | 123.349 | 60.0723 | 60.173
100.5469 | 123.4589 | -60.0677 | 63.0569 | -0.072937 | 0.0014163 | 0.065702 | 0.063476 | 0.0019077 | 0.004343 | -0.0013799 | -0.056793 | -0.0018137 | 0.065567 | 0.068831 | -0.0017432 | 0.00026062 | 0.0011643 | -0.059509 | 63.1119 | -60.3607 | 62.9837 | -59.9625 | -60.3424 | -0.041199 | -0.027466 | 63.0936 | -60.1776 | 63.2309 | -60.0632 | -60.1593 | -59.7244 | -0.29297 | 0.054931 | -0.073242 | 0.10529 | 60.0266 | -0.27466 | 60.3195 | 0.018311 | -0.10986 | 0.036621 | 0.17395 | 0.004578 | 0.34332 | -0.091553 | 0.45319 | 0.01831 | 0.39825 | 123.3444 | 0.11444 | 123.4085 | 123.4726 | 123.2712 | 123.1796 | 123.1613 | -123.4177 | -123.2346 | 123.0515 | 123.2986 | 60.0082 | 60.0403
101.4844 | 123.3765 | -60.0998 | 63.1393 | 0.0033567 | -0.00050633 | 0.063566 | 0.064544 | -0.0025785 | -0.00035682 | -0.0024481 | -0.032379 | -0.00010472 | 0.068558 | 0.067763 | -0.001316 | 0.0015424 | 0.0013779 | 0.009155 | 63.1897 | -60.3378 | 62.9608 | -59.9808 | -60.3378 | 0.045776 | 0.022888 | 63.2034 | -60.1593 | 63.1531 | -60.1227 | -60.2051 | -59.8068 | -0.23804 | 0.050354 | -0.17853 | 0.11902 | 60.1456 | -0.23804 | 60.3836 | 0 | -0.05951 | 0.064087 | 0.013733 | -0.022889 | 0.29297 | -0.10529 | 0.35248 | -0.045776 | 0.35706 | 123.2986 | 0.036621 | 123.3124 | 123.5275 | 123.3627 | 123.2895 | 123.3032 | -123.4772 | -123.2986 | 123.0606 | 123.2529 | 60.1089 | 60.1227
102.5469 | 123.3307 | -60.1227 | 63.1165 | -0.065308 | -7.913e-05 | 0.063779 | 0.064971 | -0.0015103 | 0.0011386 | 0.00075627 | -0.090363 | 0.0024589 | 0.06749 | 0.069472 | -0.0004614 | 0.0038922 | -0.0011855 | -0.059509 | 63.1851 | -60.3699 | 62.9105 | -60.0449 | -60.4111 | -0.07782 | -0.10529 | 63.1805 | -60.1868 | 63.1348 | -60.1593 | -60.2921 | -59.8343 | -0.24719 | 0.068665 | -0.20599 | 0.07782 | 60.0449 | -0.28839 | 60.2921 | -0.041199 | -0.064087 | 0.064087 | 0.018311 | -0.036621 | 0.28839 | -0.16937 | 0.35248 | -0.10529 | 0.32501 | 123.2803 | 0.027466 | 123.3215 | 123.555 | 123.3673 | 123.3078 | 123.3032 | -123.4863 | -123.3032 | 123.0331 | 123.2574 | 60.0632 | 60.0174
103.4844 | 123.3582 | -60.0952 | 63.1622 | -0.03479 | 0.00098907 | 0.062925 | 0.064331 | -0.0012967 | 7.0582e-05 | 0.00032907 | 0.004242 | 0.00074988 | 0.06749 | 0.065627 | 0.0008204 | -0.0012348 | 0.0022323 | 0.009155 | 63.2034 | -60.3104 | 62.9288 | -60.022 | -60.3516 | 0.07782 | 0.018311 | 63.208 | -60.173 | 63.1439 | -60.1135 | -60.2051 | -59.8251 | -0.21515 | 0.041199 | -0.23346 | 0.073242 | 60.173 | -0.25635 | 60.3882 | -0.041198 | -0.07782 | 0.045777 | -0.01831 | -0.01831 | 0.27008 | -0.10986 | 0.3479 | -0.032043 | 0.28839 | 123.2391 | 0.05951 | 123.317 | 123.5138 | 123.381 | 123.2986 | 123.3032 | -123.4726 | -123.3353 | 123.024 | 123.2391 | 60.1044 | 60.1135
104.5469 | 123.3261 | -60.1044 | 63.121 | -0.050049 | 0.00034827 | 0.066129 | 0.065826 | -0.0032193 | -0.00035682 | -0.0013799 | -0.10867 | 0.0013907 | 0.06749 | 0.071822 | -3.4196e-05 | 0.001115 | 0.0013779 | -0.07782 | 63.1668 | -60.3607 | 62.8876 | -60.0403 | -60.4111 | -0.091553 | -0.082397 | 63.1897 | -60.1822 | 63.1256 | -60.1639 | -60.2829 | -59.8343 | -0.25635 | 0.045776 | -0.23346 | 0.064087 | 60.0128 | -0.3067 | 60.2692 | -0.050354 | -0.07782 | 0.068664 | 0.004577 | -0.059509 | 0.27008 | -0.17853 | 0.3479 | -0.10071 | 0.32043 | 123.2483 | 0.018311 | 123.3078 | 123.5275 | 123.3719 | 123.2712 | 123.2941 | -123.4818 | -123.3032 | 122.9919 | 123.23 | 60.0266 | 60.022
105.4844 | 123.4909 | -60.0449 | 63.1027 | -0.080566 | -0.00029273 | 0.062925 | 0.062408 | -0.00065586 | 0.0017794 | -0.0015935 | 0.034759 | 0.00010888 | 0.068131 | 0.060287 | 0.001034 | -0.0012348 | -0.00011754 | -0.013733 | 63.176 | -60.3104 | 63.0203 | -59.9258 | -60.2509 | 0.091553 | 0.11444 | 63.1393 | -60.1501 | 63.2492 | -59.9854 | -60.0815 | -59.7015 | -0.2655 | 0.073242 | -0.082397 | 0.11902 | 60.1364 | -0.20599 | 60.4019 | 0.05951 | -0.10529 | 0.036621 | 0.14648 | 0.059509 | 0.34332 | -0.036621 | 0.44861 | 0.068664 | 0.38452 | 123.3307 | 0.16479 | 123.3994 | 123.4863 | 123.2895 | 123.2208 | 123.1842 | -123.4131 | -123.2529 | 123.0652 | 123.2941 | 60.0311 | 60.1593
106.4844 | 123.5229 | -60.0494 | 63.1027 | -0.03479 | 0.00098907 | 0.062925 | 0.064331 | -0.00086946 | -0.00014322 | 0.0020379 | 0.013397 | 0.00032248 | 0.065354 | 0.060287 | 0.000393 | -0.0018756 | -0.0016129 | -0.009155 | 63.1668 | -60.3241 | 63.0295 | -59.8846 | -60.2554 | 0.09613 | 0.15106 | 63.1485 | -60.1318 | 63.2584 | -59.9854 | -60.0723 | -59.6832 | -0.27466 | 0.064087 | -0.073242 | 0.16479 | 60.1456 | -0.20599 | 60.4202 | 0.068665 | -0.082398 | 0.045777 | 0.15564 | 0.064086 | 0.36621 | -0.022889 | 0.44861 | 0.059509 | 0.43945 | 123.3536 | 0.14648 | 123.3902 | 123.4909 | 123.2803 | 123.2162 | 123.1979 | -123.4268 | -123.2346 | 123.0789 | 123.3078 | 60.0403 | 60.2005
107.4844 | 123.3719 | -60.0723 | 63.1485 | -0.050049 | 0.00077547 | 0.063993 | 0.062835 | 0.0021213 | 0.0013522 | -0.0024481 | -0.0049134 | 0.00010888 | 0.064499 | 0.066054 | -0.0002478 | -0.00016658 | -0.0031081 | 0.041199 | 63.1851 | -60.3012 | 62.9929 | -59.9304 | -60.2737 | 0.091553 | 0.11444 | 63.1943 | -60.1456 | 63.1805 | -60.0632 | -60.1593 | -59.7519 | -0.22888 | 0.036621 | -0.15564 | 0.14191 | 60.1639 | -0.20142 | 60.3928 | 0.027465 | -0.073242 | 0.045776 | 0.032043 | 0.009156 | 0.32044 | -0.086975 | 0.39368 | -0.013733 | 0.37079 | 123.2941 | 0.082398 | 123.3261 | 123.4863 | 123.3398 | 123.2574 | 123.2666 | -123.4497 | -123.2941 | 123.0652 | 123.2529 | 60.1135 | 60.1868
108.5469 | 123.4314 | -60.0998 | 63.089 | -0.050049 | 0.00056187 | 0.065488 | 0.062835 | -0.00022866 | -0.00035682 | -9.8328e-05 | -0.011017 | 0.00096348 | 0.067276 | 0.070968 | -0.0019568 | 0.00090142 | -0.0011855 | -0.050354 | 63.1302 | -60.3287 | 62.9791 | -59.9396 | -60.3516 | -0.032043 | -0.027466 | 63.1302 | -60.173 | 63.1851 | -60.0998 | -60.1868 | -59.7565 | -0.22888 | 0.041199 | -0.10986 | 0.16022 | 60.0677 | -0.25177 | 60.2966 | -0.022888 | -0.073243 | 0.041199 | 0.096131 | 0 | 0.34332 | -0.086976 | 0.41656 | -0.013733 | 0.3891 | 123.3078 | 0.073243 | 123.3582 | 123.4589 | 123.3032 | 123.23 | 123.23 | -123.4177 | -123.262 | 123.0789 | 123.2849 | 60.0494 | 60.0723
109.4844 | 123.3582 | -60.0677 | 63.1668 | -0.065308 | 0.00034827 | 0.06442 | 0.064544 | -0.0023649 | -0.0016384 | 0.00054267 | -0.01712 | -0.00053192 | 0.066208 | 0.062209 | -0.0008886 | 0.00068782 | 0.0011643 | 0.032043 | 63.176 | -60.2921 | 62.97 | -59.9442 | -60.2875 | 0.091553 | 0.10986 | 63.1714 | -60.1364 | 63.1531 | -60.0769 | -60.1868 | -59.7839 | -0.2243 | 0.009155 | -0.19684 | 0.1236 | 60.1593 | -0.21973 | 60.3836 | 0.004577 | -0.068665 | 0.004578 | -0.013733 | -0.009155 | 0.28381 | -0.11902 | 0.35248 | -0.050354 | 0.3479 | 123.262 | 0.05951 | 123.2895 | 123.468 | 123.3078 | 123.2437 | 123.2391 | -123.4589 | -123.3032 | 123.0377 | 123.2208 | 60.0998 | 60.1776
110.5469 | 123.3398 | -60.1181 | 63.0844 | -0.088196 | 0.00013467 | 0.06207 | 0.062622 | -0.0034329 | -0.0016384 | 0.0011835 | -0.096466 | 0.0011771 | 0.066849 | 0.066054 | -0.0002478 | 0.00026062 | 0.00030966 | -0.10986 | 63.2034 | -60.4065 | 62.8189 | -60.054 | -60.347 | -0.11444 | -0.14648 | 63.1805 | -60.2051 | 63.1348 | -60.1913 | -60.2829 | -59.8389 | -0.28839 | 0.11902 | -0.2655 | 0.064087 | 60.0037 | -0.22888 | 60.2921 | 0.059509 | -0.086975 | 0.09613 | 0.050354 | -0.073242 | 0.27924 | -0.1648 | 0.36621 | -0.07782 | 0.35248 | 123.2254 | 0.013733 | 123.3398 | 123.6099 | 123.3856 | 123.3215 | 123.2986 | -123.4909 | -123.2895 | 122.937 | 123.2529 | 60.0082 | 59.9716
111.4844 | 123.3765 | -60.0632 | 63.1622 | -0.03479 | 0.0037661 | 0.062925 | 0.063049 | -1.486e-05 | 0.00092498 | 0.0028925 | -0.038483 | 0.00096348 | 0.065995 | 0.059218 | -0.0004614 | 0.00026062 | -0.0011855 | 0 | 63.2126 | -60.3424 | 62.915 | -60.0403 | -60.3561 | 0.013733 | -0.009155 | 63.208 | -60.1593 | 63.1577 | -60.1135 | -60.2234 | -59.7885 | -0.27924 | 0.050354 | -0.24719 | 0.022888 | 60.0769 | -0.29297 | 60.3561 | -0.013733 | -0.096131 | 0.045777 | -0.004577 | -0.050354 | 0.27466 | -0.16022 | 0.37079 | -0.064087 | 0.30212 | 123.2574 | 0.045777 | 123.317 | 123.555 | 123.3673 | 123.2758 | 123.2712 | -123.5046 | -123.3215 | 122.9782 | 123.2208 | 60.0632 | 60.054
112.5469 | 123.4314 | -60.0815 | 63.0981 | -0.088196 | 0.00077547 | 0.063779 | 0.061553 | -0.0040739 | -0.00035682 | 0.00075627 | 0.028656 | -0.00031832 | 0.068131 | 0.065627 | -0.002384 | -0.0020892 | -0.00075834 | -0.041199 | 63.1485 | -60.3195 | 62.9654 | -59.9625 | -60.3287 | 0.027466 | 0.009155 | 63.1302 | -60.1685 | 63.2172 | -60.0311 | -60.1273 | -59.7244 | -0.23804 | 0.050354 | -0.13275 | 0.11902 | 60.1089 | -0.24719 | 60.347 | -0.009155 | -0.086975 | 0.032043 | 0.11902 | 0.050354 | 0.35706 | -0.045776 | 0.44403 | 0.041199 | 0.35706 | 123.2849 | 0.13733 | 123.3856 | 123.468 | 123.2986 | 123.23 | 123.2117 | -123.4177 | -123.2666 | 123.0469 | 123.2986 | 60.0403 | 60.0906
113.4844 | 123.3582 | -60.0723 | 63.1302 | 0.049133 | 0.0012027 | 0.064847 | 0.062622 | 0.00019874 | -0.00014322 | 0.0016107 | -0.029327 | 0.0028861 | 0.069412 | 0.065414 | -0.0015296 | -0.00080758 | 0.0013779 | 0.032043 | 63.1897 | -60.3195 | 62.9471 | -59.9762 | -60.3287 | 0.054932 | 0.045776 | 63.1805 | -60.1685 | 63.1393 | -60.0861 | -60.2142 | -59.8114 | -0.24719 | 0.059509 | -0.1831 | 0.096131 | 60.1273 | -0.25635 | 60.3745 | -0.009155 | -0.09613 | 0.050354 | 0.009155 | -0.013733 | 0.26093 | -0.14191 | 0.35706 | -0.045776 | 0.34332 | 123.2666 | 0.082397 | 123.3078 | 123.5092 | 123.349 | 123.262 | 123.2529 | -123.4497 | -123.2986 | 123.0194 | 123.2117 | 60.1044 | 60.1181
114.4844 | 123.4406 | -60.054 | 63.1439 | -0.027161 | 0.00034827 | 0.062498 | 0.064117 | -0.00086946 | 0.0013522 | -0.0020209 | 0.0011902 | -0.00053192 | 0.06984 | 0.061782 | -0.0015296 | -0.0029438 | -0.0039627 | 0.027466 | 63.1577 | -60.3104 | 63.0203 | -59.903 | -60.2509 | 0.091553 | 0.13733 | 63.1851 | -60.1593 | 63.208 | -60.0266 | -60.1181 | -59.7153 | -0.25635 | 0.013733 | -0.1236 | 0.15106 | 60.1456 | -0.19684 | 60.4019 | 0.05951 | -0.10529 | 0.041199 | 0.064087 | 0.027466 | 0.33874 | -0.064087 | 0.44403 | 0.041199 | 0.40741 | 123.3307 | 0.13275 | 123.3673 | 123.468 | 123.3444 | 123.2117 | 123.2391 | -123.4543 | -123.3032 | 123.0743 | 123.262 | 60.0815 | 60.1913
115.4844 | 123.3902 | -60.0677 | 63.1577 | -0.011902 | -0.00029273 | 0.060148 | 0.06369 | -0.0021513 | -0.00014322 | 0.00032907 | -0.069 | -0.00031832 | 0.069199 | 0.067123 | -0.0015296 | 0.00026062 | 0.0013779 | -0.018311 | 63.1943 | -60.347 | 62.9333 | -60.022 | -60.3378 | 0.004578 | 0.032043 | 63.2172 | -60.1776 | 63.1668 | -60.0998 | -60.2005 | -59.7748 | -0.27924 | 0.036621 | -0.2243 | 0.045776 | 60.0723 | -0.27008 | 60.3516 | 0.009155 | -0.10986 | 0.059509 | 0.009155 | -0.032043 | 0.29297 | -0.13275 | 0.40283 | -0.022888 | 0.32501 | 123.2803 | 0.07782 | 123.3444 | 123.5413 | 123.3948 | 123.262 | 123.2849 | -123.5046 | -123.3353 | 123.0011 | 123.2346 | 60.0494 | 60.0998
116.4844 | 123.4131 | -60.0769 | 63.1348 | -0.050049 | 0.0014163 | 0.064634 | 0.062622 | -0.0025785 | 0.002634 | -9.8328e-05 | 0.028656 | 0.0020315 | 0.06749 | 0.064559 | 0.0001794 | -0.00038018 | 0.0015915 | 0.036621 | 63.1851 | -60.2966 | 63.0203 | -59.8984 | -60.2417 | 0.10529 | 0.11902 | 63.1897 | -60.1501 | 63.176 | -60.0266 | -60.1501 | -59.7336 | -0.21973 | 0.050354 | -0.11444 | 0.17853 | 60.1822 | -0.16479 | 60.4019 | 0.054932 | -0.073242 | 0.054931 | 0.041198 | 0.050354 | 0.34332 | -0.073242 | 0.41656 | 0 | 0.39825 | 123.317 | 0.1236 | 123.3261 | 123.4818 | 123.3398 | 123.262 | 123.2666 | -123.4314 | -123.2849 | 123.0972 | 123.2529 | 60.1135 | 60.1959
117.5469 | 123.4314 | -60.0723 | 63.1393 | -0.12634 | 0.00056187 | 0.062498 | 0.062622 | -0.00044226 | 0.00071138 | -0.0054389 | 0.040863 | 0.0011771 | 0.069412 | 0.068191 | 0.0001794 | 0.0015424 | 0.00030966 | 0.041199 | 63.1485 | -60.3241 | 63.0203 | -59.8801 | -60.2463 | 0.10071 | 0.13733 | 63.1805 | -60.141 | 63.2263 | -60.0082 | -60.1044 | -59.7198 | -0.25177 | 0.009156 | -0.11902 | 0.19226 | 60.173 | -0.17395 | 60.4248 | 0.07782 | -0.068664 | 0.041199 | 0.086975 | 0.064087 | 0.35248 | -0.032043 | 0.42114 | 0.036621 | 0.44403 | 123.3444 | 0.13275 | 123.3673 | 123.4726 | 123.3215 | 123.2208 | 123.2529 | -123.4634 | -123.2803 | 123.0927 | 123.2986 | 60.1135 | 60.2097
118.4844 | 123.4406 | -60.0723 | 63.1256 | -0.057678 | -0.0011471 | 0.066984 | 0.064117 | -0.0036465 | 0.0022068 | -0.0018073 | 0.034759 | -0.00031832 | 0.067704 | 0.063705 | -0.001316 | 4.7018e-05 | -0.0024673 | 0.10071 | 63.208 | -60.2646 | 62.9562 | -59.8984 | -60.1913 | 0.068665 | 0.14648 | 63.1531 | -60.1135 | 63.2355 | -60.0082 | -60.1089 | -59.7015 | -0.19226 | 0.082398 | -0.16937 | 0.17395 | 60.141 | -0.11902 | 60.3333 | 0.073242 | -0.041198 | 0.027466 | 0.10986 | 0.064087 | 0.37079 | -0.036621 | 0.41199 | 0.004577 | 0.36621 | 123.2208 | 0.10529 | 123.349 | 123.4726 | 123.2666 | 123.2803 | 123.2254 | -123.3902 | -123.2391 | 123.0286 | 123.3078 | 60.173 | 60.2188
119.4844 | 123.3948 | -60.0769 | 63.1393 | 0.026245 | 0.0022709 | 0.065275 | 0.063262 | -0.00022866 | -0.001852 | -0.0015935 | -0.059845 | -0.00053192 | 0.067917 | 0.06755 | -0.0017432 | -0.00038018 | -0.0022537 | 0 | 63.1989 | -60.3424 | 62.9608 | -60.0037 | -60.3333 | 0.018311 | 0.064087 | 63.208 | -60.1822 | 63.1805 | -60.0952 | -60.2051 | -59.761 | -0.2655 | 0.05951 | -0.17853 | 0.073242 | 60.0952 | -0.25635 | 60.3607 | 0.009155 | -0.10529 | 0.068665 | 0.041199 | -0.018311 | 0.31586 | -0.12817 | 0.42114 | -0.022888 | 0.33875 | 123.3032 | 0.086975 | 123.3627 | 123.5413 | 123.3902 | 123.2758 | 123.2849 | -123.4818 | -123.3215 | 123.0377 | 123.2574 | 60.0769 | 60.141
120.5469 | 123.436 | -60.0494 | 63.0981 | -0.065308 | 0.00077547 | 0.064207 | 0.062408 | -0.00086946 | 0.00092498 | -0.00052553 | 0.031708 | -0.00053192 | 0.067704 | 0.066695 | -3.4196e-05 | -0.00059378 | 9.6064e-05 | -0.059509 | 63.1668 | -60.3241 | 62.9562 | -59.9991 | -60.3333 | 0.018311 | -0.032043 | 63.1485 | -60.1685 | 63.1897 | -60.0586 | -60.1501 | -59.729 | -0.27466 | 0.068664 | -0.14191 | 0.050354 | 60.0677 | -0.28381 | 60.3424 | -0.009155 | -0.11902 | 0.050354 | 0.091552 | -0.009156 | 0.32043 | -0.10071 | 0.43945 | 0.018311 | 0.32501 | 123.2803 | 0.10986 | 123.3582 | 123.4909 | 123.317 | 123.2162 | 123.1979 | -123.4222 | -123.2666 | 123.0057 | 123.2391 | 59.9899 | 60.0174
121.4844 | 123.3902 | -60.0861 | 63.1348 | -0.03479 | 0.00098907 | 0.06442 | 0.064544 | -0.00065586 | -0.00014322 | 0.0011835 | -0.072052 | 0.0022453 | 0.066849 | 0.066909 | -0.0004614 | -0.00038018 | -0.0024673 | 0.004578 | 63.208 | -60.3378 | 62.9517 | -59.9991 | -60.3287 | 0.022888 | 0.054932 | 63.2126 | -60.1639 | 63.1897 | -60.0906 | -60.1959 | -59.7839 | -0.25177 | 0.073242 | -0.18311 | 0.086976 | 60.1089 | -0.24261 | 60.3607 | 0.009156 | -0.077819 | 0.077819 | 0.054931 | -0.004577 | 0.30212 | -0.10986 | 0.37994 | -0.032044 | 0.33875 | 123.2895 | 0.073242 | 123.3536 | 123.5458 | 123.3765 | 123.2941 | 123.2986 | -123.4726 | -123.2986 | 123.0377 | 123.2758 | 60.0906 | 60.141
122.5469 | 123.468 | -60.0906 | 63.089 | -0.10345 | 0.0016299 | 0.064207 | 0.063476 | -0.00022866 | -0.0012112 | 0.00096987 | -0.0049134 | -0.00010472 | 0.067276 | 0.061782 | -0.0008886 | -0.00016658 | -0.00097194 | -0.059509 | 63.1165 | -60.3333 | 62.9791 | -59.9579 | -60.3195 | -0.022888 | -0.018311 | 63.121 | -60.1868 | 63.1989 | -60.0677 | -60.1593 | -59.729 | -0.24262 | 0.027466 | -0.10986 | 0.13275 | 60.0677 | -0.22888 | 60.3104 | 0.013733 | -0.096131 | 0.032044 | 0.10986 | 0.022888 | 0.36163 | -0.068665 | 0.45776 | 0.027466 | 0.37537 | 123.3124 | 0.11902 | 123.3856 | 123.4497 | 123.3078 | 123.2071 | 123.2117 | -123.4222 | -123.2758 | 123.0698 | 123.2895 | 60.0311 | 60.0723
123.4844 | 123.4039 | -60.0906 | 63.1393 | -0.080566 | 0.00098907 | 0.06442 | 0.060485 | 0.0048983 | -0.0012112 | -0.00073913 | -0.078156 | 0.00010888 | 0.068558 | 0.064132 | -0.0011022 | 0.0013288 | -0.00054474 | -0.009155 | 63.1851 | -60.3516 | 62.9929 | -59.9899 | -60.2829 | 0.009155 | 0.045776 | 63.1851 | -60.1639 | 63.1622 | -60.1227 | -60.2142 | -59.7931 | -0.26093 | 0.045777 | -0.14648 | 0.10071 | 60.0998 | -0.19226 | 60.3607 | 0.068664 | -0.073242 | 0.045777 | 0.022888 | -0.032044 | 0.29755 | -0.1236 | 0.37079 | -0.050354 | 0.36163 | 123.3444 | 0.041198 | 123.3261 | 123.5367 | 123.349 | 123.2758 | 123.2758 | -123.4909 | -123.3032 | 123.0835 | 123.2529 | 60.0815 | 60.1364
124.4844 | 123.3627 | -60.0952 | 63.1302 | -0.019531 | -0.0015743 | 0.060789 | 0.063049 | -0.00044226 | -0.0029202 | 0.00096987 | -0.029327 | 0.00096348 | 0.068558 | 0.068618 | -0.0017432 | -0.00016658 | 0.00095066 | -0.018311 | 63.2309 | -60.3424 | 62.9379 | -60.0266 | -60.3516 | 0.009155 | 0.036621 | 63.2263 | -60.1639 | 63.1668 | -60.0815 | -60.2142 | -59.7839 | -0.24719 | 0.10071 | -0.19226 | 0.068665 | 60.1044 | -0.25635 | 60.3516 | -0.009155 | -0.068664 | 0.09613 | 0.036621 | 0.013733 | 0.31128 | -0.11902 | 0.37994 | -0.050354 | 0.31586 | 123.2803 | 0.082397 | 123.3307 | 123.5733 | 123.3902 | 123.3261 | 123.3215 | -123.4726 | -123.2941 | 123.0331 | 123.262 | 60.0769 | 60.1318
125.4844 | 123.349 | -60.0906 | 63.1302 | -0.027161 | 0.0012027 | 0.063138 | 0.064117 | 0.0012667 | 0.0022068 | 0.0016107 | -0.044586 | 0.00096348 | 0.070267 | 0.064986 | -0.0008886 | -0.00038018 | -0.00097194 | -0.027466 | 63.2217 | -60.347 | 62.915 | -60.0311 | -60.3561 | 0 | 0.004578 | 63.1989 | -60.1593 | 63.1714 | -60.0952 | -60.2097 | -59.7656 | -0.25635 | 0.091553 | -0.21515 | 0.059509 | 60.0906 | -0.2655 | 60.347 | -0.009155 | -0.068665 | 0.068665 | 0.041199 | -0.004578 | 0.32501 | -0.11902 | 0.39368 | -0.050354 | 0.31586 | 123.262 | 0.064087 | 123.3307 | 123.5687 | 123.3582 | 123.3124 | 123.2895 | -123.4772 | -123.2895 | 123.0057 | 123.262 | 60.0632 | 60.0952
126.4844 | 123.3353 | -60.1135 | 63.1577 | -0.019531 | 0.00098907 | 0.062711 | 0.061981 | -0.0021513 | 0.00092498 | -0.00031193 | 0.0011902 | 0.00053628 | 0.068558 | 0.066909 | 0.0014612 | 0.00068782 | -0.0018265 | 0 | 63.2217 | -60.3241 | 62.8967 | -59.9625 | -60.3058 | 0.022888 | 0.045776 | 63.2172 | -60.1593 | 63.1302 | -60.0998 | -60.228 | -59.8297 | -0.21057 | 0.064087 | -0.26093 | 0.15106 | 60.1364 | -0.19226 | 60.347 | 0.018311 | -0.045777 | 0.059509 | -0.027466 | 0.013733 | 0.28381 | -0.11444 | 0.32959 | -0.068664 | 0.36163 | 123.2208 | 0.05951 | 123.2895 | 123.5458 | 123.3765 | 123.3353 | 123.3307 | -123.4818 | -123.317 | 123.0103 | 123.2437 | 60.1135 | 60.1593
127.4844 | 123.3536 | -60.1044 | 63.1302 | -0.042419 | 0.0018435 | 0.06442 | 0.064758 | 0.0027621 | 0.00092498 | 0.00032907 | -0.059845 | 0.0013907 | 0.067704 | 0.06755 | 0.000393 | 0.00047422 | 0.0013779 | -0.013733 | 63.176 | -60.3561 | 62.9425 | -60.0037 | -60.3561 | -0.018311 | 0.018311 | 63.176 | -60.1776 | 63.1622 | -60.1273 | -60.2371 | -59.7931 | -0.25177 | 0.045776 | -0.18768 | 0.10071 | 60.0861 | -0.25177 | 60.3378 | 0 | -0.073242 | 0.045776 | 0.032043 | -0.022888 | 0.31128 | -0.13275 | 0.38452 | -0.05951 | 0.35248 | 123.2986 | 0.050354 | 123.3398 | 123.5321 | 123.3536 | 123.2803 | 123.2803 | -123.4863 | -123.3078 | 123.0469 | 123.2666 | 60.0906 | 60.1227
128.5469 | 123.4131 | -60.0769 | 63.0615 | -0.072937 | 0.0020573 | 0.063566 | 0.062194 | -0.00065586 | 0.00092498 | -0.0018073 | 0.0011902 | 0.00074988 | 0.068772 | 0.059432 | 0.0012476 | -0.001662 | -0.0024673 | -0.054932 | 63.1439 | -60.3287 | 62.97 | -59.9304 | -60.3195 | -0.022888 | -0.036621 | 63.1073 | -60.173 | 63.1805 | -60.0952 | -60.173 | -59.7519 | -0.25177 | 0.082398 | -0.091552 | 0.14648 | 60.054 | -0.24262 | 60.3058 | 0.009155 | -0.096131 | 0.045777 | 0.11902 | -0.018311 | 0.32501 | -0.096131 | 0.42114 | 0 | 0.39825 | 123.2986 | 0.07782 | 123.3536 | 123.4726 | 123.2803 | 123.2208 | 123.1842 | -123.3902 | -123.2346 | 123.0469 | 123.2574 | 60.022 | 60.0403
129.4844 | 123.3398 | -60.1135 | 63.1256 | -0.050049 | 0.0012027 | 0.063566 | 0.065399 | 0.0023349 | 0.0013522 | 0.0020379 | -0.056793 | 0.0018179 | 0.068131 | 0.068191 | -0.0004614 | 0.0013288 | 0.0022323 | -0.032043 | 63.1897 | -60.3516 | 62.9059 | -59.9991 | -60.3699 | -0.045776 | -0.018311 | 63.1851 | -60.1639 | 63.1302 | -60.1501 | -60.26 | -59.8068 | -0.23804 | 0.064087 | -0.21973 | 0.11444 | 60.0677 | -0.25635 | 60.3058 | -0.018311 | -0.050354 | 0.05951 | 0.004578 | -0.036621 | 0.3067 | -0.14648 | 0.35706 | -0.096131 | 0.35248 | 123.2574 | 0.013733 | 123.2941 | 123.5413 | 123.349 | 123.3032 | 123.2986 | -123.4772 | -123.2895 | 123.0194 | 123.2437 | 60.0815 | 60.0952
130.5469 | 123.4314 | -60.0906 | 63.0707 | -0.065308 | 0.00056187 | 0.06442 | 0.061981 | -0.0015103 | 0.0019932 | -0.0018073 | 0.05307 | 0.00010888 | 0.068131 | 0.061568 | -0.0008886 | -0.00080758 | 0.0013779 | -0.068665 | 63.1668 | -60.347 | 62.9333 | -59.9808 | -60.3195 | -0.004578 | -0.004578 | 63.1485 | -60.1639 | 63.1989 | -60.054 | -60.1364 | -59.729 | -0.25635 | 0.09613 | -0.13733 | 0.10986 | 60.0861 | -0.22888 | 60.3424 | 0.027466 | -0.073242 | 0.07782 | 0.12817 | 0.036621 | 0.36163 | -0.045777 | 0.43487 | 0.027465 | 0.36621 | 123.2803 | 0.10986 | 123.3627 | 123.5138 | 123.3124 | 123.2574 | 123.2391 | -123.4177 | -123.2346 | 123.024 | 123.2895 | 60.022 | 60.0861
131.4844 | 123.2941 | -60.1456 | 63.1073 | -0.057678 | 0.0018435 | 0.064207 | 0.064971 | -0.00065586 | -0.00099762 | -9.8328e-05 | -0.062897 | 0.00053628 | 0.069412 | 0.063064 | -0.0015296 | -0.001662 | 0.00095066 | -0.086975 | 63.1897 | -60.3699 | 62.883 | -60.0677 | -60.4614 | -0.11902 | -0.14648 | 63.176 | -60.2097 | 63.0707 | -60.2234 | -60.3333 | -59.8618 | -0.2243 | 0.082397 | -0.2243 | 0.07782 | 60.0266 | -0.31586 | 60.2509 | -0.091553 | -0.064087 | 0.068664 | -0.036621 | -0.07782 | 0.28381 | -0.18768 | 0.3479 | -0.1236 | 0.30212 | 123.2529 | -0.013733 | 123.2803 | 123.5596 | 123.3856 | 123.3353 | 123.3215 | -123.4772 | -123.317 | 123.0286 | 123.2162 | 60.0586 | 59.9991
132.5625 | 123.4497 | -60.0952 | 63.0615 | -0.03479 | 0.0014163 | 0.063993 | 0.06604 | 0.0031893 | -0.0014248 | -0.0015935 | -0.038483 | 0.0013907 | 0.066422 | 0.066482 | -0.0021704 | 0.00068782 | -0.0041763 | -0.11902 | 63.1485 | -60.3378 | 62.9105 | -60.0174 | -60.379 | -0.082397 | -0.07782 | 63.1393 | -60.1822 | 63.1897 | -60.0723 | -60.1776 | -59.7244 | -0.24261 | 0.086976 | -0.15106 | 0.07782 | 60.0128 | -0.28381 | 60.2554 | -0.041198 | -0.086975 | 0.07782 | 0.12817 | 0.022888 | 0.37079 | -0.082397 | 0.45776 | 0.004578 | 0.32043 | 123.2483 | 0.10986 | 123.3719 | 123.4863 | 123.3215 | 123.2437 | 123.2346 | -123.3994 | -123.2437 | 123.0057 | 123.2849 | 59.9762 | 60.0174
133.4844 | 123.3353 | -60.1227 | 63.1119 | -0.027161 | 0.00098907 | 0.06442 | 0.065612 | -0.00044226 | -0.00078402 | 0.0024653 | -0.059845 | 0.00032248 | 0.068558 | 0.067336 | -0.002384 | 0.0019696 | -0.0013991 | -0.041199 | 63.1805 | -60.3745 | 62.8876 | -60.0311 | -60.3882 | -0.068665 | -0.064087 | 63.1668 | -60.1868 | 63.1165 | -60.1501 | -60.2646 | -59.8114 | -0.25177 | 0.068665 | -0.2243 | 0.091553 | 60.054 | -0.2655 | 60.3058 | -0.013733 | -0.064087 | 0.054932 | 0.004578 | -0.027465 | 0.31128 | -0.14191 | 0.37537 | -0.077819 | 0.34332 | 123.262 | 0.036622 | 123.3032 | 123.555 | 123.3536 | 123.3032 | 123.2895 | -123.4863 | -123.2986 | 123.0103 | 123.2391 | 60.0815 | 60.0586
134.4844 | 123.4039 | -60.0906 | 63.1256 | -0.065308 | -0.0011471 | 0.065275 | 0.063476 | 0.0042575 | -0.002493 | -0.00052553 | -0.059845 | 0.00096348 | 0.06984 | 0.061141 | -0.0017432 | 0.00047422 | 0.0039413 | -0.018311 | 63.1943 | -60.3653 | 62.8372 | -59.848 | -60.3287 | 0 | 0.009155 | 63.1989 | -60.1868 | 63.1805 | -60.1135 | -60.2188 | -59.7885 | -0.27466 | 0.068665 | -0.28839 | 0.24262 | 60.0906 | -0.23804 | 60.3653 | 0.036621 | -0.096131 | 0.073243 | 0.054932 | -0.022888 | 0.30212 | -0.12817 | 0.39825 | -0.032043 | 0.51727 | 123.2025 | 0.073243 | 123.3673 | 123.5596 | 123.3856 | 123.2849 | 123.2895 | -123.4909 | -123.3124 | 122.9279 | 123.2712 | 60.0723 | 60.0998
135.5625 | 123.3627 | -60.0998 | 63.121 | -0.011902 | 0.00034827 | 0.063779 | 0.064544 | -1.486e-05 | 0.0011386 | 0.00096987 | -0.062897 | 0.00074988 | 0.068985 | 0.0652 | 0.0012476 | 0.00068782 | 9.6064e-05 | -0.11902 | 63.1851 | -60.3882 | 62.8326 | -60.0998 | -60.4477 | -0.11902 | -0.16937 | 63.176 | -60.2051 | 63.2629 | -60.173 | -60.2875 | -59.8114 | -0.28839 | 0.064087 | -0.28839 | 0 | 59.9808 | -0.3479 | 60.2692 | -0.059509 | -0.10529 | 0.054931 | 0.14191 | -0.073243 | 0.28839 | -0.18768 | 0.39368 | -0.082398 | 0.28839 | 123.2208 | 0.032043 | 123.468 | 123.5733 | 123.381 | 123.2849 | 123.2758 | -123.5092 | -123.3261 | 122.9324 | 123.3627 | 59.9808 | 59.9304
136.4844 | 123.381 | -60.0769 | 63.1027 | -0.057678 | -0.00050633 | 0.065061 | 0.063476 | 0.0023349 | -0.00057042 | 0.0016107 | -0.056793 | 0.00074988 | 0.068558 | 0.066268 | -0.0011022 | -0.00059378 | -0.0048171 | -0.027466 | 63.208 | -60.3653 | 62.97 | -59.9854 | -60.3333 | -0.022888 | 0.022888 | 63.1943 | -60.1593 | 63.1485 | -60.1227 | -60.228 | -59.7794 | -0.28839 | 0.10529 | -0.13275 | 0.091552 | 60.054 | -0.25635 | 60.3424 | 0.032043 | -0.082398 | 0.091553 | 0.045777 | -0.045777 | 0.29755 | -0.15106 | 0.37994 | -0.068664 | 0.37994 | 123.3353 | 0.036621 | 123.3078 | 123.5733 | 123.3536 | 123.2849 | 123.2712 | -123.468 | -123.262 | 123.0469 | 123.2254 | 60.0494 | 60.0998
137.5 | 123.4268 | -60.0952 | 63.0569 | -0.019531 | 0.00056187 | 0.064847 | 0.063262 | -0.0025785 | -0.00014322 | -0.0022345 | 0.12631 | 0.00053628 | 0.067063 | 0.060287 | -0.0004614 | -0.0025164 | 0.0060777 | -0.091553 | 63.1714 | -60.3195 | 62.9288 | -59.9945 | -60.3333 | 0.004578 | -0.12817 | 63.1119 | -60.173 | 63.1714 | -60.0723 | -60.173 | -59.761 | -0.2243 | 0.11444 | -0.12817 | 0.10071 | 60.0998 | -0.23804 | 60.3241 | -0.013733 | -0.07782 | 0.054931 | 0.11444 | 0.022888 | 0.33417 | -0.07782 | 0.41199 | 0 | 0.32501 | 123.2483 | 0.10071 | 123.3444 | 123.4909 | 123.2849 | 123.2666 | 123.2071 | -123.3765 | -123.23 | 123.024 | 123.2666 | 60.0037 | 59.967
138.4844 | 123.3536 | -60.1135 | 63.0981 | -0.3476 | -0.0011471 | 0.062284 | 0.062194 | 0.00062594 | 0.0013522 | 0.0016107 | -0.044586 | 0.0022453 | 0.067704 | 0.069472 | -0.0017432 | 0.001115 | -0.0016129 | 0.050354 | 63.1943 | -60.3607 | 62.9288 | -59.9899 | -60.3378 | -0.013733 | 0.022888 | 63.1577 | -60.1822 | 63.1577 | -60.1227 | -60.2188 | -59.7794 | -0.24719 | 0.09613 | -0.16937 | 0.1236 | 60.0998 | -0.2243 | 60.347 | 0.022888 | -0.068665 | 0.059509 | 0.059509 | -0.009156 | 0.33417 | -0.10529 | 0.40283 | -0.036621 | 0.37079 | 123.2895 | 0.059509 | 123.3398 | 123.555 | 123.3398 | 123.3078 | 123.2712 | -123.4589 | -123.2803 | 123.0423 | 123.2712 | 60.1639 | 60.1364
139.5781 | 123.4955 | -60.0494 | 63.0936 | -0.027161 | 0.00013467 | 0.063138 | 0.062194 | -0.0010831 | -0.0012112 | -0.00095273 | 0.062225 | 0.00053628 | 0.068131 | 0.065627 | -0.0017432 | -0.0012348 | -0.0028945 | -0.027466 | 63.1485 | -60.3287 | 62.9929 | -59.8892 | -60.2554 | 0.091553 | 0.091553 | 63.1485 | -60.1501 | 63.2538 | -59.9808 | -60.054 | -59.6832 | -0.27924 | 0.054932 | -0.10071 | 0.16022 | 60.141 | -0.20599 | 60.4202 | 0.073242 | -0.10071 | 0.054932 | 0.16022 | 0.068664 | 0.36621 | -0.004578 | 0.46692 | 0.09613 | 0.43945 | 123.3215 | 0.16937 | 123.4039 | 123.4772 | 123.2986 | 123.1979 | 123.1979 | -123.4222 | -123.2437 | 123.0423 | 123.3032 | 60.022 | 60.141
140.5 | 123.349 | -60.0769 | 63.1485 | -0.019531 | -0.00029273 | 0.062925 | 0.062835 | 0.0010531 | -0.00078402 | 0.00054267 | -0.014069 | -0.00031832 | 0.06749 | 0.063277 | -0.0011022 | 0.00047422 | 0.00073706 | -0.041199 | 63.208 | -60.3607 | 62.9013 | -60.0494 | -60.3561 | 0.027466 | 0.004578 | 63.1989 | -60.141 | 63.1256 | -60.1044 | -60.2188 | -59.7931 | -0.28381 | 0.059509 | -0.24719 | 0.027466 | 60.1044 | -0.27924 | 60.3882 | 0.004578 | -0.064087 | 0.050354 | -0.022889 | -0.027466 | 0.28381 | -0.14191 | 0.3479 | -0.07782 | 0.31128 | 123.262 | 0.036621 | 123.2666 | 123.5687 | 123.3398 | 123.2849 | 123.2758 | -123.5092 | -123.2895 | 122.9782 | 123.2025 | 60.0357 | 60.0815
141.4844 | 123.3032 | -60.1593 | 63.089 | -0.088196 | 0.0020573 | 0.062284 | 0.063903 | 0.0014803 | 0.00028418 | -0.00095273 | -0.053741 | 0.0020315 | 0.065995 | 0.069259 | -0.0008886 | 0.00090142 | 0.0011643 | -0.10986 | 63.1805 | -60.3836 | 62.851 | -60.1318 | -60.4614 | -0.10986 | -0.16479 | 63.1577 | -60.2188 | 63.1073 | -60.1913 | -60.5576 | -60.1227 | -0.2243 | 0.091553 | -0.23804 | 0.027466 | 60.0494 | -0.30212 | 60.2737 | -0.07782 | -0.059509 | 0.068665 | 0.018311 | -0.032043 | 0.036621 | -0.39825 | 0.09613 | -0.33874 | 0.25177 | 123.2346 | 0.027466 | 123.3261 | 123.5641 | 123.3765 | 123.3398 | 123.317 | -123.4726 | -123.3078 | 123.0103 | 123.2666 | 60.0494 | 59.9945
142.5469 | 123.3856 | -60.0815 | 63.1165 | -0.050049 | -7.913e-05 | 0.063993 | 0.065185 | -0.0025785 | 0.00049778 | 0.0016107 | -0.044586 | 0.0011771 | 0.068772 | 0.070327 | -0.000675 | -0.00038018 | 0.00030966 | -0.022888 | 63.2034 | -60.3241 | 62.9288 | -60.0037 | -60.3424 | 0.013733 | 0.036621 | 63.1805 | -60.1822 | 63.0386 | -59.9579 | -60.2234 | -59.7702 | -0.24262 | 0.086975 | -0.18768 | 0.07782 | 60.0952 | -0.26093 | 60.3378 | -0.01831 | -0.10071 | 0.064087 | -0.07782 | 0.1236 | 0.31128 | -0.14191 | 0.41199 | -0.041199 | 0.32044 | 123.2529 | 0.2243 | 123.2208 | 123.5275 | 123.3627 | 123.2849 | 123.262 | -123.4406 | -123.2986 | 123.0103 | 123.1201 | 60.0586 | 60.1181
143.4844 | 123.4589 | -60.0815 | 63.0707 | -0.065308 | -0.00029273 | 0.065702 | 0.062408 | 0.0019077 | 7.0582e-05 | -9.8328e-05 | -0.029327 | 0.00010888 | 0.068985 | 0.060714 | -0.0015296 | -0.0012348 | 0.00073706 | -0.091553 | 63.1348 | -60.3561 | 62.9196 | -59.9899 | -60.3699 | -0.068665 | -0.059509 | 63.1348 | -60.1959 | 63.1851 | -60.0906 | -60.1822 | -59.7198 | -0.27466 | 0.064087 | -0.15106 | 0.091553 | 60.0128 | -0.28839 | 60.2875 | -0.013733 | -0.11444 | 0.064087 | 0.11444 | -0.009155 | 0.36163 | -0.10071 | 0.47607 | 0.013733 | 0.36621 | 123.2758 | 0.10529 | 123.381 | 123.4909 | 123.3307 | 123.2162 | 123.2162 | -123.4268 | -123.2666 | 123.0011 | 123.2666 | 59.9899 | 60.022
144.4844 | 123.3307 | -60.1089 | 63.1256 | -0.050049 | 0.0012027 | 0.061857 | 0.064117 | 0.0023349 | 0.00028418 | -9.8328e-05 | -0.047638 | 0.0020315 | 0.06749 | 0.061996 | -0.0008886 | 0.00068782 | 0.00030966 | -0.082397 | 63.1851 | -60.347 | 62.8784 | -60.0449 | -60.4156 | -0.091553 | -0.09613 | 63.1943 | -60.1959 | 63.121 | -60.1685 | -60.2783 | -59.8206 | -0.23804 | 0.05951 | -0.24719 | 0.064087 | 60.0174 | -0.3067 | 60.2554 | -0.068664 | -0.086975 | 0.068665 | -0.004577 | -0.059509 | 0.28839 | -0.16937 | 0.37537 | -0.082397 | 0.30212 | 123.2254 | 0.027466 | 123.317 | 123.5321 | 123.3902 | 123.2941 | 123.3032 | -123.4726 | -123.3215 | 122.9874 | 123.23 | 60.0266 | 60.0128
145.4844 | 123.436 | -60.0769 | 63.0615 | -0.080566 | 0.0029117 | 0.065061 | 0.061981 | 0.0010531 | 0.00092498 | 0.0013971 | -0.01712 | -0.00031832 | 0.067704 | 0.068404 | 0.0006066 | 0.00026062 | 9.6064e-05 | -0.1236 | 63.1622 | -60.3745 | 62.9059 | -60.022 | -60.3516 | -0.07782 | -0.091553 | 63.1348 | -60.2097 | 63.1714 | -60.0677 | -60.1501 | -59.7336 | -0.29755 | 0.10071 | -0.15564 | 0.054931 | 59.9991 | -0.27466 | 60.2966 | 0.022889 | -0.13275 | 0.073243 | 0.10986 | 0.009155 | 0.34332 | -0.073242 | 0.47607 | 0.05951 | 0.35248 | 123.2803 | 0.14191 | 123.381 | 123.5367 | 123.3444 | 123.2391 | 123.2117 | -123.436 | -123.2712 | 122.9828 | 123.2483 | 59.9533 | 59.9854
146.5469 | 123.3536 | -60.0861 | 63.1668 | -0.011902 | -7.913e-05 | 0.060789 | 0.063476 | -0.00022866 | 0.00028418 | -0.0013799 | -0.0018616 | 0.00096348 | 0.067276 | 0.060714 | 0.0006066 | -0.0010212 | 0.00052346 | 0.082397 | 63.2858 | -60.3241 | 62.915 | -60.0769 | -60.3516 | 0.027466 | 0 | 63.1897 | -60.1593 | 63.1256 | -60.1089 | -60.2371 | -59.7885 | -0.23804 | 0.11902 | -0.25177 | 0.009156 | 60.1135 | -0.2655 | 60.3516 | -0.027465 | -0.073242 | 0.022888 | -0.041199 | -0.022888 | 0.29755 | -0.15106 | 0.37079 | -0.07782 | 0.24719 | 123.2391 | 0.050354 | 123.2849 | 123.6099 | 123.349 | 123.3719 | 123.2758 | -123.4909 | -123.3261 | 123.0011 | 123.2117 | 60.1685 | 60.0861
147.5 | 123.468 | -60.0769 | 63.0981 | -0.050049 | -0.00029273 | 0.06143 | 0.062835 | -0.0010831 | 0.00071138 | -0.0026617 | 0.059174 | -0.00010472 | 0.069626 | 0.064773 | -0.0021704 | -0.001662 | -0.00011754 | -0.013733 | 63.1439 | -60.3195 | 63.002 | -59.8709 | -60.2463 | 0.10529 | 0.13733 | 63.1393 | -60.1318 | 63.2584 | -59.9899 | -60.0769 | -59.6786 | -0.24262 | 0.045776 | -0.096131 | 0.20599 | 60.1822 | -0.16937 | 60.4248 | 0.073242 | -0.054932 | 0.041198 | 0.16022 | 0.086975 | 0.39825 | 0 | 0.45319 | 0.054932 | 0.44861 | 123.3215 | 0.14191 | 123.3902 | 123.4634 | 123.2712 | 123.2208 | 123.2162 | -123.4177 | -123.23 | 123.0789 | 123.3353 | 60.0632 | 60.2142
148.4844 | 123.3124 | -60.1318 | 63.121 | -0.080566 | 0.00034827 | 0.063779 | 0.06369 | -0.00086946 | 0.0011386 | 0.0028925 | -0.065949 | 0.00053628 | 0.067704 | 0.068831 | -0.0008886 | -0.00080758 | 9.6064e-05 | -0.11444 | 63.1851 | -60.3745 | 62.8418 | -60.1318 | -60.4568 | -0.13733 | -0.15564 | 63.1622 | -60.1868 | 63.0981 | -60.1959 | -60.3012 | -59.8434 | -0.24262 | 0.064087 | -0.27924 | 0 | 59.9945 | -0.32501 | 60.2371 | -0.082397 | -0.054932 | 0.041198 | -0.022888 | -0.064087 | 0.28839 | -0.16937 | 0.34332 | -0.11444 | 0.24262 | 123.2162 | -0.009155 | 123.2849 | 123.5596 | 123.349 | 123.317 | 123.2941 | -123.4955 | -123.3078 | 122.9736 | 123.23 | 60.0174 | 59.9762
149.5469 | 123.3765 | -60.0723 | 63.1393 | 0.018616 | -0.00071993 | 0.063993 | 0.064758 | 0.0027621 | -0.00099762 | 0.0041743 | -0.041534 | 0.0020315 | 0.068131 | 0.070754 | -0.0011022 | -0.00080758 | 0.0018051 | 0.009155 | 63.176 | -60.3149 | 62.9196 | -59.9762 | -60.3241 | 0.022888 | 0.059509 | 63.1851 | -60.1776 | 63.1622 | -60.0906 | -60.1959 | -59.7656 | -0.24261 | 0.036621 | -0.21973 | 0.096131 | 60.0952 | -0.25177 | 60.3378 | -0.009156 | -0.10529 | 0.045777 | 0.022888 | -0.01831 | 0.3067 | -0.1236 | 0.41199 | -0.018311 | 0.33874 | 123.2346 | 0.086975 | 123.3398 | 123.4909 | 123.3627 | 123.2483 | 123.2574 | -123.4543 | -123.317 | 122.9919 | 123.2346 | 60.0815 | 60.1318
150.4844 | 123.2941 | -60.0906 | 63.0981 | -0.057678 | 0.00034827 | 0.062284 | 0.064331 | 0.0031893 | -0.00057042 | 0.0020379 | -0.032379 | 0.00032248 | 0.068131 | 0.065627 | -0.000675 | -0.00080758 | -0.00097194 | -0.086975 | 63.1805 | -60.3836 | 62.8281 | -60.0677 | -60.4431 | -0.12817 | -0.17853 | 63.1577 | -60.2005 | 63.0844 | -60.2188 | -60.3241 | -59.8526 | -0.29297 | 0.082397 | -0.27008 | 0.022888 | 59.9625 | -0.35248 | 60.2554 | -0.059509 | -0.10986 | 0.059509 | -0.013733 | -0.12817 | 0.23804 | -0.23346 | 0.3479 | -0.1236 | 0.31586 | 123.2117 | -0.018311 | 123.2849 | 123.5641 | 123.3582 | 123.2712 | 123.2483 | -123.4818 | -123.2986 | 122.9187 | 123.175 | 60.0037 | 59.9121
151.5469 | 123.3398 | -60.1273 | 63.0981 | -0.057678 | 0.00034827 | 0.063566 | 0.065399 | 0.00041234 | -0.0027066 | -0.00052553 | -0.05069 | 0.0020315 | 0.068558 | 0.065841 | 0.0006066 | -0.00059378 | -0.0043899 | -0.09613 | 63.1897 | -60.379 | 62.8464 | -60.1135 | -60.466 | -0.13733 | -0.17395 | 63.1485 | -60.2234 | 63.1073 | -60.1868 | -60.3195 | -59.8251 | -0.25177 | 0.091552 | -0.25177 | 0.013733 | 59.9899 | -0.33875 | 60.2417 | -0.086975 | -0.096131 | 0.050354 | 0.009155 | -0.05951 | 0.30212 | -0.19226 | 0.39825 | -0.09613 | 0.2655 | 123.2254 | 0.036621 | 123.3307 | 123.5687 | 123.3719 | 123.317 | 123.2758 | -123.4772 | -123.3215 | 122.9736 | 123.2346 | 60.0311 | 59.9533
152.4844 | 123.4497 | -60.0723 | 63.0478 | -0.042419 | 0.0041935 | 0.065916 | 0.060699 | 0.0010531 | 0.00071138 | 0.0020379 | 0.025604 | -0.0013863 | 0.06749 | 0.065627 | -0.000675 | -0.0010212 | -0.00011754 | -0.059509 | 63.0981 | -60.3424 | 62.9242 | -59.9167 | -60.2875 | -0.027466 | -0.027466 | 63.1256 | -60.1639 | 63.208 | -60.054 | -60.1593 | -59.7244 | -0.27008 | 0.050354 | -0.1236 | 0.15564 | 60.0449 | -0.21515 | 60.3149 | 0.054931 | -0.091552 | 0.077819 | 0.16022 | 0.018311 | 0.3479 | -0.086975 | 0.43945 | 0.004577 | 0.42572 | 123.2666 | 0.10986 | 123.3719 | 123.4406 | 123.2895 | 123.1705 | 123.1979 | -123.3902 | -123.2117 | 122.9965 | 123.2803 | 60.0128 | 60.0449
153.5469 | 123.4222 | -60.054 | 63.1027 | -0.15686 | 0.00013467 | 0.061857 | 0.061981 | -0.00065586 | 0.00071138 | -0.0015935 | 0.046967 | -0.00074552 | 0.066849 | 0.066268 | -0.0021704 | -0.0020892 | -0.0011855 | 0.050354 | 63.1805 | -60.3012 | 63.002 | -59.9075 | -60.2463 | 0.10529 | 0.1236 | 63.1531 | -60.1089 | 63.2217 | -60.0311 | -60.1089 | -59.7153 | -0.24719 | 0.07782 | -0.10071 | 0.14648 | 60.1593 | -0.19226 | 60.4065 | 0.054931 | -0.054932 | 0.050354 | 0.11902 | 0.022888 | 0.33874 | -0.054932 | 0.39368 | 0 | 0.39368 | 123.3032 | 0.07782 | 123.3307 | 123.4818 | 123.262 | 123.2346 | 123.2071 | -123.4039 | -123.2117 | 123.056 | 123.2758 | 60.1044 | 60.1776
154.4844 | 123.4589 | -60.0723 | 63.0753 | -0.057678 | 0.00013467 | 0.065275 | 0.061767 | -0.0015103 | 0.00071138 | -0.0024481 | -0.0049134 | 0.00032248 | 0.065781 | 0.066695 | -0.0032386 | 0.00026062 | -0.0011855 | -0.082397 | 63.1485 | -60.3607 | 62.9562 | -59.9396 | -60.4294 | -0.09613 | -0.059509 | 63.1393 | -60.173 | 63.2034 | -60.0677 | -60.1593 | -59.7061 | -0.28839 | 0.073243 | -0.11902 | 0.13275 | 59.9762 | -0.35705 | 60.2646 | -0.068664 | -0.10071 | 0.064087 | 0.12817 | 0.004578 | 0.36621 | -0.086975 | 0.46692 | 0.013733 | 0.42114 | 123.317 | 0.10529 | 123.3765 | 123.5092 | 123.3124 | 123.2208 | 123.2117 | -123.436 | -123.2483 | 123.0286 | 123.2758 | 59.9899 | 60.0128
155.4844 | 123.4451 | -60.0815 | 63.0432 | -0.080566 | 0.0012027 | 0.065488 | 0.063262 | 0.0038303 | -0.0027066 | -0.0026617 | -0.020172 | 0.00074988 | 0.067063 | 0.071395 | -0.0017432 | -0.0014484 | -0.00011754 | -0.10529 | 63.1577 | -60.3653 | 62.9471 | -59.9854 | -60.3745 | -0.073242 | -0.050354 | 63.121 | -60.1868 | 63.2034 | -60.0906 | -60.1593 | -59.7107 | -0.28381 | 0.11444 | -0.09613 | 0.09613 | 60.0082 | -0.29297 | 60.2921 | -0.009156 | -0.10529 | 0.07782 | 0.16022 | -0.009155 | 0.37079 | -0.07782 | 0.47608 | 0.027466 | 0.37994 | 123.3124 | 0.096131 | 123.3902 | 123.5229 | 123.3078 | 123.2391 | 123.2025 | -123.4085 | -123.23 | 123.0286 | 123.2849 | 59.9762 | 60.0311
156.5469 | 123.468 | -60.0266 | 63.121 | -0.057678 | 0.0018435 | 0.065061 | 0.061767 | -0.0032193 | -0.00078402 | -0.00095273 | 0.022552 | -0.0018137 | 0.06749 | 0.065414 | -0.0015296 | -0.00059378 | 0.0030869 | -0.004578 | 63.1668 | -60.2966 | 63.0341 | -59.8709 | -60.2097 | 0.13275 | 0.14648 | 63.176 | -60.1501 | 63.2217 | -59.9762 | -60.0723 | -59.6832 | -0.27008 | 0.045776 | -0.086975 | 0.15564 | 60.1593 | -0.18311 | 60.4294 | 0.086975 | -0.1236 | 0.054931 | 0.10071 | 0.050354 | 0.34332 | -0.045777 | 0.46692 | 0.077819 | 0.42572 | 123.3307 | 0.17395 | 123.3719 | 123.4634 | 123.3261 | 123.1934 | 123.2025 | -123.4177 | -123.2712 | 123.0606 | 123.2483 | 60.022 | 60.173
157.4844 | 123.4406 | -60.054 | 63.0661 | -0.072937 | 0.00098907 | 0.063993 | 0.062835 | -0.0038603 | 0.00092498 | -0.0015935 | -0.026276 | 0.00096348 | 0.069199 | 0.070754 | -0.0015296 | -0.00038018 | -0.0050307 | -0.054932 | 63.1302 | -60.3333 | 62.9791 | -59.9442 | -60.3149 | -0.032043 | -0.27924 | 63.089 | -60.2097 | 63.208 | -60.0494 | -60.1364 | -59.7061 | -0.27924 | 0.064087 | -0.086975 | 0.10986 | 60.022 | -0.26093 | 60.3012 | 0.018311 | -0.15564 | 0.022888 | 0.14191 | 0.004578 | 0.3479 | -0.082398 | 0.50354 | 0.073242 | 0.3891 | 123.3124 | 0.16022 | 123.4177 | 123.4634 | 123.2986 | 123.1842 | 123.143 | -123.3994 | -123.2758 | 123.0331 | 123.262 | 59.9991 | 59.7748
158.5469 | 123.3536 | -60.0769 | 63.1256 | -0.019531 | 0.0018435 | 0.064207 | 0.063903 | -0.0010831 | 0.00092498 | -0.00052553 | -0.059845 | 0.0016043 | 0.067276 | 0.061355 | -0.0015296 | 0.0013288 | -0.0020401 | -0.027466 | 63.1897 | -60.3607 | 62.9333 | -60.0037 | -60.379 | -0.041199 | -0.041199 | 63.1714 | -60.1822 | 63.121 | -60.1456 | -60.2509 | -59.8114 | -0.28381 | 0.064087 | -0.19226 | 0.073242 | 60.0357 | -0.30212 | 60.3195 | -0.01831 | -0.10529 | 0.045777 | -0.004577 | -0.068665 | 0.2655 | -0.17395 | 0.37079 | -0.068664 | 0.35706 | 123.2941 | 0.036621 | 123.3032 | 123.5504 | 123.3536 | 123.2666 | 123.2483 | -123.4863 | -123.3078 | 123.0103 | 123.1979 | 60.0494 | 60.0357
159.4844 | 123.436 | -60.0677 | 63.0569 | -0.10345 | 0.0024845 | 0.063993 | 0.063476 | -0.0015103 | 0.0015658 | 0.00011527 | -0.047638 | -0.00031832 | 0.06514 | 0.064773 | -0.001316 | 0.00090142 | 0.00095066 | -0.11444 | 63.1485 | -60.3607 | 62.9379 | -60.0082 | -60.3333 | -0.064087 | -0.064087 | 63.121 | -60.2051 | 63.2034 | -60.0586 | -60.1913 | -59.729 | -0.29297 | 0.091553 | -0.11902 | 0.059509 | 60.0037 | -0.2655 | 60.2966 | 0.027466 | -0.13733 | 0.064087 | 0.14648 | 0.009155 | 0.33874 | -0.1236 | 0.47607 | 0.013733 | 0.35248 | 123.2986 | 0.14648 | 123.4085 | 123.5092 | 123.3261 | 123.2162 | 123.1888 | -123.4177 | -123.262 | 123.0057 | 123.2712 | 59.9533 | 60.0037
160.4844 | 123.3215 | -60.1273 | 63.0936 | -0.03479 | 0.00034827 | 0.067197 | 0.064331 | 0.0016939 | 0.0013522 | 0.0020379 | -0.075104 | -0.00031832 | 0.067063 | 0.073531 | -0.0021704 | 0.00026062 | -0.0028945 | -0.073242 | 63.1943 | -60.3607 | 62.8922 | -60.0403 | -60.4202 | -0.082397 | -0.1236 | 63.1851 | -60.1913 | 63.0936 | -60.1547 | -60.3195 | -59.8434 | -0.23346 | 0.10071 | -0.20142 | 0.086975 | 60.0449 | -0.29297 | 60.2783 | -0.059509 | -0.064087 | 0.091553 | 0 | -0.027466 | 0.28381 | -0.19226 | 0.3479 | -0.12817 | 0.32043 | 123.2529 | 0.036621 | 123.2849 | 123.555 | 123.3765 | 123.3215 | 123.3124 | -123.4543 | -123.2849 | 123.0194 | 123.2208 | 60.054 | 60.0037
161.5469 | 123.3124 | -60.1364 | 63.1119 | -0.050049 | 0.0014163 | 0.063993 | 0.064544 | -0.0015103 | -0.00099762 | -0.0030889 | -0.065949 | 0.00053628 | 0.067276 | 0.067123 | -0.001316 | -0.0012348 | 0.0056503 | -0.09613 | 63.2034 | -60.3653 | 62.851 | -60.0815 | -60.4294 | -0.09613 | -0.16479 | 63.176 | -60.1913 | 63.0936 | -60.2005 | -60.3012 | -59.8663 | -0.22888 | 0.091553 | -0.26093 | 0.054932 | 60.0403 | -0.29297 | 60.2692 | -0.064087 | -0.054931 | 0.064087 | -0.01831 | -0.064086 | 0.27008 | -0.16479 | 0.32501 | -0.10986 | 0.28381 | 123.2162 | -0.009155 | 123.2849 | 123.5687 | 123.3673 | 123.3398 | 123.3124 | -123.4772 | -123.3032 | 122.9874 | 123.23 | 60.0403 | 59.9716
162.4844 | 123.3582 | -60.1181 | 63.0615 | -0.12634 | 0.0012027 | 0.063138 | 0.065185 | -0.0027921 | -0.00035682 | 0.0026789 | -0.038483 | 0.00053628 | 0.067276 | 0.064345 | 0.000393 | 4.7018e-05 | -0.00033114 | -0.045776 | 63.1805 | -60.3607 | 62.8738 | -60.0815 | -60.4431 | -0.10986 | -0.15106 | 63.1393 | -60.2005 | 63.1165 | -60.1593 | -60.2646 | -59.8022 | -0.24262 | 0.11902 | -0.18768 | 0.036621 | 60.0082 | -0.32501 | 60.2509 | -0.082397 | -0.082397 | 0.07782 | 0.054932 | -0.041199 | 0.31586 | -0.14648 | 0.39825 | -0.064087 | 0.27924 | 123.2346 | 0.041198 | 123.317 | 123.5413 | 123.3398 | 123.2986 | 123.2574 | -123.4222 | -123.262 | 122.9919 | 123.2346 | 60.0723 | 59.967
163.4844 | 123.4085 | -60.0815 | 63.0798 | -0.088196 | 0.00077547 | 0.06442 | 0.061767 | 0.00041234 | 0.00049778 | 0.0024653 | 0.019501 | -0.0028817 | 0.066849 | 0.059646 | -0.0019568 | -0.001662 | 0.0024461 | -0.068665 | 63.1531 | -60.3378 | 62.9608 | -59.9442 | -60.3195 | -0.036621 | -0.027466 | 63.089 | -60.1639 | 63.1989 | -60.0723 | -60.1822 | -59.7427 | -0.25635 | 0.073242 | -0.11902 | 0.13733 | 60.0449 | -0.23804 | 60.3012 | 0.018311 | -0.082397 | 0.009155 | 0.11902 | 0.009155 | 0.33875 | -0.10071 | 0.42114 | -0.018311 | 0.39368 | 123.2986 | 0.091552 | 123.3627 | 123.4909 | 123.2529 | 123.2346 | 123.1705 | -123.4177 | -123.2437 | 123.0423 | 123.2803 | 60.0128 | 60.054
164.4844 | 123.3536 | -60.0998 | 63.0707 | -0.13397 | -0.00050633 | 0.063779 | 0.065612 | -0.0021513 | -0.0014248 | -9.8328e-05 | -0.035431 | 0.0020315 | 0.06749 | 0.058578 | 0.0001794 | 4.7018e-05 | 0.0033005 | -0.050354 | 63.1897 | -60.3607 | 62.8693 | -60.0677 | -60.4294 | -0.13275 | -0.15106 | 63.1714 | -60.2051 | 63.1119 | -60.1547 | -60.2646 | -59.8114 | -0.26093 | 0.11902 | -0.20142 | 0.032043 | 59.967 | -0.32959 | 60.228 | -0.068664 | -0.10529 | 0.10071 | 0.041198 | -0.054932 | 0.28839 | -0.16479 | 0.39368 | -0.059509 | 0.29297 | 123.23 | 0.050354 | 123.317 | 123.5504 | 123.3765 | 123.2895 | 123.2712 | -123.4314 | -123.2758 | 122.9691 | 123.2117 | 60.0494 | 59.9487
165.5469 | 123.3948 | -60.0769 | 63.1302 | -0.03479 | -0.00050633 | 0.063779 | 0.064117 | -0.0012967 | -0.0033474 | 0.00075627 | -0.038483 | 0.00096348 | 0.066635 | 0.063918 | -0.002384 | -0.00059378 | 0.0015915 | -0.013733 | 63.2217 | -60.3195 | 62.9333 | -59.9991 | -60.3195 | 0.036621 | 0.041199 | 63.176 | -60.1593 | 63.176 | -60.0723 | -60.1959 | -59.7748 | -0.24262 | 0.091553 | -0.19684 | 0.07782 | 60.1135 | -0.24262 | 60.3561 | 0 | -0.082398 | 0.045776 | 0.045776 | 0.004577 | 0.30212 | -0.11902 | 0.38452 | -0.036621 | 0.32043 | 123.2529 | 0.086975 | 123.3353 | 123.5413 | 123.3353 | 123.2986 | 123.2529 | -123.4497 | -123.2895 | 123.0103 | 123.2529 | 60.0632 | 60.1181
166.4844 | 123.4314 | -60.1456 | 63.0707 | -0.065308 | -0.00029273 | 0.06442 | 0.064758 | 0.0053255 | 0.00049778 | 0.0022517 | -0.047638 | 0.00074988 | 0.070053 | 0.068404 | 0.0001794 | -0.00016658 | -0.0011855 | -0.12817 | 63.1805 | -60.3836 | 62.8189 | -60.1273 | -60.4568 | -0.11902 | -0.17853 | 63.1485 | -60.2188 | 63.0981 | -60.1685 | -60.2921 | -59.8343 | -0.23804 | 0.10986 | -0.25177 | 0.018311 | 60.0266 | -0.31128 | 60.2646 | -0.073242 | -0.073242 | 0.07782 | 0.027466 | -0.022888 | 0.31128 | -0.14648 | 0.38452 | -0.073242 | 0.25635 | 123.2025 | 0.050354 | 123.317 | 123.5641 | 123.3673 | 123.3261 | 123.2941 | -123.4543 | -123.2895 | 122.9645 | 123.2437 | 60.0174 | 59.967
167.4844 | 123.4543 | -60.0815 | 63.0661 | -0.095825 | 0.0024845 | 0.062498 | 0.063903 | 0.0048983 | 0.0015658 | 0.0013971 | -0.01712 | 0.00032248 | 0.066849 | 0.069472 | -0.000675 | -0.0035846 | 0.00073706 | -0.10071 | 63.1439 | -60.3561 | 62.9425 | -59.9899 | -60.3561 | -0.045776 | -0.027466 | 63.1348 | -60.1822 | 63.1897 | -60.0449 | -60.1685 | -59.7336 | -0.27466 | 0.07782 | -0.1236 | 0.091553 | 60.0357 | -0.27466 | 60.3104 | 0 | -0.10071 | 0.068665 | 0.1236 | 0.036621 | 0.3479 | -0.086975 | 0.44861 | 0.013733 | 0.36621 | 123.2986 | 0.13733 | 123.3719 | 123.5001 | 123.317 | 123.2254 | 123.2162 | -123.4222 | -123.2483 | 123.024 | 123.2712 | 59.9808 | 60.054
168.5469 | 123.4222 | -60.1089 | 63.089 | -0.03479 | 0.0031253 | 0.065061 | 0.062408 | 0.0016939 | -0.0020658 | -0.0035163 | -0.059845 | 0.00096348 | 0.068131 | 0.072677 | -0.000675 | 0.00026062 | -0.00075834 | -0.13275 | 63.1348 | -60.379 | 62.8784 | -60.054 | -60.4202 | -0.10071 | -0.13733 | 63.1393 | -60.2005 | 63.1439 | -60.1135 | -60.228 | -59.7702 | -0.27008 | 0.045777 | -0.21057 | 0.054932 | 60.0082 | -0.31128 | 60.2783 | -0.041199 | -0.091552 | 0.050354 | 0.054932 | -0.004577 | 0.33874 | -0.11902 | 0.4303 | -0.027466 | 0.32501 | 123.2574 | 0.086975 | 123.3444 | 123.5138 | 123.3398 | 123.2437 | 123.2483 | -123.468 | -123.2895 | 122.9874 | 123.2529 | 59.9762 | 59.9716
169.4844 | 123.4085 | -60.0677 | 63.0753 | -0.072937 | -0.00071993 | 0.06207 | 0.06134 | -0.0010831 | 0.0011386 | -0.0022345 | 0.025604 | 0.00074988 | 0.068131 | 0.063705 | -0.000675 | -0.0012348 | -0.0011855 | -0.07782 | 63.1393 | -60.3287 | 62.9425 | -59.9533 | -60.3378 | -0.041199 | -0.045776 | 63.1073 | -60.1822 | 63.1805 | -60.0906 | -60.1776 | -59.7519 | -0.26093 | 0.064087 | -0.13275 | 0.11444 | 60.0266 | -0.27008 | 60.2875 | -0.009156 | -0.11444 | 0.032044 | 0.10529 | -0.022888 | 0.31586 | -0.10986 | 0.4303 | 0.004578 | 0.37537 | 123.2712 | 0.091553 | 123.3627 | 123.468 | 123.2895 | 123.2071 | 123.175 | -123.4039 | -123.2574 | 123.0103 | 123.2483 | 59.9899 | 60.022
170.4844 | 123.4772 | -60.0677 | 63.0524 | -0.11871 | 0.00034827 | 0.064634 | 0.063903 | 0.0012667 | 0.00049778 | 0.0018243 | -0.0079652 | 0.00053628 | 0.066635 | 0.065414 | -0.0017432 | -0.00059378 | 0.00095066 | -0.082397 | 63.1393 | -60.3653 | 62.9562 | -59.9716 | -60.3882 | -0.082397 | -0.059509 | 63.089 | -60.1776 | 63.2126 | -60.0677 | -60.1593 | -59.7107 | -0.29755 | 0.086975 | -0.09613 | 0.09613 | 59.9854 | -0.32044 | 60.2829 | -0.022889 | -0.10986 | 0.036621 | 0.16022 | 0 | 0.35706 | -0.091553 | 0.46692 | 0.01831 | 0.39368 | 123.3215 | 0.10986 | 123.3902 | 123.5046 | 123.2666 | 123.2071 | 123.1567 | -123.4177 | -123.23 | 123.024 | 123.2803 | 59.9854 | 60.0082
171.5469 | 123.3078 | -60.1273 | 63.089 | -0.011902 | -0.00050633 | 0.063352 | 0.063262 | 0.0031893 | -0.00057042 | 0.00032907 | -0.069 | 0.00096348 | 0.068772 | 0.069472 | -0.002384 | -0.00038018 | 0.0013779 | -0.091553 | 63.1897 | -60.3745 | 62.8555 | -60.1089 | -60.4568 | -0.12817 | -0.18768 | 63.1531 | -60.2051 | 63.0798 | -60.2005 | -60.2966 | -59.848 | -0.24719 | 0.10071 | -0.23346 | 0.01831 | 59.9991 | -0.32959 | 60.2463 | -0.082397 | -0.07782 | 0.064087 | -0.009155 | -0.073242 | 0.27924 | -0.16937 | 0.35706 | -0.091553 | 0.2655 | 123.23 | 0.004578 | 123.2849 | 123.5641 | 123.3582 | 123.317 | 123.2803 | -123.4634 | -123.2941 | 122.9828 | 123.2071 | 60.0357 | 59.9396
172.4844 | 123.4451 | -60.0998 | 63.0753 | -0.080566 | 0.0014163 | 0.064207 | 0.064971 | -0.0015103 | 0.0030612 | 0.00096987 | -0.01712 | 0.00010888 | 0.066849 | 0.069259 | 0.000393 | -0.00059378 | -0.0013991 | -0.082397 | 63.1531 | -60.347 | 62.9562 | -59.9396 | -60.3241 | -0.054932 | -0.045776 | 63.1073 | -60.1776 | 63.208 | -60.0632 | -60.1593 | -59.7061 | -0.24719 | 0.07782 | -0.11902 | 0.16022 | 60.0449 | -0.22431 | 60.2921 | 0.022888 | -0.07782 | 0.032044 | 0.13275 | 0.036621 | 0.39368 | -0.05951 | 0.4715 | 0.01831 | 0.40741 | 123.3032 | 0.11444 | 123.3856 | 123.5001 | 123.2849 | 123.2529 | 123.2071 | -123.4222 | -123.2529 | 123.056 | 123.3078 | 60.0174 | 60.054
173.4844 | 123.4222 | -60.0815 | 63.0661 | -0.057678 | -0.00029273 | 0.065488 | 0.061767 | -0.00086946 | -0.00078402 | -0.0015935 | 0.059174 | 0.00010888 | 0.065995 | 0.0652 | -0.0002478 | -0.0014484 | -0.0011855 | -0.091553 | 63.1531 | -60.3424 | 62.9288 | -59.9854 | -60.3287 | -0.009155 | -0.054932 | 63.1348 | -60.173 | 63.1577 | -60.0632 | -60.1822 | -59.761 | -0.26093 | 0.086975 | -0.13733 | 0.09613 | 60.0723 | -0.24719 | 60.3333 | 0.013733 | -0.091553 | 0.068665 | 0.091553 | 0.018311 | 0.32044 | -0.10071 | 0.41199 | -0.009155 | 0.35706 | 123.2712 | 0.10986 | 123.3307 | 123.4955 | 123.3078 | 123.2346 | 123.2162 | -123.4085 | -123.2391 | 123.0103 | 123.2391 | 59.9899 | 60.0266
174.4844 | 123.4222 | -60.0769 | 63.0753 | -0.10345 | 0.0018435 | 0.065061 | 0.065612 | -0.00044226 | 0.002634 | 0.0035333 | -0.0079652 | -0.0011727 | 0.067917 | 0.064559 | -0.0008886 | 0.001115 | 9.6064e-05 | -0.041199 | 63.1256 | -60.3516 | 62.97 | -59.9579 | -60.3424 | -0.036621 | -0.041199 | 63.1027 | -60.1593 | 63.208 | -60.0586 | -60.1547 | -59.7198 | -0.27466 | 0.050354 | -0.10529 | 0.11902 | 60.0403 | -0.2655 | 60.3149 | 0.009155 | -0.082398 | 0.027466 | 0.13275 | 0.01831 | 0.35705 | -0.07782 | 0.43945 | 0.004578 | 0.39368 | 123.3215 | 0.10071 | 123.3673 | 123.4772 | 123.262 | 123.2025 | 123.1796 | -123.4268 | -123.2346 | 123.0469 | 123.2849 | 60.0357 | 60.0357
175.5469 | 123.3536 | -60.0677 | 63.1165 | -0.072937 | 0.0012027 | 0.058866 | 0.062622 | 0.0034029 | 0.0019932 | 0.00011527 | -0.084259 | 0.0045951 | 0.066422 | 0.0699 | -0.0011022 | 4.7018e-05 | 0.0022323 | -0.16022 | 63.1302 | -60.3836 | 62.9196 | -60.0082 | -60.347 | -0.009155 | -0.004578 | 63.1989 | -60.173 | 63.1668 | -60.1181 | -60.2325 | -59.7794 | -0.31586 | 0.013733 | -0.19684 | 0.059509 | 60.0586 | -0.27924 | 60.3745 | 0.036621 | -0.10529 | 0.082398 | 0.050354 | -0.050354 | 0.28839 | -0.16479 | 0.39368 | -0.059509 | 0.37537 | 123.3032 | 0.054932 | 123.3398 | 123.5138 | 123.3719 | 123.1979 | 123.2666 | -123.5001 | -123.2895 | 122.9874 | 123.2346 | 59.9075 | 60.0632
176.4844 | 123.4268 | -60.0815 | 63.0478 | -0.095825 | 0.0012027 | 0.063993 | 0.060485 | -0.0010831 | 0.00071138 | -0.00095273 | 0.004242 | 0.00096348 | 0.067063 | 0.063491 | -0.0017432 | 0.00026062 | -0.00011754 | -0.064087 | 63.1165 | -60.3104 | 62.9562 | -59.9396 | -60.3149 | -0.027466 | -0.004578 | 63.1302 | -60.1593 | 63.1897 | -60.054 | -60.1593 | -59.7336 | -0.22888 | 0.068664 | -0.091553 | 0.14191 | 60.054 | -0.23346 | 60.2829 | -0.004577 | -0.07782 | 0.082397 | 0.14191 | 0.027466 | 0.3479 | -0.07782 | 0.42572 | 0 | 0.37079 | 123.2666 | 0.10529 | 123.349 | 123.4268 | 123.2895 | 123.1979 | 123.2117 | -123.3582 | -123.2071 | 123.0377 | 123.2712 | 60.0174 | 60.0769
177.5469 | 123.4497 | -60.0723 | 63.0569 | -0.080566 | 0.00013467 | 0.063779 | 0.063049 | -1.486e-05 | 0.00071138 | -0.00095273 | -0.014069 | -0.00074552 | 0.067276 | 0.060073 | -0.0034522 | -0.0014484 | 0.0011643 | -0.082397 | 63.1531 | -60.3607 | 62.9242 | -59.967 | -60.3241 | -0.054932 | -0.054932 | 63.1027 | -60.1547 | 63.2126 | -60.0586 | -60.1639 | -59.7198 | -0.28839 | 0.09613 | -0.13275 | 0.10529 | 60.0174 | -0.25177 | 60.3058 | 0.036621 | -0.082397 | 0.045776 | 0.15564 | 0.013733 | 0.35248 | -0.091552 | 0.43487 | -0.009155 | 0.39368 | 123.2849 | 0.09613 | 123.3673 | 123.5138 | 123.2574 | 123.2254 | 123.175 | -123.4177 | -123.2117 | 122.9965 | 123.2849 | 59.9899 | 60.0174
178.4844 | 123.4177 | -60.0952 | 63.0936 | -0.088196 | 0.00013467 | 0.066343 | 0.063049 | -1.486e-05 | 0.00071138 | 0.00096987 | 0.004242 | 0.00032248 | 0.068558 | 0.059218 | -0.0017432 | -0.0012348 | -0.00033114 | -0.082397 | 63.1393 | -60.3195 | 62.9517 | -59.9396 | -60.347 | -0.027466 | -0.032043 | 63.1348 | -60.1639 | 63.1805 | -60.0815 | -60.1913 | -59.7336 | -0.2243 | 0.045776 | -0.14191 | 0.15564 | 60.0677 | -0.25177 | 60.2921 | -0.027466 | -0.068664 | 0.041199 | 0.086975 | 0.013733 | 0.36163 | -0.09613 | 0.4303 | -0.027466 | 0.37994 | 123.2712 | 0.082397 | 123.3444 | 123.4589 | 123.2986 | 123.2346 | 123.23 | -123.4131 | -123.2574 | 123.0469 | 123.2758 | 60.0128 | 60.0632
179.4844 | 123.4634 | -60.0449 | 63.0753 | -0.072937 | 0.00077547 | 0.063566 | 0.061126 | -0.0012967 | 0.002634 | -0.0024481 | 0.046967 | -0.0020273 | 0.068131 | 0.067123 | -0.0008886 | -0.0018756 | -0.00011754 | -0.022888 | 63.1622 | -60.3104 | 62.9883 | -59.9258 | -60.2829 | 0.064087 | 0.068665 | 63.1577 | -60.1456 | 63.2401 | -60.0037 | -60.0998 | -59.697 | -0.2655 | 0.086975 | -0.086975 | 0.11902 | 60.1089 | -0.23804 | 60.3745 | 0.027466 | -0.10071 | 0.082398 | 0.16479 | 0.041199 | 0.3479 | -0.054931 | 0.44861 | 0.045777 | 0.38452 | 123.2986 | 0.14191 | 123.3856 | 123.4726 | 123.3032 | 123.2071 | 123.2025 | -123.3856 | -123.2208 | 123.0331 | 123.2849 | 60.022 | 60.1135
180.5469 | 123.349 | -60.0906 | 63.121 | -0.042419 | 0.0018435 | 0.064847 | 0.064331 | -0.0015103 | 0.00049778 | 0.00096987 | -0.065949 | -0.00010472 | 0.065354 | 0.072249 | -0.0025976 | 0.00026062 | 0.0033005 | -0.013733 | 63.2034 | -60.3378 | 62.9654 | -59.9716 | -60.347 | 0.009155 | 0.059509 | 63.1897 | -60.1547 | 63.1851 | -60.1089 | -60.2005 | -59.7839 | -0.24719 | 0.082397 | -0.15564 | 0.11902 | 60.0998 | -0.25635 | 60.347 | -0.009155 | -0.064087 | 0.068664 | 0.064087 | -0.018311 | 0.3067 | -0.10986 | 0.37079 | -0.045776 | 0.36621 | 123.3032 | 0.045776 | 123.3398 | 123.5413 | 123.3444 | 123.2941 | 123.2803 | -123.4589 | -123.2758 | 123.056 | 123.2758 | 60.0769 | 60.1501
181.4844 | 123.4589 | -60.0403 | 63.0936 | -0.050049 | -7.913e-05 | 0.06207 | 0.062408 | -0.00022866 | 0.0013522 | -0.0011663 | 0.046967 | -0.0011727 | 0.067063 | 0.066482 | -0.000675 | -0.0014484 | -0.0020401 | -0.004578 | 63.1622 | -60.3241 | 62.9745 | -59.9258 | -60.2692 | 0.082397 | 0.10986 | 63.1485 | -60.1318 | 63.2401 | -59.9579 | -60.0677 | -59.6878 | -0.28381 | 0.068664 | -0.11902 | 0.11444 | 60.1227 | -0.22888 | 60.4065 | 0.054932 | -0.091553 | 0.054932 | 0.14648 | 0.082397 | 0.35248 | -0.027466 | 0.44403 | 0.064087 | 0.39825 | 123.2986 | 0.17395 | 123.3719 | 123.4863 | 123.2803 | 123.2025 | 123.1888 | -123.4177 | -123.2254 | 123.0148 | 123.2803 | 60.0357 | 60.1501
182.4844 | 123.3994 | -60.0769 | 63.1165 | -0.088196 | 0.00077547 | 0.063566 | 0.06369 | 0.0014803 | -0.0033474 | -0.00073913 | 0.0011902 | 0.0020315 | 0.070908 | 0.061568 | -0.0002478 | -0.0029438 | 0.0026597 | -0.07782 | 63.1622 | -60.3241 | 62.9379 | -59.9854 | -60.3333 | -0.013733 | -0.036621 | 63.1348 | -60.1547 | 63.1622 | -60.0998 | -60.0311 | -59.6466 | -0.24719 | 0.045776 | -0.17853 | 0.091552 | 60.0632 | -0.25635 | 60.3104 | -0.009155 | -0.07782 | 0.018311 | 0.045776 | -0.022888 | 0.4303 | 0.045776 | 0.50812 | 0.1236 | 0.33875 | 123.262 | 0.054932 | 123.317 | 123.4863 | 123.2895 | 123.2391 | 123.2117 | -123.4406 | -123.2712 | 123.0148 | 123.2391 | 59.9991 | 60.0403
183.4844 | 123.4543 | -60.0311 | 63.121 | -0.095825 | 0.00034827 | 0.062711 | 0.062622 | -0.0012967 | 0.00028418 | -9.8328e-05 | 0.010345 | -0.00074552 | 0.070908 | 0.064986 | -0.002384 | -0.0010212 | -0.0033219 | 0 | 63.1622 | -60.3241 | 63.0066 | -59.8846 | -60.2325 | 0.10529 | 0.16022 | 63.1531 | -60.141 | 63.2584 | -59.9625 | -60.054 | -59.6741 | -0.29297 | 0.041198 | -0.11444 | 0.14648 | 60.1364 | -0.20142 | 60.4294 | 0.091553 | -0.10986 | 0.032043 | 0.13733 | 0.068665 | 0.35706 | -0.022888 | 0.46692 | 0.086975 | 0.43945 | 123.3307 | 0.17853 | 123.3994 | 123.4863 | 123.2941 | 123.1934 | 123.1842 | -123.4451 | -123.262 | 123.0377 | 123.2895 | 60.0311 | 60.1913
184.4844 | 123.4222 | -60.0769 | 63.0936 | -0.072937 | 0.00013467 | 0.062498 | 0.062622 | -0.00065586 | 0.00049778 | -9.8328e-05 | 0.0072936 | 0.0028861 | 0.066208 | 0.064773 | -0.0025976 | -0.0018756 | 0.0011643 | -0.059509 | 63.1439 | -60.3424 | 62.9471 | -59.9808 | -60.3333 | 0.082397 | -0.036621 | 63.1622 | -60.173 | 63.1622 | -60.0815 | -60.1639 | -59.7427 | -0.2655 | 0.050354 | -0.14648 | 0.09613 | 60.1593 | -0.25635 | 60.4248 | 0.009155 | -0.096131 | 0.068664 | 0.068664 | -0.004578 | 0.33417 | -0.086975 | 0.4303 | 0.009156 | 0.36163 | 123.2895 | 0.091553 | 123.3353 | 123.4863 | 123.3353 | 123.2208 | 123.2391 | -123.436 | -123.2666 | 123.024 | 123.2391 | 60.0174 | 60.0403
185.4844 | 123.4268 | -60.0494 | 63.0936 | -0.011902 | 0.0031253 | 0.063566 | 0.064544 | 0.0019077 | 0.0028476 | -9.8328e-05 | 0.034759 | -0.00053192 | 0.06514 | 0.061568 | -0.0017432 | 0.00026062 | 0.0035141 | 0.027466 | 63.1577 | -60.3149 | 63.0524 | -59.8526 | -60.2051 | 0.10529 | 0.14648 | 63.1485 | -60.1318 | 63.2446 | -59.9945 | -60.0861 | -59.6741 | -0.2655 | 0.064087 | -0.041199 | 0.19684 | 60.1547 | -0.15564 | 60.4202 | 0.10986 | -0.082398 | 0.054932 | 0.15106 | 0.054931 | 0.37537 | -0.036622 | 0.45776 | 0.045776 | 0.46234 | 123.3673 | 0.13733 | 123.3765 | 123.4726 | 123.2803 | 123.2071 | 123.1979 | -123.4085 | -123.2254 | 123.1018 | 123.2941 | 60.0769 | 60.1959
186.5469 | 123.4039 | -60.0769 | 63.0936 | -0.065308 | 0.00056187 | 0.06143 | 0.062622 | 0.00041234 | -0.00057042 | -0.0018073 | -0.026276 | 0.00053628 | 0.067276 | 0.063491 | -0.0004614 | -0.00059378 | 0.0015915 | -0.082397 | 63.1348 | -60.347 | 62.9379 | -59.9854 | -60.3516 | -0.054932 | -0.059509 | 63.1393 | -60.1776 | 63.1622 | -60.0723 | -60.1685 | -59.7656 | -0.27008 | 0.041199 | -0.15564 | 0.091552 | 60.022 | -0.27466 | 60.2921 | -0.004577 | -0.10071 | 0.045776 | 0.068664 | 0.004577 | 0.31128 | -0.091553 | 0.41199 | 0.009155 | 0.36163 | 123.2849 | 0.10529 | 123.3398 | 123.4818 | 123.317 | 123.2117 | 123.2162 | -123.4406 | -123.2712 | 123.0148 | 123.2391 | 59.9945 | 60.0174
187.4844 | 123.4634 | -60.0311 | 63.0844 | -0.0042723 | 0.00098907 | 0.061216 | 0.06134 | -0.0021513 | -0.00035682 | -0.0024481 | 0.0011902 | 0.00053628 | 0.065995 | 0.068831 | -0.000675 | -0.00080758 | 0.0026597 | -0.013733 | 63.1714 | -60.3012 | 63.0157 | -59.8938 | -60.2371 | 0.091553 | 0.12817 | 63.176 | -60.1318 | 63.2629 | -59.9854 | -60.0769 | -59.6695 | -0.27008 | 0.086975 | -0.068665 | 0.13733 | 60.1227 | -0.20599 | 60.3928 | 0.064086 | -0.10071 | 0.091552 | 0.17853 | 0.045776 | 0.36163 | -0.045776 | 0.46234 | 0.054932 | 0.40741 | 123.317 | 0.14648 | 123.3948 | 123.4726 | 123.3078 | 123.2025 | 123.2071 | -123.3856 | -123.2162 | 123.0469 | 123.2941 | 60.0174 | 60.1593
188.4844 | 123.4268 | -60.0906 | 63.0844 | -0.050049 | 0.0029117 | 0.062925 | 0.063476 | 0.0023349 | -0.00057042 | -0.0018073 | 0.010345 | 0.0016043 | 0.068131 | 0.061568 | 0.0001794 | -0.0012348 | -0.0018265 | -0.064087 | 63.1622 | -60.3195 | 62.9745 | -59.9625 | -60.3012 | 0.041199 | 0.050354 | 63.1485 | -60.1593 | 63.2217 | -60.0082 | -60.1227 | -59.7198 | -0.22888 | 0.077819 | -0.10986 | 0.12817 | 60.1318 | -0.21057 | 60.3607 | 0.018311 | -0.068665 | 0.064087 | 0.13733 | 0.082397 | 0.37079 | -0.032044 | 0.43945 | 0.036621 | 0.35706 | 123.2941 | 0.15106 | 123.381 | 123.4818 | 123.3078 | 123.2529 | 123.2391 | -123.4039 | -123.2437 | 123.0652 | 123.3124 | 60.0266 | 60.141
189.4844 | 123.317 | -60.1044 | 63.1348 | -0.027161 | 0.0020573 | 0.063138 | 0.06369 | -0.0045011 | 0.0011386 | -0.00095273 | -0.044586 | -0.00053192 | 0.068344 | 0.068831 | -3.4196e-05 | 0.001115 | 0.00052346 | -0.027466 | 63.2263 | -60.3287 | 62.915 | -60.0128 | -60.3424 | 0.022888 | 0.027466 | 63.2446 | -60.1456 | 63.1302 | -60.1135 | -60.2142 | -59.8068 | -0.2243 | 0.091552 | -0.21973 | 0.091553 | 60.1273 | -0.23804 | 60.3516 | -0.013733 | -0.041199 | 0.10986 | -0.004578 | -0.009155 | 0.29755 | -0.10986 | 0.33875 | -0.068664 | 0.31586 | 123.2437 | 0.032044 | 123.2758 | 123.555 | 123.3902 | 123.3307 | 123.349 | -123.4634 | -123.2803 | 123.0194 | 123.2346 | 60.0769 | 60.1318
190.4844 | 123.4451 | -60.054 | 63.1165 | -0.050049 | -0.00071993 | 0.06442 | 0.061767 | 0.00062594 | 0.0015658 | -0.0015935 | 0.016449 | -0.00010472 | 0.065781 | 0.061355 | 0.000393 | -0.00080758 | -0.00011754 | 0.022888 | 63.1531 | -60.3012 | 63.0432 | -59.8709 | -60.2325 | 0.10071 | 0.17395 | 63.1622 | -60.1273 | 63.2355 | -59.9762 | -60.0586 | -59.6786 | -0.24719 | 0.036621 | -0.073242 | 0.1831 | 60.1547 | -0.17853 | 60.4019 | 0.068664 | -0.073242 | 0.045776 | 0.11902 | 0.07782 | 0.37537 | -0.004578 | 0.44861 | 0.068664 | 0.4303 | 123.3444 | 0.15106 | 123.3627 | 123.4543 | 123.2895 | 123.2071 | 123.2162 | -123.4177 | -123.2437 | 123.0972 | 123.2895 | 60.0769 | 60.228
191.5469 | 123.4314 | -60.054 | 63.1256 | -0.019531 | -7.913e-05 | 0.061857 | 0.062194 | -0.00086946 | 0.0011386 | 0.00011527 | -0.01712 | 0.00096348 | 0.070267 | 0.072036 | -0.0004614 | -0.0010212 | 9.6064e-05 | -0.045776 | 63.1531 | -60.3058 | 62.9471 | -59.9716 | -60.3241 | 0.004578 | 0.004578 | 63.1485 | -60.1776 | 63.1989 | -60.0082 | -60.1135 | -59.7015 | -0.25177 | 0.027466 | -0.17853 | 0.082397 | 60.0586 | -0.27008 | 60.3104 | -0.018311 | -0.1236 | 0.022889 | 0.073243 | 0.045776 | 0.35248 | -0.059509 | 0.47607 | 0.064087 | 0.33417 | 123.2529 | 0.16937 | 123.3765 | 123.4589 | 123.3261 | 123.2071 | 123.2025 | -123.4314 | -123.3032 | 123.0011 | 123.2529 | 60.0082 | 60.0586
192.4844 | 123.3536 | -60.0357 | 63.1622 | -0.027161 | -7.913e-05 | 0.063566 | 0.062408 | -0.00044226 | 0.00028418 | -0.0018073 | 0.022552 | 0.0011771 | 0.066849 | 0.066909 | -0.0008886 | -0.00016658 | -0.0035355 | 0.032043 | 63.1531 | -60.3104 | 63.0478 | -59.8297 | -60.2097 | 0.10071 | 0.16022 | 63.1668 | -60.1501 | 63.2401 | -59.9762 | -60.0815 | -59.6832 | -0.27466 | -0.009155 | -0.11444 | 0.20599 | 60.1364 | -0.17395 | 60.4111 | 0.10071 | -0.11444 | 0.004578 | 0.07782 | 0.05951 | 0.35248 | -0.045776 | 0.46692 | 0.068664 | 0.48065 | 123.3582 | 0.17395 | 123.3902 | 123.4634 | 123.317 | 123.1888 | 123.2025 | -123.4726 | -123.3124 | 123.0835 | 123.2758 | 60.0677 | 60.1959
193.5469 | 123.468 | -60.0449 | 63.0936 | -0.057678 | 0.00098907 | 0.063138 | 0.06134 | 0.00019874 | 0.0019932 | -0.0030889 | 0.0011902 | -0.0037363 | 0.066208 | 0.064559 | 0.0001794 | 0.001115 | -0.00097194 | 0.027466 | 63.1668 | -60.3195 | 63.0249 | -59.8663 | -60.2509 | 0.10986 | 0.5127 | 63.2309 | -60.1227 | 63.208 | -59.9625 | -60.0998 | -59.7153 | -0.27466 | 0.073242 | -0.068665 | 0.17853 | 60.1547 | -0.20599 | 60.4294 | 0.068665 | -0.07782 | 0.13733 | 0.11444 | 0.082398 | 0.32959 | -0.054931 | 0.40741 | 0.022889 | 0.45319 | 123.3444 | 0.16022 | 123.3307 | 123.4863 | 123.3536 | 123.2117 | 123.2758 | -123.4131 | -123.2162 | 123.0698 | 123.2529 | 60.0723 | 60.5576
194.4844 | 123.4314 | -60.0357 | 63.089 | -0.050049 | 0.00034827 | 0.062284 | 0.064544 | -0.0019377 | -0.001852 | 0.0016107 | -0.01712 | -0.00074552 | 0.068344 | 0.06755 | -0.0008886 | 0.00026062 | -0.00054474 | 0.009155 | 63.1485 | -60.3195 | 63.0066 | -59.9167 | -60.2646 | 0.064087 | 0.09613 | 63.1165 | -60.1364 | 63.2263 | -60.0082 | -60.0494 | -59.6466 | -0.28381 | 0.05951 | -0.082397 | 0.11902 | 60.0998 | -0.22888 | 60.3836 | 0.054932 | -0.10071 | 0.027466 | 0.13733 | 0.027466 | 0.3891 | -0.013732 | 0.48981 | 0.086976 | 0.40283 | 123.3261 | 0.12817 | 123.3627 | 123.468 | 123.2529 | 123.1842 | 123.1522 | -123.4085 | -123.2254 | 123.0423 | 123.262 | 60.0449 | 60.1318
195.4844 | 123.3444 | -60.0723 | 63.1485 | -0.050049 | 0.00056187 | 0.063352 | 0.06369 | 0.00019874 | 7.0582e-05 | 0.00096987 | -0.023224 | 0.00032248 | 0.068558 | 0.064345 | 0.0006066 | -0.00038018 | -0.00075834 | 0.004578 | 63.1989 | -60.3149 | 62.9517 | -59.9808 | -60.3241 | 0.045776 | 0.07782 | 63.208 | -60.1593 | 63.1393 | -60.0906 | -60.2051 | -59.7885 | -0.24261 | 0.050354 | -0.19684 | 0.091553 | 60.1181 | -0.25177 | 60.3607 | -0.009156 | -0.086975 | 0.059509 | -0.009156 | -0.01831 | 0.28381 | -0.13275 | 0.37079 | -0.045776 | 0.33417 | 123.2666 | 0.068665 | 123.2986 | 123.5138 | 123.3673 | 123.2712 | 123.2803 | -123.4634 | -123.3078 | 123.024 | 123.2117 | 60.0769 | 60.1501
196.5469 | 123.4726 | -60.0311 | 63.1027 | -0.072937 | -7.913e-05 | 0.063566 | 0.063476 | -0.0021513 | -0.0012112 | -0.0011663 | 0.013397 | -0.00010472 | 0.066849 | 0.067763 | -0.001316 | -0.0014484 | -0.0020401 | -0.045776 | 63.1805 | -60.3241 | 62.9654 | -59.9579 | -60.3058 | 0.036621 | 0.036621 | 63.1485 | -60.1547 | 63.2355 | -60.0037 | -60.1227 | -59.7107 | -0.29297 | 0.07782 | -0.13733 | 0.073242 | 60.0677 | -0.27466 | 60.3607 | 0.018311 | -0.1236 | 0.045777 | 0.13275 | 0.027466 | 0.32044 | -0.091553 | 0.44403 | 0.032043 | 0.36621 | 123.2895 | 0.15106 | 123.3902 | 123.5046 | 123.3032 | 123.2117 | 123.1796 | -123.4268 | -123.2574 | 122.9965 | 123.2666 | 59.9854 | 60.0677
197.4844 | 123.3261 | -60.0998 | 63.1577 | -0.027161 | -0.00050633 | 0.061643 | 0.067108 | 0.0021213 | 0.0013522 | -0.0020209 | -0.062897 | 0.0024589 | 0.067704 | 0.064345 | 0.0001794 | 0.00047422 | 0.00052346 | -0.022888 | 63.2538 | -60.3241 | 62.9013 | -60.022 | -60.347 | 0.022888 | 0.050354 | 63.2263 | -60.1181 | 63.1119 | -60.1089 | -60.1959 | -59.8114 | -0.22431 | 0.09613 | -0.25635 | 0.077819 | 60.1227 | -0.24719 | 60.347 | -0.022888 | -0.018311 | 0.068664 | -0.045777 | -0.009156 | 0.28839 | -0.096131 | 0.3067 | -0.07782 | 0.30212 | 123.2254 | 0.009155 | 123.23 | 123.5779 | 123.3444 | 123.3536 | 123.3261 | -123.4818 | -123.2758 | 123.0011 | 123.2117 | 60.0769 | 60.1501
198.5469 | 123.4039 | -60.1044 | 63.0981 | -0.088196 | -0.00050633 | 0.064847 | 0.064544 | 0.0021213 | 0.00092498 | -0.0037299 | -0.093414 | 0.00074988 | 0.068344 | 0.069472 | -0.001316 | 0.001115 | 0.00073706 | -0.11444 | 63.1577 | -60.3745 | 62.9059 | -60.0311 | -60.3928 | -0.086975 | -0.091553 | 63.1302 | -60.1868 | 63.1989 | -60.0815 | -60.1868 | -59.7382 | -0.27008 | 0.059509 | -0.19226 | 0.073242 | 60.0174 | -0.28839 | 60.2875 | -0.01831 | -0.082398 | 0.032043 | 0.10071 | 0.022888 | 0.36621 | -0.082398 | 0.44861 | 0 | 0.34332 | 123.2803 | 0.10529 | 123.3856 | 123.5321 | 123.317 | 123.262 | 123.2346 | -123.4726 | -123.2849 | 123.0103 | 123.3032 | 59.9899 | 60.0128
199.4844 | 123.381 | -60.0677 | 63.1302 | -0.050049 | 0.00056187 | 0.062925 | 0.064758 | -0.00065586 | -0.0020658 | -0.0022345 | -0.087311 | 0.00074988 | 0.067917 | 0.071395 | -0.0015296 | 0.0013288 | -0.0026809 | 0.004578 | 63.1851 | -60.3516 | 62.9608 | -59.9945 | -60.3287 | 0.004578 | 0.064087 | 63.1897 | -60.1822 | 63.1851 | -60.0769 | -60.2051 | -59.7656 | -0.28381 | 0.054932 | -0.16937 | 0.073242 | 60.0723 | -0.26093 | 60.3561 | 0.022888 | -0.11444 | 0.059509 | 0.054932 | -0.009155 | 0.30212 | -0.13733 | 0.41656 | -0.022888 | 0.35706 | 123.3124 | 0.10529 | 123.3673 | 123.5367 | 123.3719 | 123.2529 | 123.2574 | -123.4818 | -123.3124 | 123.0286 | 123.2529 | 60.0723 | 60.1318
200.5469 | 123.4222 | -60.0906 | 63.0432 | -0.065308 | -0.00050633 | 0.063352 | 0.063262 | -0.0015103 | 0.0011386 | 0.00011527 | -0.032379 | -0.0013863 | 0.068985 | 0.063918 | 0.0018884 | -0.0012348 | 0.0028733 | 0.022888 | 63.1256 | -60.3195 | 62.9745 | -59.935 | -60.3195 | -0.032043 | 0 | 63.0981 | -60.1822 | 63.1897 | -60.0586 | -60.141 | -59.7382 | -0.22888 | 0.082397 | -0.068665 | 0.15564 | 60.0586 | -0.22888 | 60.2875 | 0 | -0.091553 | 0.054932 | 0.14648 | 0.032043 | 0.35248 | -0.050354 | 0.44403 | 0.041199 | 0.38452 | 123.2941 | 0.1236 | 123.3719 | 123.4451 | 123.2803 | 123.2162 | 123.1888 | -123.3627 | -123.2254 | 123.0652 | 123.2803 | 60.1135 | 60.0906
201.4844 | 123.3078 | -60.0906 | 63.1485 | -0.011902 | -7.913e-05 | 0.065488 | 0.063049 | -0.0010831 | -0.00078402 | 0.00054267 | -0.0018616 | 0.00096348 | 0.066849 | 0.059432 | -0.0004614 | -0.00038018 | -0.00054474 | 0.018311 | 63.1897 | -60.3195 | 62.9425 | -59.9579 | -60.3058 | 0.054932 | 0.054932 | 63.2126 | -60.1639 | 63.1485 | -60.0723 | -60.1913 | -59.7839 | -0.22888 | 0.041198 | -0.20599 | 0.13275 | 60.1456 | -0.21515 | 60.3745 | 0.013733 | -0.073242 | 0.064086 | 0 | 0.01831 | 0.3067 | -0.10071 | 0.37994 | -0.027466 | 0.36163 | 123.262 | 0.091552 | 123.3124 | 123.5092 | 123.3765 | 123.2803 | 123.3032 | -123.468 | -123.3124 | 123.0331 | 123.2391 | 60.1089 | 60.1456
202.5469 | 123.4268 | -60.0586 | 63.0936 | -0.0042723 | 0.0026981 | 0.062925 | 0.063049 | 0.0016939 | 0.00049778 | -0.00031193 | 0.043915 | -0.0013863 | 0.068131 | 0.065841 | -0.0011022 | -0.00059378 | 0.0047959 | -0.054932 | 63.1668 | -60.3149 | 62.9517 | -59.9899 | -60.3058 | 0 | -0.009155 | 63.1302 | -60.173 | 63.2126 | -60.0174 | -60.1227 | -59.7244 | -0.25635 | 0.073242 | -0.14191 | 0.068665 | 60.0586 | -0.24719 | 60.3149 | 0.009155 | -0.11444 | 0.036621 | 0.11902 | 0.041199 | 0.33417 | -0.064087 | 0.44861 | 0.050354 | 0.32501 | 123.2666 | 0.15564 | 123.3856 | 123.4818 | 123.3032 | 123.2254 | 123.1888 | -123.4085 | -123.2666 | 123.0103 | 123.2712 | 60.0037 | 60.0494
203.4844 | 123.3398 | -60.0677 | 63.1531 | -0.042419 | 0.00034827 | 0.063138 | 0.062408 | -0.00086946 | -0.0027066 | 0.00096987 | -0.053741 | 0.0033133 | 0.066422 | 0.066482 | -0.000675 | -0.00080758 | -0.0013991 | -0.022888 | 63.1989 | -60.3607 | 62.9242 | -60.0266 | -60.3424 | 0.004578 | 0.018311 | 63.2126 | -60.1776 | 63.1439 | -60.0952 | -60.2005 | -59.7839 | -0.29297 | 0.045777 | -0.22888 | 0.041199 | 60.0723 | -0.27466 | 60.3653 | 0.018311 | -0.10986 | 0.059509 | -0.009155 | -0.027466 | 0.28381 | -0.13275 | 0.39368 | -0.022888 | 0.33417 | 123.2849 | 0.082397 | 123.3215 | 123.5596 | 123.3902 | 123.2666 | 123.2803 | -123.5138 | -123.3307 | 122.9919 | 123.2117 | 60.0449 | 60.0861
204.5469 | 123.4222 | -60.0723 | 63.0661 | -0.03479 | 0.0016299 | 0.06442 | 0.062622 | -0.00086946 | -0.00099762 | -0.00031193 | -0.011017 | 0.00074988 | 0.065995 | 0.064559 | 0.0018884 | -0.00080758 | -0.0028945 | -0.050354 | 63.1165 | -60.3378 | 62.7594 | -59.9716 | -60.0128 | 0.036621 | -0.018311 | 63.1302 | -60.1364 | 63.2126 | -60.0449 | -60.1593 | -59.7198 | -0.2655 | 0.050354 | -0.3067 | 0.10071 | 60.1089 | 0.05951 | 60.3745 | 0.32501 | -0.064087 | 0.064087 | 0.14648 | 0.027466 | 0.35248 | -0.086975 | 0.41656 | -0.022888 | 0.36621 | 123.0972 | 0.091553 | 123.349 | 123.4543 | 123.2666 | 123.1888 | 123.2025 | -123.4039 | -123.2025 | 122.8317 | 123.2849 | 60.022 | 60.054
205.4844 | 123.3261 | -60.0632 | 63.1348 | 0.12543 | -0.00093353 | 0.061857 | 0.06604 | 0.00041234 | -0.00099762 | -0.0045843 | -0.056793 | 0.0013907 | 0.069199 | 0.062209 | -0.0008886 | -0.00080758 | -0.00075834 | -0.068665 | 63.2263 | -60.3149 | 62.8784 | -60.0494 | -60.3561 | 0.032043 | 0.018311 | 63.2126 | -60.1776 | 63.1393 | -60.1135 | -60.2142 | -59.7885 | -0.25177 | 0.091552 | -0.25635 | 0.013733 | 60.0952 | -0.29297 | 60.347 | -0.041199 | -0.11444 | 0.077819 | 0.004577 | -0.050354 | 0.27466 | -0.15106 | 0.3891 | -0.036621 | 0.2655 | 123.1934 | 0.064087 | 123.317 | 123.5413 | 123.3902 | 123.2895 | 123.2758 | -123.4497 | -123.3124 | 122.9416 | 123.2025 | 59.9945 | 60.0815
206.5469 | 123.4726 | -60.0586 | 63.1165 | -0.027161 | 0.00013467 | 0.063138 | 0.060913 | 0.00019874 | -0.001852 | 0.0013971 | 0.028656 | -0.00053192 | 0.066422 | 0.063064 | -0.0017432 | -0.00059378 | -0.0016129 | -0.022888 | 63.1805 | -60.3378 | 62.97 | -59.935 | -60.2737 | 0.073242 | 0.086975 | 63.1165 | -60.1456 | 63.208 | -59.9899 | -60.0952 | -59.6878 | -0.27924 | 0.064087 | -0.14648 | 0.1236 | 60.1318 | -0.21515 | 60.4111 | 0.064087 | -0.086975 | 0 | 0.091553 | 0.068665 | 0.37079 | -0.036621 | 0.45776 | 0.050354 | 0.40283 | 123.3078 | 0.15564 | 123.3536 | 123.5184 | 123.262 | 123.2391 | 123.175 | -123.4543 | -123.262 | 123.0286 | 123.2666 | 60.0357 | 60.1456
207.4844 | 123.3444 | -60.0815 | 63.1439 | 0.041504 | -0.0015743 | 0.062711 | 0.062622 | -0.0021513 | -0.00057042 | 0.0037469 | -0.053741 | 0.0024589 | 0.068344 | 0.068404 | -0.0019568 | 0.00068782 | -0.0011855 | -0.022888 | 63.1989 | -60.3378 | 62.7457 | -60.0723 | -60.347 | -0.022888 | -0.009155 | 63.2126 | -60.1776 | 63.1348 | -60.1089 | -60.2051 | -59.7885 | -0.25635 | 0.054932 | -0.39825 | 0.009155 | 60.0586 | -0.2655 | 60.3149 | -0.009155 | -0.09613 | 0.068664 | -0.009155 | -0.027466 | 0.29297 | -0.1236 | 0.3891 | -0.027466 | 0.2655 | 123.0835 | 0.068664 | 123.3124 | 123.5367 | 123.3902 | 123.2803 | 123.2941 | -123.4818 | -123.3215 | 122.8271 | 123.2162 | 60.0586 | 60.0723
208.4844 | 123.4177 | -60.0357 | 63.0981 | 0.018616 | 0.0024845 | 0.063138 | 0.061981 | -0.0015103 | -0.0020658 | 0.0011835 | 0.019501 | -0.00074552 | 0.06514 | 0.063491 | -0.0017432 | -0.00080758 | 0.0045823 | 0.013733 | 63.1622 | -60.2875 | 63.0066 | -59.8618 | -60.2142 | 0.13275 | 0.21515 | 63.1805 | -60.0861 | 63.1805 | -59.9945 | -60.0403 | -59.697 | -0.25177 | 0.064086 | -0.091553 | 0.17395 | 60.1685 | -0.17853 | 60.4202 | 0.073243 | -0.050354 | 0.082397 | 0.082397 | 0.041199 | 0.33875 | -0.004577 | 0.3891 | 0.045777 | 0.42572 | 123.2941 | 0.091553 | 123.2666 | 123.4497 | 123.2666 | 123.1979 | 123.2162 | -123.3856 | -123.1842 | 123.0423 | 123.2162 | 60.0494 | 60.2509
209.5469 | 123.3032 | -60.0632 | 63.1668 | -0.057678 | 0.00098907 | 0.062498 | 0.064331 | -0.0025785 | -0.00099762 | -0.0024481 | -0.029327 | 0.0035269 | 0.069412 | 0.064986 | 0.0001794 | -0.0018756 | 0.0043687 | 0.032043 | 63.2355 | -60.3149 | 62.9059 | -60.0082 | -60.3516 | 0.041199 | 0.032043 | 63.2034 | -60.173 | 63.1256 | -60.1089 | -60.2142 | -59.7977 | -0.25177 | 0.068665 | -0.26093 | 0.054931 | 60.1044 | -0.28839 | 60.3561 | -0.036621 | -0.10986 | 0.036621 | -0.041199 | -0.045777 | 0.2655 | -0.15106 | 0.37537 | -0.041198 | 0.3067 | 123.2208 | 0.064087 | 123.2986 | 123.5504 | 123.3765 | 123.2986 | 123.2666 | -123.4818 | -123.3398 | 122.9691 | 123.1888 | 60.0952 | 60.0952
210.4844 | 123.317 | -60.0906 | 63.1577 | -0.027161 | -7.913e-05 | 0.062925 | 0.063262 | -0.0034329 | -0.0022794 | -0.0015935 | 0.062225 | 0.0020315 | 0.070481 | 0.064773 | -3.4196e-05 | -0.0010212 | 0.00095066 | -0.027466 | 63.2309 | -60.3241 | 62.8967 | -60.0174 | -60.3561 | 0.013733 | -0.15106 | 63.2034 | -60.1593 | 63.1119 | -60.1135 | -60.2234 | -59.7931 | -0.23346 | 0.073242 | -0.26093 | 0.073242 | 60.1044 | -0.2655 | 60.3378 | -0.032043 | -0.068665 | 0.045776 | -0.045777 | -0.022888 | 0.29755 | -0.13275 | 0.36621 | -0.064087 | 0.3067 | 123.2208 | 0.045777 | 123.2712 | 123.555 | 123.3627 | 123.3215 | 123.2941 | -123.4818 | -123.317 | 122.9874 | 123.2025 | 60.0632 | 59.9396
211.4844 | 123.3719 | -60.0815 | 63.1439 | -0.03479 | 0.0029117 | 0.062498 | 0.063262 | 0.0019077 | -0.0029202 | -0.0018073 | -0.062897 | 0.0018179 | 0.066208 | 0.066054 | -0.0008886 | 0.001115 | -0.0013991 | 0.013733 | 63.1851 | -60.347 | 62.9242 | -59.9716 | -60.2921 | 0.018311 | 0.07782 | 63.1851 | -60.1501 | 63.1622 | -60.0815 | -60.1868 | -59.761 | -0.2655 | 0.041199 | -0.21973 | 0.10986 | 60.0998 | -0.21057 | 60.3653 | 0.054932 | -0.068664 | 0.041199 | 0.01831 | 0 | 0.32044 | -0.10529 | 0.3891 | -0.036622 | 0.37537 | 123.2712 | 0.068664 | 123.3124 | 123.5321 | 123.3353 | 123.2666 | 123.2666 | -123.4909 | -123.2941 | 123.0057 | 123.2437 | 60.0952 | 60.1593
212.5469 | 123.436 | -60.0586 | 63.1073 | -0.065308 | 0.00098907 | 0.062925 | 0.064117 | -0.00065586 | -0.0012112 | 0.00096987 | 0.034759 | 0.00032248 | 0.068131 | 0.067977 | -3.4196e-05 | -0.00038018 | 0.0015915 | -0.059509 | 63.1531 | -60.3058 | 62.9379 | -59.9533 | -60.3058 | 0.018311 | 0.004578 | 63.1393 | -60.141 | 63.2034 | -60.0174 | -60.1135 | -59.6924 | -0.24719 | 0.045776 | -0.16937 | 0.10529 | 60.0769 | -0.24719 | 60.3241 | 0 | -0.082397 | 0.032043 | 0.09613 | 0.041199 | 0.36621 | -0.054931 | 0.44861 | 0.027466 | 0.35248 | 123.2437 | 0.1236 | 123.3444 | 123.4589 | 123.2803 | 123.2117 | 123.1979 | -123.4131 | -123.2483 | 122.9965 | 123.262 | 59.9991 | 60.0632
213.4844 | 123.3582 | -60.0815 | 63.1165 | -0.011902 | 0.0016299 | 0.06143 | 0.063903 | 0.00041234 | 0.00049778 | -0.00095273 | -0.069 | 0.00053628 | 0.067917 | 0.064345 | -0.0028112 | 0.00068782 | -0.0020401 | 0 | 63.2217 | -60.347 | 62.9288 | -59.967 | -60.3195 | 0.022888 | 0.059509 | 63.2034 | -60.1364 | 63.1622 | -60.0815 | -60.2005 | -59.761 | -0.2655 | 0.10529 | -0.18768 | 0.11444 | 60.1044 | -0.23804 | 60.3699 | 0.027466 | -0.054932 | 0.086975 | 0.045776 | 0 | 0.32044 | -0.11902 | 0.37537 | -0.064086 | 0.37994 | 123.2758 | 0.054932 | 123.2986 | 123.5687 | 123.3398 | 123.3032 | 123.2849 | -123.4634 | -123.2529 | 123.0103 | 123.2437 | 60.0815 | 60.141
214.4844 | 123.4634 | -60.0494 | 63.1302 | -0.050049 | -0.00071993 | 0.059293 | 0.061767 | -1.486e-05 | 0.00049778 | -0.0020209 | 0.071381 | -0.00095912 | 0.066849 | 0.066695 | -0.001316 | -0.00059378 | 0.0013779 | 0.32501 | 63.2492 | -60.2829 | 62.9745 | -59.848 | -60.2646 | 0.082397 | 0.12817 | 63.1577 | -60.1501 | 63.2263 | -59.9991 | -60.0998 | -59.6695 | -0.23346 | 0.11902 | -0.15564 | 0.20142 | 60.1318 | -0.21515 | 60.3653 | 0.018311 | -0.10071 | 0.027466 | 0.09613 | 0.050354 | 0.37994 | -0.050354 | 0.48065 | 0.050354 | 0.43488 | 123.2574 | 0.15106 | 123.3765 | 123.5321 | 123.3078 | 123.2986 | 123.2071 | -123.4131 | -123.2803 | 123.024 | 123.2758 | 60.3745 | 60.1776
215.4844 | 123.3536 | -60.0952 | 63.1256 | -0.050049 | 0.0018435 | 0.065275 | 0.06369 | -1.486e-05 | -0.00035682 | 0.00011527 | -0.026276 | 0.0016043 | 0.067917 | 0.064345 | -3.4196e-05 | -0.0018756 | 0.00030966 | -0.12817 | 63.2263 | -60.3561 | 62.9059 | -60.0082 | -60.3424 | 0.013733 | 0.013733 | 63.1989 | -60.1776 | 63.1439 | -60.1089 | -60.2051 | -59.7656 | -0.26093 | 0.10071 | -0.21973 | 0.086975 | 60.1089 | -0.24719 | 60.3699 | 0.013733 | -0.082397 | 0.073243 | 0.018311 | -0.013733 | 0.32959 | -0.10986 | 0.41199 | -0.027466 | 0.3479 | 123.262 | 0.068664 | 123.3215 | 123.5825 | 123.3765 | 123.3215 | 123.2941 | -123.4818 | -123.3032 | 123.0011 | 123.2391 | 59.967 | 60.1089
216.5469 | 123.4406 | -60.0449 | 63.0798 | -0.050049 | 0.0012027 | 0.065275 | 0.061981 | -1.486e-05 | 0.00049778 | -0.00073913 | 0.0011902 | -0.00053192 | 0.066635 | 0.064132 | -0.0004614 | -0.00059378 | 0.00073706 | -0.045776 | 63.1073 | -60.3333 | 62.9791 | -59.9396 | -60.3241 | -0.041199 | -0.17395 | 63.0569 | -60.2005 | 63.208 | -60.0037 | -60.1456 | -59.7015 | -0.28839 | 0.027466 | -0.10071 | 0.10529 | 60.0037 | -0.27924 | 60.2921 | 0.009155 | -0.15564 | -0.022888 | 0.12817 | 0.041199 | 0.34332 | -0.10071 | 0.49896 | 0.054931 | 0.39368 | 123.3124 | 0.19684 | 123.4085 | 123.4406 | 123.2574 | 123.1522 | 123.1018 | -123.4131 | -123.2803 | 123.024 | 123.2529 | 59.9991 | 59.8709
217.4844 | 123.3398 | -60.0815 | 63.1348 | 0.0033567 | -0.0017881 | 0.062284 | 0.062835 | -0.0025785 | -0.002493 | 0.0018243 | 0.004242 | 0.0013907 | 0.068558 | 0.071181 | 0.000393 | -0.00080758 | 0.00030966 | -0.032043 | 63.2263 | -60.3195 | 62.7777 | -60.0769 | -60.3424 | -0.022888 | -0.009155 | 63.208 | -60.1639 | 63.1073 | -60.1364 | -60.2188 | -59.7839 | -0.23804 | 0.091552 | -0.35706 | 0.004578 | 60.0586 | -0.26093 | 60.2966 | -0.022888 | -0.082397 | 0.073242 | -0.027466 | -0.054932 | 0.29755 | -0.13733 | 0.37994 | -0.054932 | 0.24262 | 123.0972 | 0.027465 | 123.2712 | 123.5458 | 123.3719 | 123.3078 | 123.2895 | -123.4543 | -123.2986 | 122.8592 | 123.1888 | 60.0494 | 60.0723
218.4844 | 123.4131 | -60.0586 | 63.1119 | -0.065308 | 0.00098907 | 0.065061 | 0.061981 | -0.0051419 | 0.0017794 | -0.00073913 | 0.031708 | 0.00074988 | 0.069626 | 0.066482 | -0.003025 | -0.0023028 | -0.00075834 | 0.027466 | 63.1622 | -60.3104 | 63.002 | -59.8984 | -60.2463 | 0.10986 | 0.13275 | 63.1485 | -60.1501 | 63.1897 | -60.0311 | -60.1456 | -59.7107 | -0.25177 | 0.050354 | -0.10986 | 0.16022 | 60.1685 | -0.18768 | 60.4202 | 0.064087 | -0.091552 | 0.036622 | 0.07782 | 0.027466 | 0.3479 | -0.086975 | 0.43945 | 0.004577 | 0.41199 | 123.3124 | 0.11902 | 123.3398 | 123.4726 | 123.2986 | 123.2208 | 123.2071 | -123.4222 | -123.262 | 123.0606 | 123.2483 | 60.0861 | 60.1913
219.4844 | 123.3673 | -60.0632 | 63.1348 | -0.080566 | 0.00077547 | 0.064207 | 0.06369 | -0.0012967 | -0.002493 | -0.00052553 | -0.032379 | 0.0013907 | 0.068131 | 0.072036 | -0.0015296 | -0.00080758 | -0.0011855 | 0 | 63.1943 | -60.3561 | 62.9333 | -59.9808 | -60.3104 | -0.009155 | 0.054932 | 63.1851 | -60.1501 | 63.1668 | -60.0677 | -60.1959 | -59.7656 | -0.29297 | 0.059509 | -0.20142 | 0.082397 | 60.054 | -0.24719 | 60.347 | 0.045776 | -0.086975 | 0.050354 | 0.032043 | -0.004578 | 0.29755 | -0.13275 | 0.38452 | -0.045777 | 0.37537 | 123.2895 | 0.082397 | 123.317 | 123.5504 | 123.3353 | 123.2574 | 123.2483 | -123.4909 | -123.2849 | 122.9965 | 123.23 | 60.0632 | 60.1181
220.5469 | 123.4131 | -60.0952 | 63.0753 | -0.095825 | 0.00056187 | 0.065061 | 0.06369 | 0.0016939 | -0.00057042 | 0.00011527 | 0.025604 | 0.00010888 | 0.06749 | 0.0605 | -0.0011022 | -0.00016658 | 0.00073706 | -0.07782 | 63.1897 | -60.3241 | 62.9242 | -59.9899 | -60.3333 | -0.013733 | 0.10071 | 63.1668 | -60.1547 | 63.1668 | -60.054 | -60.1685 | -59.7382 | -0.22888 | 0.11444 | -0.15106 | 0.10529 | 60.0815 | -0.23804 | 60.3104 | -0.009155 | -0.059509 | 0.091553 | 0.091553 | 0.041199 | 0.35706 | -0.073242 | 0.41656 | -0.013733 | 0.33417 | 123.2483 | 0.10071 | 123.3215 | 123.5138 | 123.3215 | 123.2849 | 123.262 | -123.3994 | -123.23 | 123.0194 | 123.262 | 60.0174 | 60.1959
221.4844 | 123.3673 | -60.1044 | 63.1256 | 0.026245 | 0.00098907 | 0.063779 | 0.063903 | -0.00044226 | -0.00035682 | 0.0013971 | -0.053741 | 0.0011771 | 0.067917 | 0.066695 | -0.0011022 | 0.00047422 | -0.0043899 | -0.004578 | 63.2126 | -60.3424 | 62.9242 | -60.0128 | -60.347 | 0.022888 | 0.013733 | 63.2401 | -60.1868 | 63.1439 | -60.0815 | -60.1868 | -59.7473 | -0.23804 | 0.086975 | -0.20142 | 0.091553 | 60.1273 | -0.24261 | 60.3653 | -0.004578 | -0.082398 | 0.11444 | 0.018311 | 0.022888 | 0.35706 | -0.082398 | 0.43945 | 0 | 0.32959 | 123.2666 | 0.10529 | 123.3307 | 123.555 | 123.4268 | 123.317 | 123.3444 | -123.468 | -123.3124 | 123.0286 | 123.2483 | 60.0998 | 60.1181
222.4844 | 123.3994 | -60.0494 | 63.1119 | 0.010986 | -0.0032833 | 0.063779 | 0.061126 | 0.0010531 | 0.0019932 | -9.8328e-05 | 0.016449 | 0.0016043 | 0.068772 | 0.065414 | 0.0001794 | -0.001662 | 0.00095066 | 0.032043 | 63.1622 | -60.2921 | 63.002 | -59.8892 | -60.2417 | 0.10529 | 0.14648 | 63.176 | -60.1318 | 63.2126 | -60.0311 | -60.1181 | -59.7244 | -0.24262 | 0.050354 | -0.10986 | 0.16022 | 60.1547 | -0.19226 | 60.3973 | 0.050354 | -0.082398 | 0.064087 | 0.10071 | 0.01831 | 0.32501 | -0.068665 | 0.40741 | 0.013733 | 0.40283 | 123.2941 | 0.10071 | 123.3444 | 123.4543 | 123.3078 | 123.2117 | 123.2254 | -123.4039 | -123.2437 | 123.0515 | 123.262 | 60.0815 | 60.1959
223.5469 | 123.3078 | -60.0723 | 63.1805 | -0.027161 | 0.0012027 | 0.062711 | 0.064117 | -0.0019377 | -0.0012112 | -0.0015935 | -0.0079652 | 0.00074988 | 0.070053 | 0.061782 | -0.0015296 | -0.0023028 | -0.0037491 | -0.027466 | 63.208 | -60.3104 | 62.8967 | -60.0082 | -60.3378 | 0.032043 | 0.045776 | 63.2126 | -60.1547 | 63.1302 | -60.0952 | -60.2051 | -59.7794 | -0.23804 | 0.027466 | -0.28381 | 0.064087 | 60.1044 | -0.2655 | 60.3424 | -0.027466 | -0.082397 | 0.032043 | -0.050354 | -0.022888 | 0.29297 | -0.13275 | 0.37537 | -0.050354 | 0.30212 | 123.2071 | 0.059509 | 123.2849 | 123.5184 | 123.3673 | 123.2803 | 123.2849 | -123.4909 | -123.3353 | 122.9691 | 123.2025 | 60.0449 | 60.1181
224.4844 | 123.349 | -60.0906 | 63.1485 | 0.0033567 | -0.00093353 | 0.060575 | 0.064971 | -0.0015103 | -0.00099762 | -0.0015935 | -0.014069 | 0.00010888 | 0.06749 | 0.064345 | -0.003025 | -0.0027302 | 0.0011643 | 0.050354 | 63.2446 | -60.3058 | 62.8601 | -60.0174 | -60.3653 | -0.013733 | 0.027466 | 63.208 | -60.1593 | 63.1256 | -60.1135 | -60.1959 | -59.7702 | -0.21515 | 0.09613 | -0.28839 | 0.073242 | 60.0769 | -0.27466 | 60.2921 | -0.059509 | -0.068665 | 0.059509 | -0.022889 | -0.022888 | 0.32043 | -0.10529 | 0.3891 | -0.036621 | 0.28839 | 123.1659 | 0.045777 | 123.2849 | 123.5504 | 123.3673 | 123.3353 | 123.2986 | -123.4543 | -123.3078 | 122.9507 | 123.2162 | 60.141 | 60.1181
225.4844 | 123.3765 | -60.0677 | 63.1485 | -0.03479 | 0.00056187 | 0.065488 | 0.065399 | -0.0012967 | -0.0014248 | 0.0026789 | -0.026276 | -0.00095912 | 0.066422 | 0.064132 | -0.0028112 | 0.00068782 | -0.0020401 | -0.009155 | 63.2217 | -60.3424 | 62.9288 | -60.0037 | -60.3104 | 0.022888 | 0.068665 | 63.1943 | -60.1364 | 63.1668 | -60.0769 | -60.1868 | -59.761 | -0.27466 | 0.073242 | -0.21973 | 0.064087 | 60.0906 | -0.24262 | 60.3653 | 0.032043 | -0.068665 | 0.045776 | 0.01831 | -0.009155 | 0.3067 | -0.11902 | 0.37537 | -0.050354 | 0.33875 | 123.2712 | 0.05951 | 123.3032 | 123.5641 | 123.3307 | 123.2895 | 123.262 | -123.4909 | -123.2849 | 122.9965 | 123.2346 | 60.0586 | 60.1364
226.4844 | 123.381 | -60.0586 | 63.1943 | 0.010986 | -0.00050633 | 0.061643 | 0.06134 | -0.0027921 | -0.00014322 | 0.0020379 | 0.004242 | 0.0011771 | 0.068772 | 0.062636 | 0.000393 | -0.0014484 | -0.00054474 | -0.022888 | 63.2263 | -60.3424 | 62.8967 | -60.0128 | -60.3287 | 0.027466 | 0.022888 | 63.208 | -60.1501 | 63.1119 | -60.0952 | -60.2005 | -59.8709 | -0.28381 | 0.032043 | -0.29755 | 0.045777 | 60.0861 | -0.27008 | 60.3699 | 0.013733 | -0.091552 | 0.013733 | -0.082398 | -0.036621 | 0.18768 | -0.14191 | 0.27923 | -0.050354 | 0.32959 | 123.2391 | 0.054931 | 123.262 | 123.5687 | 123.3582 | 123.2849 | 123.2666 | -123.5367 | -123.3444 | 122.9553 | 123.1705 | 60.0357 | 60.0815
227.4844 | 123.3627 | -60.0769 | 63.1073 | -0.03479 | 0.0022709 | 0.06442 | 0.065399 | 0.00083954 | 0.00071138 | 0.00096987 | -0.035431 | 0.00096348 | 0.067276 | 0.061996 | -0.0008886 | -0.00080758 | -0.00033114 | 0.013733 | 63.2126 | -60.3287 | 62.9288 | -59.9716 | -60.3149 | 0.036621 | 0.050354 | 63.2034 | -60.1501 | 63.176 | -60.0815 | -60.1959 | -59.7656 | -0.25177 | 0.10528 | -0.17853 | 0.10529 | 60.1135 | -0.23804 | 60.3653 | 0.013733 | -0.073242 | 0.09613 | 0.068664 | -0.004578 | 0.31128 | -0.11902 | 0.38452 | -0.045777 | 0.35706 | 123.2574 | 0.068664 | 123.3261 | 123.5413 | 123.3536 | 123.2895 | 123.2803 | -123.436 | -123.2574 | 123.0057 | 123.2529 | 60.0906 | 60.1273
228.5469 | 123.3353 | -60.0861 | 63.1622 | -0.0042723 | 0.0022709 | 0.06442 | 0.062835 | 0.0016939 | -0.0012112 | 0.00096987 | 0.0072936 | 0.0013907 | 0.069199 | 0.067123 | 0.000393 | -0.0010212 | -0.0016129 | -0.027466 | 63.2217 | -60.3287 | 62.915 | -59.9945 | -60.3333 | 0.041199 | 0.032043 | 63.2172 | -60.141 | 63.1165 | -60.1044 | -60.2005 | -59.8068 | -0.24261 | 0.05951 | -0.24719 | 0.091553 | 60.1273 | -0.24719 | 60.3699 | -0.004578 | -0.054931 | 0.054932 | -0.045776 | -0.01831 | 0.27924 | -0.11444 | 0.33417 | -0.059509 | 0.33417 | 123.2437 | 0.036621 | 123.2574 | 123.5504 | 123.3582 | 123.3078 | 123.3032 | -123.4909 | -123.3032 | 123.0011 | 123.2025 | 60.0586 | 60.1181
229.4844 | 123.3353 | -60.0723 | 63.1302 | -0.065308 | -0.00029273 | 0.063993 | 0.063049 | -0.0032193 | -0.00035682 | 0.00096987 | -0.035431 | 0.0030997 | 0.066849 | 0.067763 | -0.000675 | 0.001115 | -0.00097194 | -0.018311 | 63.1805 | -60.3516 | 62.9196 | -59.9487 | -60.3516 | -0.013733 | 0.018311 | 63.1989 | -60.1501 | 63.1577 | -60.1181 | -60.2142 | -59.7702 | -0.27923 | 0.050354 | -0.21057 | 0.1236 | 60.0586 | -0.27923 | 60.3378 | 0 | -0.077819 | 0.068665 | 0.027466 | -0.045776 | 0.30212 | -0.14191 | 0.37994 | -0.064087 | 0.40283 | 123.2712 | 0.032043 | 123.3078 | 123.5321 | 123.349 | 123.2529 | 123.2712 | -123.4818 | -123.2803 | 122.9919 | 123.23 | 60.054 | 60.0906
230.5469 | 123.3948 | -60.0723 | 63.0798 | -0.042419 | -0.00029273 | 0.063779 | 0.061981 | 0.00041234 | 0.00092498 | 0.00054267 | 0.05307 | 0.00032248 | 0.068558 | 0.067123 | -0.0004614 | -0.001662 | 0.0033005 | -0.068665 | 63.1668 | -60.3333 | 62.9196 | -59.9762 | -60.141 | 0.050354 | -0.068665 | 63.1302 | -60.1456 | 63.1714 | -60.0677 | -60.1639 | -59.729 | -0.26093 | 0.086975 | -0.16022 | 0.096131 | 60.1227 | -0.068664 | 60.3836 | 0.19226 | -0.073242 | 0.050354 | 0.091553 | 0.004578 | 0.34332 | -0.091552 | 0.41656 | -0.01831 | 0.35706 | 123.2529 | 0.07782 | 123.317 | 123.5001 | 123.2758 | 123.2391 | 123.2025 | -123.4131 | -123.2254 | 122.9919 | 123.2437 | 60.0037 | 60.0037
231.4844 | 123.349 | -60.1181 | 63.1027 | 0.018616 | -7.913e-05 | 0.065275 | 0.065826 | 0.00019874 | 0.0017794 | 0.00075627 | -0.065949 | 0.0013907 | 0.066422 | 0.070968 | -0.002384 | 4.7018e-05 | 9.6064e-05 | -0.041199 | 63.1989 | -60.3561 | 62.9105 | -59.9945 | -60.3424 | -0.041199 | -0.004578 | 63.176 | -60.1547 | 63.1165 | -60.1364 | -60.2463 | -59.7931 | -0.23804 | 0.096131 | -0.19226 | 0.1236 | 60.0769 | -0.2243 | 60.3149 | 0.013733 | -0.036621 | 0.073242 | 0.013733 | -0.018311 | 0.32501 | -0.12817 | 0.36163 | -0.091553 | 0.36163 | 123.2666 | 0.01831 | 123.2712 | 123.555 | 123.3307 | 123.317 | 123.2941 | -123.4589 | -123.2574 | 123.0286 | 123.2346 | 60.0769 | 60.1135
232.5469 | 123.4497 | -60.0677 | 63.0753 | -0.027161 | 0.0014163 | 0.064634 | 0.061553 | 0.0010531 | 0.0015658 | -0.00052553 | 0.065277 | -0.00031832 | 0.068131 | 0.067123 | -0.001316 | -0.001662 | 0.0020187 | 0.004578 | 63.1943 | -60.3149 | 62.9974 | -59.9121 | -60.2463 | 0.082397 | 0.091553 | 63.1439 | -60.1501 | 63.2309 | -59.9716 | -60.0723 | -59.6832 | -0.24719 | 0.11902 | -0.077819 | 0.15564 | 60.1501 | -0.17853 | 60.3973 | 0.068664 | -0.082397 | 0.068665 | 0.15564 | 0.09613 | 0.38452 | -0.004578 | 0.46692 | 0.077819 | 0.40283 | 123.3124 | 0.17853 | 123.381 | 123.5092 | 123.2941 | 123.262 | 123.2117 | -123.3902 | -123.2254 | 123.0652 | 123.2986 | 60.0723 | 60.1593
233.5 | 123.4039 | -60.0449 | 63.0798 | 0.018616 | 0.0031253 | 0.064207 | 0.062194 | 0.0014803 | 7.0582e-05 | -0.0026617 | 0.050018 | -0.0026681 | 0.067063 | 0.059859 | -0.0036658 | -0.00016658 | -0.00075834 | 0.032043 | 63.1714 | -60.2829 | 63.0112 | -59.8663 | -60.2371 | 0.11444 | 0.15564 | 63.1485 | -60.1273 | 63.1073 | -60.1181 | -60.0677 | -59.6741 | -0.23804 | 0.091553 | -0.068665 | 0.17853 | 60.1593 | -0.19226 | 60.3973 | 0.045776 | -0.082397 | 0.068665 | 0.027466 | -0.073242 | 0.37079 | -0.022888 | 0.45319 | 0.059509 | 0.41657 | 123.2941 | 0.009155 | 123.2346 | 123.4543 | 123.2758 | 123.2162 | 123.1934 | -123.3627 | -123.2071 | 123.056 | 123.1522 | 60.0769 | 60.2005
234.5469 | 123.4268 | -60.054 | 63.0844 | -0.095825 | 0.0012027 | 0.062284 | 0.063476 | -0.00065586 | 7.0582e-05 | -0.0020209 | 0.037811 | 0.0020315 | 0.065995 | 0.06285 | -0.0019568 | -0.0010212 | -0.0018265 | -0.050354 | 63.1805 | -60.3378 | 62.9471 | -59.9625 | -60.2921 | 0.041199 | 0.041199 | 63.1348 | -60.1318 | 63.2172 | -60.0174 | -60.1089 | -59.697 | -0.28381 | 0.09613 | -0.13733 | 0.091553 | 60.0952 | -0.23804 | 60.379 | 0.045777 | -0.07782 | 0.050354 | 0.13275 | 0.036621 | 0.35706 | -0.054932 | 0.43488 | 0.022888 | 0.37537 | 123.2849 | 0.11444 | 123.349 | 123.5184 | 123.2666 | 123.2346 | 123.1888 | -123.4222 | -123.2162 | 123.0011 | 123.2712 | 60.0037 | 60.0952
235.4844 | 123.2986 | -60.0952 | 63.121 | -0.019531 | 0.0016299 | 0.066129 | 0.064971 | 0.0021213 | 7.0582e-05 | 0.0033197 | -0.090363 | 0.0024589 | 0.067063 | 0.067123 | -0.003025 | 0.00026062 | -0.0028945 | -0.059509 | 63.1805 | -60.3607 | 62.8922 | -60.0357 | -60.3973 | -0.09613 | -0.091553 | 63.1989 | -60.1913 | 63.1073 | -60.1776 | -60.26 | -59.8022 | -0.2655 | 0.059509 | -0.22888 | 0.059509 | 59.9991 | -0.30212 | 60.2646 | -0.036621 | -0.09613 | 0.07782 | -0.013733 | -0.082397 | 0.29297 | -0.16479 | 0.3891 | -0.068665 | 0.32501 | 123.2529 | 0.013733 | 123.2986 | 123.5413 | 123.3902 | 123.2758 | 123.2941 | -123.4818 | -123.3124 | 122.9874 | 123.2025 | 60.0357 | 60.0037
236.5469 | 123.3856 | -60.0586 | 63.1302 | 0.010986 | 0.00056187 | 0.063138 | 0.064971 | 0.0025485 | 0.00092498 | -0.0018073 | -0.065949 | 0.00010888 | 0.067917 | 0.071181 | -0.0025976 | -0.0012348 | -0.0013991 | -0.013733 | 63.208 | -60.3333 | 62.9333 | -59.9899 | -60.3195 | 0.013733 | 0.086975 | 63.1851 | -60.1593 | 63.1622 | -60.0769 | -60.1913 | -59.7519 | -0.27466 | 0.07782 | -0.19684 | 0.068665 | 60.0723 | -0.26093 | 60.347 | 0.013733 | -0.10071 | 0.054932 | 0.032043 | -0.01831 | 0.3067 | -0.13275 | 0.40741 | -0.032043 | 0.34332 | 123.2666 | 0.082398 | 123.3215 | 123.5413 | 123.3444 | 123.2666 | 123.2437 | -123.4634 | -123.2895 | 122.9919 | 123.2208 | 60.0449 | 60.1456
237.4844 | 123.3353 | -60.1089 | 63.121 | -0.011902 | -0.0011471 | 0.062925 | 0.064544 | 0.0021213 | -0.001852 | 0.0018243 | -0.041534 | 0.00096348 | 0.073685 | 0.069472 | 0.0006066 | -0.003371 | -0.00054474 | -0.09613 | 63.176 | -60.3882 | 62.8326 | -60.0952 | -60.4523 | -0.10986 | -0.40283 | 63.1256 | -60.228 | 63.1439 | -60.1913 | -60.3149 | -59.8068 | -0.27924 | 0.054931 | -0.28839 | 0.013733 | 59.9991 | -0.34332 | 60.2783 | -0.064087 | -0.11902 | 0.004577 | 0.022888 | -0.082397 | 0.30212 | -0.20599 | 0.42114 | -0.086975 | 0.29297 | 123.2208 | 0.036621 | 123.3719 | 123.5641 | 123.3536 | 123.2849 | 123.2346 | -123.5092 | -123.349 | 122.9416 | 123.2529 | 60.0128 | 59.7061
238.5 | 123.4177 | -60.0723 | 63.089 | -0.10345 | -0.0017881 | 0.062711 | 0.06134 | -0.0015103 | 0.0013522 | -0.00095273 | 0.05307 | -0.00010472 | 0.067276 | 0.062423 | 0.0014612 | -0.0023028 | -0.00054474 | -0.041199 | 63.1577 | -60.3195 | 62.9379 | -59.9579 | -60.3195 | 0.018311 | 0.004578 | 63.1622 | -60.1776 | 63.1897 | -60.022 | -60.1181 | -59.7198 | -0.24719 | 0.068665 | -0.15106 | 0.11444 | 60.0906 | -0.24719 | 60.3378 | 0 | -0.10529 | 0.073242 | 0.10071 | 0.050354 | 0.35248 | -0.045776 | 0.45776 | 0.059509 | 0.36163 | 123.2574 | 0.15564 | 123.3673 | 123.4772 | 123.3398 | 123.23 | 123.2346 | -123.4085 | -123.2666 | 123.0103 | 123.262 | 60.0311 | 60.0769
239.5469 | 123.349 | -60.0815 | 63.1302 | -0.03479 | -0.00029273 | 0.063566 | 0.064544 | 0.0010531 | 0.00028418 | 0.0037469 | -0.047638 | 0.0020315 | 0.068558 | 0.065627 | -0.002384 | -0.0014484 | 0.0011643 | -0.022888 | 63.1943 | -60.3424 | 62.9333 | -59.9991 | -60.3241 | 0.013733 | 0.050354 | 63.1943 | -60.141 | 63.1485 | -60.0677 | -60.2051 | -59.7473 | -0.26093 | 0.064087 | -0.19684 | 0.082398 | 60.0952 | -0.24262 | 60.3561 | 0.01831 | -0.059509 | 0.064087 | 0.018311 | 0.013733 | 0.33417 | -0.1236 | 0.39368 | -0.064087 | 0.34332 | 123.2758 | 0.073242 | 123.2895 | 123.5367 | 123.3353 | 123.2758 | 123.2758 | -123.4726 | -123.2712 | 123.0148 | 123.23 | 60.0586 | 60.1318
240.4844 | 123.3078 | -60.0998 | 63.121 | -0.03479 | 0.0016299 | 0.064634 | 0.063049 | 0.0029757 | -0.00014322 | 0.0016107 | -0.069 | 0.0020315 | 0.06749 | 0.062209 | -0.0025976 | 0.00090142 | -0.0054581 | -0.059509 | 63.1851 | -60.3699 | 62.883 | -60.0449 | -60.4156 | -0.09613 | -0.086975 | 63.1622 | -60.2005 | 63.0981 | -60.1547 | -60.2783 | -59.8251 | -0.27008 | 0.064087 | -0.23804 | 0.054931 | 60.0037 | -0.31586 | 60.2737 | -0.045776 | -0.10071 | 0.041198 | -0.022888 | -0.054932 | 0.27466 | -0.17853 | 0.37537 | -0.07782 | 0.32501 | 123.2529 | 0.045776 | 123.2986 | 123.555 | 123.3627 | 123.2849 | 123.262 | -123.4909 | -123.3215 | 122.9828 | 123.1979 | 60.0403 | 60.0128
241.5469 | 123.3719 | -60.0449 | 63.1805 | -0.050049 | -0.00050633 | 0.06143 | 0.062408 | -0.0015103 | 7.0582e-05 | -0.0015935 | 0.010345 | -0.00053192 | 0.068985 | 0.070968 | -0.001316 | 0.00068782 | -0.0024673 | -0.045776 | 63.2309 | -60.3149 | 62.8967 | -60.0082 | -60.3378 | 0.027466 | 0.013733 | 63.1989 | -60.1547 | 63.121 | -60.1089 | -60.2417 | -59.7748 | -0.27008 | 0.050354 | -0.28381 | 0.036621 | 60.0723 | -0.29297 | 60.3424 | -0.022889 | -0.10986 | 0.018311 | -0.059509 | -0.064087 | 0.27008 | -0.19684 | 0.37994 | -0.086975 | 0.3067 | 123.2117 | 0.045776 | 123.2758 | 123.5458 | 123.3536 | 123.2758 | 123.2437 | -123.4955 | -123.3353 | 122.9416 | 123.1659 | 59.9991 | 60.0586
242.4844 | 123.3261 | -60.0952 | 63.089 | -0.057678 | 0.0020573 | 0.063566 | 0.066253 | 0.0046847 | -0.00099762 | 0.0026789 | -0.05069 | 0.0018179 | 0.066422 | 0.067977 | -0.000675 | 0.00068782 | 0.0026597 | -0.018311 | 63.1897 | -60.3333 | 62.9013 | -59.9945 | -60.3607 | -0.027466 | 0 | 63.2034 | -60.1685 | 63.1302 | -60.1318 | -60.2554 | -59.7885 | -0.23804 | 0.10071 | -0.18768 | 0.10071 | 60.0677 | -0.2655 | 60.3058 | -0.027466 | -0.073242 | 0.11444 | 0.041199 | -0.036621 | 0.3067 | -0.16022 | 0.37994 | -0.086975 | 0.33875 | 123.2346 | 0.036621 | 123.2986 | 123.5229 | 123.3719 | 123.2849 | 123.2986 | -123.4222 | -123.2574 | 122.9965 | 123.2254 | 60.0769 | 60.0952
243.4844 | 123.3765 | -60.0906 | 63.0936 | -0.042419 | 0.0022709 | 0.062284 | 0.061981 | 0.00041234 | -0.00035682 | 0.0016107 | 0.050018 | -0.0020273 | 0.066422 | 0.064345 | 0.0012476 | -0.0023028 | 0.00073706 | -0.10529 | 63.1622 | -60.3378 | 62.9425 | -59.9854 | -60.3378 | -0.018311 | -0.073242 | 63.1302 | -60.1685 | 63.1622 | -60.0586 | -60.1822 | -59.7382 | -0.24719 | 0.068664 | -0.15106 | 0.10529 | 60.0723 | -0.24719 | 60.3195 | 0 | -0.07782 | 0.036621 | 0.068664 | 0.032043 | 0.35248 | -0.091553 | 0.4303 | -0.013733 | 0.35248 | 123.2803 | 0.10986 | 123.3307 | 123.5001 | 123.2986 | 123.2529 | 123.2208 | -123.4314 | -123.262 | 123.0331 | 123.2529 | 59.9854 | 60.0174
244.5469 | 123.349 | -60.0952 | 63.1073 | -0.057678 | 0.0041935 | 0.063566 | 0.062835 | 0.0031893 | 0.00092498 | 0.00054267 | -0.044586 | -0.0013863 | 0.06749 | 0.066482 | -0.0019568 | 4.7018e-05 | 0.0015915 | -0.018311 | 63.2034 | -60.3378 | 62.9242 | -59.9762 | -60.3333 | 0.013733 | 0.041199 | 63.1943 | -60.1501 | 63.1485 | -60.0815 | -60.1959 | -59.7702 | -0.24261 | 0.09613 | -0.18311 | 0.11902 | 60.1089 | -0.23804 | 60.3516 | 0.004578 | -0.054931 | 0.086975 | 0.041199 | 0.013733 | 0.32501 | -0.10071 | 0.37994 | -0.045777 | 0.36163 | 123.262 | 0.068664 | 123.2986 | 123.5413 | 123.3444 | 123.2986 | 123.2895 | -123.4451 | -123.2574 | 123.0194 | 123.2437 | 60.0769 | 60.1364
245.4844 | 123.4863 | -60.0586 | 63.0569 | -0.13397 | -7.913e-05 | 0.064847 | 0.063049 | 0.00041234 | 0.0013522 | -9.8328e-05 | -0.0018616 | -0.00010472 | 0.068985 | 0.07054 | -0.0017432 | -0.0010212 | -0.00097194 | -0.064087 | 63.1119 | -60.3424 | 62.9608 | -59.9487 | -60.3104 | -0.041199 | -0.045776 | 63.1119 | -60.1868 | 63.1897 | -60.0403 | -60.1593 | -59.697 | -0.28381 | 0.054931 | -0.096131 | 0.10986 | 60.0174 | -0.25177 | 60.3012 | 0.032043 | -0.12817 | 0.054931 | 0.13275 | 0.018311 | 0.36163 | -0.10071 | 0.48981 | 0.027466 | 0.39368 | 123.3032 | 0.14648 | 123.3765 | 123.4543 | 123.2986 | 123.1705 | 123.1705 | -123.3994 | -123.2437 | 123.0194 | 123.2483 | 59.9945 | 60.0128
246.5469 | 123.3765 | -60.0815 | 63.121 | 0.033875 | -0.00093353 | 0.061857 | 0.064544 | 0.0010531 | -0.00014322 | 0.00011527 | -0.038483 | 0.0016043 | 0.06749 | 0.073958 | -0.001316 | 0.00068782 | -0.00011754 | -0.013733 | 63.1897 | -60.3287 | 62.9288 | -59.9716 | -60.347 | 0.009155 | 0.036621 | 63.1714 | -60.1639 | 63.1668 | -60.1044 | -60.2005 | -59.7427 | -0.24719 | 0.068664 | -0.19226 | 0.10986 | 60.0906 | -0.2655 | 60.3378 | -0.018311 | -0.082397 | 0.050354 | 0.045776 | -0.022888 | 0.33875 | -0.11902 | 0.42114 | -0.036621 | 0.35706 | 123.2574 | 0.059509 | 123.3307 | 123.5184 | 123.3353 | 123.2712 | 123.2529 | -123.4497 | -123.2849 | 123.0103 | 123.2483 | 60.0677 | 60.1181
247.4844 | 123.4863 | -60.0723 | 63.0249 | -0.10345 | 0.0016299 | 0.06442 | 0.063049 | 0.0014803 | 0.0030612 | -0.00073913 | -0.014069 | -0.00010472 | 0.067276 | 0.059218 | -0.0008886 | -0.0018756 | 0.0013779 | -0.050354 | 63.1256 | -60.3241 | 62.9608 | -59.9487 | -60.2921 | -0.050354 | -0.045776 | 63.089 | -60.1501 | 63.208 | -60.0357 | -60.1501 | -59.7061 | -0.25177 | 0.10071 | -0.064087 | 0.1236 | 60.022 | -0.21973 | 60.2737 | 0.032044 | -0.077819 | 0.064087 | 0.18311 | 0.036621 | 0.36621 | -0.077819 | 0.44403 | 0 | 0.37537 | 123.2849 | 0.11444 | 123.3582 | 123.4497 | 123.2391 | 123.1979 | 123.1613 | -123.349 | -123.175 | 123.0331 | 123.2803 | 60.022 | 60.0266
248.4844 | 123.4451 | -60.0677 | 63.0569 | -0.042419 | -0.00029273 | 0.06143 | 0.063262 | 0.0012667 | 0.0015658 | -0.00095273 | 0.050018 | -0.00031832 | 0.066849 | 0.066268 | -0.0017432 | -0.0018756 | 0.0022323 | -0.064087 | 63.1485 | -60.3516 | 62.9654 | -59.9442 | -60.2829 | 0.050354 | 0.018311 | 63.1439 | -60.1501 | 63.2034 | -60.0037 | -60.0998 | -59.697 | -0.28381 | 0.091553 | -0.091553 | 0.1236 | 60.1181 | -0.21515 | 60.4019 | 0.068664 | -0.082397 | 0.086975 | 0.14648 | 0.064087 | 0.37079 | -0.032043 | 0.45319 | 0.050354 | 0.40741 | 123.317 | 0.14648 | 123.3536 | 123.5001 | 123.2941 | 123.2162 | 123.2117 | -123.4085 | -123.2071 | 123.0331 | 123.2712 | 60.0037 | 60.0861
249.5469 | 123.3398 | -60.1089 | 63.0844 | 0.0033567 | -7.913e-05 | 0.06442 | 0.064544 | 0.00019874 | -0.00078402 | -0.0035163 | -0.041534 | 0.0013907 | 0.069199 | 0.067763 | -0.0032386 | -0.00016658 | 0.0015915 | -0.10986 | 63.1485 | -60.3607 | 62.851 | -60.0677 | -60.4019 | -0.11902 | -0.13733 | 63.1531 | -60.1913 | 63.1348 | -60.1318 | -60.2417 | -59.7794 | -0.25177 | 0.064087 | -0.23346 | 0.041199 | 59.9899 | -0.29297 | 60.2417 | -0.041199 | -0.082397 | 0.068664 | 0.050354 | -0.022888 | 0.32959 | -0.13275 | 0.41199 | -0.050354 | 0.29297 | 123.2117 | 0.059509 | 123.3261 | 123.5092 | 123.3444 | 123.2574 | 123.262 | -123.4451 | -123.2758 | 122.9599 | 123.2437 | 59.9991 | 59.9716
250.4844 | 123.3398 | -60.1089 | 63.0661 | 0.0033567 | 0.00098907 | 0.065061 | 0.064544 | -1.486e-05 | -0.00078402 | 0.00011527 | -0.056793 | 0.0020315 | 0.066422 | 0.065627 | -0.002384 | -0.0014484 | 0.0018051 | -0.14191 | 63.1989 | -60.3607 | 62.851 | -60.0815 | -60.4202 | -0.11902 | -0.15106 | 63.1714 | -60.1776 | 63.1165 | -60.141 | -60.2646 | -59.7839 | -0.25177 | 0.13275 | -0.21515 | 0.027466 | 59.9899 | -0.31128 | 60.2417 | -0.059509 | -0.068664 | 0.10529 | 0.050354 | -0.032043 | 0.32501 | -0.15564 | 0.39368 | -0.086975 | 0.27924 | 123.2117 | 0.036621 | 123.2941 | 123.5596 | 123.349 | 123.3078 | 123.2803 | -123.4268 | -123.2437 | 122.9599 | 123.2254 | 59.967 | 59.9579
251.4844 | 123.3994 | -60.0632 | 63.0615 | -0.088196 | 0.00056187 | 0.065061 | 0.064544 | 0.0021213 | 0.0030612 | 0.00011527 | 0.016449 | 0.00053628 | 0.06514 | 0.066482 | -0.000675 | -0.0010212 | 0.00073706 | -0.07782 | 63.1393 | -60.3195 | 62.9471 | -59.9213 | -60.3195 | -0.027466 | -0.027466 | 63.1165 | -60.1868 | 63.1851 | -60.0861 | -60.1685 | -59.7336 | -0.25635 | 0.07782 | -0.11444 | 0.14191 | 60.0357 | -0.25635 | 60.2921 | 0 | -0.1236 | 0.054932 | 0.1236 | -0.022889 | 0.32959 | -0.10529 | 0.45319 | 0.018311 | 0.39825 | 123.2666 | 0.10071 | 123.3719 | 123.4589 | 123.3032 | 123.2025 | 123.1796 | -123.381 | -123.2483 | 123.0103 | 123.2483 | 59.9854 | 60.0357
252.5469 | 123.3627 | -60.0861 | 63.1302 | -0.03479 | 0.0012027 | 0.063352 | 0.063903 | 0.00083954 | 0.0011386 | 0.0013971 | -0.047638 | 0.0013907 | 0.066422 | 0.068831 | -0.0028112 | -0.00080758 | -0.0039627 | -0.022888 | 63.1622 | -60.3241 | 62.915 | -59.9945 | -60.3287 | -0.013733 | 0.018311 | 63.1943 | -60.1685 | 63.176 | -60.1135 | -60.2188 | -59.7519 | -0.23804 | 0.032043 | -0.21515 | 0.091553 | 60.0723 | -0.24261 | 60.3104 | -0.004577 | -0.082397 | 0.064087 | 0.045776 | -0.027465 | 0.33417 | -0.13275 | 0.41656 | -0.050354 | 0.32959 | 123.2391 | 0.054932 | 123.3444 | 123.4863 | 123.3627 | 123.2483 | 123.2803 | -123.4543 | -123.2986 | 123.0011 | 123.262 | 60.0632 | 60.1044
253.4844 | 123.3856 | -60.1044 | 63.0707 | -0.065308 | 0.0020573 | 0.063779 | 0.063476 | 0.0010531 | -0.00035682 | -0.0015935 | 0.013397 | -0.0011727 | 0.065995 | 0.060714 | -0.001316 | -0.0014484 | 0.0041551 | -0.086975 | 63.1348 | -60.3195 | 62.9379 | -59.967 | -60.3378 | -0.032043 | -0.041199 | 63.1119 | -60.173 | 63.1577 | -60.0861 | -60.1685 | -59.7382 | -0.21515 | 0.064087 | -0.13275 | 0.13733 | 60.0723 | -0.23346 | 60.2875 | -0.018311 | -0.068665 | 0.041198 | 0.086975 | 0.01831 | 0.36621 | -0.064087 | 0.43488 | 0.004578 | 0.35248 | 123.2574 | 0.086975 | 123.3307 | 123.4543 | 123.2849 | 123.2391 | 123.2162 | -123.3902 | -123.2437 | 123.0423 | 123.262 | 60.0174 | 60.0632
254.4844 | 123.4314 | -60.0861 | 63.0569 | -0.11108 | 0.0018435 | 0.062711 | 0.062622 | 0.0014803 | -0.0014248 | 0.00054267 | -0.035431 | 0.00074988 | 0.06749 | 0.061996 | -0.0019568 | -0.00016658 | -0.00054474 | -0.082397 | 63.1302 | -60.3333 | 62.9471 | -59.9533 | -60.3333 | -0.054932 | -0.059509 | 63.1027 | -60.1593 | 63.208 | -60.0449 | -60.1685 | -59.7015 | -0.24719 | 0.073242 | -0.10986 | 0.13275 | 60.0311 | -0.24719 | 60.2783 | 0 | -0.073242 | 0.045776 | 0.15106 | 0.041199 | 0.38452 | -0.082397 | 0.45776 | -0.009155 | 0.37994 | 123.2803 | 0.11444 | 123.3673 | 123.4634 | 123.262 | 123.2162 | 123.1888 | -123.3902 | -123.2162 | 123.0331 | 123.2941 | 60.0037 | 60.0266
255.4844 | 123.3856 | -60.0632 | 63.0524 | -0.13397 | 0.0014163 | 0.062925 | 0.065185 | -0.0034329 | -0.00078402 | -0.00095273 | 0.019501 | -0.0013863 | 0.066849 | 0.062423 | -0.0011022 | -0.0014484 | 0.0035141 | -0.086975 | 63.1302 | -60.3287 | 62.9425 | -59.9579 | -60.3333 | -0.036621 | -0.059509 | 63.1119 | -60.1501 | 63.1485 | -60.0769 | -60.1547 | -59.7565 | -0.2655 | 0.07782 | -0.10986 | 0.10528 | 60.0266 | -0.27008 | 60.2921 | -0.004578 | -0.086975 | 0.059509 | 0.096131 | -0.013733 | 0.3067 | -0.091553 | 0.39368 | -0.004578 | 0.37079 | 123.2712 | 0.073242 | 123.2986 | 123.4589 | 123.262 | 123.1934 | 123.175 | -123.381 | -123.2025 | 123.0057 | 123.2117 | 59.9762 | 60.0037
256.4844 | 123.4406 | -60.0815 | 63.0615 | -0.065308 | 0.00077547 | 0.065916 | 0.06369 | -0.00065586 | 7.0582e-05 | 0.0020379 | -0.047638 | 0.0020315 | 0.068344 | 0.067336 | -0.001316 | 0.00068782 | 9.6064e-05 | -0.054932 | 63.1439 | -60.3424 | 62.9333 | -59.9579 | -60.3104 | -0.041199 | -0.050354 | 63.1256 | -60.1639 | 63.2034 | -60.0494 | -60.1639 | -59.7015 | -0.26093 | 0.082398 | -0.12817 | 0.1236 | 60.0403 | -0.22888 | 60.3012 | 0.032043 | -0.082397 | 0.064087 | 0.14191 | 0.032044 | 0.37994 | -0.082397 | 0.46234 | 0 | 0.38452 | 123.2758 | 0.11444 | 123.3673 | 123.4863 | 123.2895 | 123.2254 | 123.2071 | -123.4039 | -123.2254 | 123.0148 | 123.2849 | 60.0266 | 60.0311
257.4844 | 123.3902 | -60.0906 | 63.0661 | -0.072937 | 0.00056187 | 0.063352 | 0.061126 | -0.0017239 | -0.00057042 | -0.0030889 | -0.011017 | -0.00031832 | 0.066208 | 0.068191 | -0.000675 | 0.00090142 | 0.0050095 | -0.091553 | 63.1393 | -60.3287 | 62.9425 | -59.9716 | -60.3378 | -0.032043 | -0.073242 | 63.1485 | -60.1593 | 63.1622 | -60.0815 | -60.1685 | -59.729 | -0.23804 | 0.073242 | -0.1236 | 0.11902 | 60.0586 | -0.24719 | 60.2966 | -0.009156 | -0.068665 | 0.082398 | 0.09613 | 0.009155 | 0.36163 | -0.07782 | 0.4303 | -0.009155 | 0.35706 | 123.2712 | 0.07782 | 123.3215 | 123.468 | 123.3078 | 123.23 | 123.2391 | -123.3948 | -123.2254 | 123.0331 | 123.2529 | 59.9991 | 60.0174
258.5469 | 123.3307 | -60.0998 | 63.1256 | -0.080566 | 0.0012027 | 0.064847 | 0.064758 | -0.0010831 | -0.00057042 | 0.0018243 | -0.087311 | 0.0024589 | 0.065567 | 0.066695 | 0.000393 | -0.001662 | -0.00033114 | -0.07782 | 63.1805 | -60.347 | 62.883 | -60.0311 | -60.4019 | -0.082397 | -0.09613 | 63.1989 | -60.173 | 63.1119 | -60.1547 | -60.2737 | -59.816 | -0.24719 | 0.054932 | -0.24261 | 0.068664 | 60.0174 | -0.30212 | 60.2646 | -0.054932 | -0.073243 | 0.073243 | -0.013733 | -0.054932 | 0.28381 | -0.17395 | 0.35706 | -0.10071 | 0.31586 | 123.23 | 0.018311 | 123.2849 | 123.5275 | 123.3719 | 123.2803 | 123.2986 | -123.4726 | -123.2986 | 122.9828 | 123.2117 | 60.022 | 60.0037
259.4844 | 123.4451 | -60.054 | 63.0844 | -0.065308 | 0.0014163 | 0.063138 | 0.064117 | -0.0034329 | -0.00014322 | 0.00054267 | 0.022552 | 0.0013907 | 0.068985 | 0.061355 | -0.0017432 | -0.00016658 | -0.0020401 | -0.032043 | 63.1622 | -60.2921 | 62.9791 | -59.9121 | -60.2371 | 0.086975 | 0.09613 | 63.1119 | -60.1685 | 63.2401 | -59.967 | -60.0632 | -59.6786 | -0.23804 | 0.077819 | -0.10529 | 0.14191 | 60.141 | -0.18311 | 60.379 | 0.054931 | -0.11444 | 0.027465 | 0.15564 | 0.086975 | 0.37537 | -0.009155 | 0.48981 | 0.10529 | 0.37994 | 123.2712 | 0.20142 | 123.4085 | 123.4543 | 123.2803 | 123.2162 | 123.1659 | -123.3765 | -123.2529 | 123.0331 | 123.2941 | 60.022 | 60.1501
260.5469 | 123.3719 | -60.1044 | 63.0569 | -0.019531 | -0.0013607 | 0.063138 | 0.063476 | 0.00062594 | -0.0016384 | 0.0016107 | -0.081207 | 0.0022453 | 0.066208 | 0.068191 | -0.0008886 | 0.001115 | -0.00033114 | 0.013733 | 63.176 | -60.3653 | 62.8876 | -60.0952 | -60.4248 | -0.11902 | -0.15106 | 63.1531 | -60.1868 | 63.1165 | -60.1501 | -60.2737 | -59.816 | -0.26093 | 0.11902 | -0.16937 | 0.009155 | 59.9854 | -0.32043 | 60.2463 | -0.05951 | -0.082398 | 0.09613 | 0.059509 | -0.045776 | 0.28839 | -0.16937 | 0.37079 | -0.086975 | 0.27008 | 123.2529 | 0.036622 | 123.3032 | 123.5413 | 123.3398 | 123.2803 | 123.2574 | -123.4222 | -123.2437 | 122.9919 | 123.2208 | 60.1181 | 59.9533
261.4844 | 123.4314 | -60.0723 | 63.0936 | -0.080566 | -0.00093353 | 0.065061 | 0.061981 | -0.0045011 | 0.004343 | 0.00054267 | 0.025604 | 0.00074988 | 0.066208 | 0.061782 | 0.0012476 | -0.0035846 | 0.0039413 | -0.086975 | 63.1622 | -60.3516 | 62.915 | -59.9762 | -60.3516 | 0 | -0.068665 | 63.1393 | -60.1868 | 63.1622 | -60.0677 | -60.1547 | -59.7427 | -0.27923 | 0.068664 | -0.17853 | 0.096131 | 60.0723 | -0.27923 | 60.3516 | 0 | -0.11444 | 0.045776 | 0.068664 | 0.004578 | 0.32959 | -0.082397 | 0.44403 | 0.032044 | 0.37537 | 123.2666 | 0.11902 | 123.349 | 123.5138 | 123.3261 | 123.2346 | 123.2117 | -123.4451 | -123.2803 | 122.9874 | 123.2346 | 59.9854 | 60.0037
262.5469 | 123.5275 | -60.0952 | 63.0753 | -0.11871 | 0.0012027 | 0.063566 | 0.065612 | -0.0010831 | -0.0016384 | 0.00096987 | -0.01712 | 0.00096348 | 0.065781 | 0.0652 | 0.0008204 | 0.00068782 | -0.0026809 | -0.054932 | 63.1256 | -60.3149 | 62.9562 | -59.9487 | -60.2966 | -0.036621 | -0.032043 | 63.1165 | -60.1776 | 63.2858 | -60.1547 | -60.3928 | -59.7794 | -0.21973 | 0.050354 | -0.11902 | 0.14649 | 60.0586 | -0.20142 | 60.2783 | 0.01831 | -0.082397 | 0.041199 | 0.21057 | -0.059509 | 0.31586 | -0.29755 | 0.39825 | -0.21515 | 0.36621 | 123.2712 | 0.022888 | 123.4634 | 123.4406 | 123.2941 | 123.2208 | 123.2117 | -123.3902 | -123.2529 | 123.0515 | 123.381 | 60.0403 | 60.0632
263.4844 | 123.3582 | -60.0769 | 63.0936 | 0.026245 | -0.00029273 | 0.064847 | 0.062194 | -0.00065586 | 0.0022068 | -0.0022345 | -0.011017 | 0.0013907 | 0.066635 | 0.061568 | -0.0002478 | -0.0027302 | 0.0011643 | -0.068665 | 63.1622 | -60.3104 | 62.915 | -59.9762 | -60.3241 | -0.027466 | -0.059509 | 63.1439 | -60.1639 | 63.1439 | -60.0494 | -60.1639 | -59.7336 | -0.23346 | 0.068664 | -0.17853 | 0.10071 | 60.0494 | -0.24719 | 60.2829 | -0.013733 | -0.086975 | 0.050354 | 0.050354 | 0.027466 | 0.34332 | -0.086975 | 0.4303 | 0 | 0.33417 | 123.2254 | 0.11444 | 123.3078 | 123.4726 | 123.3078 | 123.2391 | 123.2208 | -123.4039 | -123.2574 | 122.9919 | 123.2208 | 60.0082 | 60.0174
264.5469 | 123.3307 | -60.0723 | 63.1348 | -0.011902 | -0.00029273 | 0.064207 | 0.067108 | -0.00044226 | 0.00071138 | -0.0011663 | -0.072052 | 0.0011771 | 0.066635 | 0.069259 | -0.0015296 | -0.0020892 | -0.0031081 | -0.004578 | 63.2034 | -60.3424 | 62.9379 | -59.9808 | -60.3287 | 0.013733 | 0.068665 | 63.1805 | -60.141 | 63.1439 | -60.0769 | -60.1959 | -59.7565 | -0.27008 | 0.068664 | -0.19684 | 0.091553 | 60.0861 | -0.25635 | 60.3561 | 0.013733 | -0.068664 | 0.045776 | 0.009155 | -0.004577 | 0.31586 | -0.1236 | 0.38452 | -0.054932 | 0.36163 | 123.2803 | 0.064087 | 123.2849 | 123.5458 | 123.3215 | 123.2758 | 123.2529 | -123.4772 | -123.2758 | 123.0103 | 123.2162 | 60.0677 | 60.141
265.4844 | 123.4543 | -60.0174 | 63.0844 | -0.057678 | 0.0014163 | 0.063566 | 0.063903 | 0.00083954 | -0.00099762 | -0.0015935 | 0.025604 | -0.00053192 | 0.067063 | 0.057509 | -0.0019568 | 4.7018e-05 | -0.0046035 | -0.022888 | 63.1577 | -60.3149 | 62.9929 | -59.903 | -60.26 | 0.073242 | 0.09613 | 63.1348 | -60.141 | 63.2446 | -59.9762 | -60.0723 | -59.6466 | -0.29755 | 0.073242 | -0.091553 | 0.11444 | 60.0906 | -0.24262 | 60.3882 | 0.054931 | -0.1236 | 0.050354 | 0.16022 | 0.041199 | 0.37079 | -0.054932 | 0.49439 | 0.068664 | 0.41199 | 123.3078 | 0.16479 | 123.3856 | 123.4726 | 123.2758 | 123.175 | 123.1522 | -123.3994 | -123.2254 | 123.0103 | 123.262 | 59.9945 | 60.1135
266.5469 | 123.3353 | -60.0998 | 63.0981 | -0.50781 | 0.0033389 | 0.062925 | 0.065399 | 0.0023349 | -0.003561 | 0.0016107 | -0.062897 | 0.00096348 | 0.068558 | 0.068831 | -0.001316 | 0.00026062 | -0.00097194 | 0.041199 | 63.1348 | -60.3745 | 62.8784 | -60.0266 | -60.4431 | -0.13275 | -0.13733 | 63.176 | -60.2005 | 63.0981 | -60.1364 | -60.26 | -59.8022 | -0.27466 | 0.036621 | -0.21973 | 0.073242 | 59.967 | -0.34332 | 60.2417 | -0.068664 | -0.10071 | 0.077819 | 0 | -0.036622 | 0.29755 | -0.16022 | 0.39825 | -0.05951 | 0.3479 | 123.2529 | 0.064086 | 123.2986 | 123.5092 | 123.3765 | 123.2346 | 123.2758 | -123.4726 | -123.2986 | 122.9782 | 123.1979 | 60.141 | 59.9625
267.4844 | 123.436 | -60.0403 | 63.0844 | -0.050049 | 0.0018435 | 0.062284 | 0.063049 | -0.0030057 | 0.00028418 | 0.0020379 | 0.050018 | -0.0018137 | 0.066208 | 0.065841 | -0.0002478 | -0.0012348 | 0.0028733 | 0.027466 | 63.176 | -60.3058 | 63.0112 | -59.8618 | -60.2188 | 0.09613 | 0.14648 | 63.1577 | -60.1181 | 63.4186 | -60.2783 | -60.2829 | -59.7198 | -0.2655 | 0.091552 | -0.073243 | 0.17853 | 60.1364 | -0.17853 | 60.4019 | 0.086975 | -0.07782 | 0.073242 | 0.33417 | -0.23804 | 0.32043 | -0.24262 | 0.39825 | -0.1648 | 0.44403 | 123.317 | -0.16022 | 123.5367 | 123.4818 | 123.2758 | 123.2162 | 123.1979 | -123.3902 | -123.2025 | 123.0515 | 123.4589 | 60.0677 | 60.1868
268.5469 | 123.3307 | -60.1227 | 63.0936 | -0.042419 | 0.00098907 | 0.063138 | 0.064331 | 0.0010531 | -0.00035682 | -0.0013799 | -0.090363 | 0.0011771 | 0.067276 | 0.066482 | 0.0001794 | 0.00047422 | 0.0030869 | -0.10071 | 63.1668 | -60.3836 | 62.851 | -60.1227 | -60.4843 | -0.13733 | -0.15564 | 63.1668 | -60.1959 | 63.0981 | -60.173 | -60.3012 | -59.8297 | -0.26093 | 0.073242 | -0.24262 | 0 | 59.9854 | -0.36163 | 60.2463 | -0.10071 | -0.073242 | 0.073242 | 0.004578 | -0.050354 | 0.29297 | -0.17853 | 0.36621 | -0.10529 | 0.26093 | 123.2346 | 0.022888 | 123.2941 | 123.5504 | 123.3627 | 123.2895 | 123.2895 | -123.4772 | -123.2895 | 122.9736 | 123.2208 | 60.022 | 59.967
269.4844 | 123.4222 | -60.0494 | 63.0844 | -0.03479 | 0.0024845 | 0.062925 | 0.063903 | 0.00041234 | 0.0013522 | 0.0018243 | 0.034759 | 0.00074988 | 0.068131 | 0.067336 | -0.0008886 | -0.0020892 | -0.0031081 | -0.018311 | 63.1348 | -60.2829 | 62.97 | -59.903 | -60.26 | 0.073242 | 0.091553 | 63.1577 | -60.1273 | 63.2217 | -59.9899 | -60.054 | -59.6695 | -0.23346 | 0.050354 | -0.11444 | 0.14648 | 60.1227 | -0.21057 | 60.3561 | 0.022888 | -0.07782 | 0.073242 | 0.13733 | 0.059509 | 0.37994 | -0.004578 | 0.45776 | 0.073242 | 0.37994 | 123.2529 | 0.13733 | 123.349 | 123.4177 | 123.2849 | 123.1842 | 123.2071 | -123.3673 | -123.2117 | 123.0194 | 123.2712 | 60.0311 | 60.141
270.5469 | 123.4268 | -60.0769 | 63.0615 | -0.11871 | 0.0012027 | 0.065275 | 0.06668 | 0.00041234 | -0.00035682 | -0.0026617 | -0.041534 | 0.00053628 | 0.068131 | 0.068618 | -0.001316 | 4.7018e-05 | -0.00033114 | -0.045776 | 63.1073 | -60.3287 | 62.9471 | -59.9258 | -60.3333 | -0.050354 | -0.022888 | 63.1256 | -60.1913 | 63.2034 | -60.0494 | -60.1501 | -59.697 | -0.25177 | 0.045777 | -0.11444 | 0.15106 | 60.0266 | -0.25635 | 60.2783 | -0.004578 | -0.11444 | 0.064087 | 0.14191 | 0.027466 | 0.37994 | -0.073242 | 0.49439 | 0.041199 | 0.40283 | 123.2758 | 0.14191 | 123.3948 | 123.436 | 123.317 | 123.1842 | 123.2025 | -123.3902 | -123.2529 | 123.024 | 123.2803 | 60.0311 | 60.054
271.4844 | 123.4543 | -59.9991 | 63.1714 | 0.0033567 | 0.0016299 | 0.063779 | 0.063049 | -0.0012967 | -0.00057042 | -0.0011663 | 0.043915 | 0.0020315 | 0.066635 | 0.064986 | -0.0004614 | 0.00047422 | -0.0018265 | 0.036621 | 63.1622 | -60.2875 | 63.0249 | -59.8526 | -60.2188 | 0.09613 | 0.14648 | 63.1485 | -60.1181 | 63.2401 | -59.9808 | -60.0769 | -59.7656 | -0.28839 | -0.009156 | -0.14649 | 0.14648 | 60.0952 | -0.21973 | 60.3836 | 0.068665 | -0.11902 | -0.022888 | 0.068664 | 0.01831 | 0.23346 | -0.07782 | 0.35248 | 0.041199 | 0.43488 | 123.3124 | 0.13733 | 123.3582 | 123.4497 | 123.2666 | 123.1613 | 123.1476 | -123.4589 | -123.2895 | 123.024 | 123.2391 | 60.0357 | 60.1456
272.4844 | 123.3948 | -60.0677 | 63.0844 | -0.042419 | 0.0014163 | 0.061857 | 0.062835 | -0.0012967 | 0.0024204 | -0.00073913 | 0.046967 | -0.0024545 | 0.067276 | 0.065627 | -0.0008886 | -0.0025164 | -0.0016129 | -0.050354 | 63.1897 | -60.3241 | 62.9288 | -59.9625 | -60.3012 | 0.013733 | -0.018311 | 63.1439 | -60.1273 | 63.1714 | -60.0311 | -60.1364 | -59.7107 | -0.25635 | 0.10529 | -0.15564 | 0.10529 | 60.0815 | -0.23346 | 60.3378 | 0.022889 | -0.059509 | 0.059509 | 0.086975 | 0.036621 | 0.35706 | -0.068665 | 0.41656 | -0.009156 | 0.36163 | 123.2529 | 0.09613 | 123.2986 | 123.5138 | 123.2712 | 123.2574 | 123.2117 | -123.4085 | -123.2117 | 122.9965 | 123.2391 | 60.0174 | 60.0494
273.5469 | 123.4222 | -60.0586 | 63.0844 | -0.18738 | 0.00034827 | 0.06677 | 0.063049 | -0.0030057 | -0.00035682 | 0.00011527 | 0.0011902 | -0.00095912 | 0.06749 | 0.059218 | -0.001316 | -0.001662 | 0.0020187 | -0.004578 | 63.1256 | -60.3287 | 62.9929 | -59.8938 | -60.347 | -0.032043 | -0.018311 | 63.0981 | -60.1456 | 63.1851 | -60.0632 | -60.1593 | -59.7107 | -0.27008 | 0.041198 | -0.091553 | 0.16479 | 60.0266 | -0.28839 | 60.2966 | -0.018311 | -0.086975 | 0.013733 | 0.10071 | -0.004577 | 0.3479 | -0.10071 | 0.43488 | -0.013733 | 0.43487 | 123.3215 | 0.082398 | 123.3307 | 123.4543 | 123.2437 | 123.1842 | 123.1567 | -123.4131 | -123.23 | 123.0515 | 123.2437 | 60.054 | 60.0403
274.4844 | 123.4543 | -60.054 | 63.1073 | -0.095825 | 0.00013467 | 0.06207 | 0.062622 | -0.0012967 | -0.00078402 | -9.8328e-05 | 0.010345 | 0.0018179 | 0.068558 | 0.064986 | 0.0001794 | -0.0023028 | -0.0022537 | -0.009155 | 63.1714 | -60.2966 | 62.9883 | -59.9121 | -60.2692 | 0.073242 | 0.091553 | 63.1577 | -60.141 | 63.2309 | -60.0174 | -60.054 | -59.6558 | -0.24262 | 0.064087 | -0.11902 | 0.14191 | 60.1273 | -0.21515 | 60.3699 | 0.027466 | -0.086975 | 0.050354 | 0.1236 | 0.036621 | 0.39825 | 0 | 0.48523 | 0.086975 | 0.38452 | 123.2849 | 0.1236 | 123.3719 | 123.468 | 123.2986 | 123.2254 | 123.2117 | -123.4039 | -123.2483 | 123.0423 | 123.2849 | 60.0449 | 60.1456
275.5469 | 123.4406 | -60.0586 | 63.0936 | 0.010986 | 0.00098907 | 0.061857 | 0.06369 | -0.0015103 | 0.0015658 | -0.0037299 | -0.0079652 | -0.00095912 | 0.068772 | 0.064986 | -0.0025976 | -0.0012348 | -0.0018265 | -0.059509 | 63.1668 | -60.3149 | 62.9333 | -59.9625 | -60.3012 | 0.027466 | 0.004578 | 63.1348 | -60.1456 | 63.2217 | -59.9854 | -60.1135 | -59.697 | -0.25635 | 0.073242 | -0.16022 | 0.096131 | 60.0861 | -0.24261 | 60.3424 | 0.013733 | -0.086975 | 0.041199 | 0.12817 | 0.073242 | 0.36163 | -0.054931 | 0.44861 | 0.032044 | 0.35248 | 123.2483 | 0.16022 | 123.3673 | 123.4818 | 123.2803 | 123.2254 | 123.1934 | -123.4085 | -123.2391 | 122.9919 | 123.2803 | 59.9991 | 60.0632
276.4844 | 123.3902 | -60.0815 | 63.0615 | -0.042419 | -0.00029273 | 0.061002 | 0.064331 | -0.0017239 | -0.00099762 | -0.00073913 | -0.01712 | -0.00074552 | 0.067063 | 0.074599 | -0.001316 | -0.0012348 | 0.0018051 | -0.086975 | 63.1348 | -60.3195 | 62.915 | -59.9899 | -60.3424 | -0.032043 | -0.041199 | 63.1393 | -60.1868 | 63.1714 | -60.054 | -60.1639 | -59.729 | -0.23804 | 0.073243 | -0.14648 | 0.091553 | 60.0494 | -0.26093 | 60.2875 | -0.022888 | -0.10529 | 0.07782 | 0.10986 | 0.027466 | 0.35248 | -0.082397 | 0.45776 | 0.022889 | 0.32959 | 123.2346 | 0.13275 | 123.3582 | 123.4543 | 123.3261 | 123.2162 | 123.2208 | -123.381 | -123.2483 | 122.9965 | 123.2529 | 59.9945 | 60.0403
277.4844 | 123.5413 | -60.0174 | 63.1439 | -0.065308 | -0.00093353 | 0.063352 | 0.063049 | 0.00041234 | 0.00028418 | 0.0013971 | 0.0072936 | 0.0024589 | 0.066849 | 0.063918 | -0.0032386 | -0.0023028 | -0.0063125 | 0.032043 | 63.1622 | -60.3058 | 63.0432 | -59.8663 | -60.228 | 0.10986 | 0.16022 | 63.1668 | -60.1181 | 63.2309 | -59.9899 | -60.0723 | -59.7015 | -0.28839 | 0.01831 | -0.10071 | 0.15106 | 60.1273 | -0.21057 | 60.4156 | 0.07782 | -0.10071 | 0.022888 | 0.086975 | 0.027466 | 0.31586 | -0.054932 | 0.41656 | 0.045776 | 0.43945 | 123.349 | 0.12817 | 123.349 | 123.468 | 123.2849 | 123.1796 | 123.1842 | -123.4497 | -123.262 | 123.0606 | 123.2483 | 60.0494 | 60.1776
278.5469 | 123.4268 | -60.0723 | 63.0386 | -0.1416 | 0.00034827 | 0.066984 | 0.065185 | -0.0025785 | -0.00035682 | -0.00073913 | -0.023224 | 0.0020315 | 0.065995 | 0.068191 | -0.0002478 | 0.001115 | 0.0039413 | -0.036621 | 63.1393 | -60.3149 | 62.9608 | -59.9396 | -60.3195 | -0.013733 | -0.022888 | 63.1348 | -60.1456 | 63.208 | -60.0632 | -60.1456 | -59.7107 | -0.24261 | 0.10071 | -0.07782 | 0.13275 | 60.0586 | -0.24719 | 60.3012 | -0.004578 | -0.073242 | 0.096131 | 0.16937 | 0.009156 | 0.36163 | -0.073242 | 0.43488 | 0 | 0.37537 | 123.2758 | 0.082398 | 123.3536 | 123.4543 | 123.2803 | 123.2117 | 123.2071 | -123.3536 | -123.1842 | 123.0331 | 123.2803 | 60.0357 | 60.0494
279.4844 | 123.3856 | -60.0449 | 63.1165 | -0.072937 | 0.00034827 | 0.064634 | 0.064331 | -0.0027921 | -0.0031338 | 0.0018243 | 0.013397 | 0.0011771 | 0.066849 | 0.066268 | 0.0008204 | -0.00016658 | -0.00075834 | 0.013733 | 63.1302 | -60.2966 | 62.9974 | -59.8984 | -60.228 | 0.086975 | 0.1236 | 63.1531 | -60.1593 | 63.208 | -60.022 | -60.1181 | -59.7061 | -0.25177 | 0.013733 | -0.11902 | 0.14648 | 60.1318 | -0.18311 | 60.3836 | 0.068665 | -0.11444 | 0.036621 | 0.091553 | 0.022888 | 0.33874 | -0.073242 | 0.45319 | 0.041199 | 0.39825 | 123.2941 | 0.13733 | 123.3673 | 123.4268 | 123.3124 | 123.175 | 123.1979 | -123.4131 | -123.2758 | 123.0423 | 123.2529 | 60.0586 | 60.1685
280.5469 | 123.3307 | -60.0998 | 63.1073 | -0.065308 | 0.00034827 | 0.063993 | 0.064971 | -0.0012967 | -0.002493 | 0.0024653 | -0.10562 | 0.00032248 | 0.068558 | 0.0699 | -0.001316 | 0.001756 | 0.0033005 | -0.10529 | 63.176 | -60.379 | 62.851 | -60.1089 | -60.4568 | -0.15106 | -0.14648 | 63.1577 | -60.2188 | 63.1073 | -60.173 | -60.3012 | -59.8343 | -0.27924 | 0.068664 | -0.25635 | -0.009156 | 59.9487 | -0.35706 | 60.228 | -0.07782 | -0.11902 | 0.050354 | 0 | -0.073243 | 0.2655 | -0.20142 | 0.38452 | -0.082397 | 0.27008 | 123.23 | 0.045776 | 123.3261 | 123.555 | 123.3765 | 123.2758 | 123.2574 | -123.4863 | -123.3261 | 122.9507 | 123.2071 | 59.9945 | 59.9533
281.4844 | 123.3856 | -60.0586 | 63.1165 | -0.050049 | 0.0024845 | 0.063779 | 0.063903 | -0.0030057 | -0.0016384 | 0.0031061 | 0.004242 | -0.00095912 | 0.06749 | 0.063064 | -3.4196e-05 | -0.00080758 | -0.0016129 | 0.032043 | 63.1622 | -60.3012 | 62.97 | -59.8892 | -60.2417 | 0.10529 | 0.13733 | 63.1805 | -60.141 | 63.1897 | -60.022 | -60.1044 | -59.7061 | -0.24261 | 0.045776 | -0.14648 | 0.16937 | 60.1639 | -0.1831 | 60.4065 | 0.059509 | -0.082397 | 0.064087 | 0.073242 | 0.036621 | 0.35248 | -0.045776 | 0.43487 | 0.036621 | 0.41199 | 123.2712 | 0.11902 | 123.3307 | 123.4634 | 123.3215 | 123.2208 | 123.2391 | -123.4177 | -123.2574 | 123.0286 | 123.2483 | 60.0906 | 60.1959
282.4844 | 123.4634 | -60.0494 | 63.0753 | -0.057678 | 0.00034827 | 0.064207 | 0.063049 | -0.00065586 | 0.00092498 | -0.00095273 | 0.013397 | 0.00010888 | 0.068772 | 0.064986 | 0.000393 | -0.0010212 | 0.0047959 | -0.009155 | 63.1531 | -60.3241 | 63.0066 | -59.903 | -60.2646 | 0.073242 | 0.10986 | 63.1485 | -60.1089 | 63.2675 | -59.967 | -60.0815 | -59.6741 | -0.27466 | 0.07782 | -0.068664 | 0.14648 | 60.1227 | -0.21515 | 60.3973 | 0.05951 | -0.05951 | 0.073243 | 0.19226 | 0.082397 | 0.37537 | -0.032044 | 0.43488 | 0.027466 | 0.42114 | 123.3307 | 0.14191 | 123.3765 | 123.4772 | 123.2574 | 123.2025 | 123.1979 | -123.3994 | -123.1842 | 123.056 | 123.317 | 60.0403 | 60.1593
283.4844 | 123.3307 | -60.0723 | 63.1805 | -0.019531 | 0.00098907 | 0.062711 | 0.065399 | -0.0019377 | -0.00035682 | -0.0030889 | -0.026276 | 0.0011771 | 0.068985 | 0.069045 | 0.0008204 | -0.00059378 | 0.0020187 | 0.013733 | 63.208 | -60.3333 | 62.9059 | -60.022 | -60.2325 | 0.091553 | 0.050354 | 63.1989 | -60.141 | 63.1256 | -60.0815 | -60.1959 | -59.7977 | -0.26093 | 0.027466 | -0.27466 | 0.050354 | 60.1639 | -0.16022 | 60.4248 | 0.10071 | -0.068664 | 0.018311 | -0.054932 | -0.009155 | 0.27466 | -0.1236 | 0.34332 | -0.054932 | 0.31128 | 123.2391 | 0.059509 | 123.2666 | 123.5413 | 123.3398 | 123.2803 | 123.2712 | -123.5138 | -123.3215 | 122.9782 | 123.1979 | 60.0861 | 60.1227
284.5469 | 123.3902 | -60.0677 | 63.0981 | -0.11871 | 0.0035525 | 0.062498 | 0.061981 | 0.0014803 | 0.00092498 | -0.00095273 | 0.056122 | -0.00053192 | 0.066849 | 0.0652 | -0.0021704 | 4.7018e-05 | 0.0011643 | -0.082397 | 63.1714 | -60.347 | 62.9517 | -59.9854 | -60.3287 | -0.004578 | 0 | 63.1622 | -60.1547 | 63.1668 | -60.0723 | -60.173 | -59.7382 | -0.27924 | 0.073242 | -0.14649 | 0.082397 | 60.0632 | -0.26093 | 60.3424 | 0.018311 | -0.086975 | 0.064086 | 0.068664 | -0.004578 | 0.32959 | -0.10529 | 0.41656 | -0.018311 | 0.36163 | 123.2986 | 0.082397 | 123.3215 | 123.5184 | 123.317 | 123.2391 | 123.23 | -123.4451 | -123.2529 | 123.0194 | 123.2346 | 59.9854 | 60.0677
285.4844 | 123.3353 | -60.0723 | 63.1577 | -0.065308 | -0.00093353 | 0.063138 | 0.062835 | -0.0027921 | 7.0582e-05 | 0.00032907 | -0.023224 | 0.0020315 | 0.066849 | 0.061782 | 0.0006066 | -0.0010212 | -0.00011754 | -0.004578 | 63.2034 | -60.3104 | 62.9425 | -59.967 | -60.3516 | 0.018311 | 0.041199 | 63.2217 | -60.1593 | 63.1302 | -60.0906 | -60.2142 | -59.7931 | -0.23804 | 0.045776 | -0.21515 | 0.10529 | 60.0906 | -0.27923 | 60.3287 | -0.041198 | -0.086975 | 0.064087 | -0.027466 | -0.01831 | 0.27924 | -0.14191 | 0.36621 | -0.054931 | 0.34332 | 123.2529 | 0.068665 | 123.2895 | 123.5138 | 123.381 | 123.2758 | 123.2941 | -123.468 | -123.317 | 123.0148 | 123.2025 | 60.0677 | 60.1135
286.4844 | 123.3032 | -60.0723 | 63.1256 | -0.027161 | -0.00071993 | 0.063566 | 0.06604 | 0.0019077 | -0.00078402 | 0.00011527 | -0.011017 | 0.0026725 | 0.067917 | 0.070327 | 0.0001794 | -0.0012348 | 0.0013779 | -0.013733 | 63.1989 | -60.3149 | 62.9059 | -60.0037 | -60.3287 | 0.041199 | 0.036621 | 63.2217 | -60.1547 | 63.1348 | -60.0861 | -60.2005 | -59.7748 | -0.24261 | 0.073243 | -0.21973 | 0.068665 | 60.1135 | -0.25635 | 60.3561 | -0.013733 | -0.082397 | 0.096131 | 0.009156 | -0.013733 | 0.29755 | -0.12817 | 0.37994 | -0.045776 | 0.31128 | 123.2208 | 0.068664 | 123.2895 | 123.5138 | 123.3765 | 123.2712 | 123.2941 | -123.4406 | -123.2803 | 122.9782 | 123.2071 | 60.0586 | 60.1089
287.4844 | 123.3032 | -60.0815 | 63.1622 | -0.011902 | 0.0022709 | 0.062284 | 0.065612 | 0.0010531 | 0.00092498 | -0.0011663 | -0.05069 | 0.0013907 | 0.067063 | 0.072463 | 0.0012476 | 0.00026062 | 0.0039413 | -0.004578 | 63.1897 | -60.3195 | 62.9105 | -59.9991 | -60.3195 | 0.018311 | 0.045776 | 63.208 | -60.1593 | 63.1302 | -60.0952 | -60.1959 | -59.7702 | -0.23804 | 0.027466 | -0.25177 | 0.082398 | 60.0998 | -0.23804 | 60.3378 | 0 | -0.07782 | 0.045777 | -0.032043 | -0.013733 | 0.31128 | -0.11444 | 0.3891 | -0.036621 | 0.32043 | 123.23 | 0.064087 | 123.2895 | 123.5092 | 123.3673 | 123.2712 | 123.2895 | -123.4818 | -123.3215 | 122.9919 | 123.2117 | 60.0769 | 60.1273
288.4844 | 123.4634 | -60.0357 | 63.1119 | -0.065308 | 0.00077547 | 0.061857 | 0.063476 | 0.0036165 | 0.00028418 | -0.00052553 | 0.016449 | 0.0018179 | 0.070053 | 0.061996 | -0.0021704 | 4.7018e-05 | -0.0013991 | 0.018311 | 63.1805 | -60.2966 | 62.9974 | -59.8618 | -60.2142 | 0.10986 | 0.47607 | 63.2401 | -60.1273 | 63.2217 | -59.9991 | -60.0998 | -59.7107 | -0.26093 | 0.068665 | -0.11444 | 0.17395 | 60.1456 | -0.17853 | 60.4065 | 0.082398 | -0.091552 | 0.12817 | 0.10986 | 0.036622 | 0.32501 | -0.064086 | 0.41656 | 0.027466 | 0.43488 | 123.2941 | 0.12817 | 123.349 | 123.4772 | 123.3673 | 123.2162 | 123.2758 | -123.4085 | -123.2391 | 123.0331 | 123.2574 | 60.054 | 60.5118
289.5469 | 123.381 | -60.0632 | 63.1027 | -0.057678 | 0.00098907 | 0.065061 | 0.064331 | -0.0015103 | 0.00071138 | 0.0011835 | -0.026276 | -0.00053192 | 0.068772 | 0.070754 | -0.000675 | -0.00016658 | 0.0011643 | -0.068665 | 63.1348 | -60.3333 | 62.9517 | -59.9258 | -60.3241 | -0.036621 | -0.027466 | 63.1302 | -60.1501 | 63.1714 | -60.0632 | -60.1501 | -59.7198 | -0.27008 | 0.032044 | -0.15106 | 0.13733 | 60.0266 | -0.26093 | 60.2966 | 0.009155 | -0.086975 | 0.027466 | 0.068665 | 0 | 0.34332 | -0.086975 | 0.4303 | 0 | 0.40741 | 123.2849 | 0.086975 | 123.3215 | 123.468 | 123.2803 | 123.1979 | 123.1934 | -123.436 | -123.2529 | 123.0148 | 123.2346 | 59.9945 | 60.0357
290.4844 | 123.4863 | -60.022 | 63.089 | -0.10345 | 0.00098907 | 0.063352 | 0.063903 | 0.00019874 | -0.0027066 | -0.00073913 | 0.019501 | 0.00096348 | 0.068772 | 0.066695 | -0.001316 | -0.00038018 | -0.00097194 | -0.018311 | 63.1348 | -60.3241 | 63.002 | -59.8892 | -60.2371 | 0.07782 | 0.15106 | 63.1439 | -60.1181 | 63.2492 | -59.9625 | -60.0266 | -59.642 | -0.30212 | 0.045777 | -0.086975 | 0.13275 | 60.0998 | -0.21515 | 60.4019 | 0.086975 | -0.09613 | 0.054932 | 0.16022 | 0.05951 | 0.37994 | -0.004577 | 0.47607 | 0.091553 | 0.43488 | 123.3261 | 0.15564 | 123.3673 | 123.4589 | 123.262 | 123.1567 | 123.1659 | -123.4131 | -123.2071 | 123.024 | 123.2712 | 60.0037 | 60.173
291.4844 | 123.2986 | -60.0861 | 63.1531 | -0.019531 | 0.00077547 | 0.062925 | 0.063262 | 0.00083954 | 0.00092498 | 0.00054267 | -0.056793 | 0.0026725 | 0.069199 | 0.066268 | -0.0002478 | 0.00047422 | -0.0024673 | -0.022888 | 63.2217 | -60.3333 | 62.7594 | -60.1044 | -60.3287 | -0.027466 | -0.009155 | 63.2126 | -60.1593 | 63.121 | -60.1181 | -60.1868 | -59.7794 | -0.24719 | 0.068665 | -0.39368 | -0.01831 | 60.0586 | -0.24261 | 60.3058 | 0.004578 | -0.073242 | 0.059509 | -0.032043 | -0.032043 | 0.3067 | -0.10071 | 0.37994 | -0.027466 | 0.22888 | 123.0927 | 0.041199 | 123.2803 | 123.555 | 123.3719 | 123.3078 | 123.2986 | -123.4863 | -123.3124 | 122.8455 | 123.2071 | 60.0632 | 60.0769
292.5469 | 123.4131 | -60.0632 | 63.0798 | -0.088196 | 0.0014163 | 0.066343 | 0.064971 | 0.0021213 | 0.00071138 | 0.00054267 | -0.053741 | -0.00031832 | 0.067917 | 0.064345 | -0.0019568 | 0.001115 | -0.00097194 | -0.045776 | 63.1165 | -60.3241 | 62.9608 | -59.935 | -60.3149 | -0.045776 | -0.027466 | 63.121 | -60.1959 | 63.1897 | -60.0037 | -60.141 | -59.7473 | -0.26093 | 0.036621 | -0.11902 | 0.12817 | 60.0174 | -0.25177 | 60.2783 | 0.009156 | -0.13275 | 0.041199 | 0.10986 | 0.059509 | 0.31586 | -0.07782 | 0.44861 | 0.054932 | 0.3891 | 123.2849 | 0.19226 | 123.3856 | 123.4406 | 123.317 | 123.1796 | 123.1842 | -123.4039 | -123.2758 | 123.024 | 123.2529 | 60.0174 | 60.0357
293.4844 | 123.317 | -60.0677 | 63.1027 | -0.072937 | 0.00056187 | 0.060361 | 0.067108 | -0.0025785 | 0.00092498 | 0.0013971 | -0.041534 | 0.0013907 | 0.068985 | 0.069472 | 0.0006066 | 4.7018e-05 | -0.00033114 | -0.022888 | 63.2446 | -60.3241 | 62.7594 | -60.0403 | -60.3745 | -0.041199 | -0.009155 | 63.208 | -60.1776 | 63.1348 | -60.1181 | -60.2051 | -59.7702 | -0.25635 | 0.14191 | -0.34332 | 0.027466 | 60.0266 | -0.3067 | 60.2829 | -0.050354 | -0.10986 | 0.10529 | 0.032044 | -0.050354 | 0.29755 | -0.13733 | 0.40741 | -0.027466 | 0.28381 | 123.0835 | 0.059509 | 123.3124 | 123.5687 | 123.3856 | 123.3124 | 123.2758 | -123.4268 | -123.2803 | 122.8271 | 123.2025 | 60.0449 | 60.0586
294.5469 | 123.4314 | -60.054 | 63.121 | -0.027161 | -0.0017881 | 0.064847 | 0.062194 | -1.486e-05 | -0.00099762 | -0.0020209 | 0.025604 | 0.0011771 | 0.066849 | 0.061996 | 0.0008204 | -0.00080758 | -0.00075834 | -0.032043 | 63.1577 | -60.3104 | 62.9745 | -59.9258 | -60.2463 | 0.068665 | 0.054932 | 63.1439 | -60.1501 | 63.2126 | -59.9991 | -60.1044 | -59.6786 | -0.25635 | 0.036621 | -0.14648 | 0.12817 | 60.1227 | -0.19226 | 60.379 | 0.064087 | -0.09613 | 0.022888 | 0.091552 | 0.054932 | 0.37537 | -0.050354 | 0.4715 | 0.045776 | 0.38452 | 123.2849 | 0.15106 | 123.3627 | 123.468 | 123.2941 | 123.2117 | 123.1979 | -123.4314 | -123.2712 | 123.0286 | 123.2666 | 60.022 | 60.1089
295.4844 | 123.3307 | -60.0723 | 63.1531 | -0.072937 | 0.00077547 | 0.063138 | 0.06369 | -0.0045011 | 0.0011386 | 0.0043879 | -0.056793 | 0.0020315 | 0.066635 | 0.061141 | -0.0015296 | -0.0014484 | 0.0015915 | 0 | 63.2217 | -60.3333 | 62.7686 | -60.1364 | -60.3195 | -0.018311 | 0.013733 | 63.2034 | -60.1776 | 63.1348 | -60.1044 | -60.2051 | -59.7748 | -0.26093 | 0.068665 | -0.38452 | -0.064087 | 60.054 | -0.24719 | 60.3149 | 0.013733 | -0.10529 | 0.050354 | -0.01831 | -0.032043 | 0.29755 | -0.13275 | 0.40283 | -0.027466 | 0.19684 | 123.1018 | 0.073242 | 123.3124 | 123.555 | 123.381 | 123.2941 | 123.2758 | -123.4863 | -123.3307 | 122.8409 | 123.2071 | 60.0723 | 60.0861
296.4844 | 123.4085 | -60.0494 | 63.1073 | -0.03479 | 0.0016299 | 0.063566 | 0.063903 | 0.0014803 | 7.0582e-05 | -0.0018073 | 0.022552 | -0.0016001 | 0.067276 | 0.066054 | -0.0008886 | -0.001662 | -0.0022537 | 0.027466 | 63.1714 | -60.3012 | 62.9974 | -59.8938 | -60.2417 | 0.09613 | 0.12817 | 63.1851 | -60.1318 | 63.176 | -60.0449 | -60.1364 | -59.7061 | -0.25177 | 0.064087 | -0.10986 | 0.15564 | 60.1456 | -0.19226 | 60.3973 | 0.059509 | -0.082398 | 0.07782 | 0.068664 | 0.004577 | 0.34332 | -0.086976 | 0.42572 | -0.004578 | 0.40741 | 123.2986 | 0.086975 | 123.3078 | 123.4726 | 123.317 | 123.2208 | 123.2346 | -123.4085 | -123.2391 | 123.0469 | 123.2254 | 60.0769 | 60.1776
297.4844 | 123.3444 | -60.0677 | 63.1622 | -0.011902 | 0.0016299 | 0.06207 | 0.063049 | 0.0014803 | -0.00035682 | -0.0028753 | -0.035431 | 0.0011771 | 0.06514 | 0.068618 | -0.0002478 | -0.0020892 | 0.0028733 | -0.018311 | 63.208 | -60.347 | 62.8601 | -60.0082 | -60.4156 | 0.004578 | 0.018311 | 63.2172 | -60.1456 | 63.1119 | -60.0952 | -60.2188 | -59.7794 | -0.27924 | 0.045777 | -0.30212 | 0.059509 | 60.0723 | -0.3479 | 60.3516 | -0.068664 | -0.07782 | 0.054932 | -0.050354 | -0.027466 | 0.28839 | -0.15106 | 0.36621 | -0.073242 | 0.33874 | 123.2071 | 0.050354 | 123.2574 | 123.555 | 123.3627 | 123.2758 | 123.2849 | -123.5092 | -123.3078 | 122.9279 | 123.1796 | 60.0494 | 60.0861
298.4844 | 123.3582 | -60.0449 | 63.1439 | -0.065308 | 0.0016299 | 0.063779 | 0.064331 | 0.0010531 | -0.00078402 | -0.0011663 | 0.022552 | 0.00074988 | 0.064286 | 0.061782 | 0.0008204 | -0.0010212 | 0.0030869 | 0.041199 | 63.176 | -60.2966 | 62.9745 | -59.9167 | -60.2463 | 0.09613 | 0.11444 | 63.176 | -60.1776 | 63.1714 | -60.0403 | -60.1364 | -59.7153 | -0.25177 | 0.032043 | -0.16937 | 0.12817 | 60.141 | -0.20142 | 60.3928 | 0.050354 | -0.13275 | 0.032043 | 0.027466 | 0.004578 | 0.32959 | -0.091553 | 0.46234 | 0.041198 | 0.37994 | 123.2712 | 0.13733 | 123.349 | 123.4726 | 123.3536 | 123.2208 | 123.2208 | -123.4406 | -123.3215 | 123.0194 | 123.2162 | 60.0861 | 60.1593
299.5469 | 123.3673 | -60.0677 | 63.089 | -0.019531 | 0.0022709 | 0.06207 | 0.063476 | -0.0012967 | 0.0019932 | -0.00073913 | 0.016449 | 0.00074988 | 0.067063 | 0.057082 | -3.4196e-05 | -0.0012348 | 0.00095066 | -0.086975 | 63.1531 | -60.3378 | 62.915 | -59.9716 | -60.3333 | -0.041199 | -0.064087 | 63.1439 | -60.1456 | 63.1622 | -60.0677 | -60.1593 | -59.7198 | -0.27008 | 0.064087 | -0.17395 | 0.09613 | 60.0266 | -0.2655 | 60.2966 | 0.004578 | -0.07782 | 0.054932 | 0.073242 | 0 | 0.3479 | -0.091553 | 0.42572 | -0.013733 | 0.36621 | 123.2529 | 0.07782 | 123.3078 | 123.4909 | 123.2895 | 123.2208 | 123.2117 | -123.4268 | -123.2346 | 122.9828 | 123.23 | 59.9808 | 60.0037
300.4844 | 123.3261 | -60.0266 | 63.1439 | -0.03479 | 0.00034827 | 0.064207 | 0.06369 | -0.0010831 | -0.0016384 | 0.0018243 | -0.011017 | 0.0024589 | 0.067704 | 0.067763 | -0.0008886 | -0.00059378 | 0.0026597 | -0.013733 | 63.2217 | -60.3287 | 62.9059 | -60.0082 | -60.3104 | 0.018311 | 0.045776 | 63.2263 | -60.1547 | 63.121 | -60.0952 | -60.2005 | -59.7977 | -0.30212 | 0.07782 | -0.23804 | 0.01831 | 60.0449 | -0.28381 | 60.347 | 0.01831 | -0.12817 | 0.082397 | -0.022888 | -0.068665 | 0.22888 | -0.17395 | 0.35706 | -0.045776 | 0.32043 | 123.2346 | 0.059509 | 123.2758 | 123.5504 | 123.381 | 123.2483 | 123.2529 | -123.4726 | -123.2986 | 122.9324 | 123.1476 | 60.0128 | 60.0723
301.4844 | 123.3261 | -60.0906 | 63.1256 | -0.050049 | 0.0014163 | 0.063993 | 0.061553 | 0.00062594 | -0.0012112 | -0.00052553 | -0.056793 | 0.0016043 | 0.067704 | 0.063064 | -0.0002478 | -0.0010212 | 9.6064e-05 | -0.013733 | 63.2172 | -60.3287 | 62.9196 | -59.9991 | -60.3195 | 0.036621 | 0.045776 | 63.1989 | -60.1456 | 63.1531 | -60.0723 | -60.173 | -59.7015 | -0.23804 | 0.091553 | -0.20599 | 0.091553 | 60.1273 | -0.22888 | 60.3653 | 0.009155 | -0.054932 | 0.073243 | 0.027466 | 0.01831 | 0.3891 | -0.082398 | 0.44403 | -0.027466 | 0.32959 | 123.2483 | 0.073242 | 123.2986 | 123.5458 | 123.3444 | 123.3078 | 123.2895 | -123.4543 | -123.2712 | 123.0103 | 123.2437 | 60.0769 | 60.1364
302.5469 | 123.4177 | -60.0586 | 63.0936 | -0.065308 | 0.0024845 | 0.06207 | 0.062835 | 0.0034029 | 0.0019932 | 0.0013971 | 0.043915 | 0.0016043 | 0.067063 | 0.066695 | -0.0002478 | -0.0018756 | 0.0022323 | 0.068665 | 63.1897 | -60.2966 | 62.9333 | -59.9716 | -60.3104 | -0.013733 | -0.013733 | 63.1393 | -60.1639 | 63.176 | -60.0403 | -60.1456 | -59.7244 | -0.23804 | 0.09613 | -0.16022 | 0.086975 | 60.0449 | -0.25177 | 60.2829 | -0.013733 | -0.10529 | 0.045776 | 0.082397 | 0.018311 | 0.33417 | -0.086975 | 0.43945 | 0.01831 | 0.32501 | 123.23 | 0.1236 | 123.3398 | 123.4863 | 123.3032 | 123.2483 | 123.1979 | -123.3902 | -123.2574 | 122.9919 | 123.2346 | 60.1273 | 60.0449
303.4844 | 123.3536 | -60.0906 | 63.1485 | 0.018616 | -7.913e-05 | 0.063779 | 0.063903 | 0.0010531 | 0.00092498 | 0.0026789 | -0.078156 | 0.0016043 | 0.066422 | 0.066909 | -0.0004614 | -0.0014484 | 0.00095066 | -0.004578 | 63.2217 | -60.3287 | 62.9333 | -59.9808 | -60.2966 | 0.009155 | 0.07782 | 63.1989 | -60.1639 | 63.1668 | -60.0815 | -60.1959 | -59.7565 | -0.23804 | 0.073242 | -0.21515 | 0.10986 | 60.0998 | -0.20599 | 60.3378 | 0.032043 | -0.073242 | 0.050354 | 0.01831 | 0.009155 | 0.33417 | -0.10529 | 0.40741 | -0.032044 | 0.3479 | 123.262 | 0.082397 | 123.3307 | 123.5504 | 123.3627 | 123.3124 | 123.2895 | -123.4772 | -123.3124 | 123.024 | 123.2574 | 60.0861 | 60.1685
304.5469 | 123.4451 | -60.0494 | 63.0936 | -0.080566 | 0.00077547 | 0.063566 | 0.062194 | -0.0030057 | 0.0024204 | -0.0015935 | 0.025604 | 0.0022453 | 0.064926 | 0.066909 | 0.0006066 | -0.0029438 | -0.00054474 | -0.013733 | 63.1485 | -60.3149 | 62.9791 | -59.903 | -60.2463 | 0.082397 | 0.091553 | 63.1577 | -60.1227 | 63.2263 | -59.967 | -60.0586 | -59.6649 | -0.2655 | 0.054932 | -0.11444 | 0.14648 | 60.1318 | -0.19684 | 60.3973 | 0.068664 | -0.073243 | 0.064087 | 0.13275 | 0.082397 | 0.38452 | -0.009156 | 0.45776 | 0.064087 | 0.41199 | 123.2941 | 0.15564 | 123.349 | 123.4634 | 123.2803 | 123.1979 | 123.2071 | -123.4085 | -123.2162 | 123.0286 | 123.2758 | 60.0357 | 60.141
305.4844 | 123.381 | -60.0769 | 63.1302 | -0.027161 | -0.00050633 | 0.066343 | 0.064117 | 0.0016939 | -0.0029202 | 0.00054267 | -0.081207 | 0.0024589 | 0.068131 | 0.07054 | -0.0004614 | 0.001115 | -0.0018265 | -0.004578 | 63.1943 | -60.3333 | 62.9105 | -59.9808 | -60.3241 | -0.009155 | 0.1236 | 63.176 | -60.1868 | 63.1714 | -60.1044 | -60.2188 | -59.761 | -0.25635 | 0.064087 | -0.21973 | 0.09613 | 60.0677 | -0.24719 | 60.3241 | 0.009155 | -0.10986 | 0.045776 | 0.041199 | -0.027466 | 0.31586 | -0.14191 | 0.42572 | -0.032043 | 0.35248 | 123.2437 | 0.082398 | 123.3582 | 123.5275 | 123.3627 | 123.2712 | 123.2529 | -123.4634 | -123.317 | 122.9874 | 123.2483 | 60.0723 | 60.2005
306.5469 | 123.4451 | -60.054 | 63.0753 | -0.088196 | -7.913e-05 | 0.064207 | 0.062408 | -0.0030057 | 0.00028418 | 0.00054267 | 0.040863 | 0.00010888 | 0.068344 | 0.058791 | -0.0004614 | 0.0021832 | -0.00011754 | 0.022888 | 63.1393 | -60.3012 | 63.002 | -59.8526 | -60.2097 | 0.12817 | 0.14648 | 63.1531 | -60.1273 | 63.1531 | -59.935 | -60.1822 | -59.7198 | -0.24719 | 0.064087 | -0.073242 | 0.20142 | 60.1822 | -0.15564 | 60.4294 | 0.091552 | -0.073242 | 0.07782 | 0.07782 | 0.11902 | 0.33417 | -0.12817 | 0.40741 | -0.054932 | 0.44861 | 123.3032 | 0.19226 | 123.2803 | 123.4406 | 123.2803 | 123.1934 | 123.2071 | -123.3765 | -123.2025 | 123.056 | 123.2071 | 60.0769 | 60.2005
307.4844 | 123.3673 | -60.0769 | 63.1073 | 0.010986 | 0.0016299 | 0.065275 | 0.065399 | 0.0016939 | -0.00099762 | 0.0022517 | -0.059845 | 0.00096348 | 0.066849 | 0.067123 | -0.000675 | 0.0015424 | -0.00075834 | -0.009155 | 63.1943 | -60.3516 | 62.9105 | -59.9716 | -60.3287 | -0.10986 | 0.041199 | 63.176 | -60.1639 | 63.1714 | -60.0906 | -60.1913 | -59.7519 | -0.27466 | 0.086975 | -0.19684 | 0.10529 | 59.967 | -0.25177 | 60.2417 | 0.022888 | -0.086975 | 0.068664 | 0.064087 | -0.013733 | 0.32501 | -0.11444 | 0.41199 | -0.027466 | 0.37994 | 123.262 | 0.073242 | 123.3353 | 123.5458 | 123.3398 | 123.2712 | 123.2529 | -123.4589 | -123.2712 | 122.9874 | 123.2483 | 60.0677 | 60.1181
308.4844 | 123.3673 | -60.0815 | 63.121 | -0.011902 | -0.00071993 | 0.063352 | 0.062622 | -0.00044226 | -0.00057042 | -0.00073913 | -0.044586 | 0.00032248 | 0.068131 | 0.067336 | -3.4196e-05 | -0.00038018 | -0.0031081 | -0.013733 | 63.2126 | -60.2966 | 62.8922 | -59.9991 | -60.347 | 0 | 0.013733 | 63.2126 | -60.1639 | 63.1439 | -60.0677 | -60.1822 | -59.7565 | -0.21515 | 0.091552 | -0.22888 | 0.082398 | 60.0815 | -0.2655 | 60.2966 | -0.050354 | -0.082397 | 0.091552 | 0.022888 | 0.013733 | 0.32501 | -0.10071 | 0.40741 | -0.018311 | 0.29755 | 123.1888 | 0.09613 | 123.3078 | 123.5092 | 123.3765 | 123.2941 | 123.2941 | -123.4177 | -123.2849 | 122.9736 | 123.2254 | 60.0677 | 60.0952
309.4844 | 123.3215 | -60.0769 | 63.1165 | -0.050049 | 0.00098907 | 0.064207 | 0.063262 | -0.00065586 | 7.0582e-05 | -0.0015935 | -0.072052 | 0.0020315 | 0.067704 | 0.069045 | 0.000393 | -0.0018756 | 0.00030966 | -0.022888 | 63.1805 | -60.3287 | 62.9242 | -59.903 | -60.3378 | 0.009155 | 0.027466 | 63.1851 | -60.1776 | 63.1393 | -60.0906 | -60.2051 | -59.7565 | -0.25177 | 0.064087 | -0.19226 | 0.17395 | 60.0861 | -0.26093 | 60.3378 | -0.009156 | -0.10071 | 0.068665 | 0.022888 | -0.013733 | 0.32043 | -0.12817 | 0.42114 | -0.027466 | 0.42572 | 123.2529 | 0.086975 | 123.317 | 123.5092 | 123.3627 | 123.2574 | 123.262 | -123.4451 | -123.2941 | 123.0011 | 123.2162 | 60.054 | 60.1044
310.4844 | 123.3856 | -60.0906 | 63.1485 | -0.0042723 | 0.00034827 | 0.062925 | 0.062835 | -0.0032193 | -0.0020658 | -0.00031193 | -0.01712 | 0.00096348 | 0.067276 | 0.067763 | -0.000675 | -0.0018756 | -0.0018265 | -0.018311 | 63.208 | -60.3195 | 62.9013 | -59.9945 | -60.3149 | 0.018311 | 0.009155 | 63.2034 | -60.173 | 63.1485 | -60.0815 | -60.1868 | -59.7565 | -0.22888 | 0.059509 | -0.24719 | 0.09613 | 60.1089 | -0.2243 | 60.3378 | 0.004578 | -0.082398 | 0.054931 | 0 | 0.009155 | 0.33417 | -0.096131 | 0.41656 | -0.013733 | 0.32501 | 123.2208 | 0.091553 | 123.3215 | 123.5275 | 123.3765 | 123.2986 | 123.2941 | -123.468 | -123.3215 | 122.9919 | 123.2391 | 60.0723 | 60.0998
311.4844 | 123.317 | -60.0677 | 63.1165 | -0.057678 | 0.00034827 | 0.064847 | 0.063903 | 0.0019077 | -0.001852 | -0.0024481 | -0.041534 | 0.0016043 | 0.067276 | 0.069045 | -0.001316 | 0.00090142 | -0.00011754 | 0.018311 | 63.1668 | -60.347 | 62.915 | -59.9808 | -60.347 | -0.018311 | 0.022888 | 63.1897 | -60.1639 | 63.1485 | -60.1089 | -60.2142 | -59.761 | -0.27924 | 0.050354 | -0.20142 | 0.086975 | 60.0494 | -0.27924 | 60.3287 | 0 | -0.09613 | 0.073242 | 0.032044 | -0.041199 | 0.3067 | -0.14648 | 0.40283 | -0.050354 | 0.36621 | 123.262 | 0.054931 | 123.3124 | 123.5138 | 123.3536 | 123.2346 | 123.2574 | -123.4634 | -123.2803 | 122.9828 | 123.2162 | 60.0861 | 60.0906
312.5469 | 123.4085 | -60.0357 | 63.1165 | -0.03479 | 0.00077547 | 0.062711 | 0.060913 | 0.00083954 | -0.00035682 | -0.0030889 | 0.046967 | 0.00010888 | 0.06514 | 0.066054 | -0.000675 | 0.00026062 | -0.0024673 | 0.041199 | 63.176 | -60.2509 | 63.0341 | -59.9579 | -60.2692 | 0.11902 | 0.14648 | 63.1531 | -60.1456 | 63.1943 | -59.9945 | -60.0906 | -59.7061 | -0.21515 | 0.059509 | -0.082397 | 0.07782 | 60.1547 | -0.23346 | 60.3699 | -0.018311 | -0.10986 | 0.036621 | 0.07782 | 0.041199 | 0.32959 | -0.054931 | 0.43945 | 0.054932 | 0.29297 | 123.2849 | 0.15106 | 123.3398 | 123.4268 | 123.2986 | 123.2117 | 123.1888 | -123.3673 | -123.262 | 123.0698 | 123.23 | 60.0769 | 60.1822
313.4844 | 123.2895 | -60.0815 | 63.1165 | -0.080566 | 0.0014163 | 0.063352 | 0.064117 | 0.00019874 | -0.00035682 | -0.00031193 | -0.059845 | 0.0020315 | 0.068131 | 0.065414 | 0.0001794 | 0.00026062 | 0.0045823 | -0.064087 | 63.1943 | -60.3699 | 62.8784 | -60.0449 | -60.3973 | -0.091553 | -0.11444 | 63.176 | -60.1913 | 63.0569 | -60.1456 | -60.3012 | -59.8251 | -0.28839 | 0.07782 | -0.23804 | 0.036621 | 59.9899 | -0.31586 | 60.2783 | -0.027466 | -0.10986 | 0.059509 | -0.059509 | -0.064087 | 0.25635 | -0.21973 | 0.36621 | -0.10986 | 0.32501 | 123.2483 | 0.045776 | 123.2483 | 123.5641 | 123.3673 | 123.2758 | 123.2574 | -123.4863 | -123.3078 | 122.9599 | 123.1384 | 60.0174 | 59.967
314.5469 | 123.4222 | -60.0449 | 63.0753 | -0.027161 | 0.0014163 | 0.06207 | 0.060485 | -0.0019377 | 0.0013522 | -0.0037299 | 0.068329 | 0.00096348 | 0.069199 | 0.058364 | -0.0021704 | -0.0027302 | 0.00030966 | -0.013733 | 63.176 | -60.3241 | 62.9654 | -59.9442 | -60.2692 | 0.059509 | 0.068665 | 63.1302 | -60.1456 | 63.2126 | -59.9991 | -60.0906 | -59.6786 | -0.27924 | 0.10071 | -0.10986 | 0.10071 | 60.1044 | -0.2243 | 60.3836 | 0.054932 | -0.10071 | 0.054932 | 0.13733 | 0.045777 | 0.36621 | -0.045776 | 0.46692 | 0.054932 | 0.37994 | 123.2895 | 0.14648 | 123.3582 | 123.5001 | 123.2758 | 123.2208 | 123.175 | -123.3994 | -123.2208 | 123.0103 | 123.2574 | 60.0311 | 60.1135
315.4844 | 123.2895 | -60.1181 | 63.1256 | -0.027161 | 0.0016299 | 0.063566 | 0.06604 | 0.0019077 | 0.00071138 | -0.0013799 | -0.072052 | 0.0016043 | 0.065995 | 0.069472 | -0.0011022 | 0.001115 | 0.0043687 | -0.086975 | 63.1897 | -60.3561 | 62.851 | -60.0586 | -60.3973 | -0.11902 | -0.12817 | 63.1897 | -60.1959 | 63.0844 | -60.2005 | -60.2966 | -59.816 | -0.23804 | 0.064087 | -0.27466 | 0.059509 | 59.9991 | -0.27924 | 60.2371 | -0.041199 | -0.07782 | 0.064087 | -0.041198 | -0.082397 | 0.30212 | -0.17853 | 0.37994 | -0.10071 | 0.29755 | 123.2071 | -0.004577 | 123.2803 | 123.5458 | 123.3856 | 123.3078 | 123.3078 | -123.4818 | -123.3215 | 122.9691 | 123.2025 | 60.0311 | 59.9899
316.4844 | 123.3353 | -60.0632 | 63.1119 | 0.0033567 | 0.00077547 | 0.063779 | 0.063476 | 0.0044711 | -0.00099762 | 0.00011527 | -0.032379 | 0.0018179 | 0.06514 | 0.067763 | -0.0011022 | 0.00090142 | 0.00073706 | 0 | 63.1989 | -60.347 | 62.9196 | -59.9716 | -60.3104 | 0 | 0.032043 | 63.176 | -60.1776 | 63.0707 | -60.054 | -60.141 | -59.7473 | -0.28381 | 0.086976 | -0.19226 | 0.091552 | 60.0632 | -0.24719 | 60.347 | 0.036621 | -0.11444 | 0.064087 | -0.041198 | 0.009155 | 0.31586 | -0.07782 | 0.4303 | 0.036621 | 0.37537 | 123.2666 | 0.1236 | 123.2483 | 123.5458 | 123.3536 | 123.262 | 123.2391 | -123.4589 | -123.2895 | 122.9828 | 123.1338 | 60.0632 | 60.0952
317.5469 | 123.3353 | -60.0677 | 63.1165 | 0.033875 | -0.00071993 | 0.063779 | 0.064117 | 0.0046847 | 0.0013522 | -0.0020209 | -0.041534 | 0.00010888 | 0.067276 | 0.073318 | -0.0002478 | -0.00038018 | -0.0013991 | -0.013733 | 63.1943 | -60.3333 | 62.9196 | -59.9808 | -60.3195 | 0.009155 | 0.041199 | 63.2034 | -60.1593 | 63.1485 | -60.0677 | -60.1913 | -59.7427 | -0.2655 | 0.07782 | -0.19684 | 0.086975 | 60.0769 | -0.25177 | 60.3424 | 0.013733 | -0.091553 | 0.086975 | 0.032044 | 0 | 0.32501 | -0.1236 | 0.41656 | -0.032043 | 0.35248 | 123.2529 | 0.091553 | 123.3078 | 123.5275 | 123.3627 | 123.262 | 123.2712 | -123.4497 | -123.2758 | 122.9874 | 123.2162 | 60.054 | 60.1089
318.4844 | 123.3444 | -60.0769 | 63.1348 | -0.050049 | -0.00029273 | 0.063352 | 0.064117 | -0.0015103 | 0.0011386 | 0.00075627 | -0.053741 | 0.0013907 | 0.068558 | 0.065841 | -0.0028112 | -0.0020892 | -0.00075834 | -0.018311 | 63.1714 | -60.3378 | 62.915 | -59.9625 | -60.3241 | 0 | 0.091553 | 63.1714 | -60.1593 | 63.1668 | -60.1044 | -60.2142 | -59.761 | -0.26093 | 0.036621 | -0.21973 | 0.11444 | 60.0769 | -0.24719 | 60.3378 | 0.013733 | -0.082398 | 0.036621 | 0.032043 | -0.027466 | 0.31586 | -0.13733 | 0.39825 | -0.054931 | 0.37537 | 123.2529 | 0.054932 | 123.3261 | 123.5092 | 123.3307 | 123.2483 | 123.2483 | -123.4726 | -123.2941 | 122.9919 | 123.2437 | 60.0586 | 60.1685
319.4844 | 123.3307 | -60.1135 | 63.0798 | -0.027161 | -0.00029273 | 0.063138 | 0.063262 | 0.0016939 | 0.0022068 | 0.0016107 | -0.011017 | 0.00053628 | 0.067276 | 0.061996 | -0.0008886 | -0.0012348 | 0.0052231 | -0.12817 | 63.1577 | -60.3653 | 62.5946 | -60.0769 | -60.0494 | -0.082397 | -0.12817 | 63.1714 | -60.1776 | 63.1027 | -60.1685 | -60.2829 | -59.8022 | -0.25177 | 0.07782 | -0.48523 | 0.036621 | 60.0311 | 0.064087 | 60.2829 | 0.31586 | -0.064087 | 0.091553 | 0.022888 | -0.054932 | 0.31128 | -0.16937 | 0.37537 | -0.10529 | 0.28839 | 122.9599 | 0.009155 | 123.2803 | 123.5229 | 123.349 | 123.2712 | 123.2849 | -123.4451 | -123.2574 | 122.7081 | 123.2162 | 59.9854 | 59.9854
320.4844 | 123.3353 | -60.1135 | 63.0753 | -0.057678 | 0.0024845 | 0.064847 | 0.060913 | 0.0068209 | 0.0024204 | -0.00073913 | 0.031708 | 0.0020315 | 0.065354 | 0.067763 | -0.001316 | 0.00090142 | -0.00033114 | -0.11444 | 63.1577 | -60.3653 | 62.7869 | -59.7427 | -60.3745 | -0.1236 | -0.19684 | 63.176 | -60.1868 | 63.1119 | -60.1639 | -60.2783 | -59.8022 | -0.25177 | 0.082398 | -0.28839 | 0.37079 | 59.9899 | -0.26093 | 60.2417 | -0.009156 | -0.073243 | 0.10071 | 0.036621 | -0.050354 | 0.31128 | -0.16479 | 0.38452 | -0.091552 | 0.62256 | 123.1522 | 0.022889 | 123.2986 | 123.5229 | 123.3627 | 123.2712 | 123.2895 | -123.4406 | -123.262 | 122.9004 | 123.2254 | 59.9991 | 59.9167
321.4844 | 123.3398 | -60.1044 | 63.0798 | -0.065308 | 0.0012027 | 0.06442 | 0.067321 | 0.0023349 | -0.0033474 | -0.0015935 | -0.029327 | 0.0013907 | 0.067704 | 0.065414 | -0.0011022 | 0.00047422 | 0.00052346 | -0.12817 | 63.1714 | -60.3653 | 62.9425 | -60.1776 | -60.3012 | -0.059509 | -0.11902 | 63.1714 | -60.1685 | 63.0981 | -60.1547 | -60.2737 | -59.7977 | -0.26093 | 0.091553 | -0.13733 | -0.073242 | 60.0449 | -0.19684 | 60.3058 | 0.064087 | -0.064087 | 0.091553 | 0.018311 | -0.050354 | 0.3067 | -0.16937 | 0.37079 | -0.10529 | 0.18768 | 123.3078 | 0.013733 | 123.2666 | 123.5367 | 123.3398 | 123.2758 | 123.2758 | -123.4451 | -123.2483 | 123.0469 | 123.2025 | 59.9762 | 59.9854
322.5469 | 123.4177 | -60.022 | 63.0936 | -0.011902 | 0.00056187 | 0.063779 | 0.062408 | 0.0012667 | 0.00049778 | -0.0039435 | 0.068329 | 0.0020315 | 0.065567 | 0.06285 | -0.0008886 | -0.00059378 | -0.00054474 | 0.018311 | 63.1851 | -60.2737 | 62.9974 | -59.8709 | -60.2188 | 0.11444 | 0.46234 | 63.2172 | -60.1135 | 63.208 | -59.9533 | -60.1089 | -59.6924 | -0.25177 | 0.091553 | -0.09613 | 0.15106 | 60.1364 | -0.19684 | 60.3882 | 0.054932 | -0.091552 | 0.1236 | 0.11444 | 0.068665 | 0.32959 | -0.086975 | 0.42114 | 0.004577 | 0.40283 | 123.2712 | 0.16022 | 123.3215 | 123.4589 | 123.3307 | 123.2071 | 123.2391 | -123.3673 | -123.2071 | 123.0194 | 123.23 | 60.0403 | 60.4843
323.4844 | 123.3444 | -60.1364 | 63.0707 | -0.03479 | 0.00013467 | 0.06207 | 0.063903 | 0.0016939 | 0.00028418 | 0.00096987 | -0.035431 | 0.0013907 | 0.067917 | 0.063491 | -0.000675 | -0.00080758 | 0.0013779 | -0.42114 | 63.0981 | -60.4294 | 62.8647 | -60.0952 | -60.3973 | -0.086975 | -0.1236 | 63.1485 | -60.1868 | 63.0936 | -60.1639 | -60.26 | -59.7885 | -0.29297 | 0.027466 | -0.20599 | 0.041199 | 60.0494 | -0.26093 | 60.3424 | 0.032043 | -0.050354 | 0.07782 | 0.022888 | -0.027465 | 0.3479 | -0.1236 | 0.39825 | -0.073242 | 0.33417 | 123.2941 | 0.022889 | 123.2803 | 123.5275 | 123.3353 | 123.2346 | 123.2849 | -123.5001 | -123.2574 | 123.0011 | 123.23 | 59.7153 | 60.0128
324.5469 | 123.3032 | -60.1044 | 63.1165 | -0.072937 | 0.00013467 | 0.063138 | 0.065185 | 0.00062594 | -0.00014322 | -0.0013799 | -0.065949 | 0.0016043 | 0.068772 | 0.067977 | -0.0002478 | 0.00047422 | 0.00073706 | -0.086975 | 63.176 | -60.3607 | 62.8418 | -60.0403 | -60.3973 | -0.07782 | -0.12817 | 63.1897 | -60.1959 | 63.0798 | -60.1868 | -60.2966 | -59.8251 | -0.25635 | 0.059509 | -0.27466 | 0.064087 | 60.0266 | -0.29297 | 60.2829 | -0.036621 | -0.091553 | 0.073242 | -0.036621 | -0.082398 | 0.27924 | -0.19226 | 0.37079 | -0.10071 | 0.32043 | 123.2025 | 0.009155 | 123.2758 | 123.5367 | 123.3856 | 123.2803 | 123.2941 | -123.4772 | -123.3124 | 122.9462 | 123.1842 | 60.0174 | 59.9762
325.4844 | 123.3582 | -60.1044 | 63.0844 | 0.064392 | -0.00029273 | 0.063779 | 0.064331 | -0.0012967 | 0.0037022 | -0.0024481 | -0.023224 | 0.0016043 | 0.066635 | 0.06285 | 0.0006066 | 0.00068782 | 0.0020187 | -0.13275 | 63.176 | -60.3653 | 62.8281 | -60.0677 | -60.3973 | -0.10986 | -0.15564 | 63.1439 | -60.1776 | 63.1027 | -60.141 | -60.2829 | -59.7885 | -0.26093 | 0.091552 | -0.25635 | 0.036621 | 59.9945 | -0.29297 | 60.2554 | -0.032044 | -0.073242 | 0.059509 | 0.01831 | -0.036621 | 0.31586 | -0.17853 | 0.3891 | -0.10529 | 0.29755 | 123.1934 | 0.036621 | 123.2803 | 123.5413 | 123.3215 | 123.2803 | 123.2483 | -123.4497 | -123.262 | 122.9324 | 123.2071 | 59.9716 | 59.9487
326.4844 | 123.2208 | -60.1227 | 63.0157 | -0.072937 | 0.0018435 | 0.06442 | 0.06369 | 0.0010531 | -0.00078402 | -9.8328e-05 | -0.059845 | 0.0024589 | 0.070908 | 0.075667 | -0.0015296 | -0.00059378 | 0.0033005 | -0.14191 | 63.1668 | -60.3928 | 62.8052 | -60.1273 | -60.4385 | -0.13733 | -0.17853 | 63.1668 | -60.1776 | 63.0798 | -60.1776 | -60.2783 | -59.6054 | -0.27008 | 0.15106 | -0.21057 | -0.004577 | 59.9854 | -0.31586 | 60.2554 | -0.045777 | -0.054931 | 0.15106 | 0.064087 | -0.054931 | 0.51727 | -0.15564 | 0.5722 | -0.10071 | 0.2655 | 123.1979 | 0 | 123.2574 | 123.5596 | 123.3444 | 123.2895 | 123.2895 | -123.4085 | -123.1934 | 122.9279 | 123.2025 | 59.9808 | 59.9442
327.4844 | 123.4222 | -60.0906 | 63.0478 | -0.10345 | 0.0029117 | 0.065275 | 0.063049 | -0.0017239 | -0.00099762 | 0.0024653 | -0.023224 | -0.0016001 | 0.064713 | 0.062209 | -0.000675 | 0.00068782 | 0.0030869 | -0.10071 | 63.1622 | -60.3287 | 62.9196 | -59.9762 | -60.3104 | -0.027466 | -0.10986 | 63.121 | -60.1776 | 63.1989 | -60.0449 | -60.1593 | -59.6741 | -0.23804 | 0.11444 | -0.12817 | 0.11444 | 60.0632 | -0.21973 | 60.3012 | 0.01831 | -0.086975 | 0.073242 | 0.15106 | 0.045776 | 0.41656 | -0.068665 | 0.50354 | 0.01831 | 0.35248 | 123.2483 | 0.13275 | 123.3765 | 123.4909 | 123.2986 | 123.2529 | 123.2117 | -123.3765 | -123.2254 | 123.0103 | 123.2895 | 59.9899 | 59.9808
328.4844 | 123.3673 | -60.1044 | 63.089 | -0.057678 | 0.00056187 | 0.062498 | 0.065399 | -1.486e-05 | 0.0017794 | 0.0018243 | -0.044586 | 0.0018179 | 0.065995 | 0.072677 | 0.0035974 | 0.001756 | -0.0035355 | -0.11444 | 63.1714 | -60.3745 | 62.8281 | -60.0952 | -60.4477 | -0.11902 | -0.17853 | 63.1531 | -60.1959 | 63.0569 | -59.9167 | -60.2829 | -59.8526 | -0.27008 | 0.082398 | -0.26093 | 0.009155 | 59.9854 | -0.34332 | 60.2554 | -0.073242 | -0.091553 | 0.064087 | -0.032043 | 0.18768 | 0.25177 | -0.17853 | 0.34332 | -0.086975 | 0.27924 | 123.2025 | 0.27924 | 123.2529 | 123.5458 | 123.349 | 123.2758 | 123.2574 | -123.4634 | -123.2849 | 122.9324 | 123.1613 | 59.9899 | 59.9258
329.5 | 123.3902 | -60.0494 | 63.1165 | -0.042419 | 0.0018435 | 0.065061 | 0.062622 | -0.0017239 | 0.0028476 | 0.00054267 | 0.059174 | 0.00032248 | 0.066849 | 0.060287 | -0.0002478 | -0.0010212 | -0.00011754 | 0.013733 | 63.1805 | -60.2875 | 62.97 | -59.8984 | -60.2234 | 0.091553 | 0.10071 | 63.1439 | -60.1181 | 63.1851 | -59.9991 | -60.1044 | -59.7015 | -0.23804 | 0.064087 | -0.14648 | 0.15106 | 60.141 | -0.17395 | 60.379 | 0.064087 | -0.068665 | 0.027466 | 0.068665 | 0.050354 | 0.3479 | -0.054932 | 0.41656 | 0.013733 | 0.3891 | 123.2574 | 0.11902 | 123.3032 | 123.468 | 123.262 | 123.23 | 123.1934 | -123.4039 | -123.2346 | 123.0194 | 123.2346 | 60.0632 | 60.1501
330.4844 | 123.3353 | -60.1181 | 63.0981 | -0.057678 | 0.00056187 | 0.065061 | 0.063903 | -0.00065586 | -0.00099762 | -0.00095273 | -0.28873 | -0.00053192 | 0.067063 | 0.062636 | -3.4196e-05 | 0.00026062 | -0.00033114 | -0.13275 | 63.1668 | -60.3516 | 62.8372 | -60.0952 | -60.4248 | -0.13733 | -0.009155 | 63.1439 | -60.1913 | 63.0753 | -60.1227 | -60.2692 | -59.8068 | -0.23346 | 0.068664 | -0.26093 | 0.022888 | 59.9808 | -0.3067 | 60.2142 | -0.073243 | -0.073242 | 0.045776 | -0.022889 | -0.004578 | 0.31128 | -0.15106 | 0.38452 | -0.07782 | 0.25635 | 123.1888 | 0.068664 | 123.2666 | 123.5184 | 123.3353 | 123.2849 | 123.262 | -123.4497 | -123.2895 | 122.9553 | 123.1934 | 59.9854 | 60.1089
331.5469 | 123.3215 | -60.1089 | 63.0981 | -0.050049 | -7.913e-05 | 0.064634 | 0.064971 | -0.00044226 | 0.00092498 | 0.00096987 | -0.078156 | -0.00074552 | 0.06749 | 0.067763 | -0.0011022 | -0.00059378 | 0.0035141 | -0.12817 | 63.1851 | -60.3516 | 62.8281 | -60.1044 | -60.466 | -0.1236 | -0.16479 | 63.1439 | -60.2142 | 63.089 | -60.1822 | -60.2921 | -59.8206 | -0.24261 | 0.086975 | -0.27008 | 0.004578 | 59.9854 | -0.35706 | 60.228 | -0.11444 | -0.10529 | 0.045776 | -0.009156 | -0.073242 | 0.28839 | -0.18311 | 0.39368 | -0.07782 | 0.24719 | 123.1796 | 0.032043 | 123.3032 | 123.5367 | 123.3582 | 123.2941 | 123.2529 | -123.4497 | -123.3124 | 122.937 | 123.1979 | 59.9808 | 59.9442
332.4844 | 123.2941 | -60.0952 | 63.1027 | -0.072937 | 0.0020573 | 0.063993 | 0.064758 | 0.00062594 | 0.0015658 | 0.00011527 | -0.035431 | 0.0013907 | 0.066208 | 0.063705 | -0.002384 | 0.00026062 | 0.0013779 | -0.11902 | 63.176 | -60.3516 | 62.6038 | -60.1181 | -60.0082 | -0.10071 | -0.15106 | 63.1714 | -60.1776 | 63.1073 | -60.1501 | -60.2921 | -59.8114 | -0.25635 | 0.073242 | -0.49896 | -0.022888 | 59.9945 | 0.086975 | 60.2509 | 0.34332 | -0.082397 | 0.068665 | 0.004578 | -0.054931 | 0.28381 | -0.19684 | 0.36621 | -0.11444 | 0.23346 | 122.9553 | 0.027466 | 123.2849 | 123.5275 | 123.349 | 123.2712 | 123.2666 | -123.4543 | -123.2803 | 122.699 | 123.2025 | 59.9762 | 59.9442
333.5469 | 123.3719 | -60.0632 | 63.1256 | -0.042419 | 0.00034827 | 0.062498 | 0.06369 | -0.0027921 | 0.00028418 | -0.00052553 | -0.041534 | 0.00010888 | 0.063645 | 0.064986 | -0.000675 | 0.00090142 | -0.0018265 | -0.009155 | 63.2401 | -60.3287 | 62.9013 | -59.9991 | -60.3149 | 0.013733 | 0.022888 | 63.1989 | -60.1685 | 63.1439 | -60.0723 | -60.1913 | -59.7382 | -0.2655 | 0.11444 | -0.2243 | 0.064087 | 60.0769 | -0.25177 | 60.3424 | 0.013733 | -0.10529 | 0.073243 | 0.018311 | -0.009156 | 0.32501 | -0.12817 | 0.4303 | -0.022888 | 0.32959 | 123.23 | 0.09613 | 123.3124 | 123.5687 | 123.3673 | 123.3032 | 123.262 | -123.4543 | -123.2941 | 122.9645 | 123.2071 | 60.054 | 60.0861
334.5 | 123.4314 | -60.0449 | 63.1119 | -0.042419 | 0.00056187 | 0.063352 | 0.062835 | 0.00083954 | -0.0016384 | 0.0024653 | 0.089691 | -0.00053192 | 0.065995 | 0.064559 | -0.0017432 | -0.0037982 | -0.0011855 | 0.009155 | 63.1348 | -60.2966 | 62.9883 | -59.8755 | -60.2234 | 0.11902 | 0.12817 | 63.1531 | -60.1227 | 63.2446 | -59.9487 | -60.0449 | -59.642 | -0.25177 | 0.022889 | -0.1236 | 0.16937 | 60.1639 | -0.17853 | 60.4156 | 0.073242 | -0.07782 | 0.041199 | 0.13275 | 0.096131 | 0.40283 | 0 | 0.48065 | 0.07782 | 0.42114 | 123.2849 | 0.17395 | 123.3673 | 123.4314 | 123.2758 | 123.1796 | 123.1979 | -123.4085 | -123.2346 | 123.0331 | 123.2895 | 60.054 | 60.173
335.5469 | 123.2986 | -60.0769 | 63.1165 | -0.019531 | -0.00071993 | 0.065702 | 0.065399 | 0.0029757 | -0.0022794 | -0.0024481 | -0.062897 | 0.0026725 | 0.063858 | 0.063705 | -0.0008886 | 0.001756 | -0.0013991 | -0.027466 | 63.1668 | -60.3561 | 62.9059 | -59.9762 | -60.3333 | -0.036621 | -0.027466 | 63.1851 | -60.1868 | 63.1165 | -60.1364 | -60.2417 | -59.7794 | -0.27924 | 0.050354 | -0.21057 | 0.10071 | 60.0403 | -0.25635 | 60.3195 | 0.022888 | -0.10986 | 0.068665 | 0 | -0.05951 | 0.29755 | -0.16479 | 0.40741 | -0.054931 | 0.37994 | 123.262 | 0.050354 | 123.3032 | 123.5229 | 123.3719 | 123.2437 | 123.262 | -123.4726 | -123.3032 | 122.9828 | 123.1934 | 60.0494 | 60.0494
336.4844 | 123.4222 | -60.0906 | 63.0661 | -0.088196 | 0.0012027 | 0.064207 | 0.064971 | -1.486e-05 | -0.001852 | 0.0011835 | -0.0079652 | 0.0020315 | 0.069412 | 0.063705 | -0.001316 | 4.7018e-05 | -0.0022537 | -0.10071 | 63.1348 | -60.3607 | 62.9059 | -59.9945 | -60.3607 | -0.073242 | -0.068665 | 63.1256 | -60.1501 | 63.1805 | -60.0632 | -60.1318 | -59.6786 | -0.27008 | 0.068665 | -0.16022 | 0.09613 | 60.0174 | -0.27008 | 60.2875 | 0 | -0.059509 | 0.059509 | 0.11444 | 0.027466 | 0.41199 | -0.041199 | 0.4715 | 0.01831 | 0.36621 | 123.2666 | 0.086975 | 123.3307 | 123.4955 | 123.2758 | 123.2254 | 123.2162 | -123.4268 | -123.2162 | 122.9965 | 123.2712 | 59.9899 | 60.022
337.5469 | 123.381 | -60.0861 | 63.0432 | -0.03479 | 0.00098907 | 0.063993 | 0.061981 | 0.0014803 | -0.0016384 | 0.00054267 | -0.032379 | 0.00010888 | 0.067063 | 0.0652 | -0.000675 | 0.00047422 | 0.0018051 | -0.11444 | 63.1531 | -60.3378 | 62.8693 | -60.0357 | -60.4156 | -0.10071 | -0.14191 | 63.1393 | -60.1868 | 63.1393 | -60.1089 | -60.2142 | -59.7473 | -0.25177 | 0.10986 | -0.17395 | 0.050354 | 59.9854 | -0.32959 | 60.2371 | -0.077819 | -0.10071 | 0.09613 | 0.09613 | -0.022888 | 0.33875 | -0.12817 | 0.43945 | -0.027465 | 0.30212 | 123.2071 | 0.07782 | 123.3261 | 123.4909 | 123.3261 | 123.2391 | 123.2254 | -123.381 | -123.23 | 122.9553 | 123.2254 | 59.9716 | 59.9442
338.4844 | 123.4314 | -60.0815 | 63.0386 | -0.057678 | -0.0015743 | 0.066343 | 0.062622 | -0.00044226 | 0.00071138 | -0.00095273 | 0.022552 | -0.0028817 | 0.065354 | 0.069686 | -0.0019568 | -0.0014484 | -0.00097194 | -0.064087 | 63.1256 | -60.3287 | 62.9288 | -59.935 | -60.3104 | -0.15106 | 0.15106 | 63.1256 | -60.1639 | 63.2172 | -60.054 | -60.1318 | -59.6832 | -0.24719 | 0.086975 | -0.10986 | 0.14648 | 59.9304 | -0.22888 | 60.1776 | 0.01831 | -0.082397 | 0.086975 | 0.17853 | 0.027466 | 0.39825 | -0.050354 | 0.48065 | 0.032043 | 0.39368 | 123.2574 | 0.10986 | 123.381 | 123.4543 | 123.2895 | 123.2071 | 123.2071 | -123.3673 | -123.2025 | 123.0103 | 123.2986 | 60.0174 | 60.2325
339.5469 | 123.3994 | -60.0769 | 63.0295 | -0.12634 | -7.913e-05 | 0.064207 | 0.063476 | -0.0019377 | 0.0024204 | 0.00011527 | 0.013397 | -0.0013863 | 0.064499 | 0.068191 | 0.0006066 | 4.7018e-05 | 0.00095066 | -0.045776 | 63.121 | -60.2966 | 62.9288 | -59.9258 | -60.3104 | -0.032043 | -0.041199 | 63.0981 | -60.173 | 63.1943 | -60.0449 | -60.1639 | -59.7153 | -0.21973 | 0.091553 | -0.10071 | 0.15106 | 60.0449 | -0.23346 | 60.2646 | -0.013733 | -0.096131 | 0.068665 | 0.16479 | 0.032043 | 0.36163 | -0.086975 | 0.45776 | 0.009156 | 0.37079 | 123.2254 | 0.12817 | 123.3673 | 123.4177 | 123.2712 | 123.1979 | 123.175 | -123.3261 | -123.2025 | 123.0057 | 123.2712 | 60.0311 | 60.0357
340.4844 | 123.3856 | -60.0677 | 63.0753 | -0.10345 | 0.0018435 | 0.065702 | 0.063476 | -0.0040739 | -0.00014322 | -0.0024481 | 0.034759 | 0.00074988 | 0.065354 | 0.067763 | 0.001034 | -0.0012348 | -0.0020401 | -0.091553 | 63.1393 | -60.3241 | 62.9196 | -59.9396 | -60.3516 | -0.032043 | -0.068665 | 63.1165 | -60.141 | 63.1531 | -60.054 | -60.1913 | -59.7336 | -0.25635 | 0.064087 | -0.15564 | 0.12817 | 60.0357 | -0.28381 | 60.2921 | -0.027465 | -0.073242 | 0.041199 | 0.07782 | 0.013733 | 0.33417 | -0.1236 | 0.40741 | -0.050354 | 0.38452 | 123.2437 | 0.086975 | 123.2941 | 123.4634 | 123.2574 | 123.2071 | 123.1842 | -123.3994 | -123.2162 | 122.9874 | 123.2208 | 59.9762 | 59.9991
341.5469 | 123.4177 | -60.0403 | 63.0707 | -0.13397 | 0.00056187 | 0.064634 | 0.065185 | 0.00019874 | 0.0011386 | -0.0011663 | -0.01712 | 0.00010888 | 0.064926 | 0.065841 | -0.0025976 | -0.0025164 | -0.0022537 | -0.068665 | 63.121 | -60.3149 | 62.9562 | -59.9487 | -60.3149 | -0.032043 | -0.036621 | 63.1119 | -60.1685 | 63.3316 | -60.1227 | -60.0998 | -59.6878 | -0.27466 | 0.050354 | -0.11444 | 0.091553 | 60.0082 | -0.27466 | 60.2829 | 0 | -0.12817 | 0.041198 | 0.26093 | -0.082398 | 0.35248 | -0.059509 | 0.48065 | 0.068665 | 0.36621 | 123.2712 | 0.045776 | 123.5001 | 123.436 | 123.2803 | 123.1613 | 123.1522 | -123.3856 | -123.2391 | 122.9965 | 123.3719 | 59.9716 | 60.0037
342.4844 | 123.3994 | -60.0586 | 63.0386 | -0.095825 | -7.913e-05 | 0.06442 | 0.061553 | -0.00086946 | -0.0012112 | -0.0013799 | 0.004242 | 0.00010888 | 0.064286 | 0.063705 | -0.0017432 | 4.7018e-05 | 0.0041551 | -0.073242 | 63.1485 | -60.3149 | 62.9379 | -59.9258 | -60.3195 | -0.032043 | -0.036621 | 63.0981 | -60.1593 | 63.1851 | -60.0494 | -60.141 | -59.7107 | -0.25635 | 0.10986 | -0.10071 | 0.13275 | 60.0266 | -0.26093 | 60.2829 | -0.004578 | -0.10071 | 0.05951 | 0.14648 | 0.009156 | 0.3479 | -0.082397 | 0.44861 | 0.018311 | 0.3891 | 123.2529 | 0.10986 | 123.3444 | 123.4634 | 123.2574 | 123.2071 | 123.1567 | -123.3536 | -123.1979 | 122.9965 | 123.2437 | 59.9854 | 60.022
343.4844 | 123.3673 | -60.0861 | 63.0707 | -0.095825 | -0.0013607 | 0.063352 | 0.063049 | 0.0010531 | 7.0582e-05 | -0.0022345 | 0.010345 | 0.00096348 | 0.068558 | 0.059646 | -0.0002478 | -0.0012348 | 0.0018051 | -0.07782 | 63.1577 | -60.3241 | 62.9105 | -59.9716 | -60.3104 | 0 | 0.068665 | 63.1439 | -60.1273 | 63.1668 | -60.0449 | -60.1501 | -59.7198 | -0.23804 | 0.086975 | -0.16022 | 0.11444 | 60.0861 | -0.2243 | 60.3241 | 0.013733 | -0.041198 | 0.073242 | 0.09613 | 0.041199 | 0.36621 | -0.064086 | 0.40741 | -0.022888 | 0.35248 | 123.2346 | 0.082397 | 123.2941 | 123.4818 | 123.2712 | 123.2437 | 123.23 | -123.3948 | -123.1979 | 122.9965 | 123.2529 | 60.0082 | 60.1547
344.4844 | 123.3582 | -60.0906 | 63.0386 | -0.095825 | 0.0012027 | 0.06442 | 0.062622 | -0.0012967 | 0.0017794 | 0.00011527 | -0.011017 | 0.00053628 | 0.06749 | 0.062209 | -0.001316 | -0.0018756 | -0.0037491 | -0.064087 | 63.1165 | -60.3195 | 62.9471 | -59.935 | -60.3012 | -0.041199 | -0.013733 | 63.121 | -60.1593 | 63.176 | -60.0769 | -60.1639 | -59.6924 | -0.22888 | 0.07782 | -0.091552 | 0.15564 | 60.0494 | -0.21057 | 60.2783 | 0.018311 | -0.068665 | 0.082398 | 0.13733 | 0.013733 | 0.39825 | -0.073242 | 0.46692 | -0.004577 | 0.38452 | 123.2666 | 0.082398 | 123.3353 | 123.436 | 123.2803 | 123.2071 | 123.2117 | -123.3582 | -123.1979 | 123.0377 | 123.2666 | 60.0266 | 60.0769
345.5469 | 123.2849 | -60.1089 | 63.121 | -0.072937 | -7.913e-05 | 0.063993 | 0.064544 | 0.0025485 | 0.0011386 | 0.00032907 | -0.093414 | 0.00053628 | 0.067917 | 0.065841 | -0.000675 | -0.0029438 | -0.0018265 | -0.091553 | 63.176 | -60.3745 | 62.851 | -60.0449 | -60.4477 | -0.13275 | -0.16022 | 63.1668 | -60.173 | 63.0798 | -60.1868 | -60.3149 | -59.8389 | -0.2655 | 0.054931 | -0.27008 | 0.064087 | 59.9762 | -0.33875 | 60.2417 | -0.073242 | -0.064087 | 0.045776 | -0.041199 | -0.07782 | 0.27008 | -0.20599 | 0.33417 | -0.14191 | 0.32959 | 123.2254 | -0.013733 | 123.2529 | 123.5504 | 123.3398 | 123.2849 | 123.2758 | -123.4955 | -123.2941 | 122.9599 | 123.1888 | 60.0174 | 59.9487
346.4844 | 123.3902 | -60.0906 | 63.0615 | -0.11108 | 0.00077547 | 0.062925 | 0.062408 | -0.0010831 | 0.0015658 | -9.8328e-05 | 0.0011902 | -0.00031832 | 0.06514 | 0.066268 | -0.0011022 | -0.001662 | 0.0013779 | -0.091553 | 63.1485 | -60.3333 | 62.8967 | -59.9808 | -60.3333 | -0.022888 | -0.086975 | 63.1393 | -60.1547 | 63.1485 | -60.0677 | -60.1639 | -59.729 | -0.24262 | 0.086976 | -0.16479 | 0.10986 | 60.0677 | -0.24262 | 60.3104 | 0 | -0.064087 | 0.07782 | 0.086976 | 0.022888 | 0.36163 | -0.073242 | 0.42572 | -0.009155 | 0.35248 | 123.23 | 0.086975 | 123.3032 | 123.4818 | 123.2941 | 123.2391 | 123.23 | -123.3948 | -123.2162 | 122.9874 | 123.2391 | 59.9991 | 60.0037
347.4844 | 123.4268 | -60.0403 | 63.0936 | -0.057678 | 0.00034827 | 0.063352 | 0.062622 | -0.0012967 | -0.002493 | -0.00052553 | 0.025604 | -0.00010472 | 0.064926 | 0.065841 | -0.0004614 | -0.00038018 | -0.0037491 | -0.027466 | 63.176 | -60.3012 | 62.9837 | -59.8938 | -60.2509 | 0.064087 | 0.082397 | 63.1714 | -60.1273 | 63.2309 | -59.9945 | -60.0906 | -59.6878 | -0.26093 | 0.082397 | -0.10986 | 0.14648 | 60.1044 | -0.21057 | 60.3653 | 0.050354 | -0.086975 | 0.07782 | 0.13733 | 0.045776 | 0.35248 | -0.050354 | 0.43945 | 0.036621 | 0.40741 | 123.2849 | 0.13275 | 123.3582 | 123.4772 | 123.2986 | 123.2162 | 123.2117 | -123.3948 | -123.2208 | 123.024 | 123.2712 | 60.0128 | 60.1227
348.5469 | 123.3444 | -60.0723 | 63.1439 | -0.011902 | 0.0022709 | 0.063138 | 0.06668 | 0.0023349 | 0.0015658 | 0.0037469 | -0.078156 | 0.00032248 | 0.067276 | 0.073104 | -0.0004614 | -0.0010212 | -0.0026809 | -0.027466 | 63.1668 | -60.3516 | 62.9196 | -59.9808 | -60.3287 | -0.11444 | 0.027466 | 63.1897 | -60.1593 | 63.1439 | -60.0815 | -60.2051 | -59.7473 | -0.27923 | 0.022888 | -0.2243 | 0.091553 | 59.9579 | -0.25635 | 60.2371 | 0.022888 | -0.086975 | 0.045776 | 0 | -0.009155 | 0.32501 | -0.13275 | 0.41199 | -0.045776 | 0.37079 | 123.2712 | 0.07782 | 123.3032 | 123.5184 | 123.349 | 123.2391 | 123.262 | -123.4955 | -123.3032 | 122.9919 | 123.2162 | 60.0449 | 60.0998
349.4844 | 123.4451 | -60.0449 | 63.089 | -0.088196 | 0.0016299 | 0.063138 | 0.061767 | -0.0017239 | 0.00049778 | -0.00073913 | 0.037811 | -0.00095912 | 0.068558 | 0.058364 | -3.4196e-05 | -0.00080758 | 9.6064e-05 | -0.018311 | 63.1439 | -60.3012 | 62.9791 | -59.8938 | -60.2417 | 0.086975 | 0.10986 | 63.1119 | -60.1227 | 63.2172 | -59.9762 | -60.0769 | -59.6649 | -0.25635 | 0.054932 | -0.10986 | 0.15106 | 60.1318 | -0.19684 | 60.3882 | 0.059509 | -0.07782 | 0.022888 | 0.12817 | 0.068665 | 0.37994 | -0.032043 | 0.45776 | 0.045777 | 0.40741 | 123.2803 | 0.14648 | 123.3398 | 123.4451 | 123.2346 | 123.1888 | 123.1567 | -123.3902 | -123.2117 | 123.024 | 123.262 | 60.0266 | 60.1547
350.4844 | 123.4177 | -60.0586 | 63.0844 | -0.095825 | -0.00093353 | 0.06207 | 0.063049 | -0.0019377 | -0.004202 | -9.8328e-05 | 0.025604 | -0.00031832 | 0.066849 | 0.060927 | 0.0001794 | -0.0035846 | -0.00033114 | -0.07782 | 63.1256 | -60.3424 | 62.9333 | -59.9854 | -60.3149 | -0.018311 | -0.064087 | 63.1348 | -60.1364 | 63.1714 | -60.0677 | -60.1501 | -59.7244 | -0.28381 | 0.041198 | -0.15106 | 0.073242 | 60.0403 | -0.25635 | 60.3241 | 0.027466 | -0.07782 | 0.050354 | 0.086975 | -0.009155 | 0.33417 | -0.091552 | 0.41199 | -0.013732 | 0.35706 | 123.2758 | 0.068665 | 123.3078 | 123.468 | 123.2712 | 123.1842 | 123.1934 | -123.4268 | -123.2208 | 122.9919 | 123.23 | 59.9808 | 59.9945
351.4844 | 123.4406 | -60.0357 | 63.0844 | -0.065308 | -0.00050633 | 0.063993 | 0.061553 | -0.0017239 | -0.00014322 | 0.0018243 | 0.028656 | 0.0018179 | 0.064713 | 0.062209 | -0.0008886 | -0.001662 | -0.00075834 | 0 | 63.1805 | -60.2966 | 62.9929 | -59.903 | -60.2509 | 0.086975 | 0.09613 | 63.1439 | -60.1318 | 63.2309 | -59.9579 | -60.0586 | -59.6603 | -0.26093 | 0.09613 | -0.091553 | 0.13275 | 60.1227 | -0.21515 | 60.3836 | 0.045777 | -0.09613 | 0.059509 | 0.14648 | 0.07782 | 0.37537 | -0.022888 | 0.4715 | 0.073242 | 0.39368 | 123.2895 | 0.17395 | 123.3627 | 123.4772 | 123.2758 | 123.2162 | 123.1796 | -123.381 | -123.2162 | 123.0286 | 123.2666 | 60.0357 | 60.1318
352.5469 | 123.3902 | -60.0632 | 63.0707 | -0.057678 | 0.0012027 | 0.062498 | 0.064758 | 0.00083954 | -0.0012112 | 0.00011527 | -0.014069 | 0.0024589 | 0.065354 | 0.066268 | -0.0004614 | -0.001662 | -0.00054474 | -0.09613 | 63.1302 | -60.3424 | 62.9288 | -60.0037 | -60.3561 | -0.041199 | -0.064087 | 63.1256 | -60.1456 | 63.1622 | -60.0586 | -60.1593 | -59.7198 | -0.27924 | 0.059509 | -0.14191 | 0.059509 | 60.022 | -0.29297 | 60.3012 | -0.013733 | -0.082398 | 0.054931 | 0.091552 | 0.004577 | 0.34332 | -0.096131 | 0.42572 | -0.013733 | 0.33875 | 123.2712 | 0.086975 | 123.3078 | 123.4726 | 123.2712 | 123.1934 | 123.1888 | -123.4131 | -123.2162 | 122.9919 | 123.2254 | 59.967 | 59.9991
353.4844 | 123.4451 | -60.0357 | 63.089 | -0.065308 | 0.00034827 | 0.061002 | 0.064331 | -0.0015103 | 0.0015658 | -0.0033025 | 0.040863 | -0.00095912 | 0.06749 | 0.068191 | -3.4196e-05 | -0.0037982 | 0.0018051 | -0.009155 | 63.1348 | -60.2875 | 62.9883 | -59.8984 | -60.2371 | 0.073242 | 0.11902 | 63.1485 | -60.1273 | 63.2538 | -59.967 | -60.0632 | -59.642 | -0.25177 | 0.045777 | -0.10071 | 0.13733 | 60.1089 | -0.20142 | 60.3607 | 0.050354 | -0.091552 | 0.05951 | 0.1648 | 0.068665 | 0.39368 | -0.027465 | 0.48523 | 0.064087 | 0.3891 | 123.2758 | 0.16022 | 123.381 | 123.4222 | 123.2758 | 123.1705 | 123.1842 | -123.3765 | -123.2162 | 123.024 | 123.2895 | 60.0266 | 60.1547
354.5469 | 123.4314 | -60.0677 | 63.0661 | -0.072937 | 0.0022709 | 0.065275 | 0.06369 | -0.00065586 | -0.00035682 | 0.0020379 | -0.059845 | 0.00032248 | 0.067063 | 0.071822 | -0.0045202 | -0.0027302 | -0.0020401 | -0.045776 | 63.1119 | -60.3424 | 62.9791 | -59.9258 | -60.3058 | -0.036621 | -0.027466 | 63.1302 | -60.173 | 63.2812 | -60.0769 | -60.1089 | -59.6832 | -0.27466 | 0.045776 | -0.086975 | 0.14191 | 60.0311 | -0.23804 | 60.3058 | 0.036621 | -0.10529 | 0.064087 | 0.21515 | -0.009155 | 0.38452 | -0.041199 | 0.48981 | 0.064087 | 0.41656 | 123.3215 | 0.096131 | 123.4543 | 123.4543 | 123.3032 | 123.1796 | 123.1979 | -123.4085 | -123.2391 | 123.0469 | 123.349 | 60.022 | 60.0403
355.4844 | 123.3948 | -60.0357 | 63.0844 | -0.027161 | 0.00056187 | 0.062284 | 0.062835 | -0.0047147 | -0.00078402 | -0.00095273 | 0.037811 | 0.00032248 | 0.069199 | 0.067977 | -0.0025976 | -0.00080758 | -0.0011855 | 0.027466 | 63.176 | -60.3058 | 62.9974 | -59.8618 | -60.2188 | 0.10986 | 0.1236 | 63.1897 | -60.1364 | 63.2217 | -60.0266 | -60.0769 | -59.6649 | -0.27008 | 0.091552 | -0.086975 | 0.17395 | 60.1456 | -0.18311 | 60.4156 | 0.086975 | -0.10071 | 0.10529 | 0.13733 | 0.009156 | 0.37079 | -0.041198 | 0.4715 | 0.05951 | 0.44403 | 123.3032 | 0.10986 | 123.3582 | 123.4818 | 123.3261 | 123.2117 | 123.2254 | -123.3902 | -123.2208 | 123.0331 | 123.2574 | 60.0632 | 60.1593
356.4844 | 123.3902 | -60.0449 | 63.121 | -0.11108 | 0.0018435 | 0.062925 | 0.063049 | 0.00019874 | 0.00092498 | -0.0030889 | 0.074432 | 0.00096348 | 0.065781 | 0.065841 | -0.0025976 | 0.00068782 | -0.0037491 | 0.032043 | 63.1577 | -60.2921 | 63.002 | -59.8709 | -60.2234 | 0.21515 | -0.09613 | 63.1622 | -60.1318 | 63.1989 | -59.9808 | -60.0723 | -59.6786 | -0.24719 | 0.036621 | -0.11902 | 0.17395 | 60.26 | -0.17853 | 60.5072 | 0.068664 | -0.086975 | 0.041198 | 0.07782 | 0.064087 | 0.36621 | -0.027466 | 0.45319 | 0.059509 | 0.42114 | 123.2941 | 0.15106 | 123.3307 | 123.4497 | 123.2941 | 123.2025 | 123.2071 | -123.4131 | -123.2529 | 123.0469 | 123.2437 | 60.0769 | 59.9487
357.5469 | 123.4039 | -60.0769 | 63.0981 | -0.057678 | -0.00071993 | 0.063138 | 0.062835 | -0.0019377 | 0.0022068 | -0.0028753 | 0.004242 | -0.00031832 | 0.068558 | 0.064773 | -3.4196e-05 | -0.001662 | 0.0020187 | -0.059509 | 63.1622 | -60.347 | 62.9791 | -60.0494 | -60.3241 | -0.013733 | -0.027466 | 63.1302 | -60.141 | 63.176 | -60.022 | -60.1547 | -59.7015 | -0.27008 | 0.064086 | -0.11902 | 0.027466 | 60.0632 | -0.24719 | 60.3333 | 0.022888 | -0.064087 | 0.032043 | 0.077819 | 0.054931 | 0.37537 | -0.07782 | 0.43945 | -0.013733 | 0.29755 | 123.3261 | 0.11902 | 123.317 | 123.5092 | 123.2712 | 123.2391 | 123.2071 | -123.4451 | -123.2391 | 123.056 | 123.2529 | 60.0174 | 60.0494
358.4844 | 123.4222 | -60.0861 | 63.0981 | -0.019531 | 0.00013467 | 0.063138 | 0.064117 | 0.00083954 | 7.0582e-05 | -0.0041571 | 0.0072936 | 0.00032248 | 0.06749 | 0.064345 | -0.0008886 | -0.0012348 | -0.0020401 | -0.054932 | 63.1668 | -60.3104 | 62.9379 | -59.9442 | -60.2875 | 0.050354 | 0.045776 | 63.1531 | -60.141 | 63.2217 | -60.0037 | -60.0906 | -59.6832 | -0.2243 | 0.068664 | -0.16022 | 0.14191 | 60.1364 | -0.20142 | 60.3607 | 0.022888 | -0.054931 | 0.054931 | 0.1236 | 0.082398 | 0.40283 | -0.004577 | 0.45776 | 0.050354 | 0.36621 | 123.2483 | 0.13733 | 123.3627 | 123.4772 | 123.2941 | 123.2529 | 123.2391 | -123.4085 | -123.2391 | 123.024 | 123.3078 | 60.0311 | 60.1318
359.4844 | 123.4039 | -60.054 | 63.1027 | -0.027161 | 0.0022709 | 0.065275 | 0.064117 | -0.0025785 | -0.00057042 | -0.0033025 | -0.01712 | -0.0013863 | 0.065781 | 0.067977 | -0.0019568 | -0.00059378 | -0.0033219 | 0.041199 | 63.1577 | -60.2829 | 63.0295 | -59.7427 | -59.848 | 0.013733 | 0.16479 | 63.1485 | -60.1456 | 63.2355 | -59.9762 | -60.1181 | -59.6786 | -0.22888 | 0.054932 | -0.073242 | 0.31128 | 60.0677 | 0.20599 | 60.2966 | 0.43488 | -0.091553 | 0.045777 | 0.13275 | 0.07782 | 0.37537 | -0.064087 | 0.46692 | 0.027466 | 0.54016 | 123.3124 | 0.16937 | 123.381 | 123.4406 | 123.2941 | 123.2117 | 123.2025 | -123.3856 | -123.2483 | 123.0835 | 123.2895 | 60.0952 | 60.2188
360.5469 | 123.3856 | -60.0769 | 63.0569 | -0.095825 | -0.00050633 | 0.063352 | 0.063476 | 0.0016939 | -0.00099762 | -0.0026617 | -0.053741 | 0.00032248 | 0.063431 | 0.067123 | -0.0028112 | -0.0025164 | -0.00033114 | -0.068665 | 63.1348 | -60.347 | 62.9471 | -59.9396 | -60.3149 | -0.018311 | -0.027466 | 63.1256 | -60.141 | 63.176 | -60.0677 | -60.1501 | -59.7244 | -0.27008 | 0.07782 | -0.10986 | 0.13733 | 60.0586 | -0.23804 | 60.3287 | 0.032044 | -0.064087 | 0.068664 | 0.11902 | 0.009155 | 0.35248 | -0.073242 | 0.41656 | -0.009155 | 0.40741 | 123.2941 | 0.073242 | 123.317 | 123.4818 | 123.2666 | 123.2117 | 123.2025 | -123.4039 | -123.1979 | 123.024 | 123.2529 | 60.0082 | 60.0494
361.4844 | 123.2986 | -60.0586 | 63.121 | -0.065308 | 0.00077547 | 0.062925 | 0.064117 | 0.0016939 | -0.00035682 | 0.00054267 | -0.053741 | 0.0016043 | 0.065995 | 0.062423 | -0.0004614 | -0.0010212 | 0.00052346 | 0.032043 | 63.2034 | -60.3104 | 62.8967 | -60.0037 | -60.3195 | 0 | 0.045776 | 63.2172 | -60.141 | 63.121 | -60.0998 | -60.2097 | -59.7931 | -0.25177 | 0.082397 | -0.2243 | 0.054932 | 60.0586 | -0.26093 | 60.3104 | -0.009155 | -0.082397 | 0.09613 | 0 | -0.041198 | 0.2655 | -0.15106 | 0.3479 | -0.068665 | 0.3067 | 123.2071 | 0.041199 | 123.262 | 123.5138 | 123.3582 | 123.262 | 123.2758 | -123.4314 | -123.262 | 122.9553 | 123.1796 | 60.0906 | 60.1044
362.5469 | 123.3673 | -60.0769 | 63.0707 | -0.057678 | 0.0029117 | 0.064847 | 0.063049 | -0.0010831 | 7.0582e-05 | 0.00054267 | -0.035431 | 0.00074988 | 0.065354 | 0.063277 | -0.0017432 | -0.0014484 | -0.0022537 | -0.059509 | 63.1439 | -60.3287 | 62.9379 | -59.935 | -60.3241 | -0.022888 | -0.022888 | 63.1027 | -60.1501 | 63.1851 | -60.0677 | -60.1593 | -59.729 | -0.25177 | 0.073242 | -0.13275 | 0.14191 | 60.054 | -0.24719 | 60.3058 | 0.004577 | -0.073242 | 0.032043 | 0.11444 | 0.009155 | 0.3479 | -0.082398 | 0.42114 | -0.009156 | 0.39368 | 123.2666 | 0.082397 | 123.3353 | 123.4726 | 123.2529 | 123.2208 | 123.1796 | -123.3994 | -123.2208 | 123.0148 | 123.262 | 60.0174 | 60.054
363.4844 | 123.3398 | -60.054 | 63.1256 | -0.027161 | 0.0012027 | 0.061216 | 0.062408 | 0.00041234 | -0.0012112 | -9.8328e-05 | -0.014069 | 0.00010888 | 0.067063 | 0.072036 | -0.0004614 | -0.0020892 | -0.00011754 | 0.036621 | 63.1805 | -60.3104 | 62.9471 | -59.9167 | -60.2646 | 0.082397 | 0.11444 | 63.2034 | -60.1135 | 63.1485 | -60.054 | -60.173 | -59.7336 | -0.25635 | 0.054932 | -0.17853 | 0.13733 | 60.1364 | -0.21057 | 60.3928 | 0.045777 | -0.059509 | 0.07782 | 0.022889 | 0 | 0.32043 | -0.11902 | 0.37994 | -0.05951 | 0.39368 | 123.2574 | 0.059509 | 123.262 | 123.4909 | 123.317 | 123.2346 | 123.2574 | -123.436 | -123.2391 | 123.0011 | 123.2025 | 60.0906 | 60.1685
364.4844 | 123.4726 | -60.0449 | 63.1027 | -0.011902 | -0.00050633 | 0.062498 | 0.062408 | -0.0017239 | -0.0014248 | 0.00075627 | -0.0049134 | -0.00053192 | 0.066635 | 0.066054 | 0.0006066 | -0.00038018 | -0.0011855 | 0.004578 | 63.1531 | -60.2921 | 63.0295 | -59.8572 | -60.228 | 0.10529 | 0.16479 | 63.176 | -60.1181 | 63.2401 | -59.9579 | -60.0632 | -59.6603 | -0.24719 | 0.050354 | -0.073242 | 0.18768 | 60.1501 | -0.18311 | 60.3973 | 0.064087 | -0.073242 | 0.073242 | 0.13733 | 0.086975 | 0.38452 | -0.01831 | 0.45776 | 0.054932 | 0.43488 | 123.3215 | 0.16022 | 123.3582 | 123.4451 | 123.2941 | 123.1979 | 123.2208 | -123.3948 | -123.2208 | 123.0743 | 123.2849 | 60.0494 | 60.2097
365.4844 | 123.3032 | -60.0632 | 63.1256 | -0.027161 | 0.0016299 | 0.062925 | 0.065185 | 0.00019874 | 0.00092498 | 0.00075627 | -0.044586 | 0.0024589 | 0.06749 | 0.066268 | -0.001316 | -0.001662 | 0.00030966 | 0.045776 | 63.1851 | -60.3058 | 62.97 | -59.9121 | -60.2554 | 0.064087 | 0.082397 | 63.1897 | -60.141 | 63.1393 | -60.0632 | -60.1593 | -59.7427 | -0.24262 | 0.05951 | -0.15564 | 0.15106 | 60.1273 | -0.19226 | 60.3699 | 0.050354 | -0.07782 | 0.064087 | 0.013733 | 0 | 0.32043 | -0.096131 | 0.39825 | -0.018311 | 0.39368 | 123.2758 | 0.07782 | 123.2803 | 123.4909 | 123.3307 | 123.2483 | 123.2529 | -123.4314 | -123.2666 | 123.0331 | 123.2025 | 60.1089 | 60.1456
366.5469 | 123.3353 | -60.0906 | 63.0844 | -0.065308 | 0.0012027 | 0.065916 | 0.064544 | 0.0012667 | -0.0012112 | -0.0013799 | -0.087311 | 0.00032248 | 0.06514 | 0.070113 | -0.0025976 | 0.0021832 | 0.0011643 | -0.11444 | 63.1668 | -60.3561 | 62.851 | -60.0357 | -60.3973 | -0.11902 | -0.1236 | 63.1485 | -60.2005 | 63.1485 | -60.0906 | -60.2325 | -59.7519 | -0.2655 | 0.082397 | -0.23346 | 0.054931 | 59.9716 | -0.3067 | 60.2371 | -0.041199 | -0.10986 | 0.064087 | 0.064087 | 0 | 0.33875 | -0.14191 | 0.44861 | -0.032044 | 0.32043 | 123.2071 | 0.10986 | 123.349 | 123.5229 | 123.349 | 123.2574 | 123.2391 | -123.4406 | -123.2849 | 122.9416 | 123.2391 | 59.9762 | 59.967
367.4844 | 123.3948 | -60.0449 | 63.176 | 0.010986 | 0.00056187 | 0.063566 | 0.063903 | -0.00065586 | -0.00014322 | 0.00075627 | -0.05069 | 0.0022453 | 0.065995 | 0.065841 | 0.0006066 | 0.001115 | 0.0020187 | -0.050354 | 63.2401 | -60.3287 | 62.8876 | -60.0128 | -60.3287 | 0.013733 | 0.009155 | 63.2126 | -60.1685 | 63.121 | -60.0769 | -60.2051 | -59.9258 | -0.28381 | 0.064087 | -0.28839 | 0.032044 | 60.0586 | -0.28381 | 60.3424 | 0 | -0.1236 | 0.036621 | -0.054931 | -0.032043 | 0.11902 | -0.16022 | 0.24261 | -0.036621 | 0.31586 | 123.2162 | 0.091553 | 123.2895 | 123.5687 | 123.381 | 123.2849 | 123.2574 | -123.5046 | -123.3444 | 122.9324 | 123.1659 | 59.9945 | 60.054
368.5469 | 123.2941 | -60.0952 | 63.089 | -0.057678 | -0.00050633 | 0.065702 | 0.064758 | -0.0027921 | 0.00049778 | -0.0024481 | -0.0018616 | 0.0026725 | 0.066849 | 0.064773 | -0.001316 | -0.0020892 | -0.0011855 | -0.11902 | 63.1668 | -60.3836 | 62.8418 | -60.0723 | -60.5347 | -0.43488 | -0.09613 | 63.1897 | -60.173 | 63.1256 | -60.1822 | -60.2463 | -59.7748 | -0.28839 | 0.07782 | -0.24719 | 0.022888 | 59.6603 | -0.43945 | 59.9487 | -0.15106 | -0.07782 | 0.10071 | 0.036621 | -0.086975 | 0.32044 | -0.15106 | 0.39825 | -0.073242 | 0.31128 | 123.2254 | -0.009155 | 123.2986 | 123.5504 | 123.3627 | 123.262 | 123.2849 | -123.4726 | -123.262 | 122.937 | 123.2208 | 59.9762 | 59.9991
369.4844 | 123.3719 | -60.0723 | 63.1714 | -0.042419 | 0.00098907 | 0.064634 | 0.063903 | -0.00086946 | -0.0016384 | 0.0016107 | -0.023224 | 0.00010888 | 0.067704 | 0.062636 | -0.0008886 | -0.0020892 | 0.00030966 | -0.050354 | 63.2401 | -60.3012 | 62.8738 | -60.0128 | -60.3424 | 0.027466 | 0.018311 | 63.208 | -60.1547 | 63.1302 | -60.0906 | -60.2097 | -59.8984 | -0.22888 | 0.068664 | -0.29755 | 0.05951 | 60.0998 | -0.27008 | 60.3287 | -0.041199 | -0.082397 | 0.036621 | -0.041199 | -0.01831 | 0.17395 | -0.13733 | 0.25635 | -0.054932 | 0.28839 | 123.175 | 0.064087 | 123.2849 | 123.5413 | 123.3627 | 123.3124 | 123.2803 | -123.4726 | -123.3261 | 122.9462 | 123.2025 | 60.022 | 60.0906
370.4844 | 123.3719 | -60.0449 | 63.1302 | -0.088196 | 0.00034827 | 0.064847 | 0.063476 | 0.0025485 | 7.0582e-05 | 0.00054267 | 0.0011902 | -0.00031832 | 0.064926 | 0.062209 | 0.0001794 | -0.00059378 | -0.0013991 | 0.28381 | 63.2538 | -60.26 | 63.0112 | -59.8755 | -60.26 | 0.11444 | 0.13733 | 63.1577 | -60.1227 | 63.2172 | -59.9808 | -60.0861 | -59.6512 | -0.21515 | 0.1236 | -0.11902 | 0.16937 | 60.1593 | -0.21515 | 60.3745 | 0 | -0.07782 | 0.027466 | 0.086975 | 0.064087 | 0.39368 | -0.041199 | 0.4715 | 0.036621 | 0.38452 | 123.2712 | 0.14191 | 123.3398 | 123.5138 | 123.2803 | 123.2986 | 123.2025 | -123.3902 | -123.2529 | 123.056 | 123.262 | 60.3287 | 60.1822
371.5469 | 123.3994 | -60.0632 | 63.0981 | -0.1416 | -0.0020017 | 0.063779 | 0.064117 | -1.486e-05 | -0.00078402 | 0.00054267 | 0.034759 | -0.0011727 | 0.069199 | 0.06755 | 0.000393 | 4.7018e-05 | -0.00011754 | -0.086975 | 63.1577 | -60.3333 | 62.9196 | -59.9533 | -60.3195 | 0.009155 | -0.009155 | 63.1485 | -60.141 | 63.1805 | -60.0174 | -60.1135 | -59.697 | -0.27008 | 0.059509 | -0.17853 | 0.10986 | 60.0723 | -0.25635 | 60.3424 | 0.013733 | -0.07782 | 0.050354 | 0.082397 | 0.045776 | 0.36621 | -0.050354 | 0.44403 | 0.027466 | 0.37994 | 123.2529 | 0.1236 | 123.3215 | 123.4909 | 123.2895 | 123.2208 | 123.2117 | -123.4314 | -123.2391 | 122.9828 | 123.2437 | 59.9762 | 60.054
372.4844 | 123.4131 | -60.0174 | 63.0981 | -0.057678 | 0.00013467 | 0.062284 | 0.063476 | 0.0019077 | -0.0012112 | 0.0011835 | 0.016449 | 0.00053628 | 0.063431 | 0.060927 | -0.003025 | -0.00080758 | 0.00073706 | 0.018311 | 63.1805 | -60.3012 | 63.0157 | -59.848 | -60.2142 | 0.1236 | 0.15564 | 63.1851 | -60.1181 | 63.2355 | -59.9808 | -60.0494 | -59.6558 | -0.28381 | 0.082397 | -0.082398 | 0.16937 | 60.141 | -0.19684 | 60.4248 | 0.086975 | -0.10071 | 0.086975 | 0.13733 | 0.036621 | 0.36163 | -0.032043 | 0.46234 | 0.068665 | 0.45319 | 123.317 | 0.13733 | 123.3536 | 123.4818 | 123.3032 | 123.1979 | 123.2025 | -123.3994 | -123.2162 | 123.0331 | 123.2529 | 60.0357 | 60.173
373.4844 | 123.3124 | -60.0769 | 63.1577 | -0.057678 | 0.0014163 | 0.061002 | 0.064117 | -1.486e-05 | 0.00071138 | -0.00052553 | -0.044586 | -0.00053192 | 0.064926 | 0.063918 | -0.0004614 | 0.00090142 | 0.0028733 | -0.032043 | 63.2263 | -60.3104 | 62.883 | -60.0174 | -60.3333 | 0.036621 | 0.045776 | 63.2263 | -60.1273 | 63.1073 | -60.0998 | -60.2051 | -59.7839 | -0.23346 | 0.068664 | -0.27466 | 0.059509 | 60.1135 | -0.25635 | 60.347 | -0.022888 | -0.050354 | 0.068664 | -0.050354 | -0.022888 | 0.29297 | -0.12817 | 0.34332 | -0.07782 | 0.29297 | 123.1934 | 0.027466 | 123.2346 | 123.5367 | 123.3536 | 123.3032 | 123.3032 | -123.468 | -123.2849 | 122.9599 | 123.1842 | 60.0449 | 60.1227
374.5469 | 123.3948 | -60.054 | 63.089 | -0.042419 | 0.0029117 | 0.067838 | 0.062835 | 0.0012667 | -0.0016384 | 0.0018243 | 0.022552 | -0.00053192 | 0.065567 | 0.0652 | -0.002384 | -0.0012348 | 0.0026597 | 0.10071 | 63.176 | -60.3012 | 62.9379 | -59.9808 | -60.3104 | 0.009155 | -0.022888 | 63.1393 | -60.1547 | 63.1805 | -60.0311 | -60.1501 | -59.7153 | -0.24719 | 0.086975 | -0.15106 | 0.073242 | 60.0632 | -0.25635 | 60.3104 | -0.009156 | -0.10071 | 0.050354 | 0.091553 | 0.022888 | 0.33874 | -0.09613 | 0.43945 | 0.004578 | 0.32043 | 123.2391 | 0.1236 | 123.3353 | 123.4772 | 123.2941 | 123.23 | 123.1934 | -123.3902 | -123.2437 | 122.9919 | 123.2346 | 60.1547 | 60.0311
375.4844 | 123.3627 | -60.0952 | 63.1165 | -0.095825 | 0.0020573 | 0.063566 | 0.063262 | 0.0027621 | 0.00071138 | -0.0011663 | -0.084259 | 0.00096348 | 0.067917 | 0.073531 | -0.0019568 | -0.00016658 | 0.00030966 | 0 | 63.1897 | -60.3241 | 62.9196 | -59.9625 | -60.3058 | 0 | 0.050354 | 63.1897 | -60.1685 | 63.1577 | -60.0266 | -60.4248 | -59.8618 | -0.22888 | 0.073242 | -0.19684 | 0.13275 | 60.0952 | -0.21057 | 60.3241 | 0.018311 | -0.073242 | 0.073242 | 0.041199 | 0.068665 | 0.23346 | -0.32959 | 0.3067 | -0.25635 | 0.36163 | 123.2437 | 0.14191 | 123.3261 | 123.5138 | 123.3582 | 123.2849 | 123.2849 | -123.4406 | -123.2849 | 123.0148 | 123.2529 | 60.0952 | 60.1456
376.5469 | 123.3719 | -60.0632 | 63.089 | -0.095825 | 0.0029117 | 0.064847 | 0.062194 | -0.0047147 | 0.00028418 | -0.0039435 | 0.004242 | 0.00074988 | 0.067063 | 0.066054 | -3.4196e-05 | 0.00068782 | -0.00054474 | -0.09613 | 63.1531 | -60.3378 | 62.9105 | -59.9854 | -60.3333 | -0.036621 | -0.064087 | 63.121 | -60.1639 | 63.1531 | -60.054 | -60.1639 | -59.7198 | -0.27466 | 0.064087 | -0.17853 | 0.077819 | 60.0266 | -0.27008 | 60.3012 | 0.004578 | -0.10071 | 0.032044 | 0.064087 | 0.009155 | 0.34332 | -0.10071 | 0.44403 | 0 | 0.35248 | 123.2483 | 0.10986 | 123.317 | 123.4909 | 123.2849 | 123.2162 | 123.1842 | -123.4268 | -123.2529 | 122.9736 | 123.2162 | 59.967 | 59.9991
377.4844 | 123.3124 | -60.0632 | 63.1302 | -0.03479 | 0.00034827 | 0.061857 | 0.063049 | 0.00041234 | 0.0011386 | -0.00073913 | -0.041534 | 0.00096348 | 0.070053 | 0.069045 | 0.001034 | 4.7018e-05 | 0.0039413 | -0.091553 | 63.208 | -60.3104 | 62.8647 | -60.054 | -60.3195 | -0.009155 | 0.004578 | 63.2034 | -60.1547 | 63.1256 | -60.0906 | -60.2142 | -59.7702 | -0.24719 | 0.07782 | -0.2655 | 0.009155 | 60.054 | -0.25635 | 60.3012 | -0.009155 | -0.091553 | 0.073242 | -0.004578 | -0.027466 | 0.29297 | -0.15106 | 0.38452 | -0.059509 | 0.25635 | 123.175 | 0.064087 | 123.2803 | 123.5184 | 123.3582 | 123.2712 | 123.2666 | -123.4406 | -123.2849 | 122.9279 | 123.1888 | 59.9716 | 60.0677
378.4844 | 123.349 | -60.0357 | 63.1302 | -0.072937 | 0.00056187 | 0.063993 | 0.064544 | 0.00062594 | 0.00071138 | 0.0018243 | 0.028656 | -0.0016001 | 0.066635 | 0.066268 | -0.0015296 | 4.7018e-05 | 0.0030869 | 0.041199 | 63.2034 | -60.2966 | 62.9608 | -59.903 | -60.2417 | 0.091553 | 0.1236 | 63.1989 | -60.1318 | 63.176 | -60.0449 | -60.1364 | -59.729 | -0.26093 | 0.073242 | -0.16937 | 0.13275 | 60.1273 | -0.20599 | 60.3882 | 0.054932 | -0.09613 | 0.068665 | 0.045776 | -0.009155 | 0.3067 | -0.10071 | 0.40283 | -0.004578 | 0.39368 | 123.2574 | 0.086975 | 123.3078 | 123.5001 | 123.3307 | 123.2391 | 123.2346 | -123.4268 | -123.262 | 122.9965 | 123.2117 | 60.0769 | 60.1593
379.4844 | 123.3124 | -60.0494 | 63.1439 | -0.042419 | 0.0012027 | 0.063779 | 0.063049 | 0.0019077 | 7.0582e-05 | -0.00031193 | -0.026276 | 0.0011771 | 0.068131 | 0.067977 | -0.0019568 | 0.00047422 | 0.0022323 | -0.022888 | 63.1851 | -60.3104 | 62.8967 | -59.9854 | -60.3195 | 0.036621 | 0.022888 | 63.208 | -60.1456 | 63.1073 | -60.0861 | -60.1959 | -59.7702 | -0.26093 | 0.041199 | -0.24719 | 0.064086 | 60.0861 | -0.27008 | 60.347 | -0.009155 | -0.096131 | 0.064087 | -0.036621 | -0.036622 | 0.27923 | -0.14648 | 0.37537 | -0.050354 | 0.32501 | 123.2071 | 0.059509 | 123.2529 | 123.4955 | 123.3536 | 123.2346 | 123.2574 | -123.4543 | -123.2895 | 122.9462 | 123.1567 | 60.0266 | 60.0723
380.4844 | 123.349 | -60.0586 | 63.1256 | -0.057678 | 0.00056187 | 0.064847 | 0.062835 | 0.0021213 | 0.002634 | -0.00031193 | 0.0072936 | 0.00010888 | 0.065995 | 0.071822 | -0.0015296 | -0.001662 | 0.00030966 | 0.045776 | 63.1668 | -60.2875 | 62.9837 | -59.8846 | -60.228 | 0.10986 | 0.11902 | 63.1668 | -60.1273 | 63.1714 | -60.0449 | -60.1364 | -59.6878 | -0.22888 | 0.041199 | -0.14191 | 0.17395 | 60.1685 | -0.16937 | 60.3973 | 0.05951 | -0.068664 | 0.041199 | 0.045777 | 0.013733 | 0.37079 | -0.07782 | 0.43945 | -0.009156 | 0.40283 | 123.2712 | 0.082397 | 123.2986 | 123.4543 | 123.2941 | 123.2254 | 123.2254 | -123.4131 | -123.2529 | 123.0423 | 123.23 | 60.1044 | 60.1776
381.5469 | 123.381 | -60.0769 | 63.0936 | -0.027161 | 0.0016299 | 0.063566 | 0.06369 | 0.0019077 | 0.00071138 | -0.0013799 | 0.010345 | 0.0013907 | 0.066849 | 0.0652 | 0.0001794 | -0.0014484 | 0.0022323 | -0.059509 | 63.1531 | -60.3195 | 62.9196 | -59.967 | -60.3104 | 0.004578 | -0.036621 | 63.1485 | -60.1456 | 63.1714 | -60.0449 | -60.1547 | -59.7198 | -0.24262 | 0.059509 | -0.17395 | 0.10986 | 60.0815 | -0.23346 | 60.3241 | 0.009155 | -0.068665 | 0.054932 | 0.07782 | 0.032043 | 0.35705 | -0.07782 | 0.42572 | -0.009155 | 0.35248 | 123.2391 | 0.10071 | 123.317 | 123.4726 | 123.2941 | 123.23 | 123.2254 | -123.4131 | -123.2391 | 122.9965 | 123.2483 | 60.0174 | 60.0403
382.4844 | 123.317 | -60.0586 | 63.1531 | -0.050049 | -0.00093353 | 0.064207 | 0.06369 | 0.0036165 | -0.0014248 | 0.00075627 | 0.0072936 | -0.00095912 | 0.066422 | 0.066695 | -0.0004614 | 0.00068782 | 0.0024461 | -0.004578 | 63.208 | -60.3058 | 62.9333 | -59.9533 | -60.3287 | 0.032043 | 0.027466 | 63.2126 | -60.1547 | 63.1073 | -60.0861 | -60.1913 | -59.7748 | -0.24719 | 0.054932 | -0.21973 | 0.10529 | 60.0906 | -0.27008 | 60.3378 | -0.022888 | -0.09613 | 0.059509 | -0.045776 | -0.027466 | 0.28381 | -0.13275 | 0.37994 | -0.036621 | 0.35248 | 123.2391 | 0.068664 | 123.262 | 123.5138 | 123.3673 | 123.2666 | 123.2712 | -123.4589 | -123.3078 | 122.9919 | 123.1659 | 60.054 | 60.0861
383.4844 | 123.3261 | -60.0357 | 63.1302 | 0.010986 | -0.00029273 | 0.063993 | 0.064331 | 0.0010531 | -0.0014248 | -0.0015935 | -0.062897 | 0.0026725 | 0.067917 | 0.072036 | -0.0017432 | 4.7018e-05 | 0.0011643 | -0.009155 | 63.2217 | -60.3287 | 62.8967 | -59.9991 | -60.3012 | 0.004578 | 0.018311 | 63.2126 | -60.1547 | 63.1439 | -60.0677 | -60.173 | -59.7382 | -0.29297 | 0.091553 | -0.23346 | 0.036622 | 60.0403 | -0.2655 | 60.3333 | 0.027466 | -0.11902 | 0.082397 | 0.013733 | -0.032043 | 0.29755 | -0.13733 | 0.41656 | -0.018311 | 0.32959 | 123.2254 | 0.086975 | 123.2986 | 123.5504 | 123.3673 | 123.2574 | 123.2483 | -123.4589 | -123.2849 | 122.9324 | 123.1796 | 60.0266 | 60.054
384.4844 | 123.3124 | -60.0769 | 63.1531 | -0.03479 | 0.0012027 | 0.063352 | 0.062835 | -0.00044226 | -0.0016384 | 0.00032907 | 0.022552 | -0.00010472 | 0.064713 | 0.066268 | -3.4196e-05 | -0.00080758 | 0.00030966 | 0.018311 | 63.2172 | -60.3378 | 62.915 | -59.967 | -60.3058 | 0.050354 | 0.050354 | 63.1943 | -60.1501 | 63.1119 | -60.0815 | -60.1959 | -59.7794 | -0.26093 | 0.064087 | -0.23804 | 0.10986 | 60.1273 | -0.22888 | 60.3882 | 0.032044 | -0.073242 | 0.041199 | -0.041199 | -0.004578 | 0.29755 | -0.11902 | 0.37079 | -0.045777 | 0.37079 | 123.2529 | 0.068664 | 123.262 | 123.555 | 123.3444 | 123.2941 | 123.2712 | -123.4909 | -123.3032 | 122.9919 | 123.1888 | 60.0952 | 60.1273
385.4844 | 123.3536 | -60.0586 | 63.1439 | -0.042419 | -0.00093353 | 0.063352 | 0.065826 | -0.00086946 | 0.00071138 | -0.0035163 | -0.032379 | 0.0026725 | 0.06749 | 0.065627 | -0.0021704 | 0.0013288 | 0.00052346 | -0.009155 | 63.208 | -60.3058 | 62.8922 | -60.0128 | -60.3424 | 0.018311 | 0.018311 | 63.2217 | -60.141 | 63.1577 | -60.0723 | -60.1913 | -59.7519 | -0.24719 | 0.064087 | -0.25177 | 0.045777 | 60.0769 | -0.28381 | 60.3241 | -0.036621 | -0.082397 | 0.07782 | 0.013733 | -0.013733 | 0.3067 | -0.13275 | 0.3891 | -0.050354 | 0.29297 | 123.1979 | 0.068664 | 123.2986 | 123.5138 | 123.3627 | 123.2666 | 123.2803 | -123.4497 | -123.2849 | 122.9507 | 123.2162 | 60.0494 | 60.0769
386.4844 | 123.4085 | -60.0449 | 63.121 | -0.095825 | -0.00050633 | 0.063779 | 0.062835 | -0.0012967 | -0.00078402 | -0.0024481 | 0.031708 | -0.00074552 | 0.066635 | 0.066268 | -0.000675 | -0.00080758 | -0.0011855 | 0.045776 | 63.1668 | -60.3104 | 62.9837 | -59.8892 | -60.2142 | 0.091553 | 0.14191 | 63.1714 | -60.141 | 63.1943 | -59.9808 | -60.0861 | -59.6924 | -0.2655 | 0.045776 | -0.13733 | 0.15564 | 60.1364 | -0.16937 | 60.4019 | 0.096131 | -0.09613 | 0.050354 | 0.073242 | 0.064087 | 0.35248 | -0.041199 | 0.44861 | 0.054931 | 0.42114 | 123.2941 | 0.16022 | 123.3353 | 123.4772 | 123.3124 | 123.2117 | 123.2162 | -123.4314 | -123.262 | 123.0286 | 123.2391 | 60.0906 | 60.1868
387.4844 | 123.3261 | -60.0632 | 63.1577 | -0.03479 | -0.0011471 | 0.065702 | 0.065399 | -0.0021513 | -0.001852 | -0.0028753 | -0.05069 | 0.0011771 | 0.068985 | 0.063918 | -0.0017432 | 0.0013288 | -0.00075834 | -0.022888 | 63.208 | -60.3241 | 62.9013 | -60.0174 | -60.3287 | 0.018311 | 0.027466 | 63.2263 | -60.141 | 63.1485 | -60.0723 | -60.1913 | -59.7565 | -0.26093 | 0.050354 | -0.25635 | 0.045776 | 60.0815 | -0.2655 | 60.3424 | -0.004577 | -0.07782 | 0.068664 | -0.009155 | -0.009156 | 0.3067 | -0.12817 | 0.38452 | -0.050354 | 0.3067 | 123.2254 | 0.068664 | 123.2895 | 123.5321 | 123.3673 | 123.2712 | 123.2895 | -123.4818 | -123.2986 | 122.9645 | 123.2117 | 60.0403 | 60.0906
388.5469 | 123.3536 | -60.0403 | 63.1119 | -0.065308 | 0.0020573 | 0.064847 | 0.065399 | -0.0015103 | 0.00092498 | 0.00075627 | 0.025604 | 0.0013907 | 0.070053 | 0.064986 | -3.4196e-05 | -0.00080758 | 0.0015915 | 0.032043 | 63.176 | -60.3012 | 62.97 | -59.8938 | -60.2325 | 0.10529 | 0.15106 | 63.1622 | -60.141 | 63.1943 | -60.0082 | -60.1044 | -59.6878 | -0.26093 | 0.064087 | -0.14191 | 0.14648 | 60.1456 | -0.19226 | 60.4065 | 0.068664 | -0.10071 | 0.050354 | 0.082398 | 0.032043 | 0.35248 | -0.064087 | 0.45319 | 0.036621 | 0.40741 | 123.2712 | 0.13275 | 123.3353 | 123.4772 | 123.3032 | 123.2162 | 123.2025 | -123.4131 | -123.2529 | 123.0103 | 123.2346 | 60.0723 | 60.1913
389.4844 | 123.2941 | -60.0906 | 63.1256 | -0.095825 | 0.0014163 | 0.063993 | 0.065185 | -0.0012967 | -0.00035682 | 0.0022517 | -0.090363 | 0.0022453 | 0.065995 | 0.063705 | -0.0004614 | -0.0014484 | 0.00073706 | -0.032043 | 63.1531 | -60.3424 | 62.8967 | -59.9945 | -60.3424 | -0.036621 | -0.022888 | 63.1805 | -60.1456 | 63.1073 | -60.1501 | -60.228 | -59.7885 | -0.25177 | 0.027466 | -0.22888 | 0.09613 | 60.054 | -0.25177 | 60.3058 | 0 | -0.054932 | 0.054932 | -0.01831 | -0.059509 | 0.30212 | -0.13733 | 0.35706 | -0.082397 | 0.3479 | 123.2391 | -0.004577 | 123.2529 | 123.4955 | 123.3261 | 123.2437 | 123.2712 | -123.468 | -123.2712 | 122.9874 | 123.1979 | 60.0586 | 60.0677
390.5469 | 123.349 | -60.1044 | 63.0707 | -0.03479 | -0.00050633 | 0.063566 | 0.06369 | 0.00041234 | 0.0019932 | 0.00011527 | -0.059845 | 0.00074988 | 0.067704 | 0.058791 | -0.000675 | 0.00068782 | 0.00073706 | -0.11902 | 63.1622 | -60.3699 | 62.851 | -60.054 | -60.4065 | -0.12817 | -0.1236 | 63.1577 | -60.1776 | 63.1348 | -60.1135 | -60.2097 | -59.7473 | -0.2655 | 0.091552 | -0.21973 | 0.050354 | 59.9762 | -0.30212 | 60.2417 | -0.036621 | -0.073242 | 0.086975 | 0.064087 | -0.009155 | 0.35706 | -0.10529 | 0.4303 | -0.032044 | 0.31586 | 123.2208 | 0.064087 | 123.3124 | 123.5321 | 123.3353 | 123.2666 | 123.262 | -123.4406 | -123.2483 | 122.9553 | 123.2391 | 59.9854 | 59.9808
391.4844 | 123.2895 | -60.0815 | 63.0981 | -0.03479 | 0.0012027 | 0.06442 | 0.064331 | 0.0044711 | 0.0030612 | -0.00073913 | -0.059845 | 0.0028861 | 0.066849 | 0.066695 | -0.000675 | 0.001756 | 0.00052346 | -0.013733 | 63.1805 | -60.3378 | 62.9196 | -59.967 | -60.3149 | 0.009155 | 0.045776 | 63.1897 | -60.1593 | 63.1531 | -60.0769 | -60.3653 | -59.848 | -0.25635 | 0.082397 | -0.17853 | 0.11444 | 60.0906 | -0.23346 | 60.347 | 0.022889 | -0.07782 | 0.091552 | 0.054931 | 0.004578 | 0.23346 | -0.28381 | 0.31128 | -0.20599 | 0.37079 | 123.2574 | 0.082398 | 123.3124 | 123.5184 | 123.349 | 123.262 | 123.2712 | -123.436 | -123.2574 | 123.0011 | 123.2346 | 60.0677 | 60.1273
392.5469 | 123.436 | -60.0128 | 63.0661 | -0.050049 | -0.00029273 | 0.061643 | 0.060058 | 0.0010531 | 0.0028476 | -0.0050115 | 0.065277 | 0.00074988 | 0.065354 | 0.064132 | -0.0004614 | -0.0014484 | 0.0045823 | 0.045776 | 63.1668 | -60.2921 | 63.0157 | -59.8343 | -60.1822 | 0.1236 | 0.15106 | 63.1531 | -60.1227 | 63.2217 | -59.9762 | -60.0632 | -59.6558 | -0.27924 | 0.10071 | -0.050354 | 0.17853 | 60.1364 | -0.16937 | 60.4156 | 0.10986 | -0.10986 | 0.086975 | 0.15564 | 0.036621 | 0.35705 | -0.050354 | 0.46692 | 0.05951 | 0.45776 | 123.3078 | 0.14648 | 123.3444 | 123.4589 | 123.2758 | 123.1796 | 123.1659 | -123.3582 | -123.1888 | 123.0286 | 123.2346 | 60.0586 | 60.1639
393.4844 | 123.349 | -60.0815 | 63.1393 | -0.050049 | -0.0011471 | 0.063566 | 0.062835 | -0.0015103 | 0.00049778 | 0.00096987 | -0.041534 | 0.00096348 | 0.06749 | 0.070113 | -3.4196e-05 | -0.00080758 | 0.00030966 | -0.004578 | 63.1897 | -60.3516 | 62.9059 | -59.9945 | -60.2921 | 0.009155 | 0.054932 | 63.1851 | -60.1501 | 63.1485 | -60.0677 | -60.1959 | -59.729 | -0.27008 | 0.050354 | -0.23346 | 0.086975 | 60.0906 | -0.21057 | 60.3607 | 0.059509 | -0.068664 | 0.045777 | 0.009156 | 0.013733 | 0.35248 | -0.11444 | 0.42114 | -0.045777 | 0.35706 | 123.2574 | 0.082397 | 123.2986 | 123.5413 | 123.3353 | 123.2712 | 123.2666 | -123.4909 | -123.2895 | 122.9874 | 123.23 | 60.0769 | 60.1364
394.4844 | 123.3078 | -60.054 | 63.1439 | -0.027161 | 0.00056187 | 0.063566 | 0.061553 | -0.0023649 | -0.0012112 | -0.00052553 | 0.019501 | 0.0011771 | 0.066635 | 0.063491 | 0.001034 | -0.0010212 | 0.0043687 | -0.022888 | 63.1897 | -60.3195 | 62.8647 | -60.0128 | -60.3149 | 0.050354 | 0.036621 | 63.2126 | -60.1639 | 63.1073 | -60.0769 | -60.1868 | -59.761 | -0.2655 | 0.045776 | -0.27924 | 0.041199 | 60.1044 | -0.26093 | 60.3699 | 0.004578 | -0.10986 | 0.068664 | -0.036621 | -0.022888 | 0.29297 | -0.13275 | 0.40283 | -0.022889 | 0.3067 | 123.1842 | 0.086975 | 123.2712 | 123.5092 | 123.3765 | 123.2437 | 123.2666 | -123.4634 | -123.3078 | 122.9187 | 123.1613 | 60.0311 | 60.0906
395.5469 | 123.4131 | -60.0357 | 63.089 | -0.080566 | 0.0016299 | 0.063779 | 0.063903 | -1.486e-05 | -0.0016384 | -0.0026617 | 0.0072936 | -0.00031832 | 0.06749 | 0.058791 | -0.0002478 | -0.00038018 | -0.0031081 | 0.022888 | 63.1714 | -60.2966 | 63.1714 | -60.1501 | -60.4156 | 0.13275 | 0.17853 | 63.1439 | -60.1318 | 63.1943 | -59.9762 | -60.0632 | -59.6603 | -0.26093 | 0.082398 | 0.082398 | -0.11444 | 60.1685 | -0.37994 | 60.4294 | -0.11902 | -0.09613 | 0.054932 | 0.10529 | 0.05951 | 0.37537 | -0.027465 | 0.4715 | 0.068665 | 0.14648 | 123.468 | 0.15564 | 123.3261 | 123.468 | 123.2758 | 123.2071 | 123.1796 | -123.3856 | -123.2208 | 123.2071 | 123.23 | 60.0586 | 60.2142
396.4844 | 123.3444 | -60.054 | 63.1577 | -0.011902 | -0.00029273 | 0.062925 | 0.064331 | 0.00019874 | 0.00049778 | 0.00054267 | -0.053741 | 0.00074988 | 0.067704 | 0.063491 | -0.0008886 | 0.00026062 | -0.0011855 | -0.018311 | 63.2126 | -60.3333 | 62.883 | -60.0128 | -60.3195 | 0.018311 | 0.050354 | 63.2126 | -60.173 | 63.1531 | -60.0586 | -60.1822 | -59.7336 | -0.27924 | 0.054931 | -0.27466 | 0.041199 | 60.0723 | -0.2655 | 60.3516 | 0.013733 | -0.11902 | 0.054931 | -0.004578 | -0.004578 | 0.32043 | -0.12817 | 0.43945 | -0.009155 | 0.32044 | 123.2162 | 0.11444 | 123.3261 | 123.5458 | 123.3856 | 123.2666 | 123.2666 | -123.4909 | -123.3307 | 122.937 | 123.2071 | 60.0357 | 60.1044
397.5469 | 123.3307 | -60.0357 | 63.1439 | 0.0033567 | 0.0026981 | 0.063779 | 0.063476 | -0.0010831 | -0.00014322 | -0.0011663 | 0.050018 | -0.00053192 | 0.06749 | 0.067977 | -0.0015296 | -0.0010212 | -0.0026809 | 0.032043 | 63.1943 | -60.3195 | 62.97 | -59.9075 | -60.228 | 0.10071 | 0.11902 | 63.1439 | -60.1501 | 63.1393 | -60.0174 | -60.1364 | -59.7015 | -0.28381 | 0.050354 | -0.17395 | 0.12817 | 60.1364 | -0.19226 | 60.4202 | 0.091553 | -0.11444 | 0 | -0.004578 | 0.018311 | 0.33417 | -0.10071 | 0.44861 | 0.013732 | 0.41199 | 123.2895 | 0.13275 | 123.2895 | 123.5138 | 123.2941 | 123.23 | 123.1796 | -123.4634 | -123.2941 | 123.0057 | 123.175 | 60.0677 | 60.1547
398.4844 | 123.3032 | -60.0769 | 63.1393 | -0.057678 | -0.00050633 | 0.064634 | 0.065185 | -0.0017239 | -0.00099762 | 0.0013971 | -0.011017 | 0.0041679 | 0.068985 | 0.060927 | -0.0043066 | -0.0023028 | 0.0013779 | -0.041199 | 63.208 | -60.3287 | 62.8876 | -60.0174 | -60.3424 | 0.032043 | 0.032043 | 63.1943 | -60.1547 | 63.1439 | -60.2646 | -60.2142 | -59.7794 | -0.25177 | 0.068665 | -0.25177 | 0.059509 | 60.1089 | -0.2655 | 60.3607 | -0.013733 | -0.07782 | 0.054932 | 0.004578 | -0.18768 | 0.29755 | -0.13733 | 0.37537 | -0.059509 | 0.31128 | 123.2162 | -0.10986 | 123.2986 | 123.5367 | 123.349 | 123.2849 | 123.2712 | -123.468 | -123.2941 | 122.9645 | 123.2208 | 60.0357 | 60.1089
399.4844 | 123.3398 | -60.0723 | 63.1256 | -0.072937 | 0.00034827 | 0.065488 | 0.065399 | 0.00083954 | 0.00092498 | -0.0018073 | -0.023224 | 0.0011771 | 0.066422 | 0.066268 | -0.0004614 | -0.00059378 | 0.0020187 | 0.009155 | 63.2172 | -60.3333 | 62.9196 | -59.9579 | -60.3012 | 0.004578 | 0.064087 | 63.1897 | -60.1456 | 63.1485 | -60.0632 | -60.1868 | -59.7198 | -0.26093 | 0.091553 | -0.20599 | 0.11444 | 60.0769 | -0.22888 | 60.3378 | 0.032044 | -0.073242 | 0.064087 | 0.022889 | 0.009156 | 0.35248 | -0.11444 | 0.42572 | -0.041199 | 0.37537 | 123.2529 | 0.082398 | 123.2941 | 123.5504 | 123.3353 | 123.2895 | 123.262 | -123.4589 | -123.2712 | 122.9919 | 123.2208 | 60.0815 | 60.1364
400.5469 | 123.2986 | -60.0128 | 63.0661 | -0.050049 | 0.0014163 | 0.06207 | 0.063262 | -0.0019377 | -0.0012112 | -0.00052553 | 0.071381 | 0.00010888 | 0.066422 | 0.068404 | -0.0017432 | -0.00059378 | 0.00095066 | 0.045776 | 63.1714 | -60.3104 | 62.9974 | -59.8618 | -60.2051 | 0.1236 | 0.15564 | 63.1531 | -60.0952 | 63.2172 | -60.0128 | -59.6695 | -59.4498 | -0.29755 | 0.10529 | -0.068664 | 0.15106 | 60.1364 | -0.19226 | 60.434 | 0.10529 | -0.082398 | 0.086975 | 0.15106 | 0 | 0.56305 | 0.34332 | 0.64545 | 0.42572 | 0.44861 | 123.3078 | 0.082398 | 123.3124 | 123.4818 | 123.2483 | 123.1842 | 123.1659 | -123.3765 | -123.1613 | 123.0103 | 123.23 | 60.0586 | 60.1685
401.4844 | 123.3398 | -60.0723 | 63.1256 | -0.057678 | -0.0024289 | 0.06442 | 0.065612 | -1.486e-05 | 0.0013522 | 0.0020379 | -0.059845 | 0.00074988 | 0.066422 | 0.066268 | -0.0025976 | -0.00059378 | 0.0022323 | 0 | 63.2034 | -60.3241 | 62.8967 | -59.9579 | -60.3012 | 0.027466 | 0.050354 | 63.208 | -60.1913 | 63.1531 | -60.0723 | -60.1913 | -59.7427 | -0.25177 | 0.07782 | -0.22888 | 0.11444 | 60.0998 | -0.22888 | 60.3516 | 0.022889 | -0.11902 | 0.082398 | 0.027466 | 0 | 0.32959 | -0.11902 | 0.44861 | 0 | 0.36621 | 123.2208 | 0.11902 | 123.3444 | 123.5275 | 123.3994 | 123.2758 | 123.2803 | -123.4497 | -123.317 | 122.9691 | 123.2254 | 60.0723 | 60.1227
402.4844 | 123.3215 | -60.0677 | 63.1485 | -0.065308 | -0.00071993 | 0.062925 | 0.065612 | -0.0017239 | -0.00057042 | 0.0011835 | 0.025604 | -0.00031832 | 0.065567 | 0.061782 | -0.0025976 | -0.00059378 | -0.00097194 | 0 | 63.2355 | -60.3149 | 62.8647 | -60.0494 | -60.3195 | 0.022888 | 0.022888 | 63.2126 | -60.141 | 63.1256 | -60.0769 | -60.2005 | -59.7565 | -0.24719 | 0.086975 | -0.28381 | 0.018311 | 60.0906 | -0.25177 | 60.3378 | -0.004578 | -0.073242 | 0.064086 | -0.022889 | -0.009155 | 0.31128 | -0.13275 | 0.38452 | -0.059509 | 0.2655 | 123.1796 | 0.064087 | 123.2666 | 123.5504 | 123.3536 | 123.3032 | 123.2803 | -123.4634 | -123.2895 | 122.9324 | 123.1934 | 60.0677 | 60.0906
403.5469 | 123.3215 | -60.054 | 63.1393 | -0.019531 | -0.0017881 | 0.061857 | 0.064117 | 0.0016939 | -0.00078402 | -0.00095273 | -0.020172 | 0.0024589 | 0.06514 | 0.069472 | -3.4196e-05 | 0.00026062 | -0.0016129 | -0.050354 | 63.1897 | -60.3516 | 62.8784 | -60.0128 | -60.3149 | 0.013733 | 0.013733 | 63.208 | -60.1685 | 63.121 | -60.0815 | -60.1913 | -59.7519 | -0.29755 | 0.050354 | -0.26092 | 0.041199 | 60.0677 | -0.26093 | 60.3653 | 0.036621 | -0.11444 | 0.068665 | -0.01831 | -0.027466 | 0.30212 | -0.13733 | 0.41656 | -0.022888 | 0.33875 | 123.23 | 0.086975 | 123.2895 | 123.5413 | 123.3765 | 123.2437 | 123.262 | -123.4909 | -123.3078 | 122.9324 | 123.175 | 60.0037 | 60.0677
404.4844 | 123.2849 | -60.0815 | 63.1348 | 0.0033567 | -0.00071993 | 0.063352 | 0.061981 | 0.0012667 | -0.0012112 | 0.0020379 | -0.011017 | 0.00096348 | 0.067276 | 0.067336 | -3.4196e-05 | -0.001662 | 0.0020187 | -0.032043 | 63.2355 | -60.3149 | 62.7594 | -59.9579 | -60.3973 | -0.022888 | -0.018311 | 63.1989 | -60.1685 | 63.089 | -60.0906 | -60.2051 | -59.7656 | -0.23346 | 0.10071 | -0.37537 | 0.1236 | 60.0586 | -0.31586 | 60.2921 | -0.082398 | -0.086975 | 0.064087 | -0.045777 | -0.009155 | 0.31586 | -0.1236 | 0.40283 | -0.036621 | 0.35705 | 123.0743 | 0.07782 | 123.2574 | 123.5504 | 123.3673 | 123.317 | 123.2803 | -123.4497 | -123.3032 | 122.8409 | 123.1705 | 60.0494 | 60.0632
405.5469 | 123.3994 | -60.0861 | 63.0661 | 0.033875 | 0.00034827 | 0.063138 | 0.062194 | -0.00044226 | -0.00035682 | -0.0033025 | 0.022552 | 0.00053628 | 0.066849 | 0.063491 | -0.0015296 | 0.00026062 | -0.0031081 | -0.064087 | 63.1577 | -60.3149 | 62.9059 | -59.9579 | -60.3058 | 0.13733 | -0.022888 | 63.1531 | -60.1501 | 63.1531 | -60.0586 | -60.1501 | -59.7198 | -0.22888 | 0.091553 | -0.16022 | 0.12817 | 60.2234 | -0.21973 | 60.4523 | 0.009155 | -0.064086 | 0.086975 | 0.086975 | 0.027466 | 0.36621 | -0.064086 | 0.4303 | 0 | 0.35705 | 123.2208 | 0.091552 | 123.3032 | 123.4726 | 123.3032 | 123.2437 | 123.2391 | -123.381 | -123.2162 | 122.9919 | 123.2391 | 60.022 | 60.0632
406.4844 | 123.3124 | -60.0769 | 63.1622 | -0.011902 | -0.0013607 | 0.062284 | 0.063476 | -0.0015103 | -0.00014322 | 0.0022517 | -0.075104 | 0.0011771 | 0.066849 | 0.064773 | -0.0002478 | 0.00026062 | 0.0020187 | -0.041199 | 63.2401 | -60.3378 | 62.8693 | -60.022 | -60.1227 | 0.21515 | 0.073242 | 63.208 | -60.1501 | 63.0936 | -60.0723 | -60.2234 | -59.7473 | -0.26093 | 0.07782 | -0.29297 | 0.054931 | 60.2921 | -0.045777 | 60.553 | 0.21515 | -0.073242 | 0.045777 | -0.068664 | 0.004577 | 0.32959 | -0.14648 | 0.40283 | -0.073243 | 0.31586 | 123.2071 | 0.077819 | 123.2437 | 123.5779 | 123.3582 | 123.317 | 123.2849 | -123.5001 | -123.3124 | 122.9462 | 123.1705 | 60.0357 | 60.1501
407.5469 | 123.4406 | -60.0174 | 63.1073 | -0.065308 | -0.0011471 | 0.063779 | 0.064758 | 0.00062594 | -0.00014322 | 0.0016107 | 0.059174 | -0.0018137 | 0.066208 | 0.057296 | -3.4196e-05 | 0.00047422 | -0.0039627 | 0.013733 | 63.1531 | -60.2921 | 62.9929 | -59.8572 | -60.2188 | 0.11444 | 0.13733 | 63.1485 | -60.1227 | 63.2446 | -59.9533 | -60.0449 | -59.642 | -0.27466 | 0.045776 | -0.11444 | 0.16022 | 60.1318 | -0.20142 | 60.4065 | 0.073242 | -0.10529 | 0.041199 | 0.13733 | 0.064087 | 0.37537 | -0.027466 | 0.48065 | 0.07782 | 0.43488 | 123.2849 | 0.16937 | 123.3673 | 123.4451 | 123.2712 | 123.1705 | 123.1659 | -123.3994 | -123.23 | 123.0103 | 123.262 | 60.0311 | 60.1547
408.4844 | 123.3124 | -60.0815 | 63.1439 | 0.018616 | 0.00013467 | 0.063352 | 0.064117 | 0.0014803 | -0.002493 | -0.0028753 | -0.020172 | 0.0013907 | 0.064286 | 0.069259 | 0.0001794 | -0.001662 | -0.0022537 | -0.045776 | 63.2126 | -60.3104 | 62.8876 | -60.0266 | -60.3333 | 0.027466 | 0.022888 | 63.1943 | -60.1547 | 63.1073 | -60.1547 | -60.1868 | -59.7244 | -0.22888 | 0.068664 | -0.25635 | 0.054932 | 60.1089 | -0.25177 | 60.3378 | -0.022888 | -0.073242 | 0.050354 | -0.036621 | -0.073242 | 0.35706 | -0.10529 | 0.4303 | -0.032044 | 0.28381 | 123.1979 | 0 | 123.262 | 123.5229 | 123.349 | 123.2941 | 123.2758 | -123.4543 | -123.2986 | 122.9691 | 123.1888 | 60.0357 | 60.1044
409.5469 | 123.2941 | -60.054 | 63.1622 | 0.010986 | 0.0018435 | 0.062284 | 0.06369 | -1.486e-05 | -0.0037746 | -0.00073913 | -0.023224 | 0.0011771 | 0.068558 | 0.066909 | -0.0008886 | -0.0029438 | 0.00073706 | -0.032043 | 63.2126 | -60.3378 | 62.8143 | -59.8068 | -60.1776 | -0.11444 | -0.009155 | 63.2034 | -60.1868 | 63.1165 | -60.1089 | -60.2051 | -59.7519 | -0.28381 | 0.050354 | -0.3479 | 0.24719 | 59.9396 | -0.1236 | 60.2234 | 0.16022 | -0.13275 | 0.041199 | -0.045776 | -0.054932 | 0.30212 | -0.15106 | 0.43488 | -0.01831 | 0.53101 | 123.1522 | 0.07782 | 123.3032 | 123.5504 | 123.3902 | 123.2666 | 123.2574 | -123.5001 | -123.349 | 122.8683 | 123.1705 | 60.022 | 60.0449
410.4844 | 123.3444 | -60.0723 | 63.1348 | -0.011902 | 0.00098907 | 0.06442 | 0.063903 | 0.0027621 | -0.002493 | 0.00096987 | -0.069 | 0.0011771 | 0.065567 | 0.068404 | -0.0017432 | 0.00026062 | 0.00095066 | 0.004578 | 63.2172 | -60.3287 | 62.9242 | -59.9716 | -60.2966 | 0.027466 | 0.082397 | 63.2034 | -60.1547 | 63.1485 | -60.0861 | -60.1959 | -59.7382 | -0.25635 | 0.082397 | -0.21057 | 0.10071 | 60.0998 | -0.2243 | 60.3561 | 0.032043 | -0.082397 | 0.068664 | 0.013733 | -0.013733 | 0.33417 | -0.1236 | 0.41656 | -0.041199 | 0.35706 | 123.2529 | 0.068664 | 123.3032 | 123.5458 | 123.3582 | 123.2895 | 123.2758 | -123.4634 | -123.2895 | 122.9965 | 123.2208 | 60.0769 | 60.1547
411.5469 | 123.2803 | -60.0632 | 63.1302 | -0.011902 | 0.00098907 | 0.062498 | 0.063476 | -0.00086946 | 0.0011386 | 0.00032907 | 0.004242 | 0.00096348 | 0.067063 | 0.05815 | -0.0008886 | -0.00016658 | -0.0016129 | 0.013733 | 63.2126 | -60.2783 | 62.915 | -59.9625 | -60.3149 | 0.045776 | 0.09613 | 63.1897 | -60.1593 | 63.1027 | -60.0861 | -60.1822 | -59.7748 | -0.21515 | 0.082397 | -0.21515 | 0.10071 | 60.1089 | -0.25177 | 60.3241 | -0.036621 | -0.096131 | 0.059509 | -0.027466 | -0.022889 | 0.28839 | -0.11902 | 0.38452 | -0.022888 | 0.31586 | 123.1934 | 0.073242 | 123.262 | 123.4909 | 123.349 | 123.2758 | 123.2529 | -123.4085 | -123.2895 | 122.9782 | 123.1659 | 60.0769 | 60.1593
412.4844 | 123.317 | -60.0677 | 63.121 | 0.010986 | -0.00029273 | 0.060148 | 0.064758 | 0.0034029 | 0.00028418 | -0.0024481 | -0.011017 | 0.0013907 | 0.066422 | 0.064986 | -3.4196e-05 | -0.001662 | 9.6064e-05 | 0.1831 | 63.2538 | -60.2829 | 62.8601 | -60.0174 | -60.3699 | 0 | 0.004578 | 63.2126 | -60.1593 | 63.1073 | -60.0906 | -60.1959 | -59.7565 | -0.21515 | 0.13275 | -0.26093 | 0.050354 | 60.0677 | -0.30212 | 60.2829 | -0.086975 | -0.091553 | 0.091552 | -0.013733 | -0.022888 | 0.31128 | -0.12817 | 0.40283 | -0.036621 | 0.2655 | 123.143 | 0.068665 | 123.2666 | 123.5367 | 123.3719 | 123.3215 | 123.2803 | -123.4039 | -123.2803 | 122.9279 | 123.175 | 60.2509 | 60.0723
413.5469 | 123.4222 | -60.0586 | 63.1073 | -0.065308 | 0.0022709 | 0.063779 | 0.064544 | 0.0034029 | 7.0582e-05 | 0.0026789 | 0.028656 | 0.00010888 | 0.066849 | 0.063064 | -0.0008886 | -0.0023028 | -0.00097194 | 0.036621 | 63.1531 | -60.2783 | 62.9791 | -59.9991 | -60.2097 | 0.1236 | 0.14648 | 63.1393 | -60.1456 | 63.1805 | -59.9899 | -60.1044 | -59.6878 | -0.21973 | 0.045776 | -0.12817 | 0.05951 | 60.1822 | -0.15106 | 60.4019 | 0.068664 | -0.086975 | 0.032043 | 0.073242 | 0.068665 | 0.37079 | -0.045776 | 0.45776 | 0.041199 | 0.27924 | 123.2574 | 0.15564 | 123.3261 | 123.4314 | 123.2849 | 123.2117 | 123.1979 | -123.3856 | -123.2529 | 123.0377 | 123.2391 | 60.0952 | 60.2051
414.4844 | 123.3078 | -60.0769 | 63.1531 | 0.018616 | -0.00050633 | 0.062284 | 0.063049 | -0.00065586 | -0.00078402 | 0.00075627 | 0.1019 | -0.00010472 | 0.065567 | 0.069045 | -0.001316 | -0.0031574 | -0.0018265 | -0.036621 | 63.2309 | -60.3058 | 62.8693 | -60.022 | -60.3424 | 0 | -0.1831 | 63.2217 | -60.1501 | 63.0981 | -60.1135 | -60.1959 | -59.7519 | -0.22888 | 0.07782 | -0.28381 | 0.054931 | 60.0769 | -0.2655 | 60.3058 | -0.036621 | -0.073242 | 0.068665 | -0.054931 | -0.036621 | 0.32501 | -0.11902 | 0.39825 | -0.045777 | 0.28381 | 123.175 | 0.036621 | 123.2483 | 123.5367 | 123.3719 | 123.3078 | 123.2986 | -123.4589 | -123.3032 | 122.9462 | 123.175 | 60.0403 | 59.8938
415.5 | 123.3673 | -60.0677 | 63.0615 | -0.12634 | 0.00034827 | 0.066556 | 0.061126 | 0.00062594 | -0.00035682 | 0.0011835 | 0.0072936 | -0.0022409 | 0.066208 | 0.064559 | -0.002384 | -0.001662 | -0.00033114 | -0.07782 | 63.1393 | -60.3333 | 62.915 | -59.9762 | -60.3333 | -0.036621 | -0.073242 | 63.1531 | -60.1776 | 63.1348 | -60.0723 | -60.1685 | -59.7153 | -0.2655 | 0.07782 | -0.14648 | 0.091553 | 60.0311 | -0.2655 | 60.2966 | 0 | -0.10986 | 0.091553 | 0.073243 | -0.004578 | 0.35248 | -0.10071 | 0.46234 | 0.009155 | 0.35706 | 123.2483 | 0.10529 | 123.3124 | 123.4726 | 123.3307 | 123.2071 | 123.2208 | -123.3948 | -123.2391 | 122.9828 | 123.2025 | 59.9899 | 59.9945
416.5469 | 123.2941 | -60.0403 | 63.1622 | -0.065308 | -0.00029273 | 0.062284 | 0.063903 | 0.00083954 | 0.0013522 | 0.00032907 | 0.016449 | 0.00096348 | 0.065354 | 0.068618 | -0.0017432 | -0.00080758 | -0.00075834 | 0.013733 | 63.1851 | -60.3058 | 62.8876 | -60.0037 | -60.3424 | 0.086975 | 0.027466 | 63.1851 | -60.1364 | 63.1119 | -60.0906 | -60.1913 | -59.7885 | -0.2655 | 0.022889 | -0.27466 | 0.036621 | 60.1273 | -0.30212 | 60.3928 | -0.036621 | -0.096131 | 0.022889 | -0.050354 | -0.050354 | 0.25177 | -0.15106 | 0.3479 | -0.054931 | 0.30212 | 123.1934 | 0.045777 | 123.2483 | 123.4909 | 123.3215 | 123.2254 | 123.2254 | -123.468 | -123.2986 | 122.9279 | 123.1522 | 60.054 | 60.0677
417.4844 | 123.3353 | -60.0677 | 63.1119 | -0.011902 | -0.00050633 | 0.063138 | 0.064544 | -0.0019377 | -0.0027066 | -0.00031193 | -0.059845 | 0.00096348 | 0.065995 | 0.069259 | -0.0036658 | -0.00016658 | 0.00030966 | -0.009155 | 63.1805 | -60.3745 | 62.9242 | -59.9716 | -60.3333 | 0.009155 | 0.036621 | 63.1897 | -60.1501 | 63.1851 | -60.2142 | -60.1776 | -59.6878 | -0.3067 | 0.068665 | -0.18768 | 0.09613 | 60.0769 | -0.2655 | 60.3836 | 0.041199 | -0.082397 | 0.07782 | 0.073243 | -0.14648 | 0.37994 | -0.10986 | 0.46234 | -0.027466 | 0.40283 | 123.2986 | -0.064087 | 123.3353 | 123.555 | 123.3398 | 123.2483 | 123.2574 | -123.4863 | -123.262 | 122.9919 | 123.2529 | 60.0586 | 60.1044
418.4844 | 123.3307 | -60.0861 | 63.1165 | -0.019531 | 0.00034827 | 0.062925 | 0.065612 | -0.00044226 | -0.0033474 | -0.0024481 | -0.020172 | 0.0020315 | 0.067063 | 0.0652 | -0.0017432 | -0.0023028 | -0.0013991 | -0.004578 | 63.1989 | -60.3241 | 62.9059 | -59.9899 | -60.3058 | 0.032043 | 0.059509 | 63.208 | -60.1456 | 63.1485 | -60.0632 | -60.1822 | -59.729 | -0.23804 | 0.082398 | -0.21057 | 0.096131 | 60.1181 | -0.21973 | 60.3561 | 0.018311 | -0.059509 | 0.091553 | 0.032044 | 0.022889 | 0.35706 | -0.09613 | 0.41656 | -0.036621 | 0.33417 | 123.23 | 0.082398 | 123.2941 | 123.523 | 123.3536 | 123.2849 | 123.2941 | -123.4406 | -123.262 | 122.9919 | 123.2346 | 60.0815 | 60.1456
419.5469 | 123.3902 | -60.054 | 63.089 | -0.065308 | 0.00013467 | 0.064847 | 0.062194 | 0.0019077 | 0.0017794 | -0.0015935 | 0.065277 | 0.00032248 | 0.066208 | 0.05815 | 0.000393 | -0.0020892 | -0.0020401 | -0.041199 | 63.176 | -60.3058 | 62.9562 | -59.9258 | -60.2554 | 0.064087 | 0.045776 | 63.1485 | -60.1501 | 63.1943 | -59.9854 | -60.0952 | -59.6878 | -0.25177 | 0.086975 | -0.13275 | 0.12817 | 60.1181 | -0.20142 | 60.3699 | 0.050354 | -0.09613 | 0.05951 | 0.10529 | 0.068664 | 0.36621 | -0.041199 | 0.46234 | 0.054931 | 0.37994 | 123.262 | 0.16479 | 123.3444 | 123.4818 | 123.2986 | 123.23 | 123.2025 | -123.3948 | -123.2391 | 123.0103 | 123.2483 | 60.0128 | 60.0998
420.5 | 123.3902 | -60.0403 | 63.0478 | -0.065308 | 0.0012027 | 0.065702 | 0.064544 | 0.0029757 | 7.0582e-05 | 0.00054267 | 0.025604 | -0.0013863 | 0.067704 | 0.067763 | -0.0034522 | 0.00068782 | -0.00054474 | -0.073242 | 63.1302 | -60.3241 | 62.9379 | -59.9213 | -60.2966 | -0.027466 | -0.004578 | 63.121 | -60.1501 | 63.1668 | -60.0449 | -60.1501 | -59.697 | -0.28381 | 0.082397 | -0.10986 | 0.11902 | 60.0128 | -0.25635 | 60.2966 | 0.027466 | -0.10986 | 0.073242 | 0.11902 | -0.004578 | 0.34332 | -0.10986 | 0.45319 | 0 | 0.40283 | 123.262 | 0.10529 | 123.317 | 123.4543 | 123.2712 | 123.1705 | 123.1613 | -123.3719 | -123.1979 | 122.9782 | 123.2071 | 59.967 | 60.0357
421.4844 | 123.349 | -60.0723 | 63.1027 | -0.0042723 | -7.913e-05 | 0.06442 | 0.065399 | 0.00041234 | -0.00035682 | 0.0024653 | -0.065949 | 0.0018179 | 0.066208 | 0.066268 | -0.0004614 | 4.7018e-05 | 0.0013779 | 0.013733 | 63.1805 | -60.3424 | 62.9105 | -59.9625 | -60.2966 | 0.004578 | 0.054932 | 63.1989 | -60.1501 | 63.1485 | -60.0769 | -60.1776 | -59.7382 | -0.27008 | 0.07782 | -0.19226 | 0.10986 | 60.0769 | -0.2243 | 60.347 | 0.045776 | -0.077819 | 0.096131 | 0.045777 | -0.004577 | 0.33417 | -0.10529 | 0.41199 | -0.027466 | 0.37994 | 123.2529 | 0.073242 | 123.2986 | 123.5229 | 123.349 | 123.2529 | 123.2712 | -123.4451 | -123.2529 | 122.9828 | 123.2208 | 60.0861 | 60.1273
422.4844 | 123.317 | -60.0861 | 63.1302 | 0.0033567 | -0.00050633 | 0.062711 | 0.062835 | -1.486e-05 | 0.00028418 | -0.0018073 | -0.014069 | 0.0020315 | 0.064926 | 0.069686 | -0.0004614 | 0.0015424 | -0.0039627 | -0.009155 | 63.1989 | -60.3287 | 62.8738 | -60.0174 | -60.3287 | 0.004578 | 0.018311 | 63.2126 | -60.1639 | 63.1256 | -60.0906 | -60.2051 | -59.7473 | -0.24261 | 0.068665 | -0.25635 | 0.068665 | 60.0906 | -0.24261 | 60.3333 | 0 | -0.077819 | 0.082397 | -0.004578 | -0.004577 | 0.33875 | -0.11902 | 0.41656 | -0.041199 | 0.31128 | 123.2025 | 0.073242 | 123.2895 | 123.5275 | 123.3765 | 123.2849 | 123.2986 | -123.4589 | -123.2941 | 122.9599 | 123.2117 | 60.0769 | 60.1044
423.4844 | 123.3032 | -60.0861 | 63.0936 | -0.03479 | 0.0024845 | 0.063138 | 0.063049 | 0.0021213 | 0.00071138 | 0.00075627 | -0.053741 | -0.00053192 | 0.068985 | 0.061355 | -0.0008886 | -0.00038018 | -0.0031081 | -0.004578 | 63.1805 | -60.3516 | 62.9105 | -59.9625 | -60.3378 | 0.009155 | 0.032043 | 63.1897 | -60.1593 | 63.1348 | -60.0815 | -60.2737 | -59.8938 | -0.2655 | 0.086975 | -0.18311 | 0.1236 | 60.0952 | -0.25177 | 60.3607 | 0.013732 | -0.073242 | 0.09613 | 0.041199 | 0.004578 | 0.19226 | -0.18768 | 0.2655 | -0.11444 | 0.3891 | 123.262 | 0.07782 | 123.2941 | 123.5321 | 123.349 | 123.2666 | 123.2758 | -123.4451 | -123.2529 | 122.9965 | 123.2208 | 60.0815 | 60.1181
424.4844 | 123.317 | -60.054 | 63.1439 | -0.057678 | -0.00071993 | 0.062711 | 0.063262 | -0.0055691 | -0.00014322 | 0.00054267 | -0.014069 | 0.00053628 | 0.067704 | 0.064345 | 0.0001794 | -0.0023028 | 0.0045823 | -0.032043 | 63.208 | -60.3241 | 62.7411 | -60.141 | -60.2875 | -0.036621 | -0.018311 | 63.1851 | -60.1822 | 63.1256 | -60.0815 | -60.1868 | -59.761 | -0.27008 | 0.064087 | -0.40283 | -0.086975 | 60.0174 | -0.23346 | 60.2875 | 0.036621 | -0.12817 | 0.041199 | -0.018311 | -0.027466 | 0.29297 | -0.13275 | 0.42114 | -0.004578 | 0.18311 | 123.0652 | 0.10071 | 123.3078 | 123.5321 | 123.3673 | 123.262 | 123.2391 | -123.468 | -123.3261 | 122.7951 | 123.1796 | 60.022 | 60.0357
425.5625 | 123.2803 | -60.0861 | 63.1119 | -0.042419 | 0.0024845 | 0.067625 | 0.064117 | 0.0023349 | -0.00057042 | 0.0026789 | -0.053741 | 0.0016043 | 0.066635 | 0.069045 | -0.0002478 | -0.0023028 | 0.0018051 | -0.064087 | 63.1897 | -60.3516 | 62.8418 | -60.0449 | -60.3973 | -0.10529 | -0.14648 | 63.1851 | -60.1822 | 63.0707 | -60.141 | -60.3058 | -59.816 | -0.2655 | 0.07782 | -0.27008 | 0.041199 | 59.9808 | -0.31128 | 60.2463 | -0.045777 | -0.09613 | 0.073243 | -0.041198 | -0.054931 | 0.27008 | -0.21973 | 0.36621 | -0.1236 | 0.3067 | 123.1934 | 0.041199 | 123.2529 | 123.5413 | 123.3673 | 123.2758 | 123.2712 | -123.4634 | -123.2941 | 122.9279 | 123.1567 | 60.022 | 59.9396
426.4844 | 123.3261 | -60.0632 | 63.121 | -0.03479 | -0.00029273 | 0.063138 | 0.06369 | 0.0014803 | -0.0014248 | -0.00052553 | -0.0049134 | -0.00095912 | 0.065354 | 0.063064 | -0.000675 | 0.00068782 | -0.0024673 | -0.013733 | 63.2172 | -60.3287 | 62.8876 | -60.022 | -60.3287 | 0.004578 | 0.009155 | 63.1851 | -60.1456 | 63.1348 | -60.0723 | -60.1822 | -59.7382 | -0.2655 | 0.09613 | -0.23346 | 0.041198 | 60.0677 | -0.2655 | 60.3333 | 0 | -0.082398 | 0.064087 | 0.013733 | -0.009156 | 0.32501 | -0.11902 | 0.40741 | -0.036621 | 0.3067 | 123.2162 | 0.073242 | 123.2803 | 123.5458 | 123.3307 | 123.2803 | 123.2483 | -123.4497 | -123.2666 | 122.9507 | 123.1979 | 60.0494 | 60.0723
427.5469 | 123.2895 | -60.0906 | 63.1485 | 0.0033567 | -0.00050633 | 0.063352 | 0.063903 | 0.0019077 | -0.001852 | 0.0013971 | 0.022552 | 0.0011771 | 0.068131 | 0.061141 | -0.0011022 | -0.0010212 | -0.0013991 | -0.032043 | 63.2309 | -60.3287 | 62.8555 | -59.9991 | -60.3241 | 0.018311 | 0.24719 | 63.2492 | -60.1227 | 63.0981 | -60.1135 | -60.2097 | -59.7702 | -0.23804 | 0.082397 | -0.29297 | 0.091553 | 60.1089 | -0.23346 | 60.347 | 0.004577 | -0.032044 | 0.10071 | -0.050354 | -0.022888 | 0.32043 | -0.11902 | 0.35248 | -0.086975 | 0.32959 | 123.1842 | 0.009156 | 123.2208 | 123.5596 | 123.3719 | 123.3215 | 123.3398 | -123.4772 | -123.2712 | 122.9462 | 123.1888 | 60.0586 | 60.3378
428.4844 | 123.3261 | -60.054 | 63.1714 | -0.03479 | -0.00029273 | 0.062925 | 0.06369 | -0.0036465 | 0.00028418 | -0.0020209 | 0.0011902 | 0.0013907 | 0.068558 | 0.0652 | 0.0001794 | -0.0020892 | -0.00075834 | -0.045776 | 63.2217 | -60.3149 | 62.8693 | -59.9899 | -60.3287 | 0.036621 | 0.036621 | 63.2034 | -60.1456 | 63.0936 | -60.0861 | -60.1959 | -59.7794 | -0.26093 | 0.050354 | -0.30212 | 0.064087 | 60.0906 | -0.27466 | 60.3516 | -0.013733 | -0.091553 | 0.032043 | -0.07782 | -0.032044 | 0.27466 | -0.14191 | 0.36621 | -0.050354 | 0.32501 | 123.1842 | 0.059509 | 123.2391 | 123.5367 | 123.349 | 123.2758 | 123.2574 | -123.4863 | -123.317 | 122.9233 | 123.1476 | 60.0082 | 60.0906
429.4844 | 123.317 | -60.0677 | 63.121 | -0.03479 | -0.00029273 | 0.061002 | 0.064331 | 0.0012667 | -0.0012112 | -0.0011663 | -0.044586 | -0.00095912 | 0.067276 | 0.065627 | -0.0008886 | 0.00026062 | -0.0026809 | -0.009155 | 63.2034 | -60.3287 | 62.8967 | -59.9854 | -60.2921 | 0.027466 | 0.068665 | 63.1989 | -60.1456 | 63.1393 | -60.054 | -60.1639 | -59.729 | -0.26093 | 0.082397 | -0.2243 | 0.082397 | 60.0952 | -0.2243 | 60.3561 | 0.036621 | -0.07782 | 0.07782 | 0.01831 | 0.013733 | 0.33874 | -0.09613 | 0.41656 | -0.01831 | 0.34332 | 123.2254 | 0.091553 | 123.2849 | 123.5321 | 123.3444 | 123.2712 | 123.2666 | -123.4497 | -123.2666 | 122.9645 | 123.2071 | 60.0586 | 60.1364
430.5 | 123.4085 | -60.0449 | 63.0524 | -0.080566 | 0.0020573 | 0.063779 | 0.064117 | 0.00041234 | 0.0013522 | -0.0018073 | -0.0079652 | 0.00010888 | 0.069199 | 0.063705 | -0.0015296 | 0.0030378 | 0.0052231 | -0.050354 | 63.1119 | -60.3378 | 62.9379 | -59.9304 | -60.3104 | -0.032043 | -0.004578 | 63.1073 | -60.141 | 63.0753 | -59.8251 | -60.0677 | -59.7153 | -0.29297 | 0.059509 | -0.11444 | 0.11444 | 60.0128 | -0.2655 | 60.3058 | 0.027466 | -0.09613 | 0.054932 | 0.022888 | 0.21973 | 0.32959 | -0.022888 | 0.42572 | 0.073242 | 0.40741 | 123.2758 | 0.31586 | 123.2162 | 123.4497 | 123.2483 | 123.1567 | 123.1522 | -123.3902 | -123.1934 | 122.9828 | 123.1201 | 59.9945 | 60.0403
431.4844 | 123.3398 | -60.0632 | 63.1119 | -0.065308 | 0.00013467 | 0.062711 | 0.064758 | -0.0019377 | 7.0582e-05 | 0.0063105 | -0.029327 | 0.0011771 | 0.067063 | 0.068831 | -0.000675 | -0.0010212 | 0.00030966 | -0.027466 | 63.1897 | -60.3195 | 62.8464 | -60.1089 | -60.2646 | 0.004578 | 0.027466 | 63.1622 | -60.1227 | 63.1348 | -60.0952 | -60.2005 | -59.729 | -0.25635 | 0.07782 | -0.2655 | -0.045777 | 60.0677 | -0.20142 | 60.3241 | 0.054932 | -0.05951 | 0.050354 | 0.022889 | -0.032044 | 0.33417 | -0.13733 | 0.39368 | -0.077819 | 0.21057 | 123.1659 | 0.027466 | 123.2574 | 123.5092 | 123.2849 | 123.2529 | 123.2254 | -123.4314 | -123.2346 | 122.9095 | 123.1979 | 60.0357 | 60.0906
432.5469 | 123.4451 | -60.0311 | 63.0753 | 0.010986 | -0.0013607 | 0.062284 | 0.062622 | -0.00065586 | 0.00049778 | -0.0024481 | 0.062225 | 0.0013907 | 0.066635 | 0.063918 | -0.0011022 | -0.0012348 | -0.00054474 | -0.022888 | 63.176 | -60.2921 | 62.9654 | -59.8938 | -60.2325 | 0.082397 | 0.1236 | 63.1439 | -60.1227 | 63.2126 | -59.9762 | -60.0449 | -59.6375 | -0.26093 | 0.10071 | -0.10986 | 0.13733 | 60.1135 | -0.20142 | 60.3745 | 0.059509 | -0.091553 | 0.068665 | 0.13733 | 0.054932 | 0.39368 | -0.013733 | 0.48523 | 0.07782 | 0.39825 | 123.2574 | 0.14648 | 123.3353 | 123.468 | 123.2666 | 123.2071 | 123.175 | -123.3673 | -123.1979 | 122.9965 | 123.2437 | 60.0082 | 60.1547
433.4844 | 123.3307 | -60.0815 | 63.1165 | -0.019531 | -7.913e-05 | 0.064634 | 0.06604 | 0.0025485 | -0.00057042 | 0.00054267 | -0.056793 | 0.00053628 | 0.06749 | 0.068404 | -3.4196e-05 | 0.00026062 | -0.00033114 | -0.004578 | 63.1943 | -60.3333 | 62.8922 | -59.9762 | -60.3058 | -0.009155 | 0.068665 | 63.1805 | -60.141 | 63.0569 | -60.1318 | -60.1227 | -59.729 | -0.25177 | 0.07782 | -0.2243 | 0.10529 | 60.0723 | -0.2243 | 60.3241 | 0.027466 | -0.059509 | 0.064087 | -0.059509 | -0.050354 | 0.35248 | -0.041199 | 0.41199 | 0.01831 | 0.35706 | 123.2254 | 0.009155 | 123.1979 | 123.5275 | 123.3215 | 123.2758 | 123.262 | -123.4497 | -123.2574 | 122.9736 | 123.1384 | 60.0769 | 60.1501
434.5469 | 123.3627 | -60.0494 | 63.089 | -0.057678 | -0.00093353 | 0.063352 | 0.062194 | -0.00065586 | -0.0048428 | 0.0016107 | 0.046967 | 0.00032248 | 0.067704 | 0.063918 | 0.000393 | -0.0031574 | -0.00054474 | -0.064087 | 63.1805 | -60.3012 | 63.0341 | -60.0586 | -60.3378 | 0.009155 | -0.013733 | 63.1348 | -60.1593 | 63.1485 | -60.0494 | -60.1456 | -59.7015 | -0.25177 | 0.091553 | -0.054931 | -0.009156 | 60.0586 | -0.28839 | 60.3104 | -0.036622 | -0.10986 | 0.045777 | 0.05951 | 0 | 0.3479 | -0.096131 | 0.45776 | 0.013733 | 0.24261 | 123.3353 | 0.10986 | 123.3078 | 123.4818 | 123.2941 | 123.23 | 123.1842 | -123.3902 | -123.2483 | 123.0835 | 123.1979 | 59.9854 | 60.0357
435.5 | 123.2849 | -60.1089 | 63.0936 | -0.065308 | 0.00056187 | 0.063352 | 0.065612 | 0.0023349 | 0.0024204 | -9.8328e-05 | -0.090363 | 0.00010888 | 0.066422 | 0.060927 | -3.4196e-05 | 0.00026062 | -0.00075834 | -0.10071 | 63.176 | -60.3882 | 62.8143 | -60.1089 | -60.4614 | -0.11444 | -0.15106 | 63.1805 | -60.2005 | 63.0753 | -60.1593 | -60.2921 | -59.8068 | -0.27924 | 0.082397 | -0.27924 | 0 | 59.9945 | -0.35248 | 60.2737 | -0.073242 | -0.091552 | 0.086975 | -0.018311 | -0.050354 | 0.30212 | -0.18311 | 0.39368 | -0.091553 | 0.27924 | 123.2025 | 0.041198 | 123.2758 | 123.5641 | 123.381 | 123.2849 | 123.2895 | -123.4818 | -123.2941 | 122.9233 | 123.1842 | 60.0082 | 59.9579
436.5469 | 123.4406 | -60.0449 | 63.089 | -0.042419 | 0.00098907 | 0.063138 | 0.064331 | -0.0010831 | -0.0020658 | 0.00011527 | 0.05307 | -0.0022409 | 0.061081 | 0.063705 | -0.003025 | -0.0012348 | -0.0050307 | 0.013733 | 63.176 | -60.3012 | 62.9791 | -59.8618 | -60.2097 | 0.10986 | 0.39825 | 63.1989 | -60.0769 | 63.1485 | -59.9442 | -60.054 | -59.6786 | -0.25635 | 0.086975 | -0.10986 | 0.18311 | 60.1547 | -0.1648 | 60.4111 | 0.091552 | -0.032043 | 0.10986 | 0.05951 | 0.10071 | 0.36621 | -0.009155 | 0.39825 | 0.022888 | 0.43945 | 123.2803 | 0.13275 | 123.2254 | 123.4772 | 123.2758 | 123.2208 | 123.2437 | -123.3902 | -123.1659 | 123.024 | 123.1934 | 60.0586 | 60.4431
437.4844 | 123.349 | -60.0723 | 63.1119 | 0.026245 | 0.0014163 | 0.063993 | 0.064117 | 0.0010531 | -0.00035682 | -0.0013799 | -0.035431 | 0.0011771 | 0.067704 | 0.067977 | -0.000675 | -0.00080758 | 0.00052346 | -0.004578 | 63.2172 | -60.3241 | 62.9059 | -59.967 | -60.2875 | 0.018311 | 0.10529 | 63.176 | -60.1456 | 63.1348 | -60.0723 | -60.2005 | -59.729 | -0.25177 | 0.10529 | -0.20599 | 0.10529 | 60.0906 | -0.21515 | 60.3424 | 0.036621 | -0.073242 | 0.064087 | 0.022889 | 0 | 0.34332 | -0.12817 | 0.41656 | -0.054931 | 0.35706 | 123.23 | 0.073242 | 123.2803 | 123.5413 | 123.3215 | 123.2895 | 123.2483 | -123.436 | -123.2574 | 122.9782 | 123.2071 | 60.0677 | 60.1776
438.5469 | 123.3994 | -60.0266 | 63.089 | -0.03479 | 0.00034827 | 0.062498 | 0.063049 | -0.0025785 | 0.00028418 | -0.0015935 | 0.059174 | 0.00032248 | 0.067276 | 0.06755 | -0.002384 | -0.0023028 | -0.0039627 | -0.009155 | 63.1577 | -60.3012 | 62.9608 | -59.903 | -60.2692 | 0.054932 | 0.07782 | 63.1577 | -60.1364 | 63.1897 | -59.9716 | -60.0632 | -59.642 | -0.27466 | 0.068665 | -0.12817 | 0.1236 | 60.0815 | -0.24262 | 60.3561 | 0.032043 | -0.10986 | 0.068665 | 0.10071 | 0.054931 | 0.38452 | -0.036621 | 0.49439 | 0.073243 | 0.39825 | 123.262 | 0.1648 | 123.3261 | 123.4589 | 123.2941 | 123.1842 | 123.1842 | -123.3902 | -123.2254 | 122.9874 | 123.2162 | 60.0174 | 60.1044
439.4844 | 123.349 | -60.0449 | 63.1073 | -0.057678 | 0.0020573 | 0.064634 | 0.065185 | 0.0012667 | -0.0014248 | 0.0022517 | -0.059845 | 0.0018179 | 0.067704 | 0.070327 | -0.0011022 | -0.001662 | 0.0033005 | -0.009155 | 63.1943 | -60.3333 | 62.9288 | -59.9625 | -60.3333 | 0 | 0.050354 | 63.1943 | -60.1456 | 63.1393 | -60.0677 | -60.1776 | -59.7198 | -0.28839 | 0.086975 | -0.17853 | 0.082398 | 60.0449 | -0.28839 | 60.3333 | 0 | -0.10071 | 0.086975 | 0.032043 | -0.022888 | 0.32501 | -0.13275 | 0.42572 | -0.032043 | 0.37079 | 123.262 | 0.07782 | 123.2849 | 123.5275 | 123.3398 | 123.2391 | 123.2391 | -123.4406 | -123.2529 | 122.9736 | 123.1842 | 60.0357 | 60.0952
440.5 | 123.3215 | -60.0586 | 63.0936 | -0.22552 | -0.0015743 | 0.061857 | 0.063903 | 0.0012667 | 0.00028418 | -0.00052553 | -0.069 | 0.0018179 | 0.068558 | 0.066909 | -0.0017432 | 0.00090142 | -0.00075834 | 0.086975 | 63.2126 | -60.3516 | 62.8601 | -60.0677 | -60.4294 | -0.11444 | -0.14648 | 63.1531 | -60.2005 | 63.0981 | -60.1456 | -60.2737 | -59.7794 | -0.29297 | 0.11902 | -0.23346 | -0.009155 | 59.9442 | -0.37079 | 60.2371 | -0.07782 | -0.14191 | 0.059509 | 0.004578 | -0.086975 | 0.27924 | -0.21515 | 0.42114 | -0.073243 | 0.28381 | 123.2117 | 0.054931 | 123.2986 | 123.5641 | 123.3536 | 123.2712 | 123.2117 | -123.4451 | -123.2941 | 122.9187 | 123.1567 | 60.1456 | 59.9121
441.5469 | 123.4222 | -60.0403 | 63.0844 | -0.03479 | -7.913e-05 | 0.063779 | 0.061981 | -0.00044226 | 0.0024204 | -0.00031193 | 0.028656 | 0.00053628 | 0.064926 | 0.069686 | -3.4196e-05 | -0.0035846 | -0.0018265 | 0.022888 | 63.1805 | -60.2966 | 62.9837 | -59.8663 | -60.2234 | 0.11902 | 0.19226 | 63.1668 | -60.1044 | 63.2446 | -60.0861 | -60.0311 | -59.6008 | -0.25635 | 0.09613 | -0.10071 | 0.17395 | 60.1593 | -0.18311 | 60.4156 | 0.073242 | -0.064087 | 0.082397 | 0.16022 | -0.045777 | 0.43945 | 0.009155 | 0.50354 | 0.073242 | 0.4303 | 123.2803 | 0.01831 | 123.349 | 123.4772 | 123.2712 | 123.2208 | 123.2071 | -123.381 | -123.1888 | 123.024 | 123.2849 | 60.0632 | 60.2325
442.4844 | 123.3765 | -60.0494 | 63.1851 | -0.0042723 | -0.0022153 | 0.062498 | 0.063476 | 0.0023349 | -0.0020658 | 0.0020379 | -0.014069 | 0.0026725 | 0.067276 | 0.060287 | -0.0004614 | -0.001662 | 0.0013779 | -0.036621 | 63.1943 | -60.3333 | 62.883 | -60.0037 | -60.3241 | 0.036621 | 0.036621 | 63.2217 | -60.1273 | 63.1027 | -60.0998 | -60.1913 | -59.8022 | -0.28381 | 0.009155 | -0.30212 | 0.045776 | 60.0861 | -0.27466 | 60.3699 | 0.009155 | -0.07782 | 0.036621 | -0.082398 | -0.050354 | 0.24719 | -0.14191 | 0.32501 | -0.064087 | 0.32959 | 123.2162 | 0.027466 | 123.23 | 123.5275 | 123.349 | 123.2437 | 123.2712 | -123.5184 | -123.3124 | 122.9324 | 123.1522 | 60.0128 | 60.0861
443.5469 | 123.4177 | -60.0403 | 63.1302 | -0.095825 | 0.0016299 | 0.061857 | 0.062408 | -0.0051419 | 0.00028418 | -0.0013799 | 0.016449 | -0.0016001 | 0.065354 | 0.0652 | -0.0032386 | -0.0014484 | 0.0028733 | -0.013733 | 63.1622 | -60.3012 | 62.97 | -59.8572 | -60.228 | 0.073242 | 0.13733 | 63.1439 | -60.1181 | 63.1989 | -59.9854 | -60.0723 | -59.6603 | -0.26093 | 0.032043 | -0.16022 | 0.18311 | 60.1135 | -0.18768 | 60.3745 | 0.073242 | -0.07782 | 0.013733 | 0.068665 | 0.054931 | 0.37994 | -0.032044 | 0.45776 | 0.045776 | 0.44403 | 123.2712 | 0.13275 | 123.317 | 123.4634 | 123.262 | 123.2025 | 123.1842 | -123.4314 | -123.2483 | 123.0103 | 123.2391 | 60.0266 | 60.1776
444.4844 | 123.2849 | -60.0403 | 63.1531 | -0.019531 | 0.00098907 | 0.063779 | 0.064117 | 0.00062594 | 0.0017794 | 0.0013971 | -0.041534 | 0.0011771 | 0.068131 | 0.061996 | -0.0002478 | -0.001662 | -0.0033219 | -0.004578 | 63.208 | -60.3241 | 62.9288 | -59.9945 | -60.3424 | 0.050354 | 0.054932 | 63.1851 | -60.1318 | 63.1027 | -60.0998 | -60.2005 | -59.761 | -0.28381 | 0.054932 | -0.2243 | 0.045776 | 60.0906 | -0.30212 | 60.3745 | -0.01831 | -0.091553 | 0.032044 | -0.050354 | -0.059509 | 0.27924 | -0.16022 | 0.37079 | -0.068664 | 0.32959 | 123.2529 | 0.032044 | 123.2346 | 123.5321 | 123.317 | 123.2483 | 123.2254 | -123.4772 | -123.2849 | 122.9691 | 123.143 | 60.0357 | 60.0952
445.4844 | 123.3307 | -60.0677 | 63.1073 | -0.042419 | 0.00077547 | 0.063352 | 0.064971 | -0.0012967 | -0.00078402 | 0.0028925 | -0.075104 | 0.0026725 | 0.065995 | 0.066054 | -0.0002478 | -0.0014484 | -0.0018265 | -0.027466 | 63.1805 | -60.3561 | 62.8601 | -60.1227 | -60.2646 | 0.004578 | 0.027466 | 63.176 | -60.1685 | 63.1348 | -60.0952 | -60.1868 | -59.7427 | -0.28839 | 0.073242 | -0.24719 | -0.054932 | 60.0723 | -0.19684 | 60.3607 | 0.091553 | -0.10071 | 0.068664 | 0.027466 | -0.027466 | 0.32501 | -0.11902 | 0.42572 | -0.018311 | 0.23346 | 123.2162 | 0.073242 | 123.3032 | 123.5367 | 123.3444 | 123.2483 | 123.2437 | -123.4634 | -123.2758 | 122.9279 | 123.2025 | 60.0403 | 60.0952
446.5469 | 123.3536 | -60.0586 | 63.0478 | -0.072937 | 0.0022709 | 0.065061 | 0.062194 | -0.00022866 | -0.0022794 | 0.00011527 | 0.022552 | 0.0018179 | 0.068131 | 0.068618 | -0.000675 | -0.0014484 | -0.0022537 | -0.07782 | 63.1485 | -60.3378 | 62.9196 | -59.9579 | -60.3424 | -0.036621 | -0.068665 | 63.1073 | -60.173 | 63.1577 | -60.0632 | -60.1501 | -59.7061 | -0.27924 | 0.10071 | -0.12817 | 0.10071 | 60.022 | -0.28381 | 60.3012 | -0.004577 | -0.11444 | 0.059509 | 0.10986 | -0.004577 | 0.35248 | -0.091552 | 0.46692 | 0.022889 | 0.37994 | 123.2574 | 0.10986 | 123.3307 | 123.4863 | 123.2803 | 123.2071 | 123.1659 | -123.3856 | -123.2208 | 122.9782 | 123.2162 | 59.9808 | 59.9899
447.4844 | 123.3398 | -60.0357 | 63.1073 | -0.080566 | 0.0020573 | 0.063138 | 0.064544 | 0.0016939 | 0.00028418 | -0.00073913 | -0.05069 | -0.00053192 | 0.068772 | 0.066695 | -0.0025976 | -0.0025164 | -0.00033114 | -0.004578 | 63.2034 | -60.3241 | 62.9059 | -59.9808 | -60.3104 | 0.018311 | 0.054932 | 63.1989 | -60.141 | 63.1485 | -60.0769 | -60.1685 | -59.729 | -0.28839 | 0.09613 | -0.20142 | 0.054932 | 60.054 | -0.27466 | 60.3424 | 0.013733 | -0.10529 | 0.091553 | 0.041199 | -0.041198 | 0.3067 | -0.13275 | 0.41199 | -0.027466 | 0.34332 | 123.23 | 0.064087 | 123.2895 | 123.5275 | 123.3398 | 123.2391 | 123.2346 | -123.4314 | -123.2483 | 122.9416 | 123.1842 | 60.0311 | 60.0906
448.5469 | 123.4177 | -60.0174 | 63.0936 | -0.042419 | 0.0024845 | 0.06143 | 0.061981 | -0.0032193 | 0.0013522 | 0.0011835 | 0.004242 | -0.0022409 | 0.066208 | 0.065841 | -0.0017432 | -0.0025164 | 0.0011643 | 0.17395 | 63.2126 | -60.2554 | 62.915 | -59.8755 | -60.1868 | 0.064087 | 0.10986 | 63.1531 | -60.1456 | 63.1989 | -59.9808 | -60.0861 | -59.6695 | -0.23804 | 0.11902 | -0.17853 | 0.14191 | 60.0815 | -0.16937 | 60.3195 | 0.068664 | -0.12817 | 0.059509 | 0.10529 | 0.036621 | 0.3479 | -0.068665 | 0.47607 | 0.059509 | 0.37994 | 123.1705 | 0.1648 | 123.3444 | 123.468 | 123.2986 | 123.23 | 123.1705 | -123.349 | -123.2391 | 122.9324 | 123.2162 | 60.1913 | 60.1273
449.4844 | 123.3078 | -60.0861 | 63.1393 | -0.03479 | 0.00098907 | 0.06442 | 0.063476 | -0.0023649 | -0.0014248 | 0.00075627 | -0.029327 | 0.0022453 | 0.065354 | 0.063705 | -0.0011022 | 0.00047422 | -0.0024673 | -0.027466 | 63.2217 | -60.3104 | 62.8601 | -60.0128 | -60.3195 | 0.20599 | -0.091553 | 63.2309 | -60.1685 | 63.0981 | -60.0723 | -60.2142 | -59.7748 | -0.2243 | 0.082398 | -0.27924 | 0.073243 | 60.2921 | -0.23346 | 60.5164 | -0.009155 | -0.082397 | 0.091553 | -0.041198 | 0.013733 | 0.31128 | -0.12817 | 0.39368 | -0.045776 | 0.29755 | 123.1705 | 0.09613 | 123.2666 | 123.5321 | 123.3994 | 123.3078 | 123.317 | -123.4497 | -123.3078 | 122.9462 | 123.1842 | 60.0586 | 59.9945
450.5469 | 123.4222 | -60.0128 | 63.121 | -0.027161 | -0.0011471 | 0.061857 | 0.063262 | 0.00062594 | 0.00028418 | -9.8328e-05 | 0.022552 | 0.00032248 | 0.068131 | 0.064345 | -0.0015296 | -0.00059378 | 0.0013779 | -0.004578 | 63.1668 | -60.2829 | 62.9929 | -59.8755 | -60.228 | 0.10986 | 0.15106 | 63.1302 | -60.1181 | 63.2263 | -59.9579 | -60.0357 | -59.6375 | -0.27008 | 0.045776 | -0.12817 | 0.13733 | 60.1227 | -0.21515 | 60.3928 | 0.054932 | -0.10529 | 0.009155 | 0.10529 | 0.054931 | 0.37537 | -0.022889 | 0.48065 | 0.082397 | 0.40741 | 123.2758 | 0.16022 | 123.3444 | 123.4497 | 123.2483 | 123.1796 | 123.143 | -123.4039 | -123.2391 | 123.0057 | 123.2391 | 60.0082 | 60.1639
451.4844 | 123.3536 | -60.0403 | 63.1256 | -0.042419 | -0.00029273 | 0.063566 | 0.064117 | 0.00041234 | -0.00014322 | 0.00096987 | -0.062897 | 0.00032248 | 0.068131 | 0.06755 | -0.0011022 | 0.00090142 | -0.00054474 | 0.013733 | 63.1943 | -60.3516 | 62.9196 | -59.967 | -60.3058 | 0.018311 | 0.10986 | 63.1897 | -60.1547 | 63.1485 | -60.0632 | -60.1913 | -59.729 | -0.31128 | 0.068665 | -0.20599 | 0.073242 | 60.0586 | -0.2655 | 60.3699 | 0.045776 | -0.11444 | 0.064087 | 0.022889 | -0.022888 | 0.31128 | -0.15106 | 0.42572 | -0.036621 | 0.38452 | 123.2712 | 0.091553 | 123.3032 | 123.5458 | 123.3444 | 123.2346 | 123.23 | -123.4772 | -123.2803 | 122.9599 | 123.1888 | 60.054 | 60.1501
452.5469 | 123.3948 | -60.0357 | 63.0981 | -0.14923 | 0.0024845 | 0.06143 | 0.064117 | -0.00044226 | 0.0032748 | -0.0020209 | 0.062225 | -0.00010472 | 0.068344 | 0.059218 | -0.001316 | -0.00059378 | 0.0018051 | 0.004578 | 63.1531 | -60.2966 | 62.9059 | -59.9716 | -60.3195 | 0.009155 | -0.027466 | 63.1302 | -60.1547 | 63.1668 | -60.0174 | -60.1273 | -59.6878 | -0.26093 | 0.054931 | -0.19226 | 0.064087 | 60.0449 | -0.28381 | 60.3058 | -0.022888 | -0.11902 | 0.032043 | 0.068664 | 0.018311 | 0.3479 | -0.091552 | 0.46692 | 0.027466 | 0.32501 | 123.2025 | 0.13733 | 123.3215 | 123.4497 | 123.2849 | 123.1888 | 123.1659 | -123.3948 | -123.2529 | 122.9416 | 123.2025 | 60.0403 | 60.0082
453.4844 | 123.3215 | -60.0998 | 63.1577 | -0.0042723 | -0.00071993 | 0.06207 | 0.064758 | -0.00065586 | -0.00014322 | -0.0013799 | -0.0079652 | -0.00010472 | 0.066849 | 0.068404 | -0.003025 | -0.0010212 | 0.0015915 | 0.1831 | 63.2492 | -60.3012 | 62.8647 | -60.0266 | -60.3561 | 0.018311 | 0.004578 | 63.2401 | -60.141 | 63.1119 | -60.0632 | -60.2051 | -59.7427 | -0.20142 | 0.091553 | -0.29297 | 0.073242 | 60.1181 | -0.25635 | 60.3195 | -0.054932 | -0.041199 | 0.082397 | -0.045777 | 0.036621 | 0.35706 | -0.10529 | 0.39825 | -0.064087 | 0.27466 | 123.1659 | 0.07782 | 123.2529 | 123.5504 | 123.381 | 123.349 | 123.3398 | -123.4589 | -123.2986 | 122.9645 | 123.2117 | 60.2829 | 60.1044
454.4844 | 123.317 | -60.0403 | 63.1256 | 0.0033567 | -0.0011471 | 0.062284 | 0.065185 | 0.00019874 | -0.0014248 | 0.0011835 | -0.020172 | 0.0022453 | 0.068772 | 0.063277 | 0.0001794 | 0.001756 | -0.00075834 | -0.027466 | 63.2217 | -60.3104 | 62.8922 | -60.0311 | -60.3836 | 0.018311 | 0.022888 | 63.208 | -60.1456 | 63.1073 | -60.0769 | -60.2005 | -59.7702 | -0.27008 | 0.096131 | -0.23346 | 0.009155 | 60.0586 | -0.34332 | 60.3287 | -0.073242 | -0.10529 | 0.082398 | -0.01831 | -0.036621 | 0.27008 | -0.16022 | 0.37537 | -0.054931 | 0.27924 | 123.2025 | 0.068665 | 123.2529 | 123.5321 | 123.3536 | 123.262 | 123.2483 | -123.436 | -123.2712 | 122.9324 | 123.1476 | 60.0128 | 60.0632
455.5625 | 123.3215 | -60.0449 | 63.1485 | -0.11871 | -0.00071993 | 0.062284 | 0.062835 | 0.00019874 | 0.0019932 | 0.00032907 | -0.032379 | 0.0020315 | 0.068131 | 0.06285 | -0.000675 | -0.00080758 | -0.0020401 | -0.004578 | 63.2217 | -60.3561 | 62.8876 | -60.0037 | -60.347 | 0.013733 | 0.004578 | 63.2034 | -60.1593 | 63.1165 | -60.0952 | -60.1913 | -59.761 | -0.31128 | 0.073242 | -0.26093 | 0.041199 | 60.0586 | -0.30212 | 60.3699 | 0.009155 | -0.11444 | 0.054931 | -0.032044 | -0.050354 | 0.28381 | -0.14648 | 0.39825 | -0.032043 | 0.35248 | 123.2437 | 0.064087 | 123.2758 | 123.5779 | 123.3627 | 123.2666 | 123.2483 | -123.5046 | -123.3078 | 122.9324 | 123.1613 | 60.0403 | 60.0494
456.4844 | 123.3582 | -60.054 | 63.1027 | -0.042419 | 0.0029117 | 0.063566 | 0.062622 | -0.0036465 | 0.0013522 | -0.00095273 | 0.046967 | 0.0011771 | 0.068344 | 0.061996 | -0.0015296 | -0.0020892 | 0.0015915 | 0.027466 | 63.176 | -60.3195 | 62.9837 | -59.8846 | -60.2234 | 0.09613 | 0.12817 | 63.1897 | -60.1364 | 63.1714 | -60.0174 | -60.1273 | -59.6786 | -0.2655 | 0.073242 | -0.11902 | 0.16937 | 60.1501 | -0.16937 | 60.4156 | 0.09613 | -0.082398 | 0.086975 | 0.068665 | 0.036621 | 0.37537 | -0.073242 | 0.45776 | 0.009156 | 0.43487 | 123.3032 | 0.11902 | 123.3078 | 123.4955 | 123.3261 | 123.23 | 123.2437 | -123.4222 | -123.2391 | 123.0377 | 123.2254 | 60.0815 | 60.1822
457.4844 | 123.3627 | -60.054 | 63.1119 | -0.03479 | 0.00056187 | 0.062284 | 0.064758 | -1.486e-05 | -0.00035682 | 0.00096987 | -0.05069 | 0.0030997 | 0.066849 | 0.069472 | -0.0034522 | -0.0010212 | 0.0030869 | -0.018311 | 63.2126 | -60.3241 | 62.8784 | -60.0128 | -60.3058 | 0.018311 | 0.022888 | 63.1989 | -60.141 | 63.1393 | -60.0677 | -60.173 | -59.729 | -0.27008 | 0.10071 | -0.23346 | 0.041199 | 60.0723 | -0.25177 | 60.3424 | 0.018311 | -0.086975 | 0.086976 | 0.027466 | -0.013733 | 0.32501 | -0.11902 | 0.41199 | -0.032044 | 0.31128 | 123.2025 | 0.073242 | 123.2803 | 123.5367 | 123.3398 | 123.2666 | 123.2529 | -123.436 | -123.2529 | 122.9324 | 123.1934 | 60.0357 | 60.0769
458.4844 | 123.3032 | -60.0769 | 63.1256 | -0.03479 | 0.00098907 | 0.063993 | 0.064758 | 0.0025485 | 0.00028418 | 0.00032907 | 0.0011902 | 0.00010888 | 0.067063 | 0.0652 | -0.0002478 | -0.0018756 | 0.0011643 | 0.027466 | 63.208 | -60.3149 | 62.9059 | -59.9579 | -60.3241 | 0.036621 | 0.091553 | 63.1989 | -60.1181 | 63.1073 | -60.1044 | -60.1776 | -59.7656 | -0.23804 | 0.082398 | -0.21973 | 0.11902 | 60.1135 | -0.24719 | 60.3516 | -0.009156 | -0.041199 | 0.073243 | -0.01831 | -0.027466 | 0.31128 | -0.10071 | 0.35248 | -0.059509 | 0.35705 | 123.2208 | 0.013733 | 123.2254 | 123.5229 | 123.317 | 123.2849 | 123.2758 | -123.4406 | -123.2437 | 122.9828 | 123.1842 | 60.1044 | 60.1685
459.4844 | 123.3353 | -60.0677 | 63.1302 | 0.018616 | 0.00013467 | 0.062498 | 0.06604 | -0.0017239 | -0.0029202 | 0.00096987 | -0.032379 | 0.0024589 | 0.065567 | 0.067336 | -0.0008886 | 0.00068782 | 0.0013779 | -0.018311 | 63.2172 | -60.3241 | 62.8876 | -60.0037 | -60.3333 | 0.009155 | 0.032043 | 63.1805 | -60.1227 | 63.121 | -60.0815 | -60.1776 | -59.729 | -0.25635 | 0.086975 | -0.24261 | 0.064087 | 60.0769 | -0.2655 | 60.3333 | -0.009155 | -0.054932 | 0.050354 | -0.009155 | -0.013733 | 0.33874 | -0.10986 | 0.39368 | -0.054931 | 0.32044 | 123.2117 | 0.041199 | 123.2437 | 123.5413 | 123.3032 | 123.2849 | 123.2483 | -123.4543 | -123.2529 | 122.9553 | 123.1888 | 60.0494 | 60.0998
460.5469 | 123.3719 | -60.0449 | 63.0707 | -0.019531 | 0.00098907 | 0.061857 | 0.062194 | -1.486e-05 | -0.00014322 | -0.0020209 | 0.05307 | -0.0013863 | 0.068344 | 0.061568 | -0.000675 | -0.0012348 | -0.0022537 | 0.027466 | 63.1577 | -60.2829 | 62.9837 | -59.8663 | -60.2142 | 0.11444 | 0.16022 | 63.1485 | -60.1318 | 63.0524 | -60.0311 | -60.0677 | -59.6603 | -0.23804 | 0.086975 | -0.086975 | 0.17853 | 60.1593 | -0.16937 | 60.3973 | 0.068665 | -0.086975 | 0.07782 | -0.018311 | 0.013733 | 0.38452 | -0.022888 | 0.4715 | 0.064087 | 0.41657 | 123.2666 | 0.10071 | 123.1842 | 123.4406 | 123.2803 | 123.2025 | 123.1934 | -123.3536 | -123.2025 | 123.0286 | 123.0972 | 60.0723 | 60.2051
461.4844 | 123.3398 | -60.0586 | 63.121 | -0.0042723 | 0.00077547 | 0.062925 | 0.065612 | -1.486e-05 | -0.0012112 | -0.0015935 | -0.053741 | 0.0018179 | 0.069412 | 0.068404 | -0.0017432 | 0.00026062 | -0.00011754 | 0.009155 | 63.2034 | -60.3424 | 62.9105 | -59.9716 | -60.2875 | 0.009155 | 0.050354 | 63.1989 | -60.1456 | 63.1439 | -60.0632 | -60.1822 | -59.7336 | -0.28381 | 0.082397 | -0.21057 | 0.086975 | 60.0677 | -0.22888 | 60.3516 | 0.054931 | -0.086975 | 0.07782 | 0.022888 | -0.004577 | 0.32501 | -0.1236 | 0.41199 | -0.036621 | 0.37079 | 123.2529 | 0.082398 | 123.2895 | 123.5458 | 123.3444 | 123.262 | 123.2574 | -123.4634 | -123.2666 | 122.9691 | 123.2025 | 60.0677 | 60.1089
462.5469 | 123.4497 | -60.054 | 63.0753 | -0.011902 | 0.0020573 | 0.062498 | 0.063903 | -0.0019377 | 0.00071138 | -0.0011663 | 0.037811 | -0.00031832 | 0.06984 | 0.063705 | 0.0016748 | -0.0029438 | 0.0043687 | -0.022888 | 63.1805 | -60.2829 | 62.9654 | -59.903 | -60.2463 | 0.068665 | 0.10986 | 63.1393 | -60.1364 | 63.2355 | -59.9854 | -60.0677 | -59.6375 | -0.22888 | 0.10529 | -0.10986 | 0.15106 | 60.1227 | -0.19226 | 60.3516 | 0.036621 | -0.082398 | 0.064087 | 0.16022 | 0.068664 | 0.41656 | -0.013733 | 0.49896 | 0.068665 | 0.37994 | 123.2483 | 0.15106 | 123.3719 | 123.4634 | 123.2758 | 123.2346 | 123.1934 | -123.3582 | -123.2117 | 123.0194 | 123.2895 | 60.0311 | 60.1639
463.4844 | 123.317 | -60.0494 | 63.1256 | 0.08728 | -0.0017881 | 0.062284 | 0.064544 | 0.0025485 | 0.00092498 | 0.00032907 | -0.01712 | 0.0018179 | 0.069412 | 0.06285 | -0.001316 | -0.00038018 | 0.0018051 | -0.16937 | 63.2034 | -60.3378 | 62.8464 | -60.0037 | -60.3149 | 0.009155 | 0.022888 | 63.1851 | -60.1547 | 63.1165 | -60.0677 | -60.1959 | -59.7519 | -0.28839 | 0.07782 | -0.27923 | 0.045776 | 60.0586 | -0.2655 | 60.347 | 0.022889 | -0.10529 | 0.05951 | -0.009155 | -0.018311 | 0.29755 | -0.14648 | 0.40283 | -0.041199 | 0.33417 | 123.1842 | 0.086975 | 123.2712 | 123.5413 | 123.3398 | 123.2529 | 123.2346 | -123.4634 | -123.2803 | 122.8958 | 123.1659 | 59.8801 | 60.0723
464.5469 | 123.3719 | -60.0677 | 63.089 | -0.088196 | 0.00034827 | 0.062925 | 0.062835 | -0.0015103 | -0.00035682 | -0.00095273 | 0.034759 | -0.00053192 | 0.066849 | 0.0652 | -0.0034522 | -0.00016658 | -0.0024673 | -0.073242 | 63.1531 | -60.3195 | 62.8876 | -59.967 | -60.3287 | -0.027466 | -0.054932 | 63.1439 | -60.1639 | 63.1393 | -60.0449 | -60.1456 | -59.7107 | -0.25177 | 0.064087 | -0.20142 | 0.10071 | 60.0403 | -0.26093 | 60.2921 | -0.009155 | -0.09613 | 0.054932 | 0.050354 | 0.022888 | 0.35706 | -0.07782 | 0.45319 | 0.01831 | 0.35248 | 123.2071 | 0.11902 | 123.3032 | 123.4726 | 123.3078 | 123.2208 | 123.2117 | -123.4085 | -123.2529 | 122.9553 | 123.2071 | 59.9945 | 60.0128
465.5 | 123.3673 | -60.0403 | 63.0615 | -0.080566 | 0.0026981 | 0.063566 | 0.06134 | -0.0023649 | 0.0015658 | 0.00011527 | 0.013397 | 0.00096348 | 0.068558 | 0.061996 | -0.0008886 | -0.0023028 | -0.0018265 | -0.059509 | 63.1439 | -60.3241 | 62.9333 | -59.9167 | -60.3012 | -0.027466 | -0.027466 | 63.1256 | -60.1547 | 63.1668 | -60.0677 | -60.1593 | -59.7153 | -0.28381 | 0.082398 | -0.12817 | 0.1236 | 60.0128 | -0.26093 | 60.2966 | 0.022889 | -0.11444 | 0.064087 | 0.10529 | -0.027466 | 0.32501 | -0.11902 | 0.43945 | -0.004578 | 0.40741 | 123.2574 | 0.086975 | 123.3215 | 123.468 | 123.2803 | 123.1842 | 123.1659 | -123.3856 | -123.2162 | 122.9736 | 123.2071 | 59.9808 | 60.0128
466.4844 | 123.2895 | -60.0723 | 63.121 | -0.050049 | -7.913e-05 | 0.065275 | 0.063476 | -0.0015103 | -0.002493 | -0.00052553 | 0.0011902 | 0.00053628 | 0.065995 | 0.061355 | -0.001316 | -0.0031574 | 9.6064e-05 | -0.009155 | 63.2126 | -60.2966 | 62.8738 | -59.9762 | -60.3104 | 0.036621 | 0.041199 | 63.2172 | -60.1273 | 63.1165 | -60.0815 | -60.1959 | -59.7519 | -0.2243 | 0.091552 | -0.24719 | 0.096131 | 60.1089 | -0.23804 | 60.3333 | -0.013733 | -0.054931 | 0.09613 | -0.004578 | -0.009155 | 0.32044 | -0.1236 | 0.37537 | -0.068665 | 0.32043 | 123.1705 | 0.045776 | 123.2437 | 123.5092 | 123.3444 | 123.2849 | 123.2895 | -123.4177 | -123.2483 | 122.9462 | 123.1888 | 60.0632 | 60.1135
467.5469 | 123.381 | -60.0403 | 63.1027 | -0.080566 | 0.0016299 | 0.062925 | 0.063049 | 0.00062594 | -0.001852 | -0.0024481 | -0.023224 | -0.0016001 | 0.06514 | 0.065627 | -0.002384 | -0.0025164 | -0.00097194 | 0.045776 | 63.1714 | -60.2783 | 63.0157 | -59.7244 | -59.8709 | 0.018311 | 0.17395 | 63.1531 | -60.1547 | 63.208 | -59.9762 | -60.0998 | -59.6558 | -0.23804 | 0.068665 | -0.086975 | 0.31586 | 60.0586 | 0.16937 | 60.2966 | 0.40741 | -0.11444 | 0.050354 | 0.10529 | 0.064087 | 0.38452 | -0.059509 | 0.49896 | 0.054932 | 0.55389 | 123.2941 | 0.17853 | 123.3627 | 123.4497 | 123.3078 | 123.2117 | 123.1934 | -123.381 | -123.2574 | 123.056 | 123.2483 | 60.0861 | 60.2142
468.4844 | 123.3765 | -60.0494 | 63.1165 | -0.080566 | -0.00029273 | 0.063138 | 0.063049 | 0.00062594 | 0.0011386 | -0.0028753 | 0.0072936 | -0.00074552 | 0.064499 | 0.066695 | -0.0028112 | -0.0010212 | -0.0024673 | 0.036621 | 63.1668 | -60.3104 | 62.9791 | -59.8938 | -60.2188 | 0.09613 | 0.13275 | 63.1577 | -60.1181 | 63.1943 | -59.9991 | -60.0906 | -59.6878 | -0.26093 | 0.050354 | -0.13733 | 0.15564 | 60.1456 | -0.16937 | 60.4065 | 0.091553 | -0.068665 | 0.041199 | 0.07782 | 0.050354 | 0.36163 | -0.041199 | 0.4303 | 0.027466 | 0.41656 | 123.2895 | 0.11902 | 123.3124 | 123.4772 | 123.2758 | 123.2162 | 123.2071 | -123.4268 | -123.2346 | 123.0286 | 123.2437 | 60.0861 | 60.1822
469.5469 | 123.4039 | -60.0677 | 63.1165 | -0.072937 | -0.0020017 | 0.063138 | 0.064971 | -0.0030057 | 7.0582e-05 | -0.00095273 | 0.0072936 | -0.0018137 | 0.064286 | 0.065414 | 0.001034 | -0.0018756 | 0.0043687 | -0.068665 | 63.1348 | -60.3241 | 62.9105 | -59.9808 | -60.3104 | -0.013733 | -0.041199 | 63.1165 | -60.1501 | 63.1577 | -60.0403 | -60.1639 | -59.848 | -0.25635 | 0.018311 | -0.20599 | 0.086975 | 60.054 | -0.24262 | 60.3104 | 0.013733 | -0.082397 | 0 | 0.041199 | 0.027466 | 0.21973 | -0.09613 | 0.30212 | -0.013733 | 0.34332 | 123.2346 | 0.10986 | 123.3078 | 123.4589 | 123.2666 | 123.2025 | 123.1842 | -123.4406 | -123.2666 | 122.9782 | 123.2254 | 59.9991 | 60.0266
470.5 | 123.4222 | -60.0037 | 63.0981 | -0.03479 | 0.00098907 | 0.062498 | 0.061981 | 0.0012667 | -0.002493 | -0.0011663 | 0.031708 | -0.00010472 | 0.068131 | 0.067336 | -0.003025 | -0.0020892 | -0.00075834 | 0 | 63.1439 | -60.3195 | 62.9791 | -59.8892 | -60.228 | 0.09613 | 0.11444 | 63.1393 | -60.1318 | 63.208 | -59.9442 | -60.0632 | -59.6512 | -0.31586 | 0.045776 | -0.11902 | 0.11444 | 60.0998 | -0.2243 | 60.4156 | 0.091553 | -0.12817 | 0.041198 | 0.10986 | 0.059509 | 0.35248 | -0.059509 | 0.48065 | 0.068665 | 0.4303 | 123.2986 | 0.18768 | 123.3398 | 123.4634 | 123.2712 | 123.1476 | 123.143 | -123.4177 | -123.23 | 122.9828 | 123.2117 | 60.0037 | 60.1181
471.5469 | 123.2941 | -60.0769 | 63.1256 | -0.065308 | -0.0011471 | 0.063138 | 0.065399 | -0.0053555 | 0.00092498 | -0.0015935 | -0.035431 | 0.00010888 | 0.067063 | 0.066054 | -0.0002478 | -0.001662 | -0.0011855 | 0.018311 | 63.1989 | -60.3012 | 62.915 | -59.9579 | -60.3012 | 0.045776 | 0.054932 | 63.2034 | -60.1456 | 63.1256 | -60.0815 | -60.2097 | -59.7656 | -0.2243 | 0.073243 | -0.21057 | 0.11902 | 60.1227 | -0.2243 | 60.347 | 0 | -0.068665 | 0.07782 | 0 | -0.004578 | 0.31128 | -0.13275 | 0.37994 | -0.064087 | 0.34332 | 123.2162 | 0.064087 | 123.2712 | 123.5001 | 123.349 | 123.2758 | 123.2803 | -123.4268 | -123.2712 | 122.9919 | 123.2025 | 60.0952 | 60.1318
472.4844 | 123.3765 | -60.0769 | 63.1256 | -0.019531 | -0.0011471 | 0.064847 | 0.064544 | 0.0046847 | 0.0011386 | 0.00032907 | -0.065949 | -0.00031832 | 0.067276 | 0.068618 | -0.000675 | -0.00038018 | -0.0013991 | -0.018311 | 63.2034 | -60.3241 | 62.9059 | -59.9762 | -60.3149 | 0.013733 | 0.064087 | 63.1897 | -60.1547 | 63.1622 | -60.0723 | -60.1959 | -59.7061 | -0.24719 | 0.07782 | -0.21973 | 0.10071 | 60.0906 | -0.23804 | 60.3378 | 0.009156 | -0.07782 | 0.064087 | 0.036621 | 0.004577 | 0.37079 | -0.11902 | 0.44861 | -0.041199 | 0.3479 | 123.23 | 0.082397 | 123.317 | 123.5275 | 123.3444 | 123.2803 | 123.2666 | -123.4497 | -123.2803 | 122.9828 | 123.2391 | 60.0586 | 60.141
473.5469 | 123.3719 | -60.0494 | 63.1073 | -0.03479 | 0.00056187 | 0.064207 | 0.062622 | -0.0010831 | 7.0582e-05 | -0.00052553 | 0.016449 | 0.00032248 | 0.065995 | 0.067977 | -0.001316 | -0.0012348 | 0.0015915 | 0.027466 | 63.1851 | -60.2966 | 63.0203 | -59.8801 | -60.347 | 0.10529 | 0.12817 | 63.1668 | -60.1318 | 63.2126 | -59.9808 | -60.0723 | -59.6695 | -0.24719 | 0.07782 | -0.086975 | 0.16937 | 60.1547 | -0.29755 | 60.4019 | -0.050354 | -0.082398 | 0.059509 | 0.10528 | 0.068664 | 0.37994 | -0.022889 | 0.46234 | 0.059509 | 0.41656 | 123.317 | 0.15106 | 123.3444 | 123.4818 | 123.2986 | 123.2346 | 123.2162 | -123.4039 | -123.2391 | 123.0698 | 123.262 | 60.0769 | 60.1776
474.4844 | 123.2712 | -60.0769 | 63.1393 | 0.0033567 | 0.00013467 | 0.065061 | 0.065185 | -0.00065586 | -0.00035682 | 0.00032907 | -0.0018616 | 0.00096348 | 0.066635 | 0.065414 | 0.0001794 | -0.0020892 | -0.00054474 | -0.041199 | 63.2217 | -60.3241 | 62.8693 | -60.022 | -60.3104 | 0.086975 | -0.15564 | 63.2401 | -60.1685 | 63.089 | -60.0723 | -60.2051 | -59.7702 | -0.24719 | 0.082398 | -0.27008 | 0.054931 | 60.1639 | -0.23346 | 60.4111 | 0.013733 | -0.091553 | 0.10071 | -0.050354 | 0.004577 | 0.3067 | -0.12817 | 0.39825 | -0.036621 | 0.30212 | 123.1934 | 0.09613 | 123.2574 | 123.5458 | 123.4085 | 123.2986 | 123.317 | -123.4634 | -123.3078 | 122.9462 | 123.1659 | 60.0357 | 59.9213
475.5 | 123.2895 | -60.0723 | 63.1577 | 0.0033567 | -0.00029273 | 0.062284 | 0.065185 | 0.0029757 | 0.0030612 | 0.00075627 | -0.029327 | -0.00053192 | 0.067276 | 0.068618 | -3.4196e-05 | 0.00068782 | -0.0016129 | -0.036621 | 63.2034 | -60.3149 | 62.7731 | -59.967 | -60.4294 | -0.027466 | -0.009155 | 63.1805 | -60.1776 | 63.1027 | -60.0952 | -60.1868 | -59.761 | -0.24261 | 0.045776 | -0.38452 | 0.10529 | 60.0449 | -0.35705 | 60.2875 | -0.11444 | -0.10529 | 0.022888 | -0.054932 | -0.022888 | 0.31128 | -0.11444 | 0.41657 | -0.009156 | 0.3479 | 123.0881 | 0.082397 | 123.2803 | 123.5184 | 123.3582 | 123.2758 | 123.2529 | -123.4726 | -123.3353 | 122.8455 | 123.175 | 60.0357 | 60.0632
476.5469 | 123.4131 | -60.0037 | 63.0753 | -0.050049 | 0.0014163 | 0.065702 | 0.062622 | -0.0015103 | -0.0016384 | -0.00073913 | 0.046967 | 0.00010888 | 0.066208 | 0.058364 | -0.0015296 | -0.0010212 | 0.0013779 | 0 | 63.1714 | -60.3149 | 62.9745 | -59.8709 | -60.228 | 0.07782 | 0.17853 | 63.1485 | -60.141 | 63.2355 | -59.9533 | -60.0357 | -59.6191 | -0.31128 | 0.096131 | -0.10071 | 0.13275 | 60.0815 | -0.2243 | 60.3928 | 0.086975 | -0.13733 | 0.073243 | 0.16022 | 0.050354 | 0.38452 | -0.032044 | 0.52185 | 0.10529 | 0.44403 | 123.2895 | 0.18768 | 123.3765 | 123.4863 | 123.2895 | 123.175 | 123.1522 | -123.3902 | -123.2162 | 122.9782 | 123.2391 | 60.0037 | 60.1822
477.4844 | 123.3261 | -60.054 | 63.1027 | -0.042419 | 0.00077547 | 0.063779 | 0.064117 | -1.486e-05 | 0.0024204 | 0.0011835 | -0.096466 | 0.0020315 | 0.068131 | 0.061568 | -0.0017432 | 0.0023968 | -0.0035355 | -0.013733 | 63.1851 | -60.3378 | 62.9105 | -59.9716 | -60.3195 | -0.013733 | 0.10071 | 63.1577 | -60.1547 | 63.1622 | -60.0769 | -60.2188 | -59.7382 | -0.28381 | 0.082398 | -0.19226 | 0.082397 | 60.0403 | -0.2655 | 60.3241 | 0.018311 | -0.10071 | 0.054932 | 0.059509 | -0.022888 | 0.31586 | -0.1648 | 0.41656 | -0.064087 | 0.36621 | 123.2483 | 0.07782 | 123.317 | 123.5229 | 123.3124 | 123.2391 | 123.2117 | -123.4406 | -123.2574 | 122.9645 | 123.2162 | 60.0403 | 60.1547
478.5469 | 123.3994 | -60.0677 | 63.0569 | -0.095825 | 0.0014163 | 0.065061 | 0.063476 | 0.0010531 | -0.00014322 | -0.0018073 | 0.05307 | -0.0011727 | 0.066422 | 0.064986 | -0.0019568 | -0.0014484 | -0.00011754 | -0.073242 | 63.1851 | -60.3058 | 62.9059 | -59.9625 | -60.2966 | 0.013733 | -0.013733 | 63.1393 | -60.1639 | 63.1714 | -60.0082 | -60.1089 | -59.6832 | -0.23804 | 0.12817 | -0.15106 | 0.10529 | 60.0815 | -0.22888 | 60.3195 | 0.009155 | -0.09613 | 0.082397 | 0.11444 | 0.059509 | 0.38452 | -0.041199 | 0.48065 | 0.054931 | 0.34332 | 123.2117 | 0.15564 | 123.3353 | 123.4909 | 123.3032 | 123.2529 | 123.2071 | -123.3627 | -123.2208 | 122.9736 | 123.2391 | 59.9945 | 60.054
479.5 | 123.4314 | -60.022 | 63.176 | -0.072937 | 0.00056187 | 0.062711 | 0.06369 | -0.0015103 | 7.0582e-05 | 0.0011835 | 0.040863 | 0.00074988 | 0.069199 | 0.059005 | -0.0008886 | -0.0018756 | -0.0022537 | 0.018311 | 63.1531 | -60.3104 | 63.0203 | -59.8389 | -60.1913 | 0.10071 | 0.15564 | 63.1485 | -60.1135 | 63.2263 | -59.967 | -60.0632 | -59.6466 | -0.28839 | -0.022888 | -0.15564 | 0.18311 | 60.1227 | -0.16937 | 60.4111 | 0.11902 | -0.091552 | -0.027465 | 0.050354 | 0.054932 | 0.37537 | -0.041198 | 0.46692 | 0.050354 | 0.4715 | 123.3307 | 0.14648 | 123.3398 | 123.4634 | 123.262 | 123.175 | 123.1705 | -123.4863 | -123.2895 | 123.0423 | 123.2483 | 60.0403 | 60.1776
480.5625 | 123.3673 | -60.0494 | 63.0661 | -0.11108 | 0.0014163 | 0.062711 | 0.063049 | -0.0045011 | 0.00092498 | -0.0022345 | -0.0049134 | -0.00053192 | 0.063645 | 0.061141 | -0.0072974 | -0.0057208 | -0.00097194 | 0.027466 | 63.1805 | -60.2692 | 62.9883 | -59.8572 | -60.2142 | 0.10986 | 0.16937 | 63.1668 | -60.1181 | 63.3499 | -60.2829 | -60.1273 | -59.5917 | -0.21973 | 0.11444 | -0.07782 | 0.19226 | 60.1593 | -0.16479 | 60.379 | 0.054932 | -0.068665 | 0.10071 | 0.28381 | -0.23346 | 0.45776 | -0.07782 | 0.52643 | -0.009155 | 0.41199 | 123.2574 | -0.1648 | 123.468 | 123.4497 | 123.2849 | 123.23 | 123.2162 | -123.3353 | -123.1842 | 123.0377 | 123.3994 | 60.0769 | 60.2188
481.5 | 123.3444 | -60.054 | 63.0569 | -0.042419 | -0.00029273 | 0.063566 | 0.06668 | 0.0019077 | -0.0014248 | -0.00073913 | -0.059845 | 0.0018179 | 0.066208 | 0.066909 | -0.0028112 | 0.00047422 | 0.0015915 | -0.10071 | 63.1714 | -60.3516 | 62.8418 | -60.054 | -60.4156 | -0.10071 | -0.12817 | 63.1668 | -60.1685 | 63.121 | -60.1181 | -60.2463 | -59.7748 | -0.29755 | 0.11444 | -0.21515 | 0 | 59.9533 | -0.36163 | 60.2509 | -0.064087 | -0.11444 | 0.10986 | 0.064087 | -0.064087 | 0.27924 | -0.19226 | 0.39368 | -0.07782 | 0.29755 | 123.1934 | 0.050354 | 123.2895 | 123.5229 | 123.3353 | 123.2254 | 123.2208 | -123.4085 | -123.2254 | 122.8958 | 123.175 | 59.9533 | 59.9258
482.5469 | 123.3032 | -60.0586 | 63.1302 | -0.057678 | 0.0022709 | 0.065488 | 0.064971 | 0.0010531 | -0.0014248 | -0.00052553 | -0.032379 | 0.0018179 | 0.06514 | 0.064132 | -0.0002478 | -0.001662 | -0.0035355 | -0.16479 | 63.2309 | -60.3378 | 62.8693 | -59.9945 | -60.3287 | 0.013733 | 0.004578 | 63.2126 | -60.141 | 63.1256 | -60.0861 | -60.2097 | -59.7382 | -0.27924 | 0.10071 | -0.26093 | 0.064087 | 60.0723 | -0.27008 | 60.3516 | 0.009156 | -0.082397 | 0.082397 | -0.004578 | -0.027466 | 0.32043 | -0.15106 | 0.40283 | -0.068665 | 0.34332 | 123.2071 | 0.054931 | 123.2666 | 123.5687 | 123.3536 | 123.2895 | 123.2712 | -123.468 | -123.2712 | 122.9279 | 123.1842 | 59.8938 | 60.0632
483.4844 | 123.2666 | -60.0861 | 63.121 | -0.088196 | 0.00098907 | 0.064847 | 0.064117 | 0.00041234 | -0.0029202 | 0.0026789 | -0.075104 | 0.0016043 | 0.065995 | 0.06755 | -3.4196e-05 | 0.00090142 | -0.00011754 | -0.064087 | 63.1714 | -60.3836 | 62.851 | -60.0266 | -60.3653 | -0.086975 | -0.07782 | 63.1989 | -60.1868 | 63.089 | -60.1318 | -60.2509 | -59.7794 | -0.29755 | 0.050354 | -0.27008 | 0.05951 | 59.9991 | -0.27923 | 60.2966 | 0.018311 | -0.10071 | 0.07782 | -0.032044 | -0.045776 | 0.3067 | -0.16479 | 0.40741 | -0.064086 | 0.35706 | 123.2346 | 0.054932 | 123.2758 | 123.555 | 123.3856 | 123.2574 | 123.2849 | -123.5046 | -123.3078 | 122.937 | 123.175 | 60.022 | 60.0082
484.4844 | 123.2986 | -60.0769 | 63.0981 | -0.042419 | -0.00071993 | 0.064207 | 0.064544 | -0.00044226 | -0.001852 | 0.00075627 | -0.041534 | 0.0030997 | 0.066635 | 0.063064 | 0.0008204 | -0.00038018 | 0.00052346 | -0.032043 | 63.2263 | -60.3012 | 62.8693 | -60.0128 | -60.347 | 0.013733 | 0.022888 | 63.2263 | -60.1364 | 62.9562 | -60.0174 | -60.26 | -59.7656 | -0.2243 | 0.12817 | -0.22888 | 0.064087 | 60.0906 | -0.27008 | 60.3149 | -0.045777 | -0.05951 | 0.12817 | -0.14191 | 0.059509 | 0.31128 | -0.18311 | 0.37079 | -0.1236 | 0.28839 | 123.1705 | 0.11902 | 123.0927 | 123.5275 | 123.3627 | 123.3032 | 123.3032 | -123.3994 | -123.2346 | 122.9462 | 123.0331 | 60.0449 | 60.0998
485.5781 | 123.2437 | -60.0998 | 63.0798 | -0.011902 | 0.00056187 | 0.06442 | 0.064544 | 0.0027621 | -0.002493 | -0.00052553 | -0.084259 | 0.00010888 | 0.067704 | 0.070113 | -0.0015296 | 0.001756 | -0.0022537 | 0 | 63.1851 | -60.347 | 62.8922 | -59.9625 | -60.3058 | -0.004578 | 0.032043 | 63.1897 | -60.1364 | 63.1531 | -60.0677 | -60.1868 | -59.7427 | -0.24719 | 0.10529 | -0.18768 | 0.13733 | 60.0952 | -0.20599 | 60.3424 | 0.041199 | -0.036622 | 0.10986 | 0.073242 | 0.032043 | 0.35706 | -0.086976 | 0.39368 | -0.050354 | 0.38452 | 123.2391 | 0.068665 | 123.2895 | 123.5321 | 123.3261 | 123.2849 | 123.2895 | -123.4268 | -123.2162 | 122.9919 | 123.2529 | 60.0998 | 60.1318
486.4844 | 123.3307 | -60.0677 | 63.1302 | -0.072937 | 0.00034827 | 0.063566 | 0.064117 | 0.0016939 | 0.00028418 | -0.0013799 | -0.029327 | 0.0011771 | 0.066849 | 0.060927 | -0.000675 | -0.0010212 | 0.0018051 | -0.036621 | 63.2126 | -60.3378 | 62.8601 | -60.0082 | -60.3287 | 0.009155 | 0.018311 | 63.1943 | -60.1547 | 63.1256 | -60.0677 | -60.2005 | -59.7519 | -0.27008 | 0.082397 | -0.27008 | 0.059509 | 60.0769 | -0.26093 | 60.347 | 0.009156 | -0.086975 | 0.064087 | -0.004578 | 0 | 0.31586 | -0.13275 | 0.40283 | -0.045776 | 0.32959 | 123.1979 | 0.086975 | 123.2803 | 123.5504 | 123.349 | 123.2803 | 123.262 | -123.468 | -123.2849 | 122.9279 | 123.1934 | 60.0311 | 60.0861
487.5469 | 123.381 | -60.0449 | 63.1119 | 0.018616 | 0.0016299 | 0.063993 | 0.062408 | 0.0010531 | 0.00071138 | -0.00095273 | 0.050018 | 0.00032248 | 0.065995 | 0.06755 | -0.0017432 | -0.001662 | 0.00095066 | -0.027466 | 63.1577 | -60.2875 | 62.9608 | -59.8892 | -60.2371 | 0.091553 | 0.11902 | 63.1805 | -60.1227 | 63.1851 | -59.9945 | -60.0861 | -59.6786 | -0.24262 | 0.045777 | -0.15106 | 0.15564 | 60.1364 | -0.19226 | 60.379 | 0.050354 | -0.07782 | 0.068665 | 0.073243 | 0.050354 | 0.36621 | -0.041199 | 0.44403 | 0.036621 | 0.39825 | 123.2483 | 0.12817 | 123.3078 | 123.4451 | 123.3032 | 123.2025 | 123.2254 | -123.3994 | -123.2346 | 123.0057 | 123.23 | 60.0174 | 60.1639
488.4844 | 123.317 | -60.0311 | 63.1393 | -0.050049 | -0.00029273 | 0.062284 | 0.065399 | 0.0019077 | -0.00057042 | -0.00073913 | -0.0079652 | 0.00010888 | 0.066849 | 0.064773 | -0.0002478 | 0.001115 | -0.0018265 | -0.07782 | 63.2172 | -60.3058 | 62.8281 | -60.0449 | -60.2966 | -0.009155 | 0.013733 | 63.2034 | -60.1456 | 63.1027 | -60.0769 | -60.2051 | -59.7473 | -0.27466 | 0.07782 | -0.31128 | -0.013733 | 60.022 | -0.2655 | 60.2966 | 0.009155 | -0.11444 | 0.064087 | -0.036621 | -0.045776 | 0.28381 | -0.17395 | 0.39825 | -0.059509 | 0.26093 | 123.1338 | 0.068665 | 123.2483 | 123.5229 | 123.349 | 123.2483 | 123.2346 | -123.4451 | -123.2849 | 122.8592 | 123.1338 | 59.9533 | 60.0449
489.5 | 123.381 | -60.0403 | 63.0432 | -0.057678 | 0.00098907 | 0.063779 | 0.06369 | -0.0019377 | 0.00049778 | 0.00032907 | -0.035431 | 0.00032248 | 0.066635 | 0.0652 | 0.0001794 | -0.00016658 | 0.0026597 | -0.091553 | 63.1256 | -60.3561 | 62.8967 | -59.9762 | -60.3149 | -0.045776 | -0.064087 | 63.1256 | -60.1639 | 63.1851 | -60.0449 | -60.1593 | -59.6832 | -0.31586 | 0.082397 | -0.14648 | 0.064087 | 59.9945 | -0.27466 | 60.3104 | 0.041199 | -0.1236 | 0.082397 | 0.14191 | -0.004578 | 0.35706 | -0.11902 | 0.48065 | 0.004577 | 0.37994 | 123.2529 | 0.11902 | 123.349 | 123.4818 | 123.2895 | 123.1659 | 123.1659 | -123.3994 | -123.2071 | 122.937 | 123.2254 | 59.9487 | 59.9762
490.5625 | 123.3032 | -60.0769 | 63.1348 | -0.027161 | -0.00029273 | 0.062711 | 0.062835 | -0.0015103 | -0.0012112 | -0.00073913 | 0.016449 | -0.00031832 | 0.066849 | 0.058364 | -0.001316 | 0.00047422 | 0.0015915 | 0.009155 | 63.1668 | -60.3012 | 62.9196 | -59.9579 | -60.2783 | 0.054932 | 0.064087 | 63.1989 | -60.1456 | 63.1485 | -60.0769 | -60.1822 | -59.761 | -0.2243 | 0.032043 | -0.21515 | 0.11902 | 60.1318 | -0.20142 | 60.3561 | 0.022888 | -0.068665 | 0.064087 | 0.013733 | 0 | 0.31586 | -0.10529 | 0.38452 | -0.036621 | 0.34332 | 123.2208 | 0.068665 | 123.2941 | 123.468 | 123.3444 | 123.2437 | 123.2758 | -123.436 | -123.2803 | 122.9965 | 123.2254 | 60.0861 | 60.141
491.4844 | 123.2758 | -60.0723 | 63.1302 | -0.03479 | -0.0020017 | 0.062284 | 0.064758 | 0.0025485 | 0.00028418 | -0.0011663 | -0.075104 | 0.00032248 | 0.066208 | 0.070327 | -0.001316 | -0.00016658 | -0.00011754 | -0.050354 | 63.1851 | -60.3607 | 62.8601 | -60.0266 | -60.3882 | -0.082397 | -0.054932 | 63.1897 | -60.173 | 63.0936 | -60.1501 | -60.2463 | -59.7839 | -0.28839 | 0.054932 | -0.27008 | 0.045777 | 59.9899 | -0.31586 | 60.2783 | -0.027466 | -0.10071 | 0.059509 | -0.036621 | -0.077819 | 0.28839 | -0.17395 | 0.3891 | -0.073242 | 0.33417 | 123.2208 | 0.022889 | 123.2666 | 123.5458 | 123.3627 | 123.2574 | 123.262 | -123.4909 | -123.3032 | 122.9324 | 123.1659 | 60.022 | 60.0174
492.4844 | 123.3444 | -60.0586 | 63.1165 | -0.03479 | -0.00029273 | 0.063352 | 0.065399 | 0.00062594 | -0.00057042 | -0.00052553 | -0.026276 | 0.0013907 | 0.067063 | 0.062209 | -0.0017432 | -0.0014484 | 0.0013779 | -0.004578 | 63.2217 | -60.3333 | 62.9013 | -59.9533 | -60.3012 | 0.041199 | 0.073242 | 63.1805 | -60.1364 | 63.1348 | -60.0723 | -60.1639 | -59.7244 | -0.27466 | 0.10529 | -0.21515 | 0.10529 | 60.0998 | -0.24261 | 60.3745 | 0.032044 | -0.07782 | 0.064087 | 0.018311 | -0.013733 | 0.33417 | -0.10529 | 0.41199 | -0.027465 | 0.37994 | 123.2346 | 0.064087 | 123.2712 | 123.555 | 123.317 | 123.2803 | 123.2391 | -123.4497 | -123.2529 | 122.9599 | 123.1934 | 60.054 | 60.1318
493.5 | 123.3398 | -60.0906 | 63.0569 | -0.027161 | -0.00093353 | 0.063566 | 0.067321 | 0.00062594 | 0.00028418 | -0.0020209 | -0.047638 | 0.0011771 | 0.06749 | 0.067977 | -0.0034522 | -0.0014484 | 0.00052346 | -0.11902 | 63.1668 | -60.3607 | 62.851 | -60.0357 | -60.4019 | -0.10071 | -0.13275 | 63.121 | -60.1822 | 63.1393 | -60.0952 | -60.2097 | -59.7382 | -0.27008 | 0.10986 | -0.20599 | 0.054931 | 59.9899 | -0.31128 | 60.26 | -0.041199 | -0.091553 | 0.064087 | 0.082397 | -0.004578 | 0.35248 | -0.11902 | 0.44403 | -0.027466 | 0.32501 | 123.2117 | 0.086975 | 123.3215 | 123.5275 | 123.3032 | 123.2574 | 123.2117 | -123.4177 | -123.2391 | 122.9416 | 123.23 | 59.9716 | 59.9579
494.5469 | 123.3261 | -60.0677 | 63.1073 | -0.065308 | 0.00056187 | 0.061002 | 0.064758 | 0.0010531 | -0.00014322 | -9.8328e-05 | 0.004242 | 0.0033133 | 0.066849 | 0.062636 | -0.0008886 | -0.0012348 | 0.0020187 | -0.041199 | 63.2217 | -60.3333 | 62.8601 | -59.9899 | -60.3378 | 0.013733 | 0.018311 | 63.2217 | -60.1593 | 63.1943 | -59.9304 | -60.3973 | -59.9442 | -0.2655 | 0.11444 | -0.24719 | 0.07782 | 60.0815 | -0.27008 | 60.347 | -0.004578 | -0.091553 | 0.11444 | 0.086975 | 0.13733 | 0.1236 | -0.32959 | 0.21515 | -0.23804 | 0.34332 | 123.1934 | 0.22888 | 123.3536 | 123.555 | 123.381 | 123.2895 | 123.2895 | -123.4406 | -123.2666 | 122.9279 | 123.262 | 60.0266 | 60.0861
495.5 | 123.349 | -60.054 | 63.0798 | -0.050049 | 0.0018435 | 0.062925 | 0.061553 | -0.00022866 | 0.00049778 | 0.00032907 | 0.031708 | -0.00053192 | 0.068558 | 0.063705 | -0.003025 | -0.0020892 | -0.00011754 | -0.09613 | 63.1714 | -60.3241 | 62.915 | -59.9854 | -60.3333 | -0.018311 | -0.045776 | 63.1256 | -60.1639 | 63.1348 | -60.0632 | -60.1456 | -59.697 | -0.27008 | 0.091553 | -0.16479 | 0.068664 | 60.0357 | -0.27924 | 60.3058 | -0.009155 | -0.10986 | 0.045776 | 0.054932 | -0.009155 | 0.35706 | -0.091553 | 0.46692 | 0.01831 | 0.33875 | 123.2391 | 0.10071 | 123.2986 | 123.4955 | 123.2895 | 123.2254 | 123.1796 | -123.4039 | -123.2437 | 122.9691 | 123.1888 | 59.9579 | 60.0082
496.5469 | 123.3307 | -60.054 | 63.1256 | -0.050049 | 0.0029117 | 0.061857 | 0.062622 | -0.0034329 | 0.0011386 | -0.0018073 | 0.028656 | 0.00074988 | 0.067276 | 0.065414 | -0.0015296 | -0.0014484 | -0.0033219 | 0.027466 | 63.1851 | -60.2783 | 62.9425 | -59.9075 | -60.2509 | 0.091553 | 0.10529 | 63.1668 | -60.1364 | 63.1256 | -60.0494 | -60.1639 | -59.729 | -0.2243 | 0.05951 | -0.18311 | 0.14648 | 60.1456 | -0.19684 | 60.3699 | 0.027466 | -0.082398 | 0.041199 | 0 | 0.004578 | 0.32501 | -0.10986 | 0.40741 | -0.027465 | 0.37079 | 123.2208 | 0.086976 | 123.262 | 123.4634 | 123.3032 | 123.2391 | 123.2208 | -123.4039 | -123.262 | 122.9965 | 123.1796 | 60.0815 | 60.1593
497.5 | 123.2803 | -60.0861 | 63.0661 | -0.042419 | 0.00056187 | 0.063993 | 0.065826 | -0.00086946 | -0.0020658 | 0.0016107 | -0.05069 | 0.0011771 | 0.067276 | 0.066482 | -0.0019568 | 0.001115 | -0.00054474 | -0.36163 | 63.1256 | -60.4019 | 62.8235 | -60.0906 | -60.3699 | -0.10986 | -0.11902 | 63.1577 | -60.1639 | 63.0844 | -60.141 | -60.2509 | -59.7748 | -0.31586 | 0.059509 | -0.24262 | -0.004577 | 59.9762 | -0.28381 | 60.2921 | 0.032044 | -0.077819 | 0.091553 | 0.018311 | -0.054931 | 0.31128 | -0.16479 | 0.3891 | -0.086975 | 0.31128 | 123.2254 | 0.022888 | 123.2483 | 123.5275 | 123.3215 | 123.2117 | 123.2437 | -123.468 | -123.23 | 122.9095 | 123.1705 | 59.7244 | 59.967
498.4844 | 123.3582 | -60.0723 | 63.1119 | -0.0042723 | -7.913e-05 | 0.065702 | 0.065612 | -0.0019377 | 0.0017794 | 0.0028925 | -0.014069 | 0.0013907 | 0.066422 | 0.071395 | -0.0021704 | 0.001115 | -0.00097194 | -0.027466 | 63.2172 | -60.3149 | 62.883 | -60.022 | -60.3241 | 0.013733 | 0.022888 | 63.1805 | -60.1593 | 63.1302 | -60.0632 | -60.1868 | -59.7336 | -0.24261 | 0.10529 | -0.22888 | 0.050354 | 60.0861 | -0.25177 | 60.3287 | -0.009156 | -0.086975 | 0.068665 | 0.018311 | 0.009156 | 0.33875 | -0.11444 | 0.42572 | -0.027466 | 0.29297 | 123.1979 | 0.096131 | 123.2895 | 123.5321 | 123.3398 | 123.2895 | 123.2529 | -123.4268 | -123.2712 | 122.9553 | 123.2025 | 60.0449 | 60.0952
499.5469 | 123.317 | -60.0586 | 63.1485 | -0.0042723 | 0.00056187 | 0.061643 | 0.064117 | -0.00065586 | 0.00071138 | -0.00031193 | 0.071381 | -0.00053192 | 0.066849 | 0.064345 | -0.0011022 | -0.00016658 | -0.0013991 | -0.045776 | 63.2263 | -60.3195 | 62.8555 | -60.0037 | -60.3424 | 0.027466 | -0.16937 | 63.2172 | -60.1547 | 63.0798 | -60.0998 | -60.2051 | -59.761 | -0.26093 | 0.077819 | -0.29297 | 0.054932 | 60.0861 | -0.28381 | 60.347 | -0.022888 | -0.09613 | 0.068664 | -0.068665 | -0.041198 | 0.29755 | -0.14648 | 0.39368 | -0.050354 | 0.31586 | 123.175 | 0.054932 | 123.2346 | 123.5458 | 123.3719 | 123.2849 | 123.2758 | -123.468 | -123.3032 | 122.9141 | 123.1384 | 60.0128 | 59.8892
500.5 | 123.2986 | -60.0952 | 63.0936 | -0.065308 | 0.00056187 | 0.062284 | 0.064331 | 0.0025485 | -0.00099762 | -0.00031193 | -0.05069 | 0.0026725 | 0.066849 | 0.067336 | -0.0011022 | -0.0014484 | 0.0020187 | -0.10529 | 63.1668 | -60.3882 | 62.8189 | -60.0586 | -60.4156 | -0.13275 | -0.41199 | 63.1119 | -60.2005 | 63.0615 | -60.1227 | -60.2554 | -59.761 | -0.29297 | 0.073242 | -0.27466 | 0.036621 | 59.9625 | -0.32043 | 60.2554 | -0.027465 | -0.10528 | 0.01831 | -0.032044 | -0.027466 | 0.33417 | -0.16022 | 0.43945 | -0.054932 | 0.32959 | 123.2071 | 0.077819 | 123.262 | 123.555 | 123.3124 | 123.262 | 123.2071 | -123.4818 | -123.2941 | 122.9141 | 123.1567 | 59.9899 | 59.6832
501.4844 | 123.4131 | -60.0586 | 63.0661 | -0.10345 | -0.0013607 | 0.063138 | 0.065185 | 0.00019874 | -0.00078402 | 0.0035333 | -0.023224 | 0.0013907 | 0.066208 | 0.06285 | -0.0002478 | -0.00016658 | 0.0020187 | -0.10071 | 63.1531 | -60.3607 | 62.8967 | -59.967 | -60.3561 | -0.068665 | -0.064087 | 63.1256 | -60.1822 | 63.1851 | -60.054 | -60.1501 | -59.6786 | -0.30212 | 0.086975 | -0.16937 | 0.091553 | 59.9899 | -0.29755 | 60.2921 | 0.004578 | -0.1236 | 0.059509 | 0.11902 | 0.004578 | 0.37994 | -0.091552 | 0.50354 | 0.032044 | 0.39368 | 123.2574 | 0.12817 | 123.3673 | 123.5138 | 123.3078 | 123.2117 | 123.1842 | -123.4268 | -123.2483 | 122.9553 | 123.2437 | 59.9579 | 59.9945
502.4844 | 123.3124 | -60.0586 | 63.1302 | 0.010986 | -0.00093353 | 0.062498 | 0.064758 | 0.0051119 | 0.0011386 | 0.00096987 | 0.0011902 | -0.00010472 | 0.066849 | 0.061996 | -0.0004614 | -0.00038018 | -0.0013991 | -0.018311 | 63.2034 | -60.3241 | 62.8967 | -60.054 | -60.3836 | 0.004578 | 0.022888 | 63.2034 | -60.1593 | 63.0981 | -60.0906 | -60.1913 | -59.7565 | -0.2655 | 0.073242 | -0.23346 | 0.004578 | 60.0632 | -0.32501 | 60.3287 | -0.059509 | -0.10071 | 0.073242 | -0.032043 | -0.032043 | 0.30212 | -0.13275 | 0.40283 | -0.032043 | 0.27008 | 123.2208 | 0.068665 | 123.2574 | 123.5275 | 123.3627 | 123.262 | 123.262 | -123.4543 | -123.2895 | 122.9553 | 123.1567 | 60.0403 | 60.0815
503.4844 | 123.3444 | -60.0494 | 63.1165 | -0.019531 | -0.00071993 | 0.064847 | 0.065612 | -0.0010831 | 0.00071138 | -0.0024481 | -0.059845 | 0.0013907 | 0.065995 | 0.066268 | -0.0032386 | -0.00080758 | -0.0022537 | -0.009155 | 63.1989 | -60.3333 | 62.8967 | -59.9487 | -60.3195 | 0.004578 | 0.059509 | 63.1805 | -60.1547 | 63.1485 | -60.0677 | -60.173 | -59.7244 | -0.28381 | 0.082398 | -0.21973 | 0.10071 | 60.054 | -0.27008 | 60.3378 | 0.013733 | -0.10529 | 0.064087 | 0.032044 | -0.018311 | 0.32501 | -0.1236 | 0.4303 | -0.018311 | 0.38452 | 123.23 | 0.086975 | 123.3032 | 123.5321 | 123.3353 | 123.2483 | 123.23 | -123.4497 | -123.2712 | 122.9462 | 123.1979 | 60.0403 | 60.1089
504.5469 | 123.2986 | -60.0998 | 63.1393 | -0.027161 | 0.0016299 | 0.060575 | 0.064971 | -0.0023649 | -0.00078402 | 0.0020379 | -0.0049134 | 0.00010888 | 0.068344 | 0.064559 | -0.0002478 | -0.0012348 | 0.0013779 | -0.050354 | 63.2446 | -60.2783 | 62.8006 | -60.0311 | -60.3149 | -0.018311 | 0.027466 | 63.1851 | -60.1547 | 63.1027 | -60.0723 | -60.2005 | -59.7565 | -0.17853 | 0.10529 | -0.33874 | 0.068664 | 60.0815 | -0.21515 | 60.26 | -0.036621 | -0.054932 | 0.045777 | -0.036621 | 0.027465 | 0.34332 | -0.10071 | 0.39825 | -0.045776 | 0.24719 | 123.0789 | 0.082397 | 123.2574 | 123.5229 | 123.3398 | 123.3444 | 123.2849 | -123.4177 | -123.2941 | 122.9004 | 123.2025 | 60.0494 | 60.1273
505.5 | 123.3673 | -60.0815 | 63.0661 | -0.10345 | -0.0013607 | 0.062925 | 0.064331 | 0.00041234 | 0.00092498 | -0.00095273 | 0.050018 | 0.0011771 | 0.067063 | 0.063918 | -0.0011022 | -0.0010212 | 0.0030869 | -0.09613 | 63.1348 | -60.3195 | 62.8922 | -59.9625 | -60.3333 | -0.045776 | -0.059509 | 63.1393 | -60.1639 | 63.1256 | -60.0632 | -60.1364 | -59.7061 | -0.23804 | 0.068665 | -0.17395 | 0.11902 | 60.0357 | -0.25177 | 60.2737 | -0.013733 | -0.082397 | 0.073242 | 0.059509 | 0.018311 | 0.37537 | -0.054932 | 0.45776 | 0.027465 | 0.35706 | 123.2117 | 0.10071 | 123.2895 | 123.4543 | 123.3032 | 123.2162 | 123.2208 | -123.3856 | -123.23 | 122.9736 | 123.2071 | 59.9854 | 60.022
506.5469 | 123.3948 | -60.022 | 63.0753 | -0.065308 | 0.00013467 | 0.063993 | 0.064331 | -0.0021513 | -0.00078402 | -0.0011663 | 0.046967 | -0.00074552 | 0.066849 | 0.066054 | -0.0002478 | -0.003371 | 0.0013779 | -0.050354 | 63.1439 | -60.3104 | 62.9013 | -59.9579 | -60.2829 | 0.027466 | 0.004578 | 63.1393 | -60.141 | 63.176 | -59.9945 | -60.0998 | -59.6695 | -0.28839 | 0.068665 | -0.17395 | 0.064087 | 60.0494 | -0.26093 | 60.3378 | 0.027466 | -0.11902 | 0.064087 | 0.10071 | 0.027466 | 0.35248 | -0.077819 | 0.4715 | 0.041199 | 0.35248 | 123.2117 | 0.14648 | 123.317 | 123.4543 | 123.2803 | 123.1659 | 123.1613 | -123.3856 | -123.2162 | 122.9233 | 123.1979 | 59.9716 | 60.0266
507.5 | 123.349 | -60.0861 | 63.0478 | -0.057678 | 0.0029117 | 0.062925 | 0.064971 | -0.0021513 | -0.0031338 | 0.0013971 | -0.059845 | 0.00096348 | 0.065995 | 0.067123 | -0.0032386 | -0.0010212 | -0.0041763 | -0.10529 | 63.1897 | -60.3516 | 62.8601 | -60.0266 | -60.4065 | -0.10071 | -0.12817 | 63.1485 | -60.1685 | 63.1302 | -60.0952 | -60.2005 | -59.729 | -0.2655 | 0.14191 | -0.18768 | 0.05951 | 59.9854 | -0.32043 | 60.2509 | -0.054932 | -0.082397 | 0.10071 | 0.082397 | -0.009155 | 0.35706 | -0.11444 | 0.43945 | -0.032043 | 0.32501 | 123.2117 | 0.073242 | 123.2986 | 123.5413 | 123.317 | 123.2758 | 123.2346 | -123.3994 | -123.2162 | 122.9462 | 123.2162 | 59.9808 | 59.9579
508.5469 | 123.349 | -60.0174 | 63.0981 | -0.042419 | 0.0012027 | 0.068052 | 0.064758 | 0.00019874 | -0.00035682 | 0.00054267 | 0.028656 | -0.00031832 | 0.066635 | 0.066909 | -0.0017432 | -0.0012348 | 0.0022323 | -0.054932 | 63.1622 | -60.2966 | 62.9654 | -59.8938 | -60.2371 | 0.10071 | 0.13275 | 63.1668 | -60.1456 | 63.1805 | -59.9899 | -60.0952 | -59.6786 | -0.27924 | 0.064086 | -0.13275 | 0.1236 | 60.1181 | -0.21973 | 60.3973 | 0.059509 | -0.12817 | 0.068664 | 0.082397 | 0.027466 | 0.33875 | -0.07782 | 0.46692 | 0.050354 | 0.40283 | 123.262 | 0.15564 | 123.3261 | 123.4589 | 123.3124 | 123.1796 | 123.1842 | -123.3948 | -123.2437 | 122.9828 | 123.1979 | 59.9625 | 60.1501
509.4844 | 123.3124 | -60.0769 | 63.121 | -0.027161 | 0.00013467 | 0.063566 | 0.065185 | 0.00062594 | 7.0582e-05 | -0.0015935 | -0.062897 | 0.0028861 | 0.067276 | 0.065627 | -0.0028112 | 4.7018e-05 | 0.0039413 | -0.018311 | 63.1851 | -60.3607 | 62.8967 | -59.9716 | -60.3241 | -0.027466 | 0.004578 | 63.176 | -60.1593 | 63.1027 | -60.1089 | -60.228 | -59.7565 | -0.28381 | 0.064087 | -0.2243 | 0.10529 | 60.0494 | -0.24719 | 60.3333 | 0.036621 | -0.082398 | 0.054931 | -0.018311 | -0.032044 | 0.32043 | -0.15106 | 0.40283 | -0.068664 | 0.3891 | 123.2574 | 0.050354 | 123.262 | 123.5458 | 123.3353 | 123.262 | 123.2529 | -123.4818 | -123.2803 | 122.9736 | 123.1796 | 60.0586 | 60.0815
510.5625 | 123.4039 | -60.0494 | 63.0844 | -0.095825 | 0.00056187 | 0.064634 | 0.062408 | 0.0021213 | 0.00071138 | -0.0026617 | 0.037811 | -0.00053192 | 0.065354 | 0.064345 | -0.000675 | -0.001662 | 0.00095066 | -0.10071 | 63.1668 | -60.3104 | 62.9059 | -59.9625 | -60.2966 | 0.009155 | -0.004578 | 63.1348 | -60.141 | 63.1668 | -60.0128 | -60.1089 | -59.6741 | -0.26093 | 0.082397 | -0.17853 | 0.086975 | 60.0586 | -0.24719 | 60.3195 | 0.013733 | -0.091553 | 0.050354 | 0.082397 | 0.036621 | 0.37537 | -0.05951 | 0.46692 | 0.032043 | 0.3479 | 123.2162 | 0.12817 | 123.3078 | 123.4772 | 123.2758 | 123.2162 | 123.1842 | -123.3948 | -123.2254 | 122.9553 | 123.2162 | 59.9487 | 60.0449
511.5 | 123.4222 | -60.054 | 63.0707 | -0.065308 | 0.0026981 | 0.064634 | 0.063049 | 0.00019874 | -0.00057042 | -0.0030889 | 0.037811 | 0.0020315 | 0.066422 | 0.069686 | -0.0015296 | 0.00026062 | -0.0018265 | -0.045776 | 63.1622 | -60.3195 | 62.9562 | -59.9213 | -60.26 | 0.054932 | 0.068665 | 63.1348 | -60.1318 | 63.1851 | -59.9899 | -60.0723 | -59.6466 | -0.2655 | 0.091552 | -0.11444 | 0.13275 | 60.1089 | -0.20599 | 60.3745 | 0.059509 | -0.07782 | 0.064087 | 0.11444 | 0.064087 | 0.40741 | -0.018311 | 0.48523 | 0.059509 | 0.39825 | 123.2758 | 0.14191 | 123.317 | 123.4818 | 123.2666 | 123.2162 | 123.1888 | -123.3902 | -123.2025 | 123.0103 | 123.2391 | 60.0082 | 60.1227
512.4844 | 123.3078 | -60.0403 | 63.1256 | -0.057678 | -0.00050633 | 0.062925 | 0.062622 | 0.0027621 | 0.00028418 | 0.00075627 | -0.038483 | 0.0013907 | 0.067917 | 0.067336 | -0.002384 | -0.0010212 | -0.00033114 | -0.018311 | 63.2172 | -60.3287 | 62.8876 | -59.9854 | -60.3012 | 0.013733 | 0.041199 | 63.2034 | -60.1364 | 63.1393 | -60.0494 | -60.173 | -59.7427 | -0.28839 | 0.091553 | -0.23804 | 0.054931 | 60.054 | -0.26093 | 60.3424 | 0.027466 | -0.096131 | 0.07782 | 0.013733 | -0.009155 | 0.29755 | -0.13275 | 0.39368 | -0.036621 | 0.34332 | 123.2162 | 0.086976 | 123.2758 | 123.5458 | 123.3398 | 123.2574 | 123.2437 | -123.4543 | -123.262 | 122.9279 | 123.1796 | 60.022 | 60.0815
513.4844 | 123.2803 | -60.0769 | 63.089 | -0.019531 | 0.00098907 | 0.065702 | 0.063903 | -0.00065586 | -0.00078402 | -0.0035163 | -0.087311 | 0.00074988 | 0.067276 | 0.072036 | -0.0017432 | -0.0010212 | 0.00030966 | -0.073242 | 63.176 | -60.347 | 62.851 | -60.0174 | -60.3653 | -0.086975 | -0.07782 | 63.1897 | -60.173 | 63.0798 | -60.1273 | -60.26 | -59.7656 | -0.27008 | 0.086975 | -0.23804 | 0.059509 | 59.9899 | -0.28839 | 60.26 | -0.01831 | -0.096131 | 0.10071 | -0.009155 | -0.050354 | 0.31128 | -0.18311 | 0.40741 | -0.086975 | 0.32959 | 123.1979 | 0.045777 | 123.2529 | 123.5229 | 123.3627 | 123.2529 | 123.2666 | -123.436 | -123.262 | 122.9279 | 123.1567 | 60.0037 | 59.9991
514.5469 | 123.4039 | -60.0494 | 63.0615 | -0.03479 | 0.0014163 | 0.064847 | 0.062194 | -0.0019377 | 0.0015658 | -0.00052553 | 0.034759 | -0.00010472 | 0.066635 | 0.065627 | -0.0004614 | 0.00068782 | 0.00030966 | -0.068665 | 63.1485 | -60.3149 | 62.8876 | -59.9716 | -60.3104 | -0.004578 | -0.050354 | 63.1439 | -60.1456 | 63.1439 | -60.0311 | -60.1868 | -59.7153 | -0.2655 | 0.086976 | -0.17395 | 0.077819 | 60.0449 | -0.26093 | 60.3104 | 0.004577 | -0.096131 | 0.082398 | 0.082398 | 0.01831 | 0.33417 | -0.13733 | 0.4303 | -0.041199 | 0.34332 | 123.2025 | 0.11444 | 123.2895 | 123.4634 | 123.2895 | 123.1979 | 123.1934 | -123.3765 | -123.2071 | 122.937 | 123.1934 | 59.9808 | 59.9991
515.5 | 123.381 | -60.0357 | 63.0798 | -0.050049 | 0.00098907 | 0.064634 | 0.061767 | 0.0010531 | -0.004202 | -0.00073913 | 0.24228 | 0.00096348 | 0.068985 | 0.062209 | -0.0017432 | 0.00026062 | -0.0056717 | 0.022888 | 63.1943 | -60.3012 | 62.9883 | -59.8343 | -60.228 | 0.11902 | -0.050354 | 63.1714 | -60.1273 | 63.2172 | -60.0266 | -60.0677 | -59.6512 | -0.2655 | 0.11444 | -0.091553 | 0.20142 | 60.1547 | -0.19226 | 60.4202 | 0.073242 | -0.091552 | 0.091553 | 0.13733 | 0.009156 | 0.38452 | -0.032043 | 0.47607 | 0.059509 | 0.46692 | 123.2895 | 0.10071 | 123.3444 | 123.4955 | 123.2986 | 123.23 | 123.2071 | -123.381 | -123.2071 | 123.024 | 123.2529 | 60.0586 | 59.9854
516.5625 | 123.3673 | -60.0632 | 63.0661 | -0.088196 | 0.0018435 | 0.066343 | 0.063476 | -1.486e-05 | -0.0027066 | 0.0028925 | 0.004242 | -0.00053192 | 0.064713 | 0.067123 | -0.0021704 | -0.0031574 | 0.0041551 | -0.050354 | 63.1256 | -60.3241 | 62.9379 | -59.9304 | -60.3149 | -0.027466 | -0.004578 | 63.1302 | -60.1364 | 63.1714 | -60.0586 | -60.1547 | -59.7107 | -0.26093 | 0.059509 | -0.12817 | 0.13275 | 60.0357 | -0.25177 | 60.2966 | 0.009156 | -0.073243 | 0.064087 | 0.10529 | 0.004577 | 0.35248 | -0.091553 | 0.42572 | -0.01831 | 0.39368 | 123.262 | 0.07782 | 123.3078 | 123.4497 | 123.2666 | 123.1888 | 123.1934 | -123.3902 | -123.2025 | 123.0011 | 123.2346 | 60.0128 | 60.0586
517.4844 | 123.3261 | -60.0632 | 63.0936 | -0.011902 | 0.0022709 | 0.062711 | 0.064544 | -0.00086946 | -0.0014248 | -0.0024481 | -0.065949 | 0.00032248 | 0.06749 | 0.0699 | -0.001316 | -0.00038018 | 0.0026597 | 0.018311 | 63.2217 | -60.3149 | 62.9242 | -59.9442 | -60.3012 | 0.027466 | 0.073242 | 63.1989 | -60.1181 | 63.1531 | -60.054 | -60.1913 | -59.7198 | -0.25177 | 0.12817 | -0.16937 | 0.11902 | 60.0906 | -0.23804 | 60.3424 | 0.013733 | -0.054932 | 0.10529 | 0.059509 | 0.009155 | 0.34332 | -0.12817 | 0.39825 | -0.073242 | 0.37079 | 123.2391 | 0.064087 | 123.2712 | 123.5367 | 123.317 | 123.2849 | 123.262 | -123.4085 | -123.2117 | 122.9874 | 123.2162 | 60.0815 | 60.1364
518.5469 | 123.2758 | -60.0769 | 63.1302 | 0.0033567 | 0.00098907 | 0.064847 | 0.063903 | -1.486e-05 | 7.0582e-05 | 0.00096987 | -0.065949 | 0.0013907 | 0.065781 | 0.067763 | 0.0001794 | -0.0025164 | 0.00052346 | -0.036621 | 63.1989 | -60.3287 | 62.8647 | -60.0586 | -59.9716 | 0.004578 | 0.022888 | 63.1851 | -60.1685 | 63.1119 | -60.0769 | -60.2188 | -59.7519 | -0.25177 | 0.068665 | -0.2655 | 0.01831 | 60.0815 | 0.10529 | 60.3333 | 0.35706 | -0.091553 | 0.054932 | -0.018311 | 0 | 0.32501 | -0.14191 | 0.41656 | -0.050354 | 0.27008 | 123.1934 | 0.091553 | 123.2803 | 123.5275 | 123.3536 | 123.2758 | 123.262 | -123.4589 | -123.2986 | 122.9416 | 123.1888 | 60.0403 | 60.0998
519.5 | 123.3856 | -60.1044 | 63.0707 | -0.03479 | 0.00034827 | 0.063779 | 0.066467 | 0.0048983 | 0.00092498 | -0.0037299 | -0.053741 | -0.00031832 | 0.069199 | 0.066054 | -0.0019568 | -0.0012348 | 0.00073706 | -0.11902 | 63.1531 | -60.347 | 62.8555 | -60.0266 | -60.3882 | -0.10529 | -0.1236 | 63.1348 | -60.1822 | 63.1485 | -60.0677 | -60.1822 | -59.7153 | -0.24261 | 0.082397 | -0.21515 | 0.07782 | 59.9991 | -0.28381 | 60.2417 | -0.041199 | -0.07782 | 0.064087 | 0.07782 | 0.036621 | 0.3891 | -0.07782 | 0.46692 | 0 | 0.32043 | 123.2025 | 0.11444 | 123.3307 | 123.5001 | 123.317 | 123.2574 | 123.2391 | -123.4177 | -123.2529 | 122.9599 | 123.2529 | 59.9854 | 59.9808
520.4844 | 123.3032 | -60.0861 | 63.0707 | -0.095825 | 0.00056187 | 0.064207 | 0.06369 | -0.00022866 | 0.0017794 | 0.0050287 | -0.096466 | 0.0030997 | 0.065995 | 0.066054 | 0.000393 | -0.00038018 | -0.00011754 | -0.11902 | 63.1668 | -60.3836 | 62.5854 | -60.2829 | -59.9899 | 0.009155 | -0.064087 | 63.2034 | -60.1868 | 63.089 | -60.1456 | -60.2509 | -59.7885 | -0.29755 | 0.09613 | -0.48523 | -0.19684 | 60.0952 | 0.096131 | 60.3928 | 0.39368 | -0.10071 | 0.13275 | 0.01831 | -0.059509 | 0.29755 | -0.16479 | 0.39825 | -0.064086 | 0.10071 | 122.9691 | 0.041199 | 123.2758 | 123.5504 | 123.3902 | 123.2529 | 123.2895 | -123.4543 | -123.2574 | 122.6715 | 123.175 | 59.967 | 60.022
521.5 | 123.4131 | -60.0632 | 63.0432 | -0.095825 | 0.00013467 | 0.064634 | 0.062835 | 0.00041234 | 0.0028476 | -0.0028753 | -0.020172 | 0.00074988 | 0.065995 | 0.063491 | -0.0015296 | 0.00090142 | 0.00030966 | -0.064087 | 63.1302 | -60.3333 | 62.9196 | -59.9258 | -60.3058 | -0.045776 | -0.041199 | 63.1119 | -60.1639 | 63.1943 | -60.0311 | -60.1318 | -59.6695 | -0.27008 | 0.086975 | -0.1236 | 0.13733 | 60.0174 | -0.24262 | 60.2875 | 0.027466 | -0.10071 | 0.068664 | 0.15106 | 0.032043 | 0.39368 | -0.068665 | 0.49438 | 0.032043 | 0.40741 | 123.2529 | 0.13275 | 123.3582 | 123.4634 | 123.2758 | 123.1934 | 123.175 | -123.3765 | -123.2071 | 122.9828 | 123.2574 | 59.9991 | 60.022
522.4844 | 123.3261 | -60.0632 | 63.121 | -0.080566 | 0.00034827 | 0.062498 | 0.064331 | 0.00019874 | 0.0011386 | -0.00031193 | -0.026276 | -0.00031832 | 0.068344 | 0.068618 | -0.0017432 | -0.00059378 | -0.00075834 | -0.022888 | 63.1989 | -60.3287 | 62.8601 | -60.0128 | -60.3149 | 0.009155 | 0.009155 | 63.1989 | -60.141 | 63.121 | -60.0677 | -60.1822 | -59.7336 | -0.2655 | 0.07782 | -0.26093 | 0.050354 | 60.0723 | -0.25177 | 60.3378 | 0.013733 | -0.07782 | 0.07782 | 0 | -0.004578 | 0.32959 | -0.11902 | 0.40741 | -0.041199 | 0.31586 | 123.1888 | 0.073242 | 123.262 | 123.5275 | 123.3398 | 123.262 | 123.262 | -123.4497 | -123.262 | 122.9233 | 123.1842 | 60.0403 | 60.0723
523.5469 | 123.3215 | -60.0769 | 63.0936 | -0.03479 | 0.00098907 | 0.063138 | 0.063262 | 0.00041234 | -0.00057042 | -0.0024481 | -0.038483 | 0.0022453 | 0.06749 | 0.069686 | -0.001316 | 0.00090142 | -0.00054474 | -0.004578 | 63.1943 | -60.3149 | 62.915 | -59.9625 | -60.2875 | 0.009155 | 0.054932 | 63.1622 | -60.1364 | 63.1531 | -60.0769 | -60.1639 | -59.7107 | -0.23804 | 0.10071 | -0.17853 | 0.11444 | 60.0861 | -0.21057 | 60.3241 | 0.027465 | -0.05951 | 0.068664 | 0.059509 | 0 | 0.36621 | -0.086975 | 0.42572 | -0.027465 | 0.35248 | 123.23 | 0.05951 | 123.2895 | 123.5092 | 123.2986 | 123.2712 | 123.2391 | -123.4085 | -123.23 | 122.9919 | 123.23 | 60.0723 | 60.1318
524.4844 | 123.3398 | -60.0586 | 63.1119 | -0.042419 | 0.00077547 | 0.062925 | 0.065185 | -0.00086946 | -0.003561 | 0.0028925 | -0.041534 | -0.00031832 | 0.068131 | 0.065414 | 0.0014612 | -0.00016658 | -0.0035355 | 0.004578 | 63.1943 | -60.3287 | 62.8876 | -59.967 | -60.3058 | 0.018311 | 0.091553 | 63.1897 | -60.1318 | 63.1531 | -60.0586 | -60.173 | -59.7198 | -0.27008 | 0.082398 | -0.2243 | 0.091553 | 60.0769 | -0.24719 | 60.347 | 0.022888 | -0.073242 | 0.07782 | 0.041199 | 0 | 0.33874 | -0.11444 | 0.41199 | -0.041199 | 0.36163 | 123.2162 | 0.073242 | 123.2849 | 123.5229 | 123.3215 | 123.2529 | 123.2483 | -123.4406 | -123.2437 | 122.9462 | 123.2117 | 60.0632 | 60.1501
525.5 | 123.3582 | -60.0403 | 63.1348 | -0.072937 | -0.00029273 | 0.062711 | 0.063903 | -0.0015103 | 0.00049778 | 0.0022517 | 0.05307 | -0.0011727 | 0.064713 | 0.065414 | 0.0012476 | -0.0014484 | 0.0020187 | 0.009155 | 63.1485 | -60.2737 | 62.9745 | -59.8755 | -60.2142 | 0.10529 | 0.13275 | 63.1622 | -60.1135 | 63.1577 | -59.9945 | -60.0998 | -59.6832 | -0.23346 | 0.013733 | -0.16022 | 0.1648 | 60.1456 | -0.17395 | 60.379 | 0.05951 | -0.073242 | 0.027465 | 0.022888 | 0.045776 | 0.35706 | -0.059509 | 0.4303 | 0.013733 | 0.39826 | 123.2483 | 0.11902 | 123.2712 | 123.4222 | 123.2758 | 123.1888 | 123.2025 | -123.4085 | -123.2483 | 123.0148 | 123.1979 | 60.0494 | 60.173
526.5469 | 123.3353 | -60.0723 | 63.121 | -0.011902 | 0.0031253 | 0.061643 | 0.064544 | -0.00086946 | 0.0013522 | 0.0013971 | -0.01712 | 0.0018179 | 0.067917 | 0.062209 | 0.0001794 | -0.00016658 | 0.00073706 | -0.022888 | 63.2126 | -60.3424 | 62.8647 | -60.0037 | -60.3058 | 0.013733 | 0.032043 | 63.2034 | -60.1318 | 63.1302 | -60.0632 | -60.1822 | -59.7244 | -0.27008 | 0.091552 | -0.25635 | 0.068665 | 60.0861 | -0.23346 | 60.3561 | 0.036621 | -0.059509 | 0.082397 | 0.009155 | 0.009156 | 0.3479 | -0.10986 | 0.40741 | -0.050354 | 0.33875 | 123.2071 | 0.068665 | 123.262 | 123.555 | 123.3353 | 123.2849 | 123.2758 | -123.4634 | -123.2529 | 122.937 | 123.2025 | 60.0494 | 60.1044
527.4844 | 123.3582 | -60.0494 | 63.0661 | -0.080566 | -7.913e-05 | 0.06442 | 0.063262 | 0.0025485 | -0.00099762 | -0.0022345 | -0.044586 | 0.0028861 | 0.067917 | 0.067763 | -0.001316 | 0.00090142 | 0.0011643 | -0.11444 | 63.1577 | -60.3607 | 62.851 | -60.0403 | -60.379 | -0.10071 | -0.09613 | 63.1531 | -60.1776 | 63.1439 | -60.0586 | -60.1685 | -59.7153 | -0.31128 | 0.091553 | -0.21515 | 0.009155 | 59.9487 | -0.32959 | 60.26 | -0.01831 | -0.12817 | 0.086975 | 0.07782 | -0.009156 | 0.33417 | -0.11902 | 0.46234 | 0.009155 | 0.32043 | 123.2117 | 0.11902 | 123.3215 | 123.5184 | 123.3307 | 123.2071 | 123.2025 | -123.4268 | -123.2437 | 122.9004 | 123.1934 | 59.935 | 59.9533
528.5469 | 123.436 | -60.0266 | 63.0615 | -0.072937 | 0.00098907 | 0.063779 | 0.063903 | -0.00065586 | -0.00014322 | 0.00011527 | 0.068329 | -0.00053192 | 0.067063 | 0.064986 | -0.0002478 | -0.00016658 | 0.0015915 | -0.004578 | 63.1531 | -60.3241 | 62.9608 | -59.8801 | -60.228 | 0.09613 | 0.11902 | 63.1439 | -60.1227 | 63.2172 | -59.9533 | -60.0494 | -59.6283 | -0.29755 | 0.091553 | -0.10071 | 0.14648 | 60.1227 | -0.20142 | 60.4202 | 0.096131 | -0.096131 | 0.082398 | 0.15564 | 0.073242 | 0.39825 | -0.022888 | 0.49439 | 0.073243 | 0.44403 | 123.2849 | 0.16937 | 123.3398 | 123.4772 | 123.2666 | 123.1796 | 123.1705 | -123.3856 | -123.1842 | 122.9874 | 123.2437 | 60.022 | 60.1456
529.4844 | 123.2437 | -60.1089 | 63.0981 | -0.057678 | 0.00034827 | 0.065061 | 0.06668 | -0.00065586 | -0.00057042 | -0.00073913 | -0.084259 | 0.0011771 | 0.067704 | 0.066268 | -0.0019568 | 0.0026104 | 0.0018051 | -0.10071 | 63.176 | -60.3607 | 62.8006 | -60.0769 | -60.4111 | -0.11902 | -0.16479 | 63.1668 | -60.2005 | 63.0524 | -60.1685 | -60.2783 | -59.7885 | -0.25177 | 0.077819 | -0.29755 | 0.032044 | 59.9899 | -0.30212 | 60.2417 | -0.050354 | -0.091552 | 0.068664 | -0.045777 | -0.059509 | 0.32043 | -0.16937 | 0.41199 | -0.07782 | 0.28381 | 123.1613 | 0.032043 | 123.2529 | 123.5367 | 123.3673 | 123.2849 | 123.2758 | -123.4589 | -123.2986 | 122.9095 | 123.1613 | 60.0082 | 59.9442
530.5 | 123.381 | -60.0586 | 63.0707 | -0.11871 | 0.00098907 | 0.063566 | 0.063262 | 0.00019874 | -0.0014248 | -0.0015935 | 0.025604 | -0.0018137 | 0.066208 | 0.067123 | -0.0008886 | -0.0023028 | -0.0013991 | -0.064087 | 63.1531 | -60.3378 | 62.9059 | -59.9533 | -60.3241 | -0.041199 | -0.073242 | 63.1348 | -60.1776 | 63.1302 | -60.0769 | -60.1181 | -59.7015 | -0.27924 | 0.082397 | -0.16479 | 0.10529 | 60.0174 | -0.2655 | 60.2966 | 0.013733 | -0.11902 | 0.064087 | 0.059509 | -0.01831 | 0.35706 | -0.059509 | 0.47607 | 0.059509 | 0.38452 | 123.2437 | 0.10071 | 123.3078 | 123.4909 | 123.3124 | 123.2117 | 123.1934 | -123.4085 | -123.2483 | 122.9645 | 123.1888 | 59.9945 | 59.9854
531.4844 | 123.3078 | -60.0998 | 63.0707 | -0.10345 | 0.00077547 | 0.063352 | 0.067108 | 0.0031893 | 0.006052 | 0.0016107 | -0.01712 | 0.0028861 | 0.066208 | 0.062423 | -0.002384 | -0.00080758 | 0.0013779 | -0.11444 | 63.1805 | -60.3836 | 62.6358 | -59.8343 | -60.1685 | -0.1236 | -0.17395 | 63.1897 | -60.1685 | 63.1027 | -60.1501 | -60.2646 | -59.7977 | -0.28381 | 0.10986 | -0.43488 | 0.2655 | 59.9762 | -0.068665 | 60.26 | 0.21515 | -0.068665 | 0.11902 | 0.032043 | -0.050354 | 0.30212 | -0.16479 | 0.37079 | -0.09613 | 0.54932 | 123.0194 | 0.018311 | 123.2712 | 123.5641 | 123.3582 | 123.2803 | 123.2895 | -123.4543 | -123.2391 | 122.7356 | 123.2025 | 59.9854 | 59.9258
532.4844 | 123.2895 | -60.0815 | 63.089 | -0.042419 | -0.00093353 | 0.065275 | 0.064117 | 0.00083954 | 0.0017794 | 0.0016107 | -0.05069 | -0.00053192 | 0.067917 | 0.064773 | -0.0017432 | -0.00059378 | 0.0015915 | -0.050354 | 63.1622 | -60.3561 | 62.8647 | -59.9991 | -60.347 | -0.050354 | -0.045776 | 63.1851 | -60.1273 | 63.1073 | -60.1318 | -60.2234 | -59.7565 | -0.27466 | 0.073242 | -0.2243 | 0.082398 | 60.0311 | -0.2655 | 60.3058 | 0.009155 | -0.045776 | 0.096131 | 0.018311 | -0.050354 | 0.32501 | -0.14191 | 0.37079 | -0.096131 | 0.35706 | 123.2208 | -0.004578 | 123.2346 | 123.5184 | 123.3124 | 123.2437 | 123.2666 | -123.4451 | -123.2162 | 122.9462 | 123.1888 | 60.0311 | 60.0357
533.5 | 123.381 | -60.054 | 63.0707 | -0.088196 | 0.0012027 | 0.063352 | 0.062835 | 0.00041234 | 0.00071138 | -9.8328e-05 | 0.037811 | 0.00053628 | 0.066849 | 0.062209 | -3.4196e-05 | 0.00047422 | 0.0030869 | -0.10071 | 63.121 | -60.3287 | 62.8922 | -59.935 | -60.3241 | -0.036621 | -0.059509 | 63.1165 | -60.1318 | 63.1348 | -60.0677 | -60.1639 | -59.7198 | -0.27466 | 0.050354 | -0.17853 | 0.11902 | 60.0174 | -0.27008 | 60.2921 | 0.004577 | -0.07782 | 0.045776 | 0.064087 | -0.013733 | 0.33417 | -0.10986 | 0.41199 | -0.032043 | 0.39368 | 123.2208 | 0.064087 | 123.2666 | 123.4497 | 123.2483 | 123.175 | 123.1705 | -123.3994 | -123.2025 | 122.9462 | 123.1888 | 59.9533 | 59.9945
534.5625 | 123.3994 | -60.0586 | 63.0524 | -0.080566 | 0.0014163 | 0.062925 | 0.066894 | 0.0016939 | 0.00028418 | -0.0011663 | -0.044586 | 0.0020315 | 0.066849 | 0.069686 | -0.0002478 | 4.7018e-05 | -0.0026809 | -0.1236 | 63.1485 | -60.3699 | 62.8738 | -60.0082 | -60.379 | -0.09613 | -0.10529 | 63.1165 | -60.1685 | 63.1668 | -60.0632 | -60.1593 | -59.6878 | -0.31128 | 0.096131 | -0.17853 | 0.050354 | 59.9625 | -0.32043 | 60.2737 | -0.009155 | -0.10986 | 0.064087 | 0.11444 | -0.004577 | 0.37079 | -0.10071 | 0.48065 | 0.009155 | 0.36163 | 123.2437 | 0.10529 | 123.3353 | 123.5184 | 123.2849 | 123.2071 | 123.175 | -123.4222 | -123.2208 | 122.9324 | 123.2254 | 59.935 | 59.9533
535.5 | 123.3673 | -60.0174 | 63.1119 | -0.19501 | -7.913e-05 | 0.064207 | 0.065185 | -0.0066373 | 0.00071138 | 0.00011527 | 0.013397 | -0.00010472 | 0.066422 | 0.0605 | -0.0002478 | -0.0014484 | 0.00073706 | 0.032043 | 63.1393 | -60.3012 | 62.97 | -59.8709 | -60.2463 | 0.082397 | 0.12817 | 63.1485 | -60.1227 | 63.176 | -59.9854 | -60.0677 | -59.6695 | -0.28381 | 0.027466 | -0.14191 | 0.14648 | 60.0998 | -0.22888 | 60.3836 | 0.054931 | -0.10529 | 0.036622 | 0.064087 | 0.032043 | 0.3479 | -0.050354 | 0.45319 | 0.054932 | 0.4303 | 123.2712 | 0.13733 | 123.2986 | 123.4406 | 123.2712 | 123.1567 | 123.1659 | -123.4131 | -123.2346 | 122.9874 | 123.1934 | 60.0494 | 60.1456
536.5625 | 123.2758 | -60.0906 | 63.0936 | -0.095825 | 0.0014163 | 0.06442 | 0.06369 | 0.0021213 | 0.002634 | -0.0015935 | 0.083588 | 0.0030997 | 0.067917 | 0.0699 | -0.001316 | -0.00059378 | 9.6064e-05 | -0.13275 | 63.1805 | -60.3836 | 62.8326 | -59.967 | -60.8917 | -0.2655 | -0.22888 | 63.1714 | -60.1776 | 63.089 | -60.1593 | -60.2463 | -59.7794 | -0.29297 | 0.086975 | -0.26093 | 0.1236 | 59.8251 | -0.80109 | 60.1181 | -0.50812 | -0.086975 | 0.07782 | -0.004578 | -0.068665 | 0.31128 | -0.15564 | 0.39825 | -0.068665 | 0.41656 | 123.2162 | 0.01831 | 123.2666 | 123.5641 | 123.349 | 123.2712 | 123.262 | -123.4772 | -123.2712 | 122.9233 | 123.1796 | 59.9579 | 59.8618
537.4844 | 123.2941 | -60.1044 | 63.0981 | -0.23315 | 0.0039799 | 0.062711 | 0.065826 | -0.00065586 | 0.0022068 | 0.0022517 | -0.047638 | 0.0016043 | 0.066422 | 0.066054 | -0.0017432 | 0.0013288 | 0.00052346 | -0.045776 | 63.1851 | -60.3241 | 62.8967 | -59.9487 | -60.347 | -0.022888 | 0.018311 | 63.1989 | -60.1822 | 63.1302 | -60.0998 | -60.2142 | -59.7519 | -0.21973 | 0.086975 | -0.20142 | 0.15564 | 60.0815 | -0.24261 | 60.3012 | -0.022888 | -0.07782 | 0.10071 | 0.032043 | 0.004578 | 0.35248 | -0.10986 | 0.4303 | -0.032043 | 0.37537 | 123.2208 | 0.082398 | 123.3124 | 123.5092 | 123.381 | 123.2895 | 123.3032 | -123.4222 | -123.2803 | 123.0011 | 123.2346 | 60.0586 | 60.1227
538.5469 | 123.3444 | -60.054 | 63.121 | -0.042419 | 0.00077547 | 0.06207 | 0.064971 | -1.486e-05 | -0.00078402 | -0.00073913 | -0.029327 | 0.0022453 | 0.067276 | 0.066268 | 0.000393 | 0.00090142 | 0.00073706 | -0.009155 | 63.2263 | -60.3287 | 62.8784 | -59.967 | -60.3012 | 0.036621 | 0.054932 | 63.1851 | -60.1547 | 63.1393 | -60.0311 | -60.1776 | -59.729 | -0.27466 | 0.10529 | -0.24261 | 0.086975 | 60.0906 | -0.24719 | 60.3653 | 0.027466 | -0.10071 | 0.064087 | 0.01831 | 0.022888 | 0.32501 | -0.1236 | 0.42572 | -0.022888 | 0.36163 | 123.2071 | 0.1236 | 123.2941 | 123.555 | 123.3398 | 123.2803 | 123.2391 | -123.4497 | -123.2758 | 122.9324 | 123.1934 | 60.0449 | 60.1089
539.5 | 123.4039 | -60.0586 | 63.0203 | -0.057678 | 0.0031253 | 0.066984 | 0.064117 | -0.00044226 | 0.00092498 | -9.8328e-05 | -0.01712 | 0.00074988 | 0.06514 | 0.066268 | -0.000675 | -0.0023028 | 0.0015915 | -0.068665 | 63.1439 | -60.3287 | 62.9242 | -59.935 | -60.3149 | -0.041199 | -0.027466 | 63.0936 | -60.141 | 63.1897 | -60.0266 | -60.1227 | -59.8801 | -0.27008 | 0.1236 | -0.096131 | 0.1236 | 60.0174 | -0.25635 | 60.2875 | 0.013733 | -0.082397 | 0.073242 | 0.16937 | 0.032044 | 0.17853 | -0.064087 | 0.26093 | 0.01831 | 0.39368 | 123.2529 | 0.11444 | 123.3307 | 123.4726 | 123.2346 | 123.2025 | 123.1522 | -123.349 | -123.1613 | 122.9828 | 123.2483 | 59.9899 | 60.0311
540.5 | 123.3627 | -60.0632 | 63.0798 | -0.065308 | 0.00034827 | 0.064634 | 0.064331 | -0.0047147 | -0.00078402 | -0.0011663 | 0.004242 | -0.0011727 | 0.064713 | 0.056228 | -0.000675 | 0.00047422 | 9.6064e-05 | -0.082397 | 63.1577 | -60.3149 | 62.8922 | -59.9442 | -60.3287 | -0.045776 | -0.064087 | 63.1393 | -60.1639 | 63.1119 | -60.0357 | -60.1547 | -59.7107 | -0.25177 | 0.07782 | -0.18768 | 0.11902 | 60.0174 | -0.2655 | 60.2692 | -0.013733 | -0.10071 | 0.059509 | 0.032043 | 0.027465 | 0.35248 | -0.091553 | 0.45319 | 0.009155 | 0.37079 | 123.2071 | 0.12817 | 123.2758 | 123.4726 | 123.3032 | 123.2208 | 123.2025 | -123.3948 | -123.2437 | 122.9553 | 123.175 | 59.9808 | 59.9991
541.4844 | 123.262 | -60.0861 | 63.0936 | -0.088196 | -0.00071993 | 0.063993 | 0.064971 | -0.0015103 | -0.0014248 | 0.0031061 | -0.084259 | 0.0018179 | 0.066635 | 0.07054 | -0.0017432 | -0.0012348 | -0.0024673 | -0.09613 | 63.1668 | -60.3607 | 62.8098 | -60.0632 | -60.434 | -0.11444 | -0.16022 | 63.1668 | -60.1776 | 63.0569 | -60.1913 | -60.3012 | -59.8206 | -0.27466 | 0.073242 | -0.28381 | 0.022889 | 59.9716 | -0.3479 | 60.2463 | -0.073242 | -0.091552 | 0.073242 | -0.036621 | -0.10528 | 0.2655 | -0.21515 | 0.35706 | -0.1236 | 0.29755 | 123.1705 | -0.013733 | 123.2346 | 123.5275 | 123.3444 | 123.2529 | 123.2529 | -123.4543 | -123.2712 | 122.8958 | 123.143 | 59.9899 | 59.9258
542.5469 | 123.3124 | -60.0723 | 63.1073 | -0.042419 | 0.0014163 | 0.063993 | 0.06604 | 0.0012667 | -0.00078402 | 0.00054267 | -0.059845 | -0.00031832 | 0.067704 | 0.066268 | -0.0008886 | -0.0010212 | -0.0026809 | -0.027466 | 63.1851 | -60.3424 | 62.8784 | -59.9625 | -60.3104 | -0.10529 | 0.018311 | 63.1577 | -60.1364 | 63.1393 | -60.0769 | -60.1822 | -59.7382 | -0.27008 | 0.07782 | -0.22888 | 0.10986 | 59.967 | -0.23804 | 60.2371 | 0.032043 | -0.064087 | 0.050354 | 0.032043 | -0.004577 | 0.33417 | -0.10986 | 0.39825 | -0.045776 | 0.37994 | 123.2208 | 0.05951 | 123.2758 | 123.5275 | 123.2941 | 123.2574 | 123.23 | -123.4497 | -123.2437 | 122.9507 | 123.2117 | 60.0449 | 60.0906
543.4844 | 123.4177 | -60.0494 | 63.0386 | -0.080566 | 0.0012027 | 0.064207 | 0.065185 | 0.0036165 | 7.0582e-05 | -0.00073913 | -0.014069 | 0.0011771 | 0.068344 | 0.068831 | -0.0017432 | -0.00080758 | -0.0018265 | -0.091553 | 63.1393 | -60.3699 | 62.9196 | -59.9762 | -60.347 | -0.041199 | -0.059509 | 63.0936 | -60.173 | 63.1897 | -60.0494 | -60.1318 | -59.6558 | -0.32043 | 0.10071 | -0.11902 | 0.073242 | 60.0082 | -0.29755 | 60.3287 | 0.022888 | -0.1236 | 0.054932 | 0.15106 | 0 | 0.39368 | -0.082398 | 0.51727 | 0.041199 | 0.39368 | 123.2895 | 0.1236 | 123.3627 | 123.5092 | 123.2666 | 123.1888 | 123.143 | -123.4085 | -123.2117 | 122.9691 | 123.2391 | 59.9579 | 59.9899
544.4844 | 123.2895 | -60.0815 | 63.1027 | -0.10345 | 0.00034827 | 0.063138 | 0.066253 | -1.486e-05 | -0.00099762 | 0.00075627 | -0.069 | -0.00053192 | 0.065354 | 0.068191 | -0.0008886 | 0.00068782 | -0.0018265 | -0.13733 | 63.1668 | -60.3516 | 62.8647 | -59.967 | -60.3195 | -0.022888 | 0.004578 | 63.1989 | -60.1639 | 63.1256 | -60.0906 | -60.2051 | -59.7519 | -0.27008 | 0.064087 | -0.23804 | 0.11444 | 60.0586 | -0.23804 | 60.3287 | 0.032043 | -0.082397 | 0.096131 | 0.022888 | -0.009155 | 0.32959 | -0.1236 | 0.41199 | -0.041199 | 0.38452 | 123.2162 | 0.073242 | 123.2895 | 123.5184 | 123.3627 | 123.2483 | 123.2803 | -123.4543 | -123.2666 | 122.9462 | 123.2071 | 59.9442 | 60.0861
545.5625 | 123.317 | -60.0449 | 63.1393 | -0.03479 | -0.00029273 | 0.063566 | 0.062408 | 0.00083954 | 0.00028418 | -0.0015935 | 0.013397 | 0.00032248 | 0.067063 | 0.063064 | -0.0008886 | -0.0012348 | -0.0018265 | -0.032043 | 63.2126 | -60.3378 | 62.8693 | -60.0082 | -60.3149 | 0.013733 | 0.018311 | 63.2217 | -60.1089 | 63.1073 | -60.054 | -60.1822 | -59.7427 | -0.29297 | 0.073242 | -0.27008 | 0.036621 | 60.0586 | -0.27008 | 60.3516 | 0.022889 | -0.064087 | 0.082398 | -0.032043 | -0.009155 | 0.30212 | -0.13733 | 0.36621 | -0.073242 | 0.32959 | 123.2071 | 0.054932 | 123.2162 | 123.5504 | 123.3307 | 123.2574 | 123.2666 | -123.4772 | -123.2483 | 122.9141 | 123.1522 | 60.0128 | 60.0632
546.4844 | 123.317 | -60.054 | 63.1027 | -0.027161 | 0.0022709 | 0.062284 | 0.064758 | -0.00022866 | 0.00071138 | 0.0037469 | -0.044586 | 0.00010888 | 0.067063 | 0.066054 | -0.0008886 | 0.00068782 | -0.0028945 | -0.036621 | 63.1622 | -60.3241 | 62.883 | -59.967 | -60.3195 | -0.041199 | 0.068665 | 63.1714 | -60.1501 | 63.1393 | -60.0677 | -60.1822 | -59.7336 | -0.27008 | 0.059509 | -0.21973 | 0.086975 | 60.0128 | -0.2655 | 60.2829 | 0.004578 | -0.09613 | 0.068665 | 0.036621 | -0.013733 | 0.32043 | -0.12817 | 0.41656 | -0.032044 | 0.35706 | 123.2071 | 0.082397 | 123.2895 | 123.4863 | 123.3215 | 123.2162 | 123.2254 | -123.4268 | -123.2529 | 122.937 | 123.1934 | 60.0174 | 60.1227
547.4844 | 123.262 | -60.0906 | 63.0981 | -0.050049 | 0.00077547 | 0.065488 | 0.064971 | 0.0010531 | -0.00078402 | 0.0024653 | -0.041534 | 0.0016043 | 0.068772 | 0.064345 | -0.0019568 | 0.001115 | -0.0022537 | -0.091553 | 63.176 | -60.3516 | 62.8052 | -60.0586 | -60.4156 | -0.1236 | -0.16022 | 63.1577 | -60.1959 | 63.0524 | -60.1776 | -60.3058 | -59.8022 | -0.26093 | 0.077819 | -0.29297 | 0.032043 | 59.967 | -0.32501 | 60.228 | -0.064087 | -0.10529 | 0.059509 | -0.045777 | -0.086975 | 0.28839 | -0.21515 | 0.39368 | -0.10986 | 0.29297 | 123.1567 | 0.018311 | 123.2483 | 123.5275 | 123.3536 | 123.2666 | 123.2483 | -123.4497 | -123.2941 | 122.8958 | 123.143 | 59.9991 | 59.9304
548.5469 | 123.2941 | -60.0677 | 63.121 | -0.011902 | -0.00071993 | 0.062284 | 0.063476 | 0.0021213 | -0.0014248 | 0.00032907 | -0.014069 | 0.0020315 | 0.065354 | 0.062209 | 0.0001794 | 0.001115 | -0.00054474 | -0.050354 | 63.2126 | -60.3195 | 62.851 | -60.0082 | -60.3241 | 0.022888 | 0.013733 | 63.208 | -60.1456 | 62.9654 | -60.022 | -60.2417 | -59.761 | -0.25177 | 0.091552 | -0.27008 | 0.059509 | 60.0906 | -0.25635 | 60.3424 | -0.004578 | -0.07782 | 0.086975 | -0.15564 | 0.045776 | 0.3067 | -0.17395 | 0.38452 | -0.09613 | 0.31128 | 123.1705 | 0.1236 | 123.111 | 123.5321 | 123.3536 | 123.2803 | 123.2758 | -123.4406 | -123.2666 | 122.9187 | 123.0331 | 60.0174 | 60.0815
549.4844 | 123.349 | -60.0677 | 63.0524 | -0.095825 | 0.00034827 | 0.063566 | 0.062408 | 0.0046847 | 0.00092498 | -0.0013799 | 0.046967 | -0.00053192 | 0.067704 | 0.071609 | -0.001316 | -0.001662 | -0.00011754 | -0.10986 | 63.1393 | -60.3149 | 62.8784 | -59.967 | -60.3333 | -0.041199 | -0.059509 | 63.1256 | -60.1547 | 63.1302 | -60.0723 | -60.1547 | -59.7107 | -0.24719 | 0.086975 | -0.17395 | 0.10071 | 60.0266 | -0.2655 | 60.2737 | -0.018311 | -0.086975 | 0.073242 | 0.07782 | -0.004578 | 0.35706 | -0.086975 | 0.44403 | 0 | 0.3479 | 123.1934 | 0.082397 | 123.2849 | 123.4543 | 123.2803 | 123.2071 | 123.1934 | -123.3673 | -123.2071 | 122.9462 | 123.1979 | 59.9579 | 60.0082
550.4844 | 123.2758 | -60.0906 | 63.0981 | -0.03479 | 0.00098907 | 0.062498 | 0.064331 | 0.0044711 | -0.0012112 | 0.0031061 | -0.047638 | -0.0022409 | 0.067917 | 0.068191 | -0.0004614 | -0.0010212 | 0.0039413 | -0.073242 | 63.1805 | -60.3516 | 62.8372 | -60.0403 | -60.3973 | -0.086975 | -0.091553 | 63.176 | -60.1639 | 63.089 | -60.1913 | -60.2463 | -59.7794 | -0.26093 | 0.082397 | -0.26093 | 0.050354 | 60.0037 | -0.3067 | 60.2646 | -0.045777 | -0.073242 | 0.077819 | -0.009156 | -0.10071 | 0.31128 | -0.15564 | 0.38452 | -0.082398 | 0.31128 | 123.1888 | -0.027466 | 123.2529 | 123.5321 | 123.3398 | 123.2712 | 123.2666 | -123.4497 | -123.262 | 122.9279 | 123.1796 | 60.0174 | 59.9991
551.5625 | 123.3032 | -60.0906 | 63.1119 | -0.080566 | 0.00056187 | 0.064634 | 0.066467 | -0.00022866 | 0.0019932 | 0.0013971 | -0.026276 | 0.0013907 | 0.067276 | 0.06755 | -0.0034522 | -0.0027302 | 0.0013779 | -0.10529 | 63.1531 | -60.347 | 62.8098 | -60.0952 | -60.4156 | -0.11902 | -0.16937 | 63.1485 | -60.1822 | 63.2309 | -60.2188 | -60.2463 | -59.7427 | -0.25635 | 0.041199 | -0.30212 | -0.004578 | 59.9716 | -0.32501 | 60.228 | -0.068664 | -0.091553 | 0.036622 | 0.11902 | -0.12817 | 0.3479 | -0.15564 | 0.43945 | -0.064087 | 0.25177 | 123.1567 | -0.036621 | 123.4131 | 123.5001 | 123.3307 | 123.2437 | 123.2391 | -123.4589 | -123.2941 | 122.9004 | 123.3215 | 59.9854 | 59.9213
552.4844 | 123.3124 | -60.0815 | 63.1073 | -0.042419 | 0.0012027 | 0.06442 | 0.063262 | 0.00062594 | 0.0019932 | -0.00095273 | -0.044586 | 0.0016043 | 0.065567 | 0.067336 | 0.000393 | 0.0019696 | -0.0020401 | -0.013733 | 63.1943 | -60.3516 | 62.9333 | -60.1181 | -60.3561 | 0.036621 | 0.032043 | 63.176 | -60.1273 | 63.1302 | -60.0906 | -60.1868 | -59.7244 | -0.27008 | 0.086975 | -0.17395 | -0.036621 | 60.1181 | -0.27466 | 60.3882 | -0.004578 | -0.045776 | 0.068664 | 0.022888 | -0.009155 | 0.35706 | -0.10529 | 0.40283 | -0.05951 | 0.23346 | 123.2849 | 0.036621 | 123.2574 | 123.5458 | 123.3032 | 123.2758 | 123.2574 | -123.4589 | -123.2346 | 123.0148 | 123.2117 | 60.0677 | 60.1135
553.4844 | 123.2758 | -60.1135 | 63.0981 | -0.027161 | 0.0020573 | 0.065275 | 0.066253 | 0.00019874 | -0.00035682 | 0.0011835 | -0.056793 | 0.0022453 | 0.068344 | 0.062209 | 0.0001794 | -0.00038018 | -0.00097194 | -0.082397 | 63.1668 | -60.3516 | 62.8006 | -60.0952 | -60.4431 | -0.12817 | -0.16479 | 63.176 | -60.1913 | 63.0341 | -60.1593 | -60.2829 | -59.7702 | -0.23804 | 0.068664 | -0.29755 | 0.01831 | 59.9854 | -0.32959 | 60.2234 | -0.091553 | -0.07782 | 0.077819 | -0.064087 | -0.045777 | 0.34332 | -0.16937 | 0.42114 | -0.091553 | 0.25635 | 123.1522 | 0.032043 | 123.2254 | 123.5184 | 123.3673 | 123.2803 | 123.2895 | -123.4497 | -123.2895 | 122.9141 | 123.1476 | 60.0311 | 59.9487
554.4844 | 123.3353 | -60.0632 | 63.0844 | -0.011902 | 0.00077547 | 0.063566 | 0.063476 | -0.0036465 | 0.00092498 | -0.0018073 | -0.041534 | 0.0016043 | 0.065567 | 0.066482 | 0.002102 | -0.0010212 | -0.00054474 | -0.009155 | 63.1897 | -60.3241 | 62.8784 | -59.9579 | -60.3195 | -0.013733 | 0.022888 | 63.1851 | -60.1547 | 63.1989 | -60.0861 | -60.173 | -59.7107 | -0.26093 | 0.10529 | -0.20599 | 0.10528 | 60.0494 | -0.25635 | 60.3104 | 0.004578 | -0.091553 | 0.10071 | 0.11444 | -0.022889 | 0.35248 | -0.10986 | 0.44403 | -0.018311 | 0.36621 | 123.2025 | 0.068664 | 123.3536 | 123.5138 | 123.3398 | 123.2529 | 123.2483 | -123.4085 | -123.2391 | 122.9416 | 123.262 | 60.054 | 60.0861
555.5625 | 123.4131 | -60.0494 | 63.0615 | -0.050049 | -0.00029273 | 0.062925 | 0.061767 | -0.0010831 | 0.002634 | -0.0033025 | 0.086639 | -0.0013863 | 0.069412 | 0.057937 | -0.000675 | -0.0037982 | 9.6064e-05 | -0.068665 | 63.1668 | -60.2921 | 62.9196 | -59.9396 | -60.2783 | 0.036621 | 0.032043 | 63.121 | -60.1639 | 63.176 | -59.9945 | -60.1089 | -59.6786 | -0.24262 | 0.10529 | -0.14191 | 0.10986 | 60.0861 | -0.22888 | 60.3287 | 0.013733 | -0.11444 | 0.05951 | 0.11444 | 0.054931 | 0.37079 | -0.05951 | 0.48523 | 0.054931 | 0.35248 | 123.2117 | 0.16937 | 123.3398 | 123.4589 | 123.2849 | 123.2162 | 123.1705 | -123.3536 | -123.2254 | 122.9691 | 123.2254 | 59.9808 | 60.0815
556.4844 | 123.3124 | -60.0632 | 63.121 | -0.019531 | 0.00098907 | 0.063566 | 0.064117 | 0.0010531 | 0.0019932 | 0.00032907 | 0.004242 | 0.0020315 | 0.06984 | 0.060927 | -0.0019568 | -0.00038018 | 0.00073706 | -0.004578 | 63.208 | -60.3149 | 62.8922 | -59.9808 | -60.3104 | 0.018311 | 0.054932 | 63.1897 | -60.1639 | 63.1439 | -60.0769 | -60.1547 | -59.6924 | -0.25177 | 0.086975 | -0.22888 | 0.082397 | 60.0815 | -0.24719 | 60.3333 | 0.004577 | -0.10071 | 0.068664 | 0.022888 | -0.013733 | 0.37079 | -0.091553 | 0.4715 | 0.009155 | 0.33417 | 123.2071 | 0.086975 | 123.3078 | 123.5229 | 123.3536 | 123.2712 | 123.2529 | -123.436 | -123.2849 | 122.9553 | 123.2071 | 60.0586 | 60.1181
557.5625 | 123.3948 | -60.0815 | 63.0569 | -0.080566 | 0.0024845 | 0.063993 | 0.063049 | 0.0038303 | -0.00014322 | 0.0020379 | 0.046967 | 0.00096348 | 0.069626 | 0.064773 | -0.0032386 | -0.0027302 | -0.00097194 | -0.054932 | 63.1256 | -60.3287 | 62.9517 | -59.7107 | -60.2783 | -0.050354 | -0.032043 | 63.1256 | -60.1273 | 63.1714 | -60.022 | -60.1501 | -59.6786 | -0.24719 | 0.068664 | -0.10529 | 0.37079 | 60.0311 | -0.19684 | 60.2783 | 0.050354 | -0.045776 | 0.068664 | 0.11444 | 0.059509 | 0.40283 | -0.068664 | 0.44861 | -0.022888 | 0.61798 | 123.2803 | 0.10528 | 123.2986 | 123.4543 | 123.2529 | 123.2071 | 123.2071 | -123.3856 | -123.1842 | 123.0331 | 123.2529 | 60.0266 | 60.0494
558.4844 | 123.3215 | -60.0769 | 63.0844 | 0.0033567 | -0.00029273 | 0.063779 | 0.064758 | 0.0034029 | -0.00078402 | 0.0013971 | -0.062897 | 0.0013907 | 0.068131 | 0.066268 | -0.0017432 | -0.0014484 | -0.0031081 | -0.004578 | 63.1989 | -60.3424 | 62.9059 | -59.967 | -60.3149 | 0.009155 | 0.059509 | 63.1622 | -60.1273 | 63.1485 | -60.0677 | -60.1868 | -59.7153 | -0.2655 | 0.11444 | -0.17853 | 0.10986 | 60.0861 | -0.23804 | 60.3516 | 0.027466 | -0.050354 | 0.077819 | 0.064087 | 0.009155 | 0.36163 | -0.10986 | 0.41199 | -0.05951 | 0.37537 | 123.2483 | 0.059509 | 123.2758 | 123.5413 | 123.2895 | 123.2758 | 123.2391 | -123.4268 | -123.2117 | 122.9828 | 123.2254 | 60.0723 | 60.1364
559.4844 | 123.262 | -60.1044 | 63.0753 | -0.050049 | 0.0020573 | 0.063566 | 0.064758 | -0.00065586 | -0.0016384 | -0.0024481 | -0.05069 | 0.00096348 | 0.067276 | 0.065414 | -0.0017432 | 4.7018e-05 | -0.00033114 | -0.10529 | 63.1805 | -60.379 | 62.7869 | -60.0998 | -60.4294 | -0.13275 | -0.16022 | 63.1439 | -60.2051 | 63.0753 | -60.1501 | -60.2829 | -59.7794 | -0.27466 | 0.10529 | -0.28839 | 0.004578 | 59.9716 | -0.32501 | 60.2463 | -0.050354 | -0.10071 | 0.068665 | 0 | -0.045776 | 0.32501 | -0.17853 | 0.42572 | -0.07782 | 0.27924 | 123.1659 | 0.054932 | 123.2803 | 123.5596 | 123.349 | 123.2849 | 123.2483 | -123.4543 | -123.2803 | 122.8912 | 123.1796 | 59.9991 | 59.9442
560.5625 | 123.2803 | -60.0632 | 63.1485 | -0.011902 | 0.0018435 | 0.061857 | 0.063903 | -0.0042875 | -0.00035682 | 0.00075627 | 0.016449 | 0.0016043 | 0.067276 | 0.060287 | 0.0001794 | -0.0012348 | 0.00073706 | -0.059509 | 63.2217 | -60.3195 | 62.8555 | -59.9945 | -60.3149 | 0.027466 | 0.018311 | 63.2172 | -60.1593 | 63.1073 | -60.1044 | -60.2005 | -59.7427 | -0.25635 | 0.073242 | -0.29297 | 0.068664 | 60.0906 | -0.25177 | 60.347 | 0.004578 | -0.096131 | 0.068664 | -0.041199 | -0.041199 | 0.32043 | -0.13733 | 0.41656 | -0.041198 | 0.32501 | 123.175 | 0.054932 | 123.2666 | 123.5413 | 123.3765 | 123.2849 | 123.2803 | -123.468 | -123.3078 | 122.9187 | 123.1705 | 60.0037 | 60.0815
561.4844 | 123.2941 | -60.0952 | 63.1256 | -0.042419 | 0.0022709 | 0.063993 | 0.065185 | 0.0036165 | 0.0019932 | -0.0024481 | -0.053741 | 0.0018179 | 0.068131 | 0.06755 | -0.000675 | 0.001756 | 0.0033005 | -0.11444 | 63.1897 | -60.3561 | 62.8052 | -60.0906 | -60.4111 | -0.13275 | -0.18768 | 63.1714 | -60.1822 | 63.0798 | -60.1639 | -60.2829 | -59.7931 | -0.26093 | 0.064087 | -0.32043 | 0.004578 | 59.9625 | -0.31586 | 60.2234 | -0.054932 | -0.086975 | 0.045777 | -0.045776 | -0.068664 | 0.30212 | -0.18768 | 0.3891 | -0.10071 | 0.2655 | 123.1613 | 0.018311 | 123.262 | 123.5458 | 123.3536 | 123.2849 | 123.2666 | -123.4818 | -123.3078 | 122.9004 | 123.175 | 59.9808 | 59.9075
562.4844 | 123.3078 | -60.0769 | 63.0844 | -0.072937 | 0.0018435 | 0.064207 | 0.067535 | 0.0012667 | -0.00035682 | 0.00096987 | -0.047638 | 0.0022453 | 0.065567 | 0.064773 | -0.0017432 | -0.00016658 | 0.00073706 | -0.032043 | 63.1897 | -60.3561 | 62.8922 | -59.967 | -60.3195 | -0.013733 | 0.032043 | 63.1668 | -60.1547 | 63.1393 | -60.0769 | -60.1868 | -59.7382 | -0.27924 | 0.10529 | -0.19226 | 0.10986 | 60.0632 | -0.24262 | 60.3424 | 0.036621 | -0.07782 | 0.082397 | 0.054931 | 0 | 0.33874 | -0.10986 | 0.41656 | -0.032044 | 0.3891 | 123.2483 | 0.07782 | 123.2941 | 123.5458 | 123.3215 | 123.2666 | 123.2437 | -123.4406 | -123.2391 | 122.9691 | 123.2162 | 60.0449 | 60.1089
563.5625 | 123.2712 | -60.1044 | 63.0936 | -0.088196 | 0.0022709 | 0.06442 | 0.065399 | 0.0031893 | -0.0022794 | -0.0011663 | -0.05069 | 0.00074988 | 0.071121 | 0.063277 | -0.0002478 | -0.0010212 | -0.00075834 | -0.11444 | 63.1851 | -60.3653 | 62.8143 | -60.1044 | -60.4477 | -0.14648 | -0.15564 | 63.1531 | -60.2005 | 63.0615 | -60.1547 | -60.2646 | -59.7885 | -0.26093 | 0.091553 | -0.27924 | 0 | 59.9579 | -0.34332 | 60.2188 | -0.082398 | -0.09613 | 0.059509 | -0.032044 | -0.050354 | 0.31586 | -0.16022 | 0.41199 | -0.064087 | 0.26093 | 123.1796 | 0.045776 | 123.262 | 123.5504 | 123.3536 | 123.2895 | 123.2574 | -123.4589 | -123.2941 | 122.9187 | 123.1659 | 59.9899 | 59.9487
564.4844 | 123.2941 | -60.0677 | 63.0844 | -0.011902 | 0.0014163 | 0.06442 | 0.064117 | -0.00022866 | 0.0024204 | -0.00031193 | -0.026276 | 0.0022453 | 0.069199 | 0.066054 | -0.0004614 | 0.00026062 | -0.00097194 | -0.041199 | 63.1943 | -60.3149 | 62.8555 | -59.9808 | -60.3333 | -0.050354 | -0.045776 | 63.1943 | -60.173 | 63.121 | -60.1273 | -60.228 | -59.761 | -0.24719 | 0.10986 | -0.22888 | 0.086975 | 60.0174 | -0.2655 | 60.2646 | -0.018311 | -0.10529 | 0.10986 | 0.036621 | -0.059509 | 0.3067 | -0.16022 | 0.41199 | -0.054931 | 0.33417 | 123.1705 | 0.045777 | 123.2941 | 123.5092 | 123.3673 | 123.262 | 123.262 | -123.3994 | -123.2574 | 122.9233 | 123.1888 | 60.0266 | 60.022
565.5 | 123.381 | -60.0449 | 63.0569 | -0.042419 | 0.0014163 | 0.064207 | 0.063903 | -0.0045011 | 0.00092498 | -0.0035163 | 0.068329 | -0.0022409 | 0.070053 | 0.060073 | -0.002384 | -0.0010212 | 0.0020187 | -0.073242 | 63.1393 | -60.3104 | 62.8784 | -59.9808 | -60.3012 | -0.013733 | -0.068665 | 63.1073 | -60.1456 | 63.1393 | -60.0494 | -60.1501 | -59.7015 | -0.2655 | 0.082397 | -0.17853 | 0.064087 | 60.0311 | -0.25635 | 60.2966 | 0.009156 | -0.10071 | 0.050354 | 0.082397 | -0.004577 | 0.34332 | -0.10529 | 0.44403 | -0.004577 | 0.32959 | 123.1888 | 0.096131 | 123.2849 | 123.4497 | 123.2529 | 123.1842 | 123.1522 | -123.3673 | -123.2025 | 122.9233 | 123.1842 | 59.9716 | 59.9762
566.4844 | 123.3215 | -60.054 | 63.089 | -0.042419 | 0.00056187 | 0.062498 | 0.063476 | 0.00083954 | -0.00035682 | -0.0018073 | -0.041534 | -0.00031832 | 0.063858 | 0.068618 | -0.0019568 | -0.00038018 | 0.0011643 | -0.027466 | 63.176 | -60.3378 | 62.8876 | -59.9579 | -60.3058 | -0.022888 | 0.045776 | 63.1577 | -60.141 | 63.1439 | -60.0952 | -60.1822 | -59.7336 | -0.28381 | 0.086975 | -0.20142 | 0.09613 | 60.0311 | -0.25177 | 60.3149 | 0.032044 | -0.086975 | 0.068665 | 0.054932 | -0.041199 | 0.32043 | -0.12817 | 0.40741 | -0.041199 | 0.37994 | 123.2254 | 0.045776 | 123.2849 | 123.5138 | 123.2986 | 123.23 | 123.2117 | -123.4268 | -123.23 | 122.9416 | 123.1979 | 60.0266 | 60.0998
567.5469 | 123.3261 | -60.0906 | 63.0569 | -0.080566 | -0.00029273 | 0.063779 | 0.064331 | 0.00083954 | -0.0014248 | -0.00073913 | -0.032379 | 0.0020315 | 0.068772 | 0.059859 | -0.001316 | -0.00059378 | -0.00075834 | -0.1236 | 63.1485 | -60.3745 | 62.8281 | -60.054 | -60.3882 | -0.11902 | -0.14191 | 63.1668 | -60.2005 | 63.1073 | -60.1135 | -60.228 | -59.761 | -0.28381 | 0.091553 | -0.22888 | 0.036621 | 59.9716 | -0.29755 | 60.2554 | -0.013733 | -0.10986 | 0.10986 | 0.050354 | -0.022888 | 0.32959 | -0.13733 | 0.43945 | -0.027466 | 0.32044 | 123.2025 | 0.086975 | 123.3078 | 123.523 | 123.3673 | 123.2391 | 123.2574 | -123.4314 | -123.2574 | 122.9187 | 123.1979 | 59.967 | 59.9487
568.4844 | 123.2574 | -60.0861 | 63.0936 | -0.11871 | 0.00098907 | 0.065275 | 0.065826 | -0.0012967 | 0.0017794 | 0.00011527 | -0.044586 | 0.00053628 | 0.065995 | 0.066268 | -0.001316 | 0.0015424 | -0.0018265 | -0.064087 | 63.1805 | -60.3561 | 62.8326 | -60.0357 | -60.3882 | -0.10071 | -0.10071 | 63.1714 | -60.1685 | 63.0661 | -60.1593 | -60.2692 | -59.7702 | -0.27008 | 0.086975 | -0.26093 | 0.050354 | 59.9854 | -0.30212 | 60.2554 | -0.032044 | -0.082397 | 0.07782 | -0.027466 | -0.073242 | 0.31586 | -0.1831 | 0.39825 | -0.10071 | 0.32043 | 123.1888 | 0.009155 | 123.2346 | 123.5367 | 123.3398 | 123.2666 | 123.2574 | -123.4497 | -123.262 | 122.9187 | 123.1522 | 60.022 | 59.9854
569.4844 | 123.2758 | -60.1089 | 63.089 | -0.072937 | 0.0014163 | 0.062498 | 0.066253 | -0.00086946 | 0.0011386 | -0.0022345 | -0.047638 | 0.0018179 | 0.067063 | 0.061782 | -0.0021704 | -0.0010212 | 0.0075729 | -0.13275 | 63.1897 | -60.3561 | 62.7823 | -60.0998 | -60.4431 | -0.12817 | -0.16479 | 63.1851 | -60.1822 | 63.0707 | -60.1776 | -60.2783 | -59.7748 | -0.24719 | 0.10071 | -0.3067 | 0.009156 | 59.9808 | -0.33417 | 60.228 | -0.086975 | -0.073242 | 0.096131 | -0.01831 | -0.068664 | 0.33417 | -0.16937 | 0.40741 | -0.09613 | 0.25635 | 123.1384 | 0.004578 | 123.2529 | 123.5458 | 123.3673 | 123.2986 | 123.2941 | -123.4451 | -123.2712 | 122.8912 | 123.1796 | 59.9762 | 59.9442
570.4844 | 123.2849 | -60.0906 | 63.1165 | -0.065308 | 0.00034827 | 0.064207 | 0.064117 | -0.0019377 | -0.00057042 | -0.00073913 | -0.044586 | 0.0016043 | 0.068131 | 0.064773 | -0.002384 | -0.00016658 | 0.0035141 | -0.068665 | 63.176 | -60.3378 | 62.8372 | -60.0266 | -60.3607 | -0.07782 | -0.073242 | 63.1668 | -60.1547 | 63.0615 | -60.1364 | -60.2509 | -59.7565 | -0.24719 | 0.059509 | -0.27924 | 0.064087 | 60.0128 | -0.27008 | 60.26 | -0.022888 | -0.064087 | 0.050354 | -0.054932 | -0.045777 | 0.33417 | -0.16022 | 0.39825 | -0.09613 | 0.31128 | 123.175 | 0.01831 | 123.2162 | 123.5138 | 123.3215 | 123.2666 | 123.2574 | -123.4543 | -123.2712 | 122.9279 | 123.1522 | 60.022 | 60.0174
571.5625 | 123.3353 | -60.0952 | 63.0707 | -0.088196 | 0.00013467 | 0.060575 | 0.065826 | -0.0015103 | -0.00078402 | -0.00052553 | 0.004242 | 0.00032248 | 0.067917 | 0.069472 | -0.0032386 | 4.7018e-05 | 9.6064e-05 | -0.054932 | 63.2034 | -60.3333 | 62.8235 | -60.0494 | -60.4019 | -0.11902 | -0.14648 | 63.1714 | -60.173 | 63.0936 | -60.1273 | -60.2371 | -59.7748 | -0.23804 | 0.13275 | -0.24719 | 0.045777 | 59.9762 | -0.3067 | 60.2142 | -0.068665 | -0.07782 | 0.10071 | 0.022888 | -0.032043 | 0.32044 | -0.14191 | 0.39825 | -0.064087 | 0.28381 | 123.1567 | 0.045777 | 123.2666 | 123.5367 | 123.3444 | 123.2986 | 123.2666 | -123.4039 | -123.2437 | 122.9187 | 123.1888 | 60.0403 | 59.9487
572.4844 | 123.3353 | -60.054 | 63.0936 | -0.042419 | 0.0012027 | 0.061643 | 0.063903 | -0.0017239 | 0.0011386 | 0.00011527 | -0.011017 | 0.00096348 | 0.06749 | 0.061355 | -0.0017432 | 0.00047422 | -0.0031081 | -0.027466 | 63.1714 | -60.3424 | 62.8876 | -59.9579 | -60.3241 | -0.027466 | 0.018311 | 63.1714 | -60.1639 | 63.1485 | -60.0723 | -60.1959 | -59.7336 | -0.28839 | 0.07782 | -0.20599 | 0.09613 | 60.0266 | -0.27008 | 60.3149 | 0.01831 | -0.10986 | 0.07782 | 0.054932 | -0.018311 | 0.32043 | -0.14191 | 0.4303 | -0.032044 | 0.38452 | 123.23 | 0.091552 | 123.3124 | 123.5138 | 123.3353 | 123.2254 | 123.2254 | -123.436 | -123.2574 | 122.9416 | 123.2025 | 60.0266 | 60.0723
573.4844 | 123.4039 | -60.0632 | 63.0157 | -0.088196 | 0.00077547 | 0.063779 | 0.064331 | 0.0016939 | -0.00035682 | -0.0026617 | 0.013397 | 0.00096348 | 0.066208 | 0.056869 | -0.0017432 | -0.0025164 | 0.0020187 | -0.086975 | 63.1302 | -60.347 | 62.9196 | -59.9442 | -60.3149 | -0.059509 | -0.050354 | 63.1073 | -60.141 | 63.1805 | -60.0311 | -60.1501 | -59.6786 | -0.28381 | 0.11444 | -0.09613 | 0.11902 | 60.0037 | -0.25177 | 60.2875 | 0.032044 | -0.07782 | 0.091553 | 0.1648 | 0.032043 | 0.38452 | -0.086975 | 0.46234 | -0.009155 | 0.40283 | 123.2666 | 0.10986 | 123.3215 | 123.4772 | 123.2483 | 123.1934 | 123.1705 | -123.3627 | -123.1567 | 122.9828 | 123.2437 | 59.9762 | 60.0128
574.5469 | 123.2986 | -60.0677 | 63.089 | -0.027161 | 0.0014163 | 0.061643 | 0.064971 | 0.0025485 | -0.001852 | -0.0028753 | -0.038483 | 0.0011771 | 0.06749 | 0.066054 | -0.0021704 | -0.0031574 | 0.0043687 | -0.018311 | 63.1805 | -60.3516 | 62.9013 | -59.9808 | -60.3058 | -0.004578 | 0.027466 | 63.176 | -60.1685 | 63.1393 | -60.0586 | -60.1868 | -59.7336 | -0.28381 | 0.091553 | -0.18768 | 0.086975 | 60.0632 | -0.23804 | 60.347 | 0.045776 | -0.10071 | 0.086975 | 0.050354 | 0.009155 | 0.33417 | -0.11902 | 0.43487 | -0.018311 | 0.37079 | 123.2529 | 0.10986 | 123.3078 | 123.5321 | 123.3444 | 123.2483 | 123.2437 | -123.4406 | -123.2574 | 122.9691 | 123.2071 | 60.0494 | 60.0952
575.5 | 123.3673 | -60.0586 | 63.0386 | -0.11871 | 0.0012027 | 0.063138 | 0.063476 | 0.0010531 | -0.0027066 | -0.00052553 | 0.034759 | 0.00010888 | 0.065781 | 0.059859 | 0.0008204 | -0.00038018 | 0.00030966 | -0.07782 | 63.1165 | -60.3149 | 62.9059 | -59.9121 | -60.3012 | -0.032043 | -0.036621 | 63.0936 | -60.1318 | 63.1622 | -60.0632 | -60.1547 | -59.697 | -0.25635 | 0.07782 | -0.13275 | 0.14648 | 60.0266 | -0.24261 | 60.2829 | 0.013733 | -0.073242 | 0.054932 | 0.1236 | -0.004577 | 0.36163 | -0.09613 | 0.43488 | -0.022888 | 0.40283 | 123.2208 | 0.068665 | 123.2941 | 123.4314 | 123.2254 | 123.175 | 123.1522 | -123.3536 | -123.1705 | 122.9645 | 123.2208 | 59.9808 | 60.022
576.4844 | 123.2803 | -60.0723 | 63.0844 | -0.095825 | 0.0022709 | 0.065061 | 0.066894 | 0.0023349 | -0.0033474 | 0.0018243 | -0.044586 | -0.00095912 | 0.067276 | 0.068191 | 0.001034 | -0.00059378 | -0.0028945 | -0.064087 | 63.1851 | -60.3516 | 62.851 | -60.0357 | -60.3745 | -0.086975 | -0.10071 | 63.1714 | -60.1456 | 63.0707 | -60.1501 | -60.2371 | -59.7748 | -0.27923 | 0.10071 | -0.23346 | 0.036621 | 59.9854 | -0.30212 | 60.2646 | -0.022889 | -0.073242 | 0.086975 | -0.013733 | -0.077819 | 0.29755 | -0.16479 | 0.37079 | -0.091553 | 0.31586 | 123.2025 | -0.004577 | 123.2162 | 123.5367 | 123.317 | 123.2574 | 123.2437 | -123.436 | -123.23 | 122.9233 | 123.143 | 60.0082 | 59.9716
577.5625 | 123.3765 | -60.0403 | 63.0707 | -0.065308 | 0.0035525 | 0.064207 | 0.062408 | -0.0010831 | -0.0014248 | -0.0026617 | 0.031708 | -0.00074552 | 0.065781 | 0.064132 | -0.0025976 | -0.0018756 | -0.0013991 | -0.091553 | 63.1485 | -60.2921 | 62.8647 | -59.967 | -60.3195 | -0.041199 | -0.086975 | 63.1393 | -60.1501 | 63.121 | -60.0494 | -60.1501 | -59.7061 | -0.25177 | 0.07782 | -0.20599 | 0.073242 | 59.9991 | -0.27924 | 60.2509 | -0.027466 | -0.10986 | 0.068664 | 0.050354 | -0.009155 | 0.33417 | -0.10986 | 0.44403 | 0 | 0.32501 | 123.1567 | 0.10071 | 123.2712 | 123.4406 | 123.2895 | 123.1888 | 123.1796 | -123.3627 | -123.2208 | 122.905 | 123.1613 | 59.9487 | 59.9533
578.4844 | 123.3261 | -60.0586 | 63.0981 | 0.0033567 | -7.913e-05 | 0.065061 | 0.065185 | 0.0019077 | -0.00057042 | -0.00095273 | -0.053741 | 0.0024589 | 0.065354 | 0.064773 | -0.004093 | 0.00026062 | 0.0018051 | 0.004578 | 63.208 | -60.3195 | 62.9013 | -59.9396 | -60.3012 | 0.027466 | 0.050354 | 63.1622 | -60.1639 | 63.1485 | -60.0769 | -60.1913 | -59.7061 | -0.26093 | 0.10986 | -0.19684 | 0.11902 | 60.0861 | -0.24261 | 60.347 | 0.018311 | -0.10529 | 0.064086 | 0.050354 | -0.01831 | 0.35248 | -0.13275 | 0.45776 | -0.027466 | 0.37994 | 123.2208 | 0.086975 | 123.3124 | 123.5275 | 123.3261 | 123.2666 | 123.2208 | -123.4177 | -123.262 | 122.9599 | 123.2071 | 60.0632 | 60.1089
579.5469 | 123.3124 | -60.0815 | 63.1119 | -0.011902 | 0.00013467 | 0.060575 | 0.064117 | 0.00041234 | -0.0016384 | 0.00032907 | -0.029327 | -0.00095912 | 0.066635 | 0.067763 | -0.0025976 | -0.00080758 | 0.00095066 | -0.16479 | 63.1531 | -60.3699 | 62.8784 | -59.9808 | -60.3241 | -0.022888 | 0.013733 | 63.1577 | -60.1456 | 63.121 | -60.0998 | -60.2097 | -59.7382 | -0.28839 | 0.041199 | -0.23346 | 0.10071 | 60.0586 | -0.24262 | 60.347 | 0.045776 | -0.064087 | 0.045777 | 0.009156 | -0.01831 | 0.34332 | -0.12817 | 0.40741 | -0.064087 | 0.3891 | 123.2483 | 0.045777 | 123.2666 | 123.5229 | 123.3032 | 123.2346 | 123.2391 | -123.4818 | -123.2574 | 122.9599 | 123.2025 | 59.9167 | 60.0952
580.5 | 123.381 | -60.0677 | 63.0432 | -0.14923 | 0.0024845 | 0.063779 | 0.063903 | -1.486e-05 | -0.0014248 | -0.0024481 | 0.022552 | 0.00053628 | 0.065354 | 0.063918 | -0.0025976 | -0.00080758 | 0.0018051 | 0.082397 | 63.1348 | -60.3012 | 62.9471 | -59.9213 | -60.2966 | -0.041199 | -0.027466 | 63.1256 | -60.1501 | 63.1805 | -60.0311 | -60.1318 | -59.6924 | -0.23346 | 0.091553 | -0.09613 | 0.14648 | 60.0266 | -0.22888 | 60.26 | 0.004577 | -0.082397 | 0.082397 | 0.13733 | 0.036621 | 0.37537 | -0.064087 | 0.45776 | 0.01831 | 0.37994 | 123.2483 | 0.11902 | 123.3307 | 123.436 | 123.2758 | 123.2025 | 123.1934 | -123.3444 | -123.1934 | 123.0148 | 123.2483 | 60.1501 | 60.0403
581.4844 | 123.3994 | -60.0357 | 63.0524 | -0.088196 | 0.0012027 | 0.063138 | 0.064331 | -0.0030057 | 0.0011386 | 0.0022517 | 0.010345 | 0.00053628 | 0.067704 | 0.072463 | -0.003025 | -0.0014484 | 0.00095066 | -0.059509 | 63.1073 | -60.3424 | 62.9425 | -59.9442 | -60.2829 | -0.045776 | -0.036621 | 63.1027 | -60.1547 | 63.1897 | -60.0266 | -60.1318 | -59.6695 | -0.3067 | 0.054932 | -0.10986 | 0.091553 | 59.9899 | -0.24719 | 60.2966 | 0.059509 | -0.11902 | 0.050354 | 0.13733 | 0.009156 | 0.36621 | -0.09613 | 0.48523 | 0.022888 | 0.39825 | 123.2849 | 0.12817 | 123.3444 | 123.4497 | 123.2574 | 123.143 | 123.1384 | -123.3948 | -123.2071 | 122.9782 | 123.2254 | 59.9762 | 59.9991
582.5469 | 123.2941 | -60.0861 | 63.1165 | 0.0033567 | -0.00050633 | 0.06207 | 0.064758 | -0.0055691 | -0.00014322 | 0.00011527 | -0.0079652 | 0.0026725 | 0.06514 | 0.058578 | -0.0002478 | -0.0012348 | -0.00011754 | -0.050354 | 63.2263 | -60.3012 | 62.7823 | -59.7839 | -60.2097 | -0.11444 | -0.018311 | 63.1897 | -60.1456 | 63.0981 | -60.0952 | -60.1959 | -59.7382 | -0.21515 | 0.10986 | -0.33417 | 0.30212 | 59.9716 | -0.1236 | 60.1868 | 0.091552 | -0.059509 | 0.073242 | -0.01831 | -0.009155 | 0.3479 | -0.10986 | 0.40741 | -0.050354 | 0.51727 | 123.0835 | 0.050354 | 123.2437 | 123.5275 | 123.3353 | 123.3124 | 123.2758 | -123.4177 | -123.262 | 122.8683 | 123.1842 | 60.0357 | 60.0677
583.4844 | 123.3902 | -60.0815 | 63.0569 | -0.095825 | 0.00056187 | 0.063566 | 0.063262 | -0.00022866 | -0.0016384 | -0.00052553 | -0.029327 | -0.00010472 | 0.066422 | 0.066909 | -0.002384 | -0.0025164 | -0.00011754 | -0.11902 | 63.1348 | -60.3653 | 62.851 | -59.9991 | -60.3653 | -0.09613 | -0.09613 | 63.121 | -60.1593 | 63.1714 | -60.0723 | -60.173 | -59.6878 | -0.28381 | 0.07782 | -0.20599 | 0.082398 | 59.9854 | -0.28381 | 60.2692 | 0 | -0.07782 | 0.064087 | 0.11444 | 0.009155 | 0.39368 | -0.091553 | 0.4715 | -0.013733 | 0.36621 | 123.2162 | 0.086975 | 123.3307 | 123.5001 | 123.2803 | 123.2162 | 123.2025 | -123.4222 | -123.2162 | 122.9324 | 123.2529 | 59.9625 | 59.9854
584.4844 | 123.3124 | -60.0906 | 63.0569 | -0.10345 | 0.0022709 | 0.064207 | 0.062408 | -0.0030057 | -0.002493 | 0.0026789 | -0.059845 | 0.00032248 | 0.06749 | 0.069045 | -3.4196e-05 | -0.00016658 | 0.00030966 | -0.12817 | 63.1668 | -60.3882 | 62.8235 | -60.0998 | -60.2554 | -0.10986 | -0.11902 | 63.1851 | -60.173 | 63.0753 | -60.1318 | -60.2554 | -59.7702 | -0.29755 | 0.10986 | -0.23346 | -0.009155 | 59.9808 | -0.16479 | 60.2783 | 0.13275 | -0.082398 | 0.12817 | 0.01831 | -0.041199 | 0.32043 | -0.16479 | 0.40283 | -0.082397 | 0.28839 | 123.2117 | 0.041199 | 123.2483 | 123.555 | 123.3582 | 123.2574 | 123.2758 | -123.4451 | -123.23 | 122.9141 | 123.1659 | 59.9625 | 59.9716
585.4844 | 123.4039 | -60.0677 | 63.0707 | -0.065308 | -0.00029273 | 0.061857 | 0.063476 | -0.00065586 | 0.00049778 | -0.00073913 | 0.050018 | 0.00096348 | 0.066422 | 0.062636 | 0.0006066 | -0.0037982 | -0.00033114 | 0.050354 | 63.2172 | -60.3058 | 62.8967 | -59.9625 | -60.2921 | 0.013733 | -0.032043 | 63.1393 | -60.1639 | 63.1485 | -60.022 | -60.1135 | -59.6741 | -0.23804 | 0.14648 | -0.17395 | 0.10529 | 60.0815 | -0.2243 | 60.3195 | 0.013733 | -0.09613 | 0.068664 | 0.07782 | 0.045776 | 0.39368 | -0.045776 | 0.48981 | 0.050354 | 0.34332 | 123.2025 | 0.14191 | 123.3124 | 123.5229 | 123.3032 | 123.2849 | 123.2071 | -123.3765 | -123.2346 | 122.9645 | 123.2162 | 60.1181 | 60.0357
586.5469 | 123.3078 | -60.0769 | 63.1027 | -0.03479 | 0.00098907 | 0.061643 | 0.064544 | -0.0010831 | -0.0012112 | -0.0013799 | -0.044586 | 0.0011771 | 0.069199 | 0.064986 | -0.0011022 | -0.0014484 | -0.0026809 | -0.054932 | 63.2584 | -60.3149 | 62.796 | -60.2051 | -60.3241 | 0 | 0 | 63.1989 | -60.1822 | 63.0981 | -60.0952 | -60.1776 | -59.7427 | -0.23804 | 0.15564 | -0.3067 | -0.12817 | 60.0769 | -0.24719 | 60.3149 | -0.009156 | -0.10529 | 0.096131 | -0.004577 | -0.018311 | 0.33417 | -0.10071 | 0.43945 | 0.004578 | 0.10986 | 123.111 | 0.086975 | 123.2803 | 123.5733 | 123.381 | 123.3353 | 123.2758 | -123.4177 | -123.2849 | 122.8729 | 123.175 | 60.022 | 60.0769
587.4844 | 123.3719 | -60.054 | 63.0432 | -0.065308 | -0.0026425 | 0.064207 | 0.063476 | 0.00041234 | -0.0031338 | 0.0013971 | -0.014069 | 0.0011771 | 0.06749 | 0.063277 | -0.0032386 | 0.001756 | 0.0011643 | -0.10986 | 63.1439 | -60.3516 | 62.8555 | -59.9945 | -60.3607 | -0.10071 | -0.082397 | 63.1302 | -60.1593 | 63.1622 | -60.0082 | -60.2051 | -59.729 | -0.29755 | 0.10071 | -0.18768 | 0.059509 | 59.9533 | -0.3067 | 60.2509 | -0.009156 | -0.10529 | 0.086975 | 0.11902 | 0.045776 | 0.32501 | -0.15106 | 0.4303 | -0.045776 | 0.35706 | 123.2071 | 0.15106 | 123.3215 | 123.4955 | 123.2895 | 123.1979 | 123.1842 | -123.3948 | -123.2025 | 122.9095 | 123.2162 | 59.9442 | 59.9716
588.4844 | 123.2574 | -60.1044 | 63.1027 | -0.095825 | 0.0012027 | 0.063993 | 0.064971 | -0.0023649 | 0.0024204 | 0.0018243 | -0.099518 | 0.0013907 | 0.066422 | 0.069045 | -0.0004614 | 0.00047422 | 0.0018051 | -0.11902 | 63.1851 | -60.379 | 62.8143 | -60.1089 | -60.4477 | -0.14191 | -0.17395 | 63.1714 | -60.1913 | 63.0615 | -60.1501 | -60.2692 | -59.7794 | -0.27466 | 0.082398 | -0.28839 | -0.004578 | 59.9625 | -0.34332 | 60.2371 | -0.068665 | -0.086975 | 0.068665 | -0.041199 | -0.045776 | 0.32501 | -0.16479 | 0.41199 | -0.07782 | 0.27008 | 123.1934 | 0.041199 | 123.2529 | 123.5641 | 123.3627 | 123.2895 | 123.2758 | -123.4818 | -123.2941 | 122.9187 | 123.1659 | 59.9854 | 59.9304
589.4844 | 123.381 | -60.0357 | 63.0432 | -0.057678 | 0.0022709 | 0.065488 | 0.06604 | 0.0010531 | 0.002634 | 0.00054267 | 0.004242 | 0.0013907 | 0.067276 | 0.062209 | 0.0006066 | -0.0023028 | -0.0039627 | -0.059509 | 63.1256 | -60.3287 | 62.915 | -59.903 | -60.2966 | -0.027466 | -0.032043 | 63.1348 | -60.1593 | 63.1668 | -60.0266 | -60.141 | -59.697 | -0.29297 | 0.082397 | -0.12817 | 0.13275 | 60.0082 | -0.26093 | 60.3012 | 0.032043 | -0.1236 | 0.091553 | 0.1236 | 0.009156 | 0.33875 | -0.10529 | 0.46234 | 0.018311 | 0.42572 | 123.2437 | 0.13275 | 123.3261 | 123.4543 | 123.2941 | 123.1613 | 123.1705 | -123.3719 | -123.2025 | 122.9507 | 123.2025 | 59.9762 | 60.0037
590.4844 | 123.3765 | -60.0677 | 63.0615 | -0.072937 | 0.00077547 | 0.062711 | 0.065399 | 0.0023349 | -0.00014322 | 0.0011835 | -0.023224 | 0.00010888 | 0.066422 | 0.064132 | -0.003025 | 0.00047422 | -0.0031081 | -0.10529 | 63.1302 | -60.3333 | 62.8693 | -59.9899 | -60.3378 | -0.07782 | -0.086975 | 63.0981 | -60.1593 | 63.1485 | -60.022 | -60.1456 | -59.6924 | -0.2655 | 0.068665 | -0.19226 | 0.07782 | 59.9899 | -0.27008 | 60.2554 | -0.004578 | -0.091553 | 0.036622 | 0.086976 | 0.045776 | 0.37537 | -0.07782 | 0.46692 | 0.013733 | 0.34332 | 123.2025 | 0.13733 | 123.3078 | 123.4634 | 123.2574 | 123.1979 | 123.1659 | -123.3948 | -123.2208 | 122.937 | 123.2162 | 59.9625 | 59.9808
591.5469 | 123.3398 | -60.0586 | 63.0707 | -0.0042723 | -0.00093353 | 0.063138 | 0.064758 | -0.0038603 | 0.0013522 | 0.00032907 | -0.041534 | -0.00074552 | 0.067276 | 0.065414 | -0.001316 | -0.00080758 | 0.0033005 | -0.11902 | 63.1622 | -60.3607 | 62.8281 | -60.0403 | -60.3973 | -0.11444 | -0.13275 | 63.1393 | -60.1913 | 63.1119 | -60.1044 | -60.2234 | -59.7473 | -0.30212 | 0.091552 | -0.24262 | 0.018311 | 59.9442 | -0.33875 | 60.2463 | -0.036621 | -0.13275 | 0.068664 | 0.041198 | -0.045776 | 0.31128 | -0.16479 | 0.44403 | -0.032044 | 0.32043 | 123.1888 | 0.086975 | 123.3032 | 123.5229 | 123.3307 | 123.2208 | 123.1979 | -123.4314 | -123.262 | 122.8867 | 123.1705 | 59.9396 | 59.9258
592.4844 | 123.2529 | -60.1044 | 63.0615 | -0.080566 | 0.0022709 | 0.06442 | 0.064758 | 0.0012667 | -0.00099762 | 0.0026789 | -0.065949 | 0.00074988 | 0.064926 | 0.067336 | -0.0017432 | 0.00047422 | 0.0065049 | -0.10986 | 63.1668 | -60.3607 | 62.7914 | -60.1089 | -60.4385 | -0.11902 | -0.16022 | 63.1485 | -60.1913 | 63.0753 | -60.141 | -60.2783 | -59.7839 | -0.25635 | 0.10529 | -0.27008 | -0.004578 | 59.9854 | -0.33417 | 60.2417 | -0.07782 | -0.086975 | 0.086976 | 0.013733 | -0.036621 | 0.32043 | -0.17395 | 0.40741 | -0.086975 | 0.25177 | 123.1522 | 0.050354 | 123.2666 | 123.5275 | 123.3398 | 123.2712 | 123.2529 | -123.4222 | -123.2529 | 122.8958 | 123.1796 | 59.9945 | 59.9442
593.4844 | 123.3627 | -60.0769 | 63.0341 | -0.011902 | 0.00098907 | 0.063779 | 0.063476 | -0.0036465 | -0.00014322 | -0.0022345 | 0.016449 | -0.0018137 | 0.066422 | 0.065414 | 0.0008204 | -0.0014484 | -0.00011754 | -0.068665 | 63.1531 | -60.3058 | 62.9242 | -59.9213 | -60.2737 | -0.032043 | -0.022888 | 63.1119 | -60.1547 | 63.1714 | -60.0266 | -60.1273 | -59.6786 | -0.22888 | 0.11902 | -0.10986 | 0.15564 | 60.0449 | -0.19684 | 60.2737 | 0.032043 | -0.07782 | 0.077819 | 0.13733 | 0.050354 | 0.39825 | -0.050354 | 0.47607 | 0.027466 | 0.38452 | 123.23 | 0.12817 | 123.3261 | 123.4589 | 123.2666 | 123.23 | 123.1888 | -123.3398 | -123.1888 | 123.0011 | 123.2483 | 60.0082 | 60.054
594.4844 | 123.2895 | -60.0952 | 63.0753 | -0.050049 | -0.0026425 | 0.065275 | 0.065399 | -0.0017239 | 0.00092498 | 0.00054267 | -0.035431 | 0.0026725 | 0.066422 | 0.065841 | -0.0011022 | -0.00016658 | -0.00054474 | -0.12817 | 63.1577 | -60.3607 | 62.7914 | -59.9579 | -60.4019 | -0.15564 | -0.17395 | 63.1714 | -60.1776 | 63.0844 | -60.1456 | -60.2509 | -59.7702 | -0.2655 | 0.082398 | -0.28381 | 0.13733 | 59.9396 | -0.3067 | 60.2051 | -0.041199 | -0.082397 | 0.096131 | 0.009156 | -0.050354 | 0.32501 | -0.15564 | 0.40741 | -0.073242 | 0.40283 | 123.1522 | 0.032043 | 123.262 | 123.5184 | 123.349 | 123.2529 | 123.2666 | -123.436 | -123.2529 | 122.8867 | 123.1796 | 59.967 | 59.9213
595.5625 | 123.2849 | -60.0723 | 63.0936 | -0.057678 | 0.0020573 | 0.06677 | 0.066467 | 0.0027621 | 0.00049778 | -0.0011663 | -0.069 | 0.0020315 | 0.066635 | 0.068191 | -0.0004614 | -0.0010212 | -0.00075834 | -0.036621 | 63.1989 | -60.3516 | 62.8693 | -59.9762 | -60.3378 | -0.036621 | -0.027466 | 63.1897 | -60.1685 | 63.1027 | -60.1273 | -60.2325 | -59.7656 | -0.27923 | 0.10529 | -0.2243 | 0.096131 | 60.0357 | -0.2655 | 60.3149 | 0.013732 | -0.09613 | 0.09613 | 0.009155 | -0.054931 | 0.3067 | -0.16022 | 0.40283 | -0.064087 | 0.37537 | 123.2208 | 0.041199 | 123.2712 | 123.5504 | 123.3582 | 123.2712 | 123.262 | -123.4451 | -123.262 | 122.9416 | 123.175 | 60.0357 | 60.0449
596.4844 | 123.2849 | -60.0906 | 63.0844 | -0.042419 | 0.00056187 | 0.066343 | 0.064971 | -0.00022866 | -0.0022794 | -0.00031193 | -0.011017 | -0.00010472 | 0.068985 | 0.064773 | -0.0019568 | -0.0027302 | -0.0022537 | -0.14648 | 63.1622 | -60.3699 | 62.8143 | -60.0632 | -60.4797 | -0.41199 | -0.050354 | 63.1531 | -60.173 | 63.1119 | -60.1547 | -60.2371 | -59.7473 | -0.27924 | 0.077819 | -0.27008 | 0.027466 | 59.6786 | -0.3891 | 59.9579 | -0.10986 | -0.082398 | 0.068664 | 0.027465 | -0.064087 | 0.34332 | -0.14648 | 0.42572 | -0.064087 | 0.3067 | 123.1842 | 0.018311 | 123.2849 | 123.5321 | 123.3261 | 123.2529 | 123.2437 | -123.4543 | -123.2574 | 122.905 | 123.2025 | 59.9442 | 60.0403
597.5 | 123.2986 | -60.0494 | 63.1165 | -0.042419 | 0.0014163 | 0.063352 | 0.061981 | -0.0010831 | -0.00014322 | 0.0011835 | 0.031708 | 0.00010888 | 0.066849 | 0.066909 | -0.0015296 | -0.0035846 | -0.00097194 | -0.004578 | 63.2034 | -60.2783 | 62.8876 | -59.9396 | -60.2829 | 0.045776 | 0.045776 | 63.1805 | -60.1456 | 63.1073 | -60.0769 | -60.173 | -59.7382 | -0.22888 | 0.086975 | -0.22888 | 0.10986 | 60.0952 | -0.23346 | 60.3241 | -0.004578 | -0.096131 | 0.064087 | -0.009155 | -0.027466 | 0.31128 | -0.1236 | 0.40741 | -0.027466 | 0.33875 | 123.1659 | 0.068665 | 123.2529 | 123.4818 | 123.3261 | 123.2529 | 123.23 | -123.3948 | -123.262 | 122.937 | 123.1567 | 60.0449 | 60.0952
598.5625 | 123.4085 | -60.0403 | 63.0524 | -0.011902 | 0.00056187 | 0.063993 | 0.066894 | 0.0021213 | 7.0582e-05 | 0.00096987 | -0.029327 | 0.0030997 | 0.066849 | 0.057937 | -0.001316 | 0.00090142 | -0.0020401 | -0.082397 | 63.1302 | -60.3378 | 62.9196 | -59.935 | -60.3058 | -0.045776 | -0.045776 | 63.1119 | -60.1318 | 63.1989 | -60.0174 | -60.1318 | -59.6512 | -0.29755 | 0.07782 | -0.13275 | 0.10529 | 59.9945 | -0.2655 | 60.2921 | 0.032044 | -0.091553 | 0.059509 | 0.14648 | 0.022888 | 0.3891 | -0.091553 | 0.48065 | 0 | 0.40283 | 123.2574 | 0.11444 | 123.3307 | 123.468 | 123.2437 | 123.1705 | 123.1522 | -123.3902 | -123.1842 | 122.9599 | 123.2391 | 59.9579 | 59.9945
599.5 | 123.2803 | -60.0586 | 63.1531 | -0.03479 | 0.00034827 | 0.061857 | 0.064971 | 0.00041234 | 0.00049778 | -0.0024481 | -0.0049134 | 0.0013907 | 0.06749 | 0.066268 | -0.0004614 | -0.001662 | 0.0013779 | -0.032043 | 63.2126 | -60.3104 | 62.8647 | -59.9808 | -60.3287 | 0.013733 | 0.027466 | 63.2126 | -60.1273 | 63.0844 | -60.0769 | -60.173 | -59.7565 | -0.25177 | 0.059509 | -0.28839 | 0.07782 | 60.0723 | -0.27008 | 60.3241 | -0.01831 | -0.068664 | 0.059509 | -0.068664 | -0.01831 | 0.30212 | -0.11444 | 0.37079 | -0.045777 | 0.32959 | 123.175 | 0.050354 | 123.2117 | 123.5229 | 123.3398 | 123.2712 | 123.2712 | -123.4634 | -123.2803 | 122.9233 | 123.143 | 60.0266 | 60.0861
600.5469 | 123.2758 | -60.0815 | 63.1073 | 0.0033567 | 0.00013467 | 0.062925 | 0.06604 | 0.0055393 | -0.0014248 | 0.00096987 | -0.059845 | 0.00053628 | 0.066635 | 0.068831 | -0.0008886 | -0.001662 | 0.00052346 | -0.086975 | 63.1805 | -60.347 | 62.851 | -60.0357 | -60.3745 | -0.09613 | -0.10529 | 63.1668 | -60.1776 | 63.0753 | -60.1822 | -60.2692 | -59.7794 | -0.2655 | 0.073242 | -0.25635 | 0.045776 | 59.9854 | -0.29297 | 60.2509 | -0.027466 | -0.09613 | 0.059509 | -0.032044 | -0.10071 | 0.30212 | -0.18768 | 0.39825 | -0.091553 | 0.31128 | 123.1979 | -0.004578 | 123.2529 | 123.5275 | 123.3444 | 123.262 | 123.2483 | -123.4543 | -123.2849 | 122.9324 | 123.1567 | 59.9945 | 59.9762
601.4844 | 123.3719 | -60.0677 | 63.0615 | -0.057678 | 0.00034827 | 0.065702 | 0.06369 | 0.0016939 | 0.0013522 | -9.8328e-05 | 0.004242 | 0.00010888 | 0.066635 | 0.060073 | -0.001316 | -0.0012348 | 0.0039413 | -0.082397 | 63.1256 | -60.3058 | 62.8922 | -59.9487 | -60.3287 | -0.041199 | -0.059509 | 63.121 | -60.1639 | 63.1256 | -60.0449 | -60.1456 | -59.7015 | -0.23804 | 0.064087 | -0.16937 | 0.11902 | 60.0266 | -0.26093 | 60.2646 | -0.022888 | -0.09613 | 0.05951 | 0.064087 | 0.022888 | 0.36621 | -0.07782 | 0.46234 | 0.01831 | 0.35706 | 123.1979 | 0.11902 | 123.2895 | 123.4314 | 123.2849 | 123.1934 | 123.1888 | -123.3673 | -123.2254 | 122.9599 | 123.1934 | 59.9854 | 60.0082
602.5 | 123.3536 | -60.0357 | 63.089 | -0.057678 | 0.00056187 | 0.063779 | 0.063476 | 0.0014803 | 0.00049778 | 0.00075627 | 0.022552 | -0.0024545 | 0.068772 | 0.061782 | -3.4196e-05 | 0.001756 | 9.6064e-05 | -0.068665 | 63.1531 | -60.3058 | 62.9837 | -59.9487 | -60.3653 | 0.009155 | -0.018311 | 63.1393 | -60.141 | 63.1393 | -60.0266 | -60.1273 | -59.6878 | -0.27008 | 0.064087 | -0.10528 | 0.086976 | 60.0449 | -0.32959 | 60.3149 | -0.059509 | -0.10529 | 0.050354 | 0.050354 | 0.009156 | 0.3479 | -0.091552 | 0.45319 | 0.013733 | 0.35706 | 123.2895 | 0.11444 | 123.2803 | 123.4589 | 123.2803 | 123.1888 | 123.175 | -123.3948 | -123.23 | 123.0194 | 123.175 | 59.967 | 60.0174
603.5469 | 123.3124 | -60.0357 | 63.1256 | -0.057678 | -7.913e-05 | 0.063352 | 0.065185 | -0.0019377 | 0.0015658 | -0.0024481 | 0.004242 | -0.00053192 | 0.064286 | 0.06285 | -0.003025 | -0.0012348 | -0.00075834 | 0.027466 | 63.1897 | -60.2829 | 62.9288 | -59.9121 | -60.2509 | 0.07782 | 0.10529 | 63.1989 | -60.1044 | 63.1348 | -60.0494 | -60.1456 | -59.7198 | -0.24719 | 0.064087 | -0.19684 | 0.1236 | 60.1135 | -0.21515 | 60.3607 | 0.032044 | -0.068664 | 0.073243 | 0.009156 | -0.013732 | 0.31586 | -0.10986 | 0.38452 | -0.041199 | 0.37079 | 123.2117 | 0.054932 | 123.2391 | 123.4726 | 123.3032 | 123.2254 | 123.2346 | -123.4085 | -123.23 | 122.9645 | 123.1705 | 60.0632 | 60.141
604.4844 | 123.3215 | -60.0861 | 63.0707 | -0.14923 | -0.0013607 | 0.062711 | 0.067535 | -0.0027921 | -0.0022794 | 0.00011527 | -0.084259 | 0.0011771 | 0.065781 | 0.061996 | -0.003025 | -0.00080758 | -0.0018265 | -0.1236 | 63.1393 | -60.3836 | 62.851 | -60.1044 | -60.26 | -0.10071 | -0.10529 | 63.1851 | -60.1776 | 63.0798 | -60.1227 | -60.2554 | -59.761 | -0.29755 | 0.068664 | -0.21973 | -0.01831 | 59.9854 | -0.17395 | 60.2829 | 0.1236 | -0.091552 | 0.11444 | 0.009155 | -0.036621 | 0.32501 | -0.16937 | 0.41657 | -0.07782 | 0.27924 | 123.2346 | 0.054931 | 123.2574 | 123.5229 | 123.3627 | 123.2254 | 123.2712 | -123.4543 | -123.2483 | 122.937 | 123.1659 | 59.9625 | 59.9808
605.5 | 123.4039 | -60.0494 | 63.0844 | -0.088196 | 0.00056187 | 0.062925 | 0.064544 | -0.0019377 | -0.0014248 | -0.0018073 | 0.043915 | -0.00095912 | 0.066849 | 0.066482 | -0.0019568 | -0.0035846 | -0.0011855 | -0.086975 | 63.1485 | -60.3149 | 62.9105 | -59.9442 | -60.3104 | 0.013733 | -0.013733 | 63.1439 | -60.1456 | 63.176 | -59.9854 | -60.0861 | -59.6695 | -0.2655 | 0.064087 | -0.17395 | 0.10529 | 60.0632 | -0.26093 | 60.3287 | 0.004577 | -0.096131 | 0.059509 | 0.091552 | 0.064086 | 0.37994 | -0.036622 | 0.47607 | 0.059509 | 0.37079 | 123.2254 | 0.16022 | 123.3215 | 123.4634 | 123.2895 | 123.1979 | 123.1934 | -123.3994 | -123.23 | 122.9599 | 123.2254 | 59.9625 | 60.0357
606.5469 | 123.2986 | -60.0403 | 63.1393 | -0.065308 | -0.00071993 | 0.062925 | 0.064117 | 0.0012667 | -0.0039884 | -0.0030889 | -0.011017 | -0.0013863 | 0.064072 | 0.059218 | -0.0008886 | -0.00059378 | 0.00030966 | 0.027466 | 63.176 | -60.3012 | 62.9013 | -59.9442 | -60.2646 | 0.050354 | 0.064087 | 63.1943 | -60.1456 | 63.0844 | -60.054 | -60.1913 | -59.7565 | -0.26093 | 0.036621 | -0.23804 | 0.09613 | 60.0906 | -0.2243 | 60.3516 | 0.036621 | -0.10529 | 0.054932 | -0.054931 | -0.013733 | 0.28381 | -0.15106 | 0.3891 | -0.045776 | 0.35706 | 123.2025 | 0.091553 | 123.23 | 123.4772 | 123.3398 | 123.2162 | 123.2346 | -123.4406 | -123.2849 | 122.9416 | 123.1247 | 60.0677 | 60.1044
607.5 | 123.4177 | -60.022 | 63.0981 | -0.050049 | 0.00013467 | 0.06442 | 0.064544 | 0.00041234 | 0.0011386 | 0.0016107 | 0.028656 | 0.0011771 | 0.067063 | 0.066482 | -0.000675 | -0.0014484 | 0.0013779 | -0.036621 | 63.1577 | -60.2966 | 62.9471 | -59.8984 | -60.2509 | 0.054932 | 0.059509 | 63.1439 | -60.1227 | 63.1851 | -59.9762 | -60.0815 | -59.6603 | -0.27466 | 0.059509 | -0.15106 | 0.1236 | 60.0769 | -0.22888 | 60.3516 | 0.045777 | -0.10071 | 0.045776 | 0.086975 | 0.045777 | 0.36163 | -0.059509 | 0.46234 | 0.041199 | 0.39825 | 123.2437 | 0.14648 | 123.3078 | 123.4543 | 123.2666 | 123.1796 | 123.1659 | -123.3948 | -123.2208 | 122.9691 | 123.2071 | 59.9854 | 60.0815
608.5469 | 123.262 | -60.0906 | 63.1027 | -0.03479 | -7.913e-05 | 0.062711 | 0.06604 | 0.0036165 | -0.00057042 | 0.00032907 | -0.093414 | 0.0028861 | 0.06749 | 0.06755 | -0.0019568 | 0.00090142 | 0.00052346 | -0.07782 | 63.1851 | -60.3561 | 62.8326 | -60.0311 | -60.3836 | -0.09613 | -0.1236 | 63.1851 | -60.1776 | 63.0661 | -60.1456 | -60.2646 | -59.7977 | -0.2655 | 0.082398 | -0.27008 | 0.059509 | 59.9945 | -0.29297 | 60.26 | -0.027466 | -0.086975 | 0.082398 | -0.036621 | -0.054932 | 0.29297 | -0.17395 | 0.37994 | -0.086975 | 0.32501 | 123.1888 | 0.032043 | 123.2437 | 123.5413 | 123.3627 | 123.2758 | 123.2758 | -123.4589 | -123.2803 | 122.9233 | 123.1567 | 60.0128 | 59.967
609.4844 | 123.3582 | -60.0449 | 63.0524 | -0.057678 | 0.00098907 | 0.062711 | 0.062835 | 0.0021213 | 0.00049778 | 0.00075627 | -0.0049134 | 0.00032248 | 0.065781 | 0.066268 | -0.0019568 | -0.0014484 | 0.00030966 | -0.059509 | 63.089 | -60.3516 | 62.9379 | -59.8801 | -60.3195 | -0.050354 | -0.027466 | 63.1027 | -60.1547 | 63.176 | -60.0311 | -60.1227 | -59.6924 | -0.3067 | 0.036621 | -0.11444 | 0.16479 | 59.9945 | -0.27466 | 60.3012 | 0.032043 | -0.10986 | 0.050354 | 0.1236 | 0.013733 | 0.35248 | -0.07782 | 0.46234 | 0.032043 | 0.4715 | 123.2895 | 0.1236 | 123.3307 | 123.4406 | 123.2574 | 123.1338 | 123.1476 | -123.4039 | -123.2071 | 122.9828 | 123.2208 | 59.9854 | 60.0174
610.5469 | 123.317 | -60.0723 | 63.0936 | 0.018616 | 0.00034827 | 0.063566 | 0.065612 | -0.0012967 | -0.0020658 | -9.8328e-05 | -0.047638 | 0.0033133 | 0.065995 | 0.06755 | -0.002384 | 0.0019696 | -0.00033114 | -0.027466 | 63.208 | -60.3378 | 62.8738 | -59.9945 | -60.3287 | -0.004578 | -0.004578 | 63.2126 | -60.1501 | 63.121 | -60.0494 | -60.1822 | -59.7198 | -0.2655 | 0.11444 | -0.21973 | 0.07782 | 60.0677 | -0.25635 | 60.3333 | 0.009156 | -0.077819 | 0.11902 | 0.027466 | 0.022889 | 0.35248 | -0.10986 | 0.4303 | -0.032044 | 0.34332 | 123.2117 | 0.10071 | 123.2712 | 123.5458 | 123.3627 | 123.2803 | 123.2849 | -123.4314 | -123.2437 | 122.9462 | 123.1934 | 60.0449 | 60.0677
611.4844 | 123.3124 | -60.0952 | 63.0707 | -0.027161 | -0.0011471 | 0.061857 | 0.064758 | 0.00062594 | 0.00028418 | -0.00073913 | -0.056793 | 0.0024589 | 0.065995 | 0.0652 | -0.0011022 | -0.001662 | -0.0011855 | -0.09613 | 63.1577 | -60.3699 | 62.8418 | -60.054 | -60.3973 | -0.13275 | -0.15106 | 63.1393 | -60.1776 | 63.121 | -60.1089 | -60.2371 | -59.7473 | -0.27466 | 0.086975 | -0.22888 | 0.041199 | 59.9625 | -0.30212 | 60.2371 | -0.027466 | -0.082397 | 0.068664 | 0.050354 | -0.013733 | 0.3479 | -0.14191 | 0.4303 | -0.05951 | 0.31586 | 123.2117 | 0.068664 | 123.2986 | 123.5275 | 123.317 | 123.2529 | 123.2346 | -123.4406 | -123.2483 | 122.937 | 123.2162 | 59.9991 | 59.9442
612.5625 | 123.3765 | -60.0677 | 63.0844 | -0.095825 | -0.0032833 | 0.062925 | 0.062408 | 0.0012667 | 0.0017794 | -0.0022345 | 0.043915 | 0.00032248 | 0.069412 | 0.061141 | 0.0001794 | -0.0031574 | 0.00095066 | 0.041199 | 63.1897 | -60.3104 | 62.9013 | -59.9533 | -60.3195 | -0.009155 | -0.032043 | 63.1485 | -60.1364 | 63.1485 | -60.0357 | -60.1089 | -59.6695 | -0.24262 | 0.10529 | -0.18311 | 0.11444 | 60.0586 | -0.25177 | 60.3012 | -0.009155 | -0.068665 | 0.064087 | 0.064087 | 0.032043 | 0.39825 | -0.041199 | 0.46692 | 0.027466 | 0.35706 | 123.2117 | 0.10071 | 123.2849 | 123.5001 | 123.2849 | 123.2574 | 123.2162 | -123.3948 | -123.2208 | 122.9691 | 123.2162 | 60.1089 | 60.0357
613.4844 | 123.2849 | -60.0723 | 63.0707 | 0.14069 | 0.0022709 | 0.065061 | 0.063903 | 0.0010531 | -0.00078402 | 0.0028925 | -0.075104 | -0.00095912 | 0.064926 | 0.066054 | -0.001316 | 0.00026062 | -0.00054474 | -0.13733 | 63.1714 | -60.347 | 62.8235 | -60.0677 | -60.3745 | -0.1236 | -0.14191 | 63.1531 | -60.1822 | 63.0981 | -60.1318 | -60.2554 | -59.7748 | -0.27466 | 0.10071 | -0.24719 | 0.004578 | 59.9487 | -0.30212 | 60.2234 | -0.027466 | -0.10986 | 0.082397 | 0.027466 | -0.059509 | 0.29755 | -0.1831 | 0.40741 | -0.073242 | 0.27924 | 123.1705 | 0.050354 | 123.2803 | 123.5184 | 123.3353 | 123.2437 | 123.2254 | -123.4177 | -123.2529 | 122.8958 | 123.1705 | 59.935 | 59.9304
614.4844 | 123.2712 | -60.0815 | 63.0753 | -0.088196 | 0.0035525 | 0.06442 | 0.065185 | -0.0023649 | 0.0015658 | -0.0015935 | -0.069 | -0.00010472 | 0.066635 | 0.069045 | -0.0025976 | 0.0015424 | 0.00030966 | -0.14191 | 63.1897 | -60.3699 | 62.8098 | -60.0769 | -60.4385 | -0.15564 | -0.18768 | 63.1439 | -60.1959 | 63.0798 | -60.1501 | -60.2921 | -59.7839 | -0.28839 | 0.11444 | -0.2655 | 0.004578 | 59.9258 | -0.35706 | 60.2142 | -0.068665 | -0.11444 | 0.068665 | 0.004578 | -0.068664 | 0.29755 | -0.21057 | 0.41199 | -0.09613 | 0.29297 | 123.1796 | 0.045777 | 123.2758 | 123.5596 | 123.3398 | 123.2712 | 123.2254 | -123.4451 | -123.2712 | 122.8912 | 123.1613 | 59.9396 | 59.8938
615.5625 | 123.4222 | -60.0128 | 63.0844 | -0.072937 | -0.0024289 | 0.062711 | 0.062408 | -0.0064237 | 0.00092498 | -0.0013799 | 0.037811 | 0.00096348 | 0.066635 | 0.062209 | -0.002384 | -0.0018756 | 0.00095066 | -0.009155 | 63.1577 | -60.2921 | 62.97 | -59.8389 | -60.2097 | 0.10986 | 0.14648 | 63.1485 | -60.1089 | 63.2309 | -59.9304 | -60.0494 | -59.6375 | -0.27924 | 0.073242 | -0.11444 | 0.17395 | 60.1227 | -0.19684 | 60.4019 | 0.082397 | -0.096131 | 0.064087 | 0.14648 | 0.082397 | 0.37537 | -0.036621 | 0.4715 | 0.05951 | 0.45319 | 123.262 | 0.17853 | 123.3398 | 123.4497 | 123.2574 | 123.1705 | 123.1613 | -123.3765 | -123.1934 | 122.9828 | 123.2437 | 60.0037 | 60.1593
616.4844 | 123.2941 | -60.0861 | 63.089 | -0.080566 | -0.0013607 | 0.062711 | 0.064544 | 0.00083954 | 0.00049778 | 0.0020379 | -0.099518 | -0.00053192 | 0.06514 | 0.068191 | -0.003025 | 0.001115 | 0.00052346 | -0.045776 | 63.1851 | -60.347 | 62.8647 | -59.9854 | -60.3516 | -0.07782 | -0.054932 | 63.1851 | -60.1593 | 63.0981 | -60.1135 | -60.2509 | -59.7748 | -0.26092 | 0.096131 | -0.2243 | 0.10071 | 60.0082 | -0.2655 | 60.2692 | -0.004577 | -0.073242 | 0.096131 | 0.009156 | -0.027465 | 0.31128 | -0.16479 | 0.38452 | -0.091552 | 0.36163 | 123.2117 | 0.045777 | 123.2574 | 123.5321 | 123.3444 | 123.2712 | 123.2712 | -123.436 | -123.2483 | 122.9507 | 123.1842 | 60.0403 | 60.0311
617.4844 | 123.3856 | -60.0403 | 63.0341 | -0.13397 | 0.00034827 | 0.064207 | 0.065399 | -0.0019377 | -0.00078402 | -0.00073913 | -0.0079652 | 0.0024589 | 0.067063 | 0.070113 | 0.000393 | 0.0013288 | -0.0022537 | -0.07782 | 63.1165 | -60.3149 | 62.9974 | -59.9625 | -60.2051 | -0.013733 | 0.004578 | 63.1256 | -60.1273 | 63.1943 | -60.0037 | -60.1227 | -59.6558 | -0.27466 | 0.082397 | -0.036621 | 0.07782 | 60.0266 | -0.16479 | 60.3012 | 0.10986 | -0.086975 | 0.091552 | 0.16022 | 0.036621 | 0.38452 | -0.082398 | 0.4715 | 0.004577 | 0.35248 | 123.3124 | 0.1236 | 123.3215 | 123.4314 | 123.2529 | 123.1567 | 123.1659 | -123.349 | -123.1613 | 123.0377 | 123.2346 | 59.9625 | 60.0449
618.5469 | 123.3398 | -60.0494 | 63.0844 | -0.057678 | 0.00077547 | 0.06207 | 0.064331 | 0.0010531 | -0.0029202 | 0.0011835 | -0.075104 | -0.0011727 | 0.066635 | 0.065414 | -0.0017432 | -0.00016658 | 9.6064e-05 | -0.004578 | 63.1943 | -60.3104 | 62.8967 | -59.9396 | -60.2783 | 0.009155 | 0.064087 | 63.2034 | -60.141 | 63.1439 | -60.054 | -60.173 | -59.7153 | -0.26093 | 0.10986 | -0.18768 | 0.10986 | 60.0586 | -0.22888 | 60.3195 | 0.032044 | -0.091553 | 0.11902 | 0.059509 | -0.004578 | 0.33417 | -0.1236 | 0.42572 | -0.032044 | 0.37079 | 123.2071 | 0.086975 | 123.2849 | 123.5046 | 123.3444 | 123.2437 | 123.2529 | -123.3948 | -123.2254 | 122.9462 | 123.1934 | 60.0449 | 60.1135
619.4844 | 123.3856 | -60.0174 | 63.0707 | -0.10345 | 0.0014163 | 0.065488 | 0.064117 | -0.0012967 | 0.0011386 | -0.0011663 | 0.05307 | -0.00031832 | 0.068344 | 0.066482 | -0.0025976 | -0.0018756 | -0.0022537 | -0.073242 | 63.1165 | -60.3241 | 62.9379 | -59.8434 | -60.5988 | -0.17395 | -0.068665 | 63.1348 | -60.1456 | 63.1714 | -60.054 | -60.0861 | -59.6741 | -0.3067 | 0.045776 | -0.13275 | 0.17395 | 59.8434 | -0.58136 | 60.1501 | -0.27466 | -0.12817 | 0.064087 | 0.10071 | -0.036621 | 0.34332 | -0.068665 | 0.4715 | 0.059509 | 0.48065 | 123.262 | 0.091553 | 123.317 | 123.4406 | 123.2803 | 123.1338 | 123.1522 | -123.3948 | -123.2162 | 122.9553 | 123.1888 | 59.9442 | 59.9487
620.4844 | 123.3948 | -60.0494 | 63.0478 | -0.080566 | -0.00050633 | 0.063138 | 0.063262 | 0.0014803 | 0.0013522 | 0.00096987 | -0.056793 | -0.0011727 | 0.067063 | 0.064345 | -0.0036658 | -0.0010212 | -0.0031081 | -0.10529 | 63.1348 | -60.3333 | 62.9059 | -59.9487 | -60.2966 | -0.064087 | -0.045776 | 63.0936 | -60.1776 | 63.1897 | -60.0266 | -60.1273 | -59.6466 | -0.28381 | 0.086975 | -0.14191 | 0.10071 | 59.9854 | -0.24719 | 60.2692 | 0.036621 | -0.12817 | 0.045776 | 0.14191 | 0.022888 | 0.40283 | -0.07782 | 0.53101 | 0.050354 | 0.38452 | 123.2391 | 0.15106 | 123.3673 | 123.468 | 123.2712 | 123.1842 | 123.143 | -123.381 | -123.2254 | 122.9553 | 123.2391 | 59.9442 | 60.0037
621.4844 | 123.3902 | -60.0586 | 63.0386 | -0.080566 | 0.0016299 | 0.06442 | 0.064117 | 0.0021213 | -0.00014322 | 0.00032907 | -0.020172 | 0.0011771 | 0.064499 | 0.06755 | -0.0032386 | -0.0014484 | 0.0043687 | -0.11902 | 63.1577 | -60.3424 | 62.8967 | -59.9533 | -60.3149 | -0.07782 | -0.082397 | 63.1119 | -60.1639 | 63.1622 | -60.0357 | -60.1364 | -59.6558 | -0.28381 | 0.11902 | -0.14191 | 0.10529 | 59.9808 | -0.25635 | 60.2646 | 0.027466 | -0.10529 | 0.073242 | 0.1236 | 0.022888 | 0.40283 | -0.07782 | 0.50812 | 0.027465 | 0.3891 | 123.2391 | 0.12817 | 123.3261 | 123.5001 | 123.2758 | 123.2162 | 123.1705 | -123.381 | -123.2025 | 122.9553 | 123.2208 | 59.9396 | 59.9762
622.5469 | 123.3078 | -60.0769 | 63.0981 | -0.03479 | -0.0011471 | 0.06442 | 0.065826 | -0.00022866 | -0.00099762 | -0.00052553 | -0.041534 | 0.00032248 | 0.065567 | 0.072463 | -0.0017432 | 0.0015424 | 0.0037277 | -0.036621 | 63.1989 | -60.3241 | 62.8784 | -59.9762 | -60.3424 | -0.054932 | -0.036621 | 63.1622 | -60.1547 | 63.1027 | -60.1227 | -60.2234 | -59.7519 | -0.24719 | 0.10071 | -0.21973 | 0.10071 | 60.022 | -0.2655 | 60.2692 | -0.01831 | -0.07782 | 0.064086 | 0.004577 | -0.045777 | 0.32501 | -0.14648 | 0.40283 | -0.068665 | 0.3479 | 123.2025 | 0.032043 | 123.2574 | 123.523 | 123.317 | 123.2758 | 123.2391 | -123.4222 | -123.2529 | 122.9553 | 123.1796 | 60.0403 | 60.0403
623.4844 | 123.3627 | -60.0632 | 63.0707 | -0.065308 | 0.0012027 | 0.064207 | 0.065185 | 0.0053255 | 0.0011386 | -0.00052553 | -0.044586 | 0.0022453 | 0.066849 | 0.068618 | -0.0011022 | 0.00090142 | 0.0020187 | -0.1236 | 63.1577 | -60.3516 | 62.8738 | -59.9808 | -60.347 | -0.10071 | -0.086975 | 63.121 | -60.1639 | 63.1577 | -60.0311 | -60.1456 | -59.6741 | -0.28839 | 0.086975 | -0.19684 | 0.082397 | 59.9625 | -0.28381 | 60.2509 | 0.004577 | -0.10071 | 0.050354 | 0.086975 | 0.032043 | 0.3891 | -0.082398 | 0.48981 | 0.01831 | 0.37079 | 123.2254 | 0.13275 | 123.3215 | 123.5092 | 123.2849 | 123.2208 | 123.1842 | -123.4222 | -123.2346 | 122.937 | 123.2208 | 59.9396 | 59.9762
624.4844 | 123.3627 | -60.0632 | 63.0249 | -0.11108 | -7.913e-05 | 0.065702 | 0.064971 | -0.0015103 | 0.0011386 | 0.0013971 | -0.029327 | 0.0018179 | 0.066208 | 0.062209 | -0.002384 | -0.0010212 | 0.00052346 | -0.13275 | 63.1622 | -60.3378 | 62.883 | -59.9945 | -60.3516 | -0.086975 | -0.10986 | 63.1073 | -60.1547 | 63.176 | -60.0952 | -60.1685 | -59.6649 | -0.27466 | 0.13733 | -0.14191 | 0.068664 | 59.9762 | -0.28839 | 60.2509 | -0.013732 | -0.091553 | 0.082398 | 0.15106 | -0.032044 | 0.39825 | -0.10529 | 0.48981 | -0.013733 | 0.34332 | 123.2208 | 0.059509 | 123.3307 | 123.5001 | 123.262 | 123.2254 | 123.1705 | -123.3627 | -123.1796 | 122.9462 | 123.2391 | 59.9304 | 59.9533
625.5 | 123.4268 | -60.0357 | 63.1119 | -0.042419 | 0.00077547 | 0.060575 | 0.062622 | -0.0012967 | -0.0020658 | -9.8328e-05 | 0.037811 | -0.00053192 | 0.065354 | 0.062636 | -0.0015296 | -0.0014484 | 0.0011643 | -0.013733 | 63.1577 | -60.2875 | 62.9562 | -59.8572 | -60.2188 | 0.10071 | 0.13275 | 63.1714 | -60.0998 | 63.2263 | -59.9396 | -60.0449 | -59.642 | -0.25177 | 0.045777 | -0.15564 | 0.17853 | 60.1364 | -0.18311 | 60.3882 | 0.068665 | -0.064086 | 0.05951 | 0.11444 | 0.096131 | 0.39368 | -0.009155 | 0.45776 | 0.054931 | 0.4303 | 123.2437 | 0.16022 | 123.3261 | 123.4451 | 123.2712 | 123.1934 | 123.2071 | -123.3994 | -123.2117 | 122.9919 | 123.262 | 60.022 | 60.1685
626.5469 | 123.3215 | -60.0815 | 63.1073 | -0.027161 | 0.0012027 | 0.063138 | 0.065612 | 0.00041234 | -0.00078402 | -0.00052553 | -0.035431 | -0.0013863 | 0.064926 | 0.066268 | -0.0011022 | 0.00068782 | -0.00011754 | -0.004578 | 63.1851 | -60.3333 | 62.8876 | -59.967 | -60.3104 | -0.009155 | 0.041199 | 63.208 | -60.1501 | 63.1439 | -60.0586 | -60.173 | -59.7153 | -0.25177 | 0.07782 | -0.21973 | 0.11444 | 60.0723 | -0.22888 | 60.3241 | 0.022888 | -0.068664 | 0.10071 | 0.036621 | 0.022888 | 0.36621 | -0.091553 | 0.43487 | -0.022889 | 0.36621 | 123.2208 | 0.091552 | 123.2941 | 123.5184 | 123.3582 | 123.2666 | 123.2895 | -123.4406 | -123.2574 | 122.9691 | 123.2254 | 60.0769 | 60.1227
627.4844 | 123.3765 | -60.054 | 63.0341 | -0.057678 | 0.00034827 | 0.063993 | 0.064544 | -0.0049283 | 0.0037022 | 0.0041743 | -0.032379 | -0.00074552 | 0.065354 | 0.065627 | 0.0006066 | -0.00038018 | 0.0024461 | -0.050354 | 63.121 | -60.3058 | 62.9288 | -59.9258 | -60.2966 | -0.054932 | -0.050354 | 63.0936 | -60.1501 | 63.1897 | -60.0082 | -60.1273 | -59.6466 | -0.25177 | 0.086975 | -0.10529 | 0.12817 | 59.9991 | -0.24262 | 60.2509 | 0.009155 | -0.09613 | 0.059509 | 0.15564 | 0.045776 | 0.40741 | -0.073242 | 0.50354 | 0.022888 | 0.37994 | 123.2346 | 0.14191 | 123.3398 | 123.4268 | 123.2437 | 123.175 | 123.1476 | -123.3398 | -123.1842 | 122.9828 | 123.2437 | 60.0037 | 60.0037
628.4844 | 123.3627 | -60.0586 | 63.0753 | -0.10345 | -7.913e-05 | 0.063138 | 0.064331 | 0.0023349 | -0.0014248 | 0.0018243 | -0.047638 | 0.00074988 | 0.065567 | 0.059005 | -0.0008886 | -0.00038018 | -0.0020401 | -0.13275 | 63.1531 | -60.3607 | 62.8601 | -60.0082 | -60.379 | -0.12817 | -0.11902 | 63.1485 | -60.1593 | 63.1393 | -60.0494 | -60.1593 | -59.6878 | -0.30212 | 0.07782 | -0.21515 | 0.050354 | 59.9304 | -0.32043 | 60.2325 | -0.01831 | -0.10071 | 0.073243 | 0.064087 | 0.009156 | 0.37079 | -0.10071 | 0.4715 | 0 | 0.35248 | 123.2208 | 0.10986 | 123.2986 | 123.5138 | 123.3078 | 123.2117 | 123.2071 | -123.436 | -123.2346 | 122.9187 | 123.1979 | 59.9258 | 59.9396
629.5625 | 123.3765 | -60.0311 | 63.0432 | -0.065308 | -7.913e-05 | 0.064847 | 0.065185 | -0.0012967 | 0.00049778 | -0.00031193 | -0.014069 | 0.0016043 | 0.064072 | 0.059646 | -0.001316 | -0.00059378 | 0.00030966 | -0.059509 | 63.121 | -60.3104 | 62.9196 | -59.903 | -60.2875 | -0.054932 | -0.032043 | 63.1027 | -60.141 | 63.0203 | -60.0632 | -59.8846 | -59.4681 | -0.27924 | 0.07782 | -0.1236 | 0.12817 | 59.9762 | -0.25635 | 60.2554 | 0.022888 | -0.10986 | 0.059509 | -0.022888 | -0.032043 | 0.56305 | 0.14648 | 0.67291 | 0.25635 | 0.40741 | 123.23 | 0.07782 | 123.1613 | 123.4314 | 123.2437 | 123.1522 | 123.1338 | -123.3536 | -123.1842 | 122.9507 | 123.0515 | 59.9716 | 59.9991
630.4844 | 123.4039 | -60.0494 | 63.0524 | -0.03479 | 0.00098907 | 0.063352 | 0.065399 | 0.0021213 | 0.0015658 | 0.0020379 | -0.020172 | -0.00074552 | 0.066849 | 0.064132 | -0.0019568 | 0.00047422 | -0.0024673 | -0.064087 | 63.1439 | -60.3424 | 62.9105 | -59.9258 | -60.2829 | -0.054932 | -0.059509 | 63.1348 | -60.1639 | 63.1714 | -60.0266 | -60.1364 | -59.6603 | -0.29297 | 0.091553 | -0.14191 | 0.1236 | 59.9945 | -0.23346 | 60.2875 | 0.059509 | -0.11444 | 0.082398 | 0.11902 | 0.022888 | 0.3891 | -0.086976 | 0.50354 | 0.027465 | 0.41656 | 123.2529 | 0.13733 | 123.3353 | 123.4863 | 123.2986 | 123.1934 | 123.1842 | -123.3948 | -123.2162 | 122.9599 | 123.2208 | 59.9854 | 59.9899
631.4844 | 123.3994 | -60.0311 | 63.0524 | -0.095825 | 0.00098907 | 0.06442 | 0.064544 | 0.00041234 | 0.00049778 | -0.0020209 | -0.011017 | -0.00010472 | 0.06749 | 0.069686 | -0.0032386 | 0.00026062 | -0.0011855 | -0.041199 | 63.1348 | -60.3287 | 62.9196 | -59.9121 | -60.3012 | -0.064087 | -0.050354 | 63.1073 | -60.1318 | 63.1851 | -60.022 | -60.1364 | -59.6695 | -0.29755 | 0.082398 | -0.13275 | 0.11902 | 59.967 | -0.27008 | 60.2646 | 0.027466 | -0.10071 | 0.054932 | 0.13275 | 0.009155 | 0.36163 | -0.10529 | 0.46234 | -0.004578 | 0.41656 | 123.2483 | 0.10986 | 123.317 | 123.4634 | 123.2391 | 123.1659 | 123.1384 | -123.381 | -123.1842 | 122.9507 | 123.2162 | 59.9899 | 59.9808
632.4844 | 123.3948 | -60.0861 | 63.0295 | -0.050049 | 0.00056187 | 0.064847 | 0.065612 | 0.0029757 | -0.00078402 | 0.0024653 | -0.044586 | -0.00010472 | 0.068131 | 0.06755 | -0.0025976 | -0.00016658 | -0.0026809 | -0.10986 | 63.1027 | -60.3378 | 62.915 | -59.9213 | -60.2966 | -0.068665 | -0.045776 | 63.1302 | -60.1593 | 63.2034 | -60.0266 | -60.1227 | -59.642 | -0.25177 | 0.073242 | -0.11444 | 0.1648 | 60.0174 | -0.21057 | 60.2692 | 0.041199 | -0.073242 | 0.10071 | 0.17395 | 0.05951 | 0.44403 | -0.036621 | 0.51727 | 0.036621 | 0.41656 | 123.2529 | 0.13275 | 123.3627 | 123.4406 | 123.2895 | 123.1888 | 123.2162 | -123.3673 | -123.1888 | 123.0011 | 123.2895 | 59.9762 | 60.0403
633.4844 | 123.3582 | -60.0586 | 63.0753 | -0.072937 | 0.00034827 | 0.063566 | 0.064331 | -0.00022866 | 0.0019932 | 0.00011527 | 0.0072936 | 0.00053628 | 0.065354 | 0.060073 | -0.0028112 | -0.0037982 | 0.0033005 | -0.09613 | 63.1348 | -60.3104 | 62.8922 | -59.967 | -60.3104 | -0.032043 | -0.059509 | 63.1119 | -60.1181 | 63.1439 | -60.022 | -60.1501 | -59.7061 | -0.25177 | 0.05951 | -0.18311 | 0.091553 | 60.0266 | -0.25177 | 60.2783 | 0 | -0.059509 | 0.036621 | 0.068665 | 0.036621 | 0.35248 | -0.091552 | 0.41199 | -0.032043 | 0.34332 | 123.2025 | 0.09613 | 123.262 | 123.4451 | 123.23 | 123.1934 | 123.1705 | -123.3856 | -123.1934 | 122.9507 | 123.2025 | 59.9625 | 59.9991
634.5469 | 123.2712 | -60.0723 | 63.1119 | -0.095825 | -0.00029273 | 0.064207 | 0.065399 | 0.0023349 | -0.00057042 | -0.0013799 | -0.078156 | 0.0016043 | 0.064499 | 0.064345 | -0.0017432 | 0.0015424 | -0.0020401 | -0.068665 | 63.1851 | -60.3607 | 62.8464 | -60.0174 | -60.3561 | -0.086975 | -0.07782 | 63.1897 | -60.1593 | 63.089 | -60.1318 | -60.2554 | -59.7565 | -0.28839 | 0.073243 | -0.2655 | 0.054932 | 59.9854 | -0.28381 | 60.2737 | 0.004578 | -0.086975 | 0.07782 | -0.022888 | -0.059509 | 0.31586 | -0.1831 | 0.40283 | -0.09613 | 0.34332 | 123.2071 | 0.027466 | 123.2483 | 123.5458 | 123.349 | 123.2574 | 123.262 | -123.4726 | -123.2712 | 122.9187 | 123.1613 | 60.0037 | 59.9945
635.5 | 123.3582 | -60.0677 | 63.0707 | 0.19409 | -0.00071993 | 0.062284 | 0.062408 | -0.00022866 | -0.0027066 | -0.00073913 | 0.040863 | 0.00053628 | 0.065995 | 0.063064 | -0.0008886 | -0.0010212 | -0.0011855 | -0.13733 | 63.1622 | -60.2875 | 62.9013 | -59.9579 | -60.3012 | -0.009155 | -0.022888 | 63.1256 | -60.1318 | 63.1714 | -59.9899 | -60.1089 | -59.6649 | -0.21973 | 0.091552 | -0.16937 | 0.10986 | 60.0586 | -0.23346 | 60.2783 | -0.013732 | -0.064087 | 0.054931 | 0.10071 | 0.07782 | 0.40283 | -0.041199 | 0.46692 | 0.022888 | 0.32959 | 123.1888 | 0.14191 | 123.3032 | 123.4497 | 123.2574 | 123.23 | 123.1934 | -123.3582 | -123.2025 | 122.9691 | 123.2391 | 59.9304 | 60.0449
636.5469 | 123.317 | -60.0815 | 63.0707 | -0.088196 | 0.00013467 | 0.062925 | 0.066253 | -0.0045011 | 7.0582e-05 | 0.0016107 | -0.093414 | 0.00053628 | 0.064926 | 0.067977 | -0.0019568 | -0.00080758 | -0.0022537 | -0.13275 | 63.1668 | -60.3973 | 62.8418 | -60.0952 | -60.2646 | -0.1236 | -0.11902 | 63.1805 | -60.1822 | 63.0753 | -60.1181 | -60.2463 | -59.761 | -0.31586 | 0.09613 | -0.22888 | -0.013733 | 59.9579 | -0.1831 | 60.2737 | 0.13275 | -0.10071 | 0.10986 | 0.004577 | -0.036621 | 0.32044 | -0.16479 | 0.42114 | -0.064087 | 0.30212 | 123.2391 | 0.064087 | 123.2574 | 123.5641 | 123.3627 | 123.2483 | 123.262 | -123.468 | -123.2529 | 122.9233 | 123.1567 | 59.9487 | 59.9625
637.4844 | 123.3627 | -60.0586 | 63.0615 | -0.057678 | -0.00029273 | 0.064207 | 0.063476 | -0.00065586 | 0.00092498 | -0.0013799 | 0.010345 | 0.00010888 | 0.066208 | 0.066268 | -0.0019568 | -0.0014484 | 0.0011643 | -0.07782 | 63.1393 | -60.3058 | 62.915 | -59.9258 | -60.3058 | -0.027466 | -0.068665 | 63.1256 | -60.1547 | 63.1531 | -60.0449 | -60.1501 | -59.7061 | -0.24719 | 0.07782 | -0.14648 | 0.13275 | 60.0311 | -0.24719 | 60.2783 | 0 | -0.09613 | 0.064087 | 0.091553 | 0.013733 | 0.35248 | -0.091552 | 0.44861 | 0.004578 | 0.37994 | 123.2208 | 0.10986 | 123.3078 | 123.4451 | 123.2803 | 123.1979 | 123.1842 | -123.3673 | -123.2162 | 122.9736 | 123.2117 | 59.9808 | 59.9899
638.5469 | 123.3124 | -60.0586 | 63.1439 | -0.042419 | -0.00093353 | 0.06143 | 0.067748 | 0.0023349 | -0.0014248 | -0.00095273 | -0.035431 | 0.00032248 | 0.067276 | 0.066695 | -0.001316 | -0.0018756 | -0.0016129 | -0.059509 | 63.1943 | -60.3378 | 62.8738 | -60.0266 | -60.3058 | 0 | 0.018311 | 63.2034 | -60.1227 | 63.1073 | -60.054 | -60.173 | -59.7107 | -0.27924 | 0.050354 | -0.27008 | 0.032044 | 60.0586 | -0.24719 | 60.3378 | 0.032044 | -0.064087 | 0.059509 | -0.036621 | 0.004578 | 0.3479 | -0.11444 | 0.41199 | -0.050354 | 0.31128 | 123.2117 | 0.068665 | 123.23 | 123.5321 | 123.3261 | 123.2529 | 123.262 | -123.4818 | -123.2666 | 122.9324 | 123.1659 | 59.9991 | 60.0769
639.4844 | 123.349 | -60.0449 | 63.089 | -0.050049 | 0.0026981 | 0.062284 | 0.064971 | 0.00019874 | 7.0582e-05 | -0.0022345 | 0.019501 | -0.00053192 | 0.068772 | 0.062209 | -0.0021704 | -0.0010212 | 0.0056503 | -0.10986 | 63.1714 | -60.3287 | 62.8922 | -59.9716 | -60.3149 | -0.050354 | -0.091553 | 63.1256 | -60.1593 | 63.1485 | -60.0449 | -60.141 | -59.697 | -0.28381 | 0.082398 | -0.19684 | 0.073242 | 59.9945 | -0.27008 | 60.2783 | 0.013733 | -0.11444 | 0.036621 | 0.05951 | 0 | 0.3479 | -0.09613 | 0.46234 | 0.018311 | 0.35706 | 123.2208 | 0.11444 | 123.3078 | 123.5001 | 123.2849 | 123.2162 | 123.1705 | -123.4177 | -123.2483 | 122.937 | 123.1934 | 59.935 | 59.9533
640.5469 | 123.2941 | -60.0815 | 63.1119 | -0.1416 | 0.0026981 | 0.063993 | 0.065185 | -0.00086946 | -0.0020658 | 0.0026789 | -0.087311 | 0.0026725 | 0.069199 | 0.064345 | -0.000675 | -0.0035846 | -0.00033114 | -0.11902 | 63.1622 | -60.3882 | 62.8098 | -60.0861 | -60.4065 | -0.13733 | -0.19226 | 63.1577 | -60.2005 | 63.1256 | -60.1456 | -60.3149 | -59.7702 | -0.3067 | 0.050354 | -0.30212 | -0.004578 | 59.9442 | -0.32501 | 60.2509 | -0.01831 | -0.11902 | 0.045777 | 0.013733 | -0.064087 | 0.31128 | -0.23346 | 0.4303 | -0.11444 | 0.30212 | 123.1979 | 0.054931 | 123.3261 | 123.5504 | 123.3582 | 123.2437 | 123.2391 | -123.5001 | -123.3124 | 122.8912 | 123.2071 | 59.9625 | 59.8892
641.5 | 123.4131 | -60.0494 | 63.0844 | -0.065308 | 0.00034827 | 0.062711 | 0.062408 | -0.00086946 | 0.00071138 | -0.0028753 | 0.040863 | 0.0020315 | 0.066422 | 0.062209 | -3.4196e-05 | -0.0010212 | 0.0022323 | -0.07782 | 63.1714 | -60.2829 | 62.9242 | -59.9121 | -60.2509 | 0.041199 | 0.032043 | 63.1439 | -60.1456 | 63.1943 | -59.9762 | -60.0861 | -59.6512 | -0.23346 | 0.086975 | -0.16022 | 0.13733 | 60.0906 | -0.20142 | 60.3241 | 0.032044 | -0.096131 | 0.059509 | 0.10986 | 0.073242 | 0.39825 | -0.036622 | 0.49439 | 0.059509 | 0.37079 | 123.2071 | 0.16937 | 123.3398 | 123.4543 | 123.2895 | 123.2208 | 123.1934 | -123.3673 | -123.23 | 122.9736 | 123.2437 | 59.9716 | 60.0815
642.5469 | 123.2712 | -60.0906 | 63.0936 | -0.057678 | -0.00071993 | 0.065061 | 0.067748 | 0.0023349 | 0.00092498 | 0.0024653 | -0.087311 | 0.0020315 | 0.066422 | 0.070327 | -0.000675 | 0.00026062 | -0.00075834 | -0.07782 | 63.1622 | -60.3516 | 62.8418 | -60.0311 | -60.3699 | -0.11902 | -0.11444 | 63.1805 | -60.1547 | 63.0844 | -60.1639 | -60.3012 | -59.7839 | -0.26093 | 0.068664 | -0.25177 | 0.059509 | 59.9716 | -0.27924 | 60.2325 | -0.018311 | -0.064087 | 0.086975 | -0.009155 | -0.073242 | 0.3067 | -0.21057 | 0.37079 | -0.14648 | 0.32043 | 123.1934 | -0.009155 | 123.2391 | 123.5138 | 123.3353 | 123.2529 | 123.2712 | -123.4451 | -123.2483 | 122.9324 | 123.175 | 60.0128 | 59.9762
643.4844 | 123.3948 | -60.0449 | 63.0707 | -0.088196 | -0.0015743 | 0.06207 | 0.064331 | -0.00086946 | 0.00092498 | -0.00095273 | 0.059174 | -0.00074552 | 0.067063 | 0.064132 | 0.000393 | 0.00047422 | 0.0011643 | -0.07782 | 63.1668 | -60.3378 | 62.9059 | -59.935 | -60.2737 | 0 | 0.013733 | 63.1439 | -60.1135 | 63.208 | -59.9808 | -60.0861 | -59.6603 | -0.29297 | 0.09613 | -0.16479 | 0.10986 | 60.0449 | -0.22888 | 60.3378 | 0.064087 | -0.068664 | 0.073242 | 0.13733 | 0.064087 | 0.38452 | -0.041199 | 0.45319 | 0.027465 | 0.40283 | 123.2437 | 0.13275 | 123.3215 | 123.5046 | 123.2574 | 123.2117 | 123.1888 | -123.4085 | -123.1842 | 122.9507 | 123.2529 | 59.967 | 60.0586
644.4844 | 123.3673 | -60.0449 | 63.0341 | -0.16449 | -0.0011471 | 0.063138 | 0.064544 | -0.0023649 | -0.00078402 | -0.0026617 | -0.01712 | 0.0018179 | 0.065781 | 0.063064 | -0.0008886 | -0.00016658 | -0.0011855 | 0.068665 | 63.0936 | -60.2875 | 62.9471 | -59.9075 | -60.2921 | -0.054932 | -0.036621 | 63.1073 | -60.1227 | 63.1851 | -60.0266 | -60.1273 | -59.6649 | -0.24262 | 0.059509 | -0.086975 | 0.13733 | 59.9899 | -0.24719 | 60.2325 | -0.004577 | -0.07782 | 0.073242 | 0.15106 | 0.018311 | 0.37994 | -0.082397 | 0.45776 | -0.004577 | 0.37994 | 123.2346 | 0.096131 | 123.3078 | 123.381 | 123.23 | 123.1384 | 123.1522 | -123.3215 | -123.1567 | 122.9919 | 123.23 | 60.1135 | 60.0082
645.5625 | 123.3856 | -60.0632 | 63.0615 | -0.057678 | 0.00077547 | 0.061857 | 0.065612 | -0.0019377 | -0.0014248 | 0.0022517 | 0.019501 | 0.00053628 | 0.067276 | 0.061355 | -0.001316 | -0.0020892 | -0.0020401 | -0.10071 | 63.1439 | -60.3149 | 62.8967 | -59.9625 | -60.3195 | -0.068665 | -0.091553 | 63.1027 | -60.1456 | 63.1348 | -60.054 | -60.1364 | -59.7015 | -0.25177 | 0.082398 | -0.16479 | 0.10071 | 59.9945 | -0.25635 | 60.2463 | -0.004578 | -0.082398 | 0.041199 | 0.073243 | 0.009155 | 0.36163 | -0.073243 | 0.44403 | 0.009155 | 0.35248 | 123.2117 | 0.091553 | 123.2803 | 123.4589 | 123.2483 | 123.2071 | 123.1659 | -123.3765 | -123.2071 | 122.9599 | 123.1979 | 59.9625 | 59.9716
646.4844 | 123.3719 | -60.0723 | 63.0707 | -0.10345 | 0.00034827 | 0.061643 | 0.064544 | -0.00022866 | 0.00071138 | -0.0013799 | 0.022552 | 0.00053628 | 0.065995 | 0.069045 | -0.000675 | -0.0010212 | 0.0035141 | -0.09613 | 63.1348 | -60.3195 | 62.8967 | -59.9625 | -60.3241 | -0.036621 | -0.07782 | 63.1485 | -60.1501 | 63.1485 | -60.0586 | -60.1501 | -59.697 | -0.24719 | 0.064087 | -0.17395 | 0.10986 | 60.0357 | -0.25177 | 60.2829 | -0.004578 | -0.077819 | 0.07782 | 0.07782 | 0.013733 | 0.37537 | -0.077819 | 0.45319 | 0 | 0.35706 | 123.2162 | 0.091552 | 123.2986 | 123.4543 | 123.2986 | 123.2071 | 123.2208 | -123.3902 | -123.2208 | 122.9691 | 123.2208 | 59.9762 | 59.9945
647.5469 | 123.3856 | -60.0632 | 63.0661 | -0.011902 | 0.0018435 | 0.064207 | 0.066253 | -0.0023649 | -0.0020658 | -0.0011663 | -0.078156 | 0.0011771 | 0.066422 | 0.069045 | -0.0015296 | -0.00080758 | 0.00052346 | -0.13733 | 63.1485 | -60.3653 | 62.8693 | -60.0037 | -60.3653 | -0.11444 | -0.10986 | 63.1393 | -60.1593 | 63.1668 | -60.054 | -60.1685 | -59.6649 | -0.30212 | 0.082398 | -0.19684 | 0.059509 | 59.9487 | -0.30212 | 60.2509 | 0 | -0.096131 | 0.073242 | 0.10071 | 0.009155 | 0.39825 | -0.10529 | 0.49438 | -0.009155 | 0.36163 | 123.2346 | 0.10529 | 123.3261 | 123.5138 | 123.2986 | 123.2117 | 123.2025 | -123.4314 | -123.2254 | 122.9324 | 123.23 | 59.9258 | 59.9533
648.4844 | 123.3948 | -60.0494 | 63.0157 | -0.072937 | 0.00056187 | 0.065061 | 0.064544 | -0.0023649 | -0.00014322 | -0.0011663 | 0.034759 | 0.00074988 | 0.068772 | 0.067977 | -0.0019568 | -0.00016658 | 0.00030966 | -0.07782 | 63.1302 | -60.3058 | 62.9242 | -59.8251 | -60.6171 | -0.15564 | -0.09613 | 63.121 | -60.1181 | 63.176 | -60.0266 | -60.1089 | -59.6832 | -0.25635 | 0.11444 | -0.091553 | 0.2243 | 59.8938 | -0.56763 | 60.1501 | -0.31128 | -0.068665 | 0.10529 | 0.16022 | 0.022888 | 0.36621 | -0.05951 | 0.43487 | 0.009155 | 0.48065 | 123.23 | 0.091553 | 123.2941 | 123.436 | 123.2391 | 123.1796 | 123.1705 | -123.3215 | -123.1338 | 122.9736 | 123.2254 | 59.9716 | 59.9533
649.4844 | 123.3673 | -60.0449 | 63.0707 | -0.050049 | -0.00050633 | 0.063566 | 0.063262 | 0.00083954 | -0.00078402 | 0.0011835 | 0.034759 | 0.00010888 | 0.064499 | 0.060073 | -0.0019568 | -0.00080758 | 0.00073706 | -0.082397 | 63.1668 | -60.3195 | 62.8326 | -59.9258 | -60.3241 | -0.018311 | -0.036621 | 63.1531 | -60.1456 | 63.1439 | -60.0174 | -60.1273 | -59.6832 | -0.27466 | 0.09613 | -0.23804 | 0.11902 | 60.0266 | -0.27924 | 60.3012 | -0.004578 | -0.10071 | 0.082397 | 0.073242 | 0.027466 | 0.36163 | -0.082397 | 0.46234 | 0.018311 | 0.39368 | 123.1522 | 0.12817 | 123.2895 | 123.4863 | 123.2986 | 123.2117 | 123.1979 | -123.3902 | -123.2162 | 122.8775 | 123.1888 | 59.9625 | 60.0082
650.5625 | 123.3215 | -60.054 | 63.0524 | -0.080566 | 0.0018435 | 0.065916 | 0.064117 | -0.0010831 | 0.00049778 | 0.00011527 | -0.01712 | 0.00096348 | 0.064499 | 0.0652 | -0.0028112 | 4.7018e-05 | 0.00052346 | -0.086975 | 63.1348 | -60.3195 | 62.9105 | -59.935 | -60.3287 | -0.064087 | -0.059509 | 63.1165 | -60.1456 | 63.1485 | -60.0586 | -60.1456 | -59.6832 | -0.2655 | 0.082398 | -0.14191 | 0.11902 | 59.9899 | -0.27466 | 60.2554 | -0.009155 | -0.091553 | 0.064087 | 0.096131 | -0.004578 | 0.37079 | -0.091553 | 0.46234 | 0 | 0.38452 | 123.23 | 0.086975 | 123.2941 | 123.4543 | 123.262 | 123.1888 | 123.1705 | -123.3719 | -123.1979 | 122.9645 | 123.2025 | 59.967 | 59.9945
651.4844 | 123.4131 | -60.0403 | 63.0707 | -0.042419 | -0.00029273 | 0.060789 | 0.062408 | -0.0053555 | -0.001852 | -0.00095273 | 0.013397 | 0.0024589 | 0.066635 | 0.067336 | -0.0011022 | -0.00059378 | 0.0011643 | -0.050354 | 63.1393 | -60.3241 | 62.9471 | -59.9258 | -60.2463 | 0.050354 | 0.068665 | 63.1348 | -60.1181 | 63.208 | -59.9716 | -60.0861 | -59.6558 | -0.28381 | 0.068664 | -0.1236 | 0.11444 | 60.0906 | -0.20599 | 60.3745 | 0.07782 | -0.07782 | 0.064087 | 0.13733 | 0.068664 | 0.38452 | -0.045777 | 0.46234 | 0.032043 | 0.39825 | 123.2712 | 0.14648 | 123.3261 | 123.4634 | 123.2529 | 123.1796 | 123.175 | -123.3948 | -123.1888 | 122.9874 | 123.2483 | 59.9899 | 60.1089
652.5469 | 123.2941 | -60.0632 | 63.1073 | -0.080566 | 0.00098907 | 0.062925 | 0.064758 | 0.0012667 | -0.001852 | -0.00052553 | -0.093414 | -0.00074552 | 0.06749 | 0.068831 | -0.0025976 | 4.7018e-05 | -0.00033114 | -0.036621 | 63.1943 | -60.3241 | 62.8922 | -59.9533 | -60.3195 | -0.022888 | 0.036621 | 63.1805 | -60.1227 | 63.1439 | -60.0586 | -60.1822 | -59.8618 | -0.26093 | 0.086975 | -0.21515 | 0.10986 | 60.0403 | -0.25635 | 60.3012 | 0.004578 | -0.05951 | 0.073242 | 0.036621 | 0.004577 | 0.20142 | -0.11902 | 0.26093 | -0.059509 | 0.37079 | 123.2162 | 0.064087 | 123.2666 | 123.5184 | 123.3032 | 123.2574 | 123.2437 | -123.4314 | -123.23 | 122.9553 | 123.2071 | 60.0266 | 60.0998
653.4844 | 123.3627 | -60.0769 | 63.0707 | -0.011902 | -0.0013607 | 0.063993 | 0.063903 | -0.0025785 | -0.00078402 | -0.0022345 | -0.0018616 | -0.00074552 | 0.067276 | 0.061996 | -0.0017432 | -0.00016658 | -0.0016129 | -0.11444 | 63.1256 | -60.3149 | 62.8922 | -59.9716 | -60.3378 | -0.050354 | -0.068665 | 63.1439 | -60.1547 | 63.1348 | -60.0494 | -60.1456 | -59.697 | -0.23804 | 0.054931 | -0.17853 | 0.10529 | 60.0266 | -0.26093 | 60.2646 | -0.022889 | -0.07782 | 0.073242 | 0.064087 | 0.027466 | 0.37994 | -0.068665 | 0.45776 | 0.009155 | 0.34332 | 123.2071 | 0.10529 | 123.2895 | 123.4406 | 123.2986 | 123.2025 | 123.2208 | -123.3856 | -123.2254 | 122.9691 | 123.2117 | 59.9625 | 60.0082
654.4844 | 123.3948 | -60.0403 | 63.0203 | -0.095825 | 0.00013467 | 0.06442 | 0.064331 | 0.0027621 | 0.0019932 | 0.00032907 | -0.084259 | 0.0020315 | 0.065995 | 0.070754 | -0.0017432 | 0.001115 | 0.0011643 | -0.13733 | 63.1348 | -60.3424 | 62.8693 | -60.0037 | -60.347 | -0.11444 | -0.11444 | 63.1302 | -60.1868 | 63.1668 | -59.9991 | -60.2371 | -59.7336 | -0.30212 | 0.11444 | -0.15106 | 0.036621 | 59.9258 | -0.3067 | 60.228 | -0.004578 | -0.14648 | 0.10986 | 0.14648 | 0.041199 | 0.3067 | -0.19684 | 0.45319 | -0.050354 | 0.33875 | 123.2117 | 0.18768 | 123.3536 | 123.4772 | 123.317 | 123.175 | 123.1705 | -123.3627 | -123.2071 | 122.9095 | 123.2071 | 59.903 | 59.9258
655.5469 | 123.3994 | -60.0311 | 63.0432 | -0.057678 | 0.00034827 | 0.064847 | 0.064117 | -0.00044226 | 0.0011386 | 0.00096987 | -0.047638 | -0.00074552 | 0.068131 | 0.074599 | -0.0008886 | -0.0018756 | 0.0013779 | -0.07782 | 63.1027 | -60.3378 | 62.9425 | -59.8938 | -60.2829 | -0.068665 | -0.050354 | 63.121 | -60.1501 | 63.3087 | -60.0815 | -60.0723 | -59.6329 | -0.3067 | 0.059509 | -0.10071 | 0.13733 | 59.9625 | -0.25177 | 60.2692 | 0.054932 | -0.11902 | 0.07782 | 0.2655 | -0.050354 | 0.39825 | -0.041199 | 0.51727 | 0.077819 | 0.44403 | 123.2803 | 0.068664 | 123.4589 | 123.4406 | 123.2712 | 123.1338 | 123.1522 | -123.381 | -123.1934 | 122.9736 | 123.3398 | 59.9533 | 59.9808
656.4844 | 123.3673 | -60.0403 | 63.0386 | -0.065308 | 0.0026981 | 0.06442 | 0.064331 | -0.0021513 | -0.00035682 | 0.0016107 | -0.05069 | -0.0013863 | 0.065567 | 0.065841 | -0.002384 | 0.00026062 | -0.00075834 | -0.086975 | 63.0981 | -60.3195 | 62.9425 | -59.8709 | -60.3058 | -0.07782 | -0.032043 | 63.1393 | -60.1318 | 63.1851 | -60.022 | -60.1227 | -59.6649 | -0.27924 | 0.05951 | -0.09613 | 0.16937 | 59.9625 | -0.2655 | 60.2417 | 0.013733 | -0.091553 | 0.10071 | 0.14648 | 0.01831 | 0.37537 | -0.082398 | 0.46692 | 0.009155 | 0.44861 | 123.262 | 0.10986 | 123.317 | 123.4177 | 123.2712 | 123.1384 | 123.1796 | -123.3582 | -123.1705 | 122.9828 | 123.2254 | 59.9533 | 60.0082
657.5 | 123.3444 | -60.0357 | 63.0844 | -0.0042723 | 0.00034827 | 0.063138 | 0.064331 | 0.00041234 | 0.00028418 | 0.00075627 | -0.0018616 | 0.00053628 | 0.067063 | 0.062423 | -0.0025976 | -0.00016658 | -0.00054474 | 0.009155 | 63.1668 | -60.2646 | 62.9471 | -59.8755 | -60.2142 | 0.073242 | 0.10986 | 63.1668 | -60.1044 | 63.1668 | -59.9945 | -60.1044 | -59.697 | -0.22888 | 0.082397 | -0.13733 | 0.16022 | 60.1089 | -0.17853 | 60.3378 | 0.050354 | -0.068664 | 0.082397 | 0.082397 | 0.041199 | 0.33875 | -0.068664 | 0.40741 | 0 | 0.3891 | 123.2117 | 0.10986 | 123.2712 | 123.4314 | 123.2712 | 123.2025 | 123.2025 | -123.349 | -123.1888 | 122.9828 | 123.2025 | 60.0449 | 60.1456
658.5469 | 123.2849 | -60.0586 | 63.1256 | -0.050049 | 0.00013467 | 0.065488 | 0.066253 | 0.00041234 | 0.00028418 | 0.00054267 | -0.090363 | 0.0022453 | 0.065781 | 0.06755 | -0.002384 | 0.0013288 | -0.00097194 | -0.10071 | 63.1805 | -60.3561 | 62.8647 | -60.022 | -60.3836 | -0.11902 | -0.082397 | 63.1851 | -60.173 | 63.089 | -60.1364 | -60.2417 | -59.7748 | -0.29755 | 0.054932 | -0.26093 | 0.036621 | 59.9396 | -0.32501 | 60.2371 | -0.027466 | -0.11444 | 0.05951 | -0.036621 | -0.07782 | 0.28381 | -0.1831 | 0.39825 | -0.068664 | 0.33417 | 123.2208 | 0.036621 | 123.262 | 123.5367 | 123.3582 | 123.2391 | 123.2437 | -123.4818 | -123.2986 | 122.9233 | 123.1476 | 59.9579 | 59.9762
659.5 | 123.3261 | -60.0586 | 63.1119 | 0.0033567 | 0.00098907 | 0.063779 | 0.064544 | -0.00022866 | -0.00035682 | 0.00011527 | -0.065949 | 0.00053628 | 0.068344 | 0.067977 | -0.0008886 | 0.00068782 | -0.0022537 | -0.041199 | 63.208 | -60.3333 | 62.8601 | -59.9899 | -60.3058 | -0.013733 | -0.004578 | 63.1851 | -60.141 | 63.1485 | -60.0494 | -60.1593 | -59.7061 | -0.27466 | 0.096131 | -0.25177 | 0.068665 | 60.0449 | -0.24719 | 60.3195 | 0.027466 | -0.082397 | 0.073243 | 0.036622 | 0.009156 | 0.35248 | -0.10071 | 0.43487 | -0.018311 | 0.34332 | 123.1934 | 0.091553 | 123.2895 | 123.5413 | 123.3261 | 123.2666 | 123.2437 | -123.4451 | -123.2529 | 122.9187 | 123.2071 | 60.0174 | 60.054
660.4844 | 123.3719 | -60.0494 | 63.0798 | -0.072937 | -0.00071993 | 0.062925 | 0.060913 | -0.00044226 | -0.00099762 | -0.00031193 | 0.019501 | -0.0013863 | 0.066422 | 0.06285 | -0.0011022 | -0.0020892 | 0.0020187 | -0.10529 | 63.1577 | -60.3287 | 62.883 | -59.9625 | -60.2966 | -0.045776 | -0.073242 | 63.1393 | -60.1547 | 63.1622 | -60.0449 | -60.1364 | -59.7015 | -0.27924 | 0.07782 | -0.19684 | 0.086975 | 60.0037 | -0.24719 | 60.2829 | 0.032043 | -0.10529 | 0.059509 | 0.082397 | 0.004577 | 0.3479 | -0.086976 | 0.45319 | 0.01831 | 0.36621 | 123.2117 | 0.10986 | 123.317 | 123.4863 | 123.2941 | 123.2071 | 123.1888 | -123.4085 | -123.2346 | 122.9324 | 123.2117 | 59.9442 | 59.9762
661.4844 | 123.3719 | -60.0357 | 63.0615 | -0.057678 | -7.913e-05 | 0.067411 | 0.065185 | -0.00044226 | 0.0015658 | -0.0020209 | -0.0049134 | 0.00096348 | 0.067704 | 0.065414 | -0.0028112 | 0.00047422 | 0.00030966 | -0.086975 | 63.1348 | -60.2921 | 62.915 | -59.935 | -60.3058 | -0.068665 | -0.064087 | 63.1485 | -60.1639 | 63.1439 | -60.0494 | -60.1456 | -59.7015 | -0.25635 | 0.073243 | -0.14648 | 0.10071 | 59.967 | -0.27008 | 60.2234 | -0.013733 | -0.12817 | 0.086976 | 0.082398 | -0.013732 | 0.33417 | -0.10986 | 0.46234 | 0.01831 | 0.35706 | 123.2071 | 0.11444 | 123.3078 | 123.4268 | 123.3124 | 123.1705 | 123.1842 | -123.3536 | -123.2254 | 122.9507 | 123.1796 | 59.9487 | 59.9716
662.4844 | 123.3627 | -60.0357 | 63.0936 | -0.1416 | -0.00071993 | 0.06207 | 0.065612 | -0.0021513 | -0.0020658 | -0.0011663 | 0.013397 | 0.00096348 | 0.065567 | 0.066482 | 0.000393 | -0.00059378 | -0.0018265 | -0.10529 | 63.1622 | -60.3058 | 62.8967 | -59.9579 | -60.3012 | -0.050354 | -0.07782 | 63.1393 | -60.1364 | 63.1485 | -60.0494 | -60.141 | -59.7061 | -0.27008 | 0.068664 | -0.19684 | 0.07782 | 59.9854 | -0.2655 | 60.2554 | 0.004578 | -0.10071 | 0.045776 | 0.054932 | -0.013732 | 0.32959 | -0.10529 | 0.4303 | -0.004577 | 0.3479 | 123.2025 | 0.086976 | 123.2849 | 123.468 | 123.2758 | 123.1979 | 123.175 | -123.3994 | -123.23 | 122.9324 | 123.1842 | 59.9304 | 59.9579
663.5 | 123.349 | -60.022 | 63.1302 | 0.026245 | 0.0012027 | 0.06442 | 0.065185 | -0.0021513 | -0.0016384 | -0.00073913 | -0.014069 | 0.00010888 | 0.068344 | 0.062423 | -0.002384 | -0.0010212 | -0.0016129 | -0.064087 | 63.1348 | -60.3058 | 62.9517 | -59.8846 | -60.2188 | 0.050354 | 0.10986 | 63.1668 | -60.1044 | 63.1851 | -59.9854 | -60.0998 | -59.6466 | -0.28381 | 0.004578 | -0.17853 | 0.13733 | 60.0723 | -0.19684 | 60.3561 | 0.086975 | -0.082397 | 0.036621 | 0.054932 | 0.036621 | 0.37537 | -0.077819 | 0.45776 | 0.004578 | 0.42114 | 123.2574 | 0.11902 | 123.2895 | 123.4406 | 123.2712 | 123.1567 | 123.1888 | -123.436 | -123.2346 | 122.9736 | 123.2071 | 59.9579 | 60.1318
664.5469 | 123.3261 | -60.054 | 63.1256 | -0.019531 | -7.913e-05 | 0.063779 | 0.066253 | 0.0061801 | -0.0014248 | -0.0022345 | -0.099518 | -0.00031832 | 0.064713 | 0.075027 | -0.0021704 | -0.00038018 | 0.0033005 | -0.036621 | 63.1622 | -60.3424 | 62.8876 | -59.967 | -60.3012 | -0.050354 | 0.086975 | 63.1805 | -60.1547 | 63.1531 | -60.0677 | -60.173 | -59.7153 | -0.28839 | 0.036621 | -0.23804 | 0.086975 | 60.0037 | -0.24719 | 60.2921 | 0.041199 | -0.10071 | 0.054932 | 0.027466 | -0.013733 | 0.33874 | -0.11902 | 0.43945 | -0.018311 | 0.37537 | 123.23 | 0.086975 | 123.3078 | 123.5046 | 123.3353 | 123.2162 | 123.2346 | -123.468 | -123.2803 | 122.9416 | 123.2071 | 60.0174 | 60.141
665.4844 | 123.4085 | -59.9762 | 63.1485 | -0.042419 | -0.00029273 | 0.062284 | 0.063262 | -0.0036465 | -0.0020658 | 0.00032907 | 0.034759 | -0.00031832 | 0.065354 | 0.061568 | -0.0019568 | -0.00080758 | 0.0013779 | 0.018311 | 63.1851 | -60.2646 | 63.002 | -59.8206 | -60.2051 | 0.07782 | 0.13733 | 63.1622 | -60.1135 | 63.2126 | -59.9533 | -60.0403 | -59.6146 | -0.28839 | 0.036621 | -0.14648 | 0.15564 | 60.054 | -0.22888 | 60.3424 | 0.059509 | -0.13733 | 0.013732 | 0.064086 | 0.022888 | 0.36163 | -0.064087 | 0.49896 | 0.073242 | 0.44403 | 123.2666 | 0.16022 | 123.3261 | 123.4497 | 123.2758 | 123.1613 | 123.1384 | -123.4131 | -123.262 | 122.9782 | 123.1888 | 59.9945 | 60.1135
666.5469 | 123.3627 | -60.0449 | 63.0478 | -0.072937 | 0.0018435 | 0.063993 | 0.06369 | 0.0023349 | -0.00035682 | -0.00052553 | -0.011017 | -0.00031832 | 0.067704 | 0.067123 | -0.0021704 | -0.00016658 | -0.00054474 | -0.07782 | 63.121 | -60.3149 | 62.9105 | -59.9167 | -60.2783 | -0.059509 | -0.032043 | 63.1119 | -60.1501 | 63.1851 | -60.0403 | -60.141 | -59.6878 | -0.27008 | 0.073242 | -0.13733 | 0.12817 | 59.9854 | -0.23346 | 60.2554 | 0.036621 | -0.10529 | 0.064086 | 0.13733 | 0.004578 | 0.35706 | -0.09613 | 0.46234 | 0.009155 | 0.39825 | 123.2254 | 0.10986 | 123.3353 | 123.436 | 123.262 | 123.1659 | 123.1567 | -123.3627 | -123.1979 | 122.9553 | 123.23 | 59.967 | 60.0128
667.4844 | 123.4406 | -60.0082 | 63.0844 | -0.065308 | -0.00050633 | 0.063352 | 0.063049 | -0.00044226 | 0.0011386 | -0.0013799 | 0.0072936 | 0.00074988 | 0.068344 | 0.066482 | -0.0008886 | -0.0020892 | 0.0020187 | 0.027466 | 63.1805 | -60.2737 | 62.9745 | -59.8389 | -60.2005 | 0.09613 | 0.16022 | 63.1714 | -60.1135 | 63.208 | -59.9487 | -59.8206 | -59.404 | -0.2655 | 0.09613 | -0.10986 | 0.16937 | 60.1044 | -0.19226 | 60.3699 | 0.073243 | -0.10529 | 0.086975 | 0.1236 | 0.05951 | 0.60425 | 0.18768 | 0.70953 | 0.29297 | 0.43488 | 123.2483 | 0.1648 | 123.3215 | 123.4543 | 123.2849 | 123.1888 | 123.1796 | -123.3582 | -123.1979 | 122.9828 | 123.2162 | 60.0357 | 60.1685
668.5469 | 123.4131 | -60.0357 | 63.0386 | -0.057678 | 0.0012027 | 0.064634 | 0.065826 | 0.00062594 | 7.0582e-05 | 0.00075627 | -0.059845 | -0.00053192 | 0.06514 | 0.069045 | -0.0025976 | 0.00047422 | -0.0024673 | -0.07782 | 63.1119 | -60.3287 | 62.9288 | -59.9213 | -60.2966 | -0.064087 | -0.036621 | 63.1073 | -60.1501 | 63.1943 | -60.0082 | -60.1227 | -59.6512 | -0.29297 | 0.073242 | -0.10986 | 0.11444 | 59.9716 | -0.26093 | 60.2646 | 0.032043 | -0.11444 | 0.068665 | 0.15564 | 0.027466 | 0.38452 | -0.086975 | 0.49896 | 0.027465 | 0.40741 | 123.2574 | 0.14191 | 123.3444 | 123.4406 | 123.2574 | 123.1476 | 123.143 | -123.3673 | -123.1888 | 122.9645 | 123.23 | 59.9579 | 59.9991
669.4844 | 123.3536 | -60.0494 | 63.0661 | -0.088196 | -0.0015743 | 0.062711 | 0.065185 | 0.0021213 | -0.00057042 | 0.0046015 | 0.013397 | -0.0022409 | 0.067063 | 0.066695 | -0.0011022 | 0.00068782 | 0.00095066 | -0.11444 | 63.1439 | -60.3149 | 62.8922 | -59.9396 | -60.3241 | -0.050354 | -0.068665 | 63.1439 | -60.1501 | 63.1531 | -60.0266 | -60.1456 | -59.6832 | -0.2655 | 0.07782 | -0.17395 | 0.10986 | 59.9991 | -0.27466 | 60.2646 | -0.009156 | -0.10071 | 0.07782 | 0.086975 | 0.022888 | 0.36621 | -0.096131 | 0.46692 | 0.004577 | 0.37537 | 123.2071 | 0.1236 | 123.3032 | 123.4589 | 123.2941 | 123.1934 | 123.1934 | -123.381 | -123.2162 | 122.9416 | 123.2025 | 59.935 | 59.9808
670.5469 | 123.2574 | -60.0723 | 63.089 | -0.095825 | 0.00056187 | 0.065275 | 0.065612 | -0.00065586 | 0.0017794 | -9.8328e-05 | -0.099518 | 0.00010888 | 0.065567 | 0.06755 | -0.0021704 | -0.00038018 | 0.0030869 | -0.11444 | 63.1805 | -60.3745 | 62.8098 | -60.1044 | -60.4294 | -0.1831 | -0.17395 | 63.1714 | -60.2142 | 63.089 | -60.1456 | -60.2692 | -59.7748 | -0.30212 | 0.091553 | -0.27924 | -0.032043 | 59.8892 | -0.35705 | 60.1913 | -0.054931 | -0.14191 | 0.082398 | 0 | -0.073242 | 0.29755 | -0.19684 | 0.43945 | -0.054932 | 0.27008 | 123.1842 | 0.068664 | 123.3032 | 123.555 | 123.3856 | 123.2529 | 123.2437 | -123.4634 | -123.3032 | 122.8821 | 123.1613 | 59.9579 | 59.8984
671.4844 | 123.3948 | -60.022 | 63.0524 | -0.065308 | -0.0015743 | 0.06143 | 0.065185 | -0.00065586 | 0.0017794 | -0.0011663 | 0.037811 | -0.0011727 | 0.067276 | 0.067977 | -0.000675 | -0.0014484 | -0.0018265 | 0.013733 | 63.1805 | -60.2921 | 62.9837 | -59.8343 | -60.1868 | 0.073242 | 0.13733 | 63.1439 | -60.1135 | 63.3957 | -60.2509 | -60.2554 | -59.6786 | -0.27008 | 0.12817 | -0.068664 | 0.18768 | 60.0952 | -0.16479 | 60.3653 | 0.10529 | -0.091552 | 0.091553 | 0.34332 | -0.22888 | 0.34332 | -0.23346 | 0.43488 | -0.14191 | 0.45776 | 123.2758 | -0.13733 | 123.5092 | 123.4726 | 123.2574 | 123.2025 | 123.1659 | -123.3444 | -123.1659 | 123.0057 | 123.4177 | 60.0357 | 60.1593
672.4844 | 123.3444 | -60.0677 | 63.0936 | -0.11108 | 0.00077547 | 0.062498 | 0.06369 | 0.0010531 | 0.0011386 | -0.0033025 | 0.0072936 | 0.00096348 | 0.06514 | 0.063705 | -0.0017432 | -0.0018756 | -0.00097194 | -0.11902 | 63.1485 | -60.2921 | 62.8784 | -59.9579 | -60.3104 | -0.045776 | -0.068665 | 63.1531 | -60.1456 | 63.1622 | -60.0357 | -60.1273 | -59.6924 | -0.2243 | 0.054932 | -0.21515 | 0.10986 | 60.022 | -0.24262 | 60.2463 | -0.018311 | -0.07782 | 0.059509 | 0.068664 | 0.032043 | 0.37537 | -0.059509 | 0.45319 | 0.018311 | 0.33417 | 123.1705 | 0.10986 | 123.3078 | 123.4406 | 123.2986 | 123.2162 | 123.2208 | -123.3856 | -123.2391 | 122.9462 | 123.23 | 59.9487 | 59.9991
673.5469 | 123.3307 | -60.0586 | 63.0753 | -0.080566 | 0.00077547 | 0.064634 | 0.062622 | -0.0010831 | -0.00099762 | -0.0041571 | -0.0018616 | -0.00074552 | 0.069199 | 0.068404 | -0.0008886 | -0.001662 | -0.0016129 | -0.11444 | 63.1119 | -60.3195 | 62.8922 | -59.9533 | -60.3241 | -0.068665 | -0.07782 | 63.121 | -60.1593 | 63.1393 | -60.0403 | -60.1456 | -59.6924 | -0.26093 | 0.036621 | -0.18311 | 0.10529 | 59.9899 | -0.2655 | 60.2509 | -0.004578 | -0.10071 | 0.045777 | 0.064087 | 0.018311 | 0.36621 | -0.086975 | 0.46692 | 0.013733 | 0.36621 | 123.2117 | 0.11902 | 123.2986 | 123.4314 | 123.2803 | 123.1705 | 123.1796 | -123.3948 | -123.2346 | 122.9507 | 123.1979 | 59.9442 | 59.9808
674.4844 | 123.4314 | -60.0082 | 63.0753 | 0.018616 | -0.00071993 | 0.063566 | 0.062622 | -0.0010831 | 0.00028418 | -0.0024481 | 0.0072936 | -0.00053192 | 0.066635 | 0.063491 | -0.0017432 | 0.00068782 | 0.0050095 | -0.041199 | 63.1439 | -60.2737 | 62.9654 | -59.8892 | -60.2417 | 0.041199 | 0.086975 | 63.1439 | -60.1227 | 63.2355 | -59.935 | -60.054 | -59.6191 | -0.2655 | 0.068665 | -0.10986 | 0.11902 | 60.0494 | -0.23346 | 60.3149 | 0.032044 | -0.11444 | 0.068665 | 0.16022 | 0.073242 | 0.3891 | -0.045776 | 0.50354 | 0.068665 | 0.38452 | 123.2391 | 0.18768 | 123.3582 | 123.4177 | 123.2666 | 123.1522 | 123.1522 | -123.349 | -123.1979 | 122.9736 | 123.2437 | 59.967 | 60.0952
675.5625 | 123.2712 | -60.0723 | 63.1439 | -0.050049 | -0.0028561 | 0.06143 | 0.064117 | 0.0027621 | -0.0012112 | -0.00073913 | -0.038483 | 0.0016043 | 0.066422 | 0.067977 | -0.0017432 | -0.00038018 | -0.0013991 | 0.009155 | 63.2172 | -60.3012 | 62.883 | -59.9899 | -60.3149 | -0.013733 | 0 | 63.2355 | -60.1364 | 63.1073 | -60.0677 | -60.2005 | -59.7702 | -0.22888 | 0.073242 | -0.26093 | 0.082398 | 60.0586 | -0.24261 | 60.2875 | -0.013733 | -0.064087 | 0.091553 | -0.036621 | 0.004578 | 0.30212 | -0.12817 | 0.36621 | -0.064086 | 0.31128 | 123.1842 | 0.068665 | 123.2437 | 123.5184 | 123.3719 | 123.2895 | 123.3078 | -123.4451 | -123.2803 | 122.9553 | 123.1796 | 60.0815 | 60.0723
676.4844 | 123.3536 | -60.0586 | 63.0981 | -0.042419 | 0.00077547 | 0.064634 | 0.062408 | 0.00062594 | -0.001852 | 0.00011527 | 0.004242 | 0.0020315 | 0.06749 | 0.066482 | -0.0028112 | -0.0018756 | -0.00075834 | -0.10071 | 63.1622 | -60.3195 | 62.9059 | -59.9487 | -60.2921 | -0.018311 | -0.022888 | 63.1577 | -60.1501 | 63.176 | -59.9854 | -60.0952 | -59.6558 | -0.26093 | 0.064086 | -0.19226 | 0.10986 | 60.0403 | -0.23346 | 60.3012 | 0.027466 | -0.091552 | 0.059509 | 0.077819 | 0.073242 | 0.40283 | -0.036621 | 0.49438 | 0.054931 | 0.37079 | 123.2254 | 0.16479 | 123.3261 | 123.4818 | 123.3078 | 123.2208 | 123.2162 | -123.4177 | -123.2483 | 122.9645 | 123.2346 | 59.9579 | 60.0357
677.5469 | 123.3673 | -60.0174 | 63.0753 | -0.0042723 | 0.00098907 | 0.064847 | 0.065185 | 0.00041234 | -0.0012112 | -0.0024481 | 0.0011902 | 0.00096348 | 0.06514 | 0.069259 | -0.0002478 | -0.0012348 | 0.0013779 | 0.009155 | 63.1714 | -60.2646 | 62.9745 | -59.8526 | -60.1913 | 0.07782 | 0.14191 | 63.1714 | -60.1089 | 63.2721 | -59.7198 | -60.2875 | -59.8984 | -0.24719 | 0.096131 | -0.10071 | 0.16479 | 60.0952 | -0.17395 | 60.3424 | 0.073242 | -0.091553 | 0.096131 | 0.19684 | 0.29755 | 0.11902 | -0.27008 | 0.21057 | -0.17853 | 0.41199 | 123.2391 | 0.3891 | 123.381 | 123.436 | 123.2803 | 123.1888 | 123.1888 | -123.3398 | -123.1842 | 122.9919 | 123.2895 | 60.0266 | 60.1593
678.4844 | 123.3673 | -60.0403 | 63.0936 | -0.10345 | 0.0022709 | 0.063138 | 0.064331 | -0.0012967 | -0.0022794 | -0.0011663 | 0.013397 | 0.00032248 | 0.068558 | 0.063277 | -0.000675 | -0.0010212 | 9.6064e-05 | -0.10986 | 63.1165 | -60.3104 | 62.9059 | -59.9533 | -60.3012 | -0.054932 | -0.054932 | 63.1348 | -60.1456 | 63.1531 | -60.0266 | -60.1501 | -59.697 | -0.27008 | 0.022888 | -0.18768 | 0.086975 | 59.9854 | -0.26093 | 60.2554 | 0.009156 | -0.10529 | 0.041199 | 0.059509 | 0.013733 | 0.34332 | -0.10986 | 0.44861 | -0.004577 | 0.35706 | 123.2162 | 0.11902 | 123.2986 | 123.4268 | 123.2803 | 123.1567 | 123.175 | -123.4039 | -123.2391 | 122.9462 | 123.1934 | 59.9304 | 59.9854
679.5 | 123.262 | -60.0677 | 63.1302 | 0.0033567 | -0.00029273 | 0.06207 | 0.066253 | 0.0010531 | -0.00078402 | 0.00032907 | -0.069 | 0.0016043 | 0.06749 | 0.068404 | 0.0014612 | 0.00047422 | -0.0016129 | -0.054932 | 63.2263 | -60.3333 | 62.8647 | -59.9808 | -60.3149 | -0.013733 | -0.004578 | 63.2217 | -60.1456 | 63.1165 | -60.1318 | -60.2234 | -59.7198 | -0.2655 | 0.09613 | -0.2655 | 0.086975 | 60.054 | -0.24719 | 60.3195 | 0.018311 | -0.07782 | 0.091553 | -0.013733 | -0.064087 | 0.3479 | -0.15564 | 0.42572 | -0.07782 | 0.35248 | 123.1979 | 0.013733 | 123.262 | 123.5596 | 123.3673 | 123.2941 | 123.2895 | -123.4634 | -123.2758 | 122.9324 | 123.1842 | 60.0128 | 60.0632
680.5469 | 123.4131 | -60.0494 | 63.089 | -0.080566 | 0.00056187 | 0.06143 | 0.063262 | -0.00044226 | 0.00049778 | -0.0024481 | 0.019501 | 0.0020315 | 0.064713 | 0.067977 | -0.000675 | -0.0025164 | -0.0035355 | -0.086975 | 63.1622 | -60.3516 | 62.9333 | -59.9258 | -60.2783 | -0.004578 | 0.009155 | 63.1622 | -60.1135 | 63.1943 | -59.9854 | -60.0723 | -59.6512 | -0.30212 | 0.073242 | -0.15564 | 0.1236 | 60.0449 | -0.22888 | 60.347 | 0.073242 | -0.064087 | 0.073242 | 0.10529 | 0.064086 | 0.39825 | -0.022889 | 0.46234 | 0.041198 | 0.42572 | 123.2849 | 0.12817 | 123.3078 | 123.5138 | 123.2758 | 123.2117 | 123.2117 | -123.4406 | -123.2025 | 122.9828 | 123.2437 | 59.9625 | 60.0586
681.5 | 123.2986 | -60.0449 | 63.121 | -0.057678 | -0.00050633 | 0.062284 | 0.064971 | 0.0012667 | 7.0582e-05 | 0.0026789 | -0.093414 | 0.00053628 | 0.066422 | 0.068618 | -0.001316 | 0.00026062 | 0.0011643 | -0.018311 | 63.176 | -60.3149 | 62.9059 | -59.9121 | -60.2966 | -0.018311 | 0.054932 | 63.1943 | -60.141 | 63.1485 | -60.0677 | -60.1547 | -59.7061 | -0.27008 | 0.054931 | -0.21515 | 0.13275 | 60.0266 | -0.25177 | 60.2966 | 0.01831 | -0.09613 | 0.073242 | 0.027466 | -0.022888 | 0.33874 | -0.10986 | 0.43487 | -0.013733 | 0.40283 | 123.2208 | 0.073242 | 123.2895 | 123.4909 | 123.3353 | 123.2208 | 123.2391 | -123.436 | -123.262 | 122.9507 | 123.1934 | 60.0266 | 60.0998
682.5 | 123.381 | -60.054 | 63.0295 | -0.11108 | -7.913e-05 | 0.06143 | 0.06369 | 0.0012667 | 0.0011386 | 0.0016107 | -0.038483 | 0.00074988 | 0.066849 | 0.066268 | -0.000675 | 4.7018e-05 | 0.0039413 | 0.050354 | 63.1393 | -60.3104 | 62.9333 | -59.9121 | -60.3012 | -0.073242 | -0.018311 | 63.1027 | -60.1639 | 63.1805 | -60.0174 | -60.1318 | -59.6786 | -0.25635 | 0.10986 | -0.09613 | 0.14191 | 59.9808 | -0.24719 | 60.2371 | 0.009156 | -0.10986 | 0.073242 | 0.15106 | 0.036621 | 0.37537 | -0.07782 | 0.48523 | 0.032043 | 0.39825 | 123.2437 | 0.14648 | 123.3444 | 123.4497 | 123.2666 | 123.1934 | 123.1567 | -123.3398 | -123.1934 | 122.9874 | 123.2346 | 60.1044 | 60.0357
683.5625 | 123.3902 | -60.022 | 63.0661 | -0.019531 | 0.0014163 | 0.065702 | 0.063476 | -0.0038603 | -0.00078402 | -0.0020209 | 0.010345 | 0.00032248 | 0.064926 | 0.070113 | 0.0006066 | -0.00016658 | 0.00073706 | -0.004578 | 63.1348 | -60.2966 | 62.9745 | -59.848 | -60.1959 | 0.064087 | 0.13733 | 63.1531 | -60.1227 | 63.2584 | -60.0174 | -60.0815 | -59.6054 | -0.27466 | 0.068665 | -0.091553 | 0.17395 | 60.0861 | -0.17395 | 60.3607 | 0.10071 | -0.10071 | 0.086975 | 0.19226 | 0.004578 | 0.41657 | -0.059509 | 0.51727 | 0.041199 | 0.44861 | 123.2712 | 0.10529 | 123.381 | 123.4314 | 123.2758 | 123.1567 | 123.175 | -123.3627 | -123.1888 | 122.9965 | 123.2803 | 60.0174 | 60.1593
684.4844 | 123.3627 | -60.0403 | 63.0798 | -0.050049 | -0.00050633 | 0.063779 | 0.064758 | -0.0045011 | 0.00071138 | -0.00052553 | 0.016449 | 0.00010888 | 0.064072 | 0.066482 | -0.000675 | -0.001662 | 0.0020187 | -0.09613 | 63.1439 | -60.3058 | 62.9105 | -59.9899 | -60.2737 | -0.022888 | -0.041199 | 63.0981 | -60.1501 | 63.1577 | -60.0082 | -60.1089 | -59.6832 | -0.2655 | 0.064087 | -0.16937 | 0.050354 | 60.0174 | -0.23346 | 60.2829 | 0.032043 | -0.10986 | 0.018311 | 0.07782 | 0.032043 | 0.35706 | -0.068665 | 0.46692 | 0.041198 | 0.31586 | 123.2162 | 0.14191 | 123.3078 | 123.4497 | 123.2483 | 123.1842 | 123.1384 | -123.3856 | -123.23 | 122.9507 | 123.1979 | 59.9442 | 59.9991
685.4844 | 123.2758 | -60.0998 | 63.0981 | -0.042419 | 0.0035525 | 0.066984 | 0.066894 | -0.00044226 | 0.0037022 | -9.8328e-05 | -0.12088 | 0.0018179 | 0.068131 | 0.072677 | -0.0021704 | 0.00026062 | -0.00054474 | -0.11444 | 63.176 | -60.3561 | 62.8418 | -60.0311 | -60.3699 | -0.13733 | -0.14191 | 63.1851 | -60.1685 | 63.0707 | -60.1456 | -60.2646 | -59.7931 | -0.25635 | 0.077819 | -0.25635 | 0.068664 | 59.9625 | -0.27008 | 60.2188 | -0.013733 | -0.068665 | 0.086975 | -0.027466 | -0.045777 | 0.3067 | -0.16479 | 0.37537 | -0.09613 | 0.32501 | 123.1979 | 0.022888 | 123.2391 | 123.5321 | 123.3536 | 123.2758 | 123.2849 | -123.4543 | -123.2666 | 122.9416 | 123.1705 | 59.9854 | 59.9579
686.4844 | 123.3994 | -60.0037 | 63.0844 | -0.050049 | -0.00029273 | 0.061857 | 0.061767 | 0.00083954 | -0.0027066 | 0.00011527 | 0.010345 | 0.00032248 | 0.066208 | 0.05815 | -0.001316 | 0.00047422 | -0.00075834 | -0.022888 | 63.1577 | -60.2692 | 62.9837 | -59.8206 | -60.1868 | 0.082397 | 0.13733 | 63.1439 | -60.0769 | 63.2309 | -59.9442 | -60.0403 | -59.6191 | -0.2655 | 0.073242 | -0.10071 | 0.1831 | 60.0861 | -0.18311 | 60.3516 | 0.082397 | -0.073242 | 0.059509 | 0.14648 | 0.059509 | 0.38452 | -0.036621 | 0.45776 | 0.036621 | 0.44861 | 123.2529 | 0.13275 | 123.3078 | 123.4268 | 123.2208 | 123.1613 | 123.1476 | -123.3536 | -123.1613 | 122.9874 | 123.2346 | 59.9808 | 60.141
687.4844 | 123.3215 | -60.0311 | 63.1256 | -0.042419 | 0.00098907 | 0.063566 | 0.064117 | -0.0025785 | -0.0031338 | -0.0035163 | -0.020172 | 0.00096348 | 0.066422 | 0.0699 | -0.0011022 | -0.00059378 | 0.0013779 | -0.004578 | 63.1989 | -60.2783 | 62.9288 | -59.9075 | -60.2554 | 0.018311 | 0.064087 | 63.2355 | -60.141 | 63.121 | -60.0586 | -60.1776 | -59.7427 | -0.24719 | 0.073243 | -0.19684 | 0.1236 | 60.0494 | -0.2243 | 60.2966 | 0.022888 | -0.10986 | 0.10986 | -0.004577 | -0.027466 | 0.28839 | -0.14648 | 0.39825 | -0.036621 | 0.37079 | 123.2071 | 0.082397 | 123.262 | 123.4772 | 123.3765 | 123.23 | 123.2666 | -123.4039 | -123.2666 | 122.9599 | 123.1522 | 60.0266 | 60.0952
688.5625 | 123.4497 | -60.0082 | 63.1805 | -0.03479 | 0.0018435 | 0.064634 | 0.064544 | -0.0017239 | 0.0013522 | -0.0013799 | 0.025604 | -0.00074552 | 0.066849 | 0.063277 | -0.0002478 | -0.0014484 | 0.0020187 | 0 | 63.1531 | -60.2737 | 62.9929 | -59.8206 | -60.2051 | 0.068665 | 0.13733 | 63.1577 | -60.0998 | 63.208 | -59.967 | -60.0357 | -59.8068 | -0.2655 | -0.027466 | -0.18768 | 0.18768 | 60.0769 | -0.19684 | 60.3424 | 0.068665 | -0.091552 | -0.022888 | 0.027466 | 0.041199 | 0.20142 | -0.027466 | 0.29297 | 0.064086 | 0.45319 | 123.2666 | 0.13275 | 123.3078 | 123.4268 | 123.2574 | 123.1613 | 123.1659 | -123.4543 | -123.2803 | 123.0011 | 123.2162 | 60.0082 | 60.1456
689.4844 | 123.3994 | -60.0403 | 63.1073 | 0.0033567 | 0.0026981 | 0.062498 | 0.064331 | -0.0017239 | -0.001852 | 0.00096987 | -0.044586 | -0.0016001 | 0.064713 | 0.0699 | -0.0047338 | 4.7018e-05 | 0.0018051 | -0.018311 | 63.1805 | -60.2737 | 63.0432 | -60.2051 | -60.2829 | 0.073242 | 0.16937 | 63.1531 | -60.1135 | 63.208 | -59.9625 | -60.0403 | -59.6283 | -0.23346 | 0.073242 | -0.064087 | -0.16479 | 60.1135 | -0.24262 | 60.347 | -0.009155 | -0.073242 | 0.045776 | 0.10071 | 0.07782 | 0.41199 | 0 | 0.48523 | 0.073242 | 0.068665 | 123.317 | 0.15106 | 123.3215 | 123.4543 | 123.2666 | 123.2208 | 123.1934 | -123.381 | -123.2208 | 123.0835 | 123.2483 | 60.022 | 60.2097
690.4844 | 123.3444 | -60.054 | 63.1302 | -0.019531 | 0.0046207 | 0.063138 | 0.066894 | 0.0031893 | -0.00014322 | 0.00011527 | -0.087311 | 0.00074988 | 0.063858 | 0.065627 | -0.0008886 | 0.0013288 | 0.0028733 | -0.032043 | 63.2217 | -60.3287 | 62.9059 | -59.9533 | -60.2966 | -0.036621 | 0.054932 | 63.2034 | -60.1227 | 63.1439 | -60.0632 | -60.1685 | -59.7015 | -0.27466 | 0.091553 | -0.2243 | 0.10071 | 60.0174 | -0.24262 | 60.2921 | 0.032043 | -0.068665 | 0.073242 | 0.013733 | -0.009155 | 0.35248 | -0.11444 | 0.42114 | -0.045776 | 0.37537 | 123.2346 | 0.05951 | 123.2666 | 123.5504 | 123.3261 | 123.2758 | 123.2574 | -123.4589 | -123.2529 | 122.9599 | 123.1979 | 60.022 | 60.1089
691.5625 | 123.3765 | -60.0266 | 63.121 | -0.050049 | 0.00098907 | 0.063138 | 0.062835 | -0.0027921 | -0.00035682 | -0.0015935 | 0.0011902 | 0.00010888 | 0.063431 | 0.067336 | 0.000393 | -0.0018756 | -0.00097194 | 0.12817 | 63.2217 | -60.2509 | 62.9196 | -59.848 | -60.1776 | 0.009155 | 0.09613 | 63.1531 | -60.1135 | 63.1943 | -59.9762 | -60.0769 | -59.6329 | -0.2243 | 0.10071 | -0.20142 | 0.17853 | 60.0357 | -0.15106 | 60.26 | 0.073242 | -0.086975 | 0.032043 | 0.073242 | 0.050354 | 0.39368 | -0.050354 | 0.48065 | 0.036621 | 0.40283 | 123.1705 | 0.13733 | 123.3078 | 123.4726 | 123.2666 | 123.2483 | 123.1796 | -123.3719 | -123.2346 | 122.9462 | 123.2208 | 60.1547 | 60.1227
692.4844 | 123.3856 | -60.0494 | 63.0844 | -0.027161 | -0.0020017 | 0.065275 | 0.064117 | 0.0019077 | 0.00049778 | 0.00032907 | 0.031708 | -0.00031832 | 0.066849 | 0.062636 | -0.0015296 | -0.0025164 | 0.0020187 | -0.091553 | 63.1805 | -60.3195 | 62.9013 | -59.935 | -60.2829 | -0.022888 | 0 | 63.1531 | -60.1273 | 63.2034 | -59.9716 | -60.0861 | -59.6695 | -0.27008 | 0.09613 | -0.18311 | 0.11444 | 60.0266 | -0.23346 | 60.2966 | 0.036621 | -0.07782 | 0.068664 | 0.11902 | 0.077819 | 0.37994 | -0.036622 | 0.45776 | 0.041198 | 0.38452 | 123.2208 | 0.15564 | 123.3307 | 123.5001 | 123.2803 | 123.23 | 123.2025 | -123.4039 | -123.2117 | 122.9507 | 123.2529 | 59.9579 | 60.0494
693.5 | 123.3307 | -60.0998 | 63.0844 | 0.09491 | 0.00077547 | 0.06442 | 0.066894 | 0.00062594 | 0.00028418 | 0.00096987 | -0.078156 | 0.0020315 | 0.063858 | 0.071395 | -0.0028112 | 0.002824 | 0.0020187 | -0.18768 | 63.1622 | -60.3561 | 62.8326 | -60.0586 | -60.3607 | -0.15564 | -0.16022 | 63.1485 | -60.1685 | 63.1165 | -60.1273 | -60.2554 | -59.7473 | -0.25635 | 0.077819 | -0.25177 | 0.041198 | 59.9442 | -0.26093 | 60.2005 | -0.004578 | -0.068665 | 0.064087 | 0.032043 | -0.027466 | 0.35248 | -0.15564 | 0.42114 | -0.086975 | 0.29755 | 123.1888 | 0.041199 | 123.2849 | 123.5184 | 123.317 | 123.262 | 123.2483 | -123.4406 | -123.2529 | 122.9324 | 123.2162 | 59.9121 | 59.9396
694.4844 | 123.4497 | -60.0266 | 63.0661 | -0.019531 | -0.00050633 | 0.063779 | 0.063476 | 0.00062594 | 0.00049778 | -0.0022345 | 0.004242 | -0.00074552 | 0.065995 | 0.064773 | -0.002384 | -0.0012348 | -0.0028945 | 0 | 63.1577 | -60.2783 | 62.9837 | -59.8389 | -60.2005 | 0.073242 | 0.14648 | 63.1668 | -60.0998 | 63.3682 | -59.7931 | -60.4111 | -59.848 | -0.25177 | 0.091553 | -0.082397 | 0.18768 | 60.0998 | -0.17395 | 60.3516 | 0.07782 | -0.073242 | 0.10071 | 0.30212 | 0.23346 | 0.17853 | -0.38452 | 0.25177 | -0.31128 | 0.43945 | 123.262 | 0.3067 | 123.468 | 123.436 | 123.2666 | 123.1842 | 123.1934 | -123.3444 | -123.1659 | 123.0103 | 123.3948 | 60.0266 | 60.173
695.5625 | 123.3307 | -60.0403 | 63.1348 | -0.019531 | -0.00071993 | 0.062711 | 0.064758 | 0.0019077 | -0.001852 | -0.00052553 | -0.035431 | 0.0011771 | 0.066635 | 0.064773 | -0.0019568 | -0.00016658 | -0.0035355 | -0.036621 | 63.1897 | -60.3378 | 62.8876 | -59.9716 | -60.3104 | -0.036621 | 0.022888 | 63.208 | -60.1364 | 63.1485 | -60.054 | -60.1593 | -59.7061 | -0.29755 | 0.054931 | -0.24719 | 0.068664 | 60.0037 | -0.27008 | 60.3012 | 0.027466 | -0.096131 | 0.073242 | 0.013733 | -0.013733 | 0.33417 | -0.11902 | 0.4303 | -0.022888 | 0.36621 | 123.2254 | 0.082398 | 123.2849 | 123.5275 | 123.3444 | 123.23 | 123.2483 | -123.4726 | -123.2712 | 122.9279 | 123.1888 | 60.0037 | 60.0632
696.4844 | 123.3719 | -60.0403 | 63.0844 | -0.057678 | 0.0012027 | 0.064634 | 0.063262 | 0.0012667 | -0.0039884 | 0.00054267 | 0.016449 | 0.0018179 | 0.064926 | 0.060927 | -3.4196e-05 | -0.0010212 | 0.0013779 | -0.10529 | 63.1714 | -60.3058 | 62.9974 | -60.0174 | -60.3424 | -0.041199 | -0.041199 | 63.1485 | -60.1318 | 63.1485 | -60.0311 | -60.1181 | -59.6558 | -0.2655 | 0.086975 | -0.086975 | 0.022888 | 59.9991 | -0.30212 | 60.2646 | -0.036621 | -0.091553 | 0.064087 | 0.064087 | 0.009155 | 0.38452 | -0.07782 | 0.47607 | 0.013733 | 0.28839 | 123.3032 | 0.10071 | 123.2803 | 123.4772 | 123.2803 | 123.2117 | 123.1888 | -123.3902 | -123.2162 | 123.0377 | 123.1888 | 59.935 | 59.9991
697.5 | 123.2941 | -60.0449 | 63.1348 | -0.072937 | 0.00056187 | 0.063993 | 0.063903 | -0.0023649 | 0.00049778 | -0.0015935 | -0.0018616 | -0.0011727 | 0.066849 | 0.065841 | -0.0021704 | -0.0018756 | 9.6064e-05 | -0.027466 | 63.1714 | -60.2829 | 62.9105 | -59.9304 | -60.2509 | 0.022888 | 0.032043 | 63.1943 | -60.1089 | 63.1302 | -60.0632 | -60.1593 | -59.729 | -0.23804 | 0.036621 | -0.22431 | 0.11444 | 60.0677 | -0.20599 | 60.3058 | 0.032044 | -0.064087 | 0.059509 | -0.004578 | -0.01831 | 0.31586 | -0.11444 | 0.37994 | -0.050354 | 0.35248 | 123.1934 | 0.045777 | 123.2391 | 123.4543 | 123.3032 | 123.2162 | 123.2391 | -123.4177 | -123.2437 | 122.9553 | 123.175 | 60.0174 | 60.0769
698.5469 | 123.3765 | -60.0586 | 63.0753 | -0.072937 | -0.00093353 | 0.064634 | 0.063049 | -0.0021513 | -0.00057042 | -0.0030889 | -0.047638 | 0.00010888 | 0.068558 | 0.065627 | -0.0011022 | -0.0027302 | 0.00095066 | -0.11902 | 63.1485 | -60.3012 | 62.9242 | -59.9808 | -60.1501 | 0.036621 | -0.045776 | 63.1302 | -60.1364 | 63.1531 | -60.022 | -60.1364 | -59.6924 | -0.24261 | 0.073243 | -0.15106 | 0.07782 | 60.0952 | -0.091552 | 60.3378 | 0.15106 | -0.07782 | 0.054932 | 0.07782 | 0.036621 | 0.36621 | -0.07782 | 0.44403 | 0 | 0.32043 | 123.2254 | 0.11444 | 123.2895 | 123.4497 | 123.2666 | 123.2071 | 123.1888 | -123.3765 | -123.2117 | 122.9828 | 123.2117 | 59.9396 | 60.0128
699.4844 | 123.2712 | -60.0723 | 63.1027 | -0.080566 | 0.0018435 | 0.064634 | 0.06668 | 0.0055393 | -0.00078402 | 0.0028925 | -0.10562 | -0.00074552 | 0.068558 | 0.065627 | -0.0002478 | 4.7018e-05 | 0.00095066 | -0.07782 | 63.1897 | -60.3058 | 62.8784 | -59.9945 | -60.3333 | -0.11902 | -0.07782 | 63.1622 | -60.1364 | 63.1027 | -60.1181 | -60.2142 | -59.761 | -0.23346 | 0.086975 | -0.2243 | 0.07782 | 59.9533 | -0.26093 | 60.1868 | -0.027466 | -0.064087 | 0.059509 | 0 | -0.045776 | 0.31128 | -0.14191 | 0.37537 | -0.077819 | 0.31128 | 123.1842 | 0.018311 | 123.2391 | 123.4955 | 123.2986 | 123.262 | 123.2346 | -123.4085 | -123.2391 | 122.9507 | 123.175 | 59.9945 | 59.9945
700.5469 | 123.3353 | -60.054 | 63.0569 | -0.088196 | 0.00056187 | 0.063993 | 0.062622 | 0.0027621 | 7.0582e-05 | 0.0031061 | 0.013397 | -0.00053192 | 0.064713 | 0.063491 | -0.0038794 | -0.0014484 | -0.0013991 | -0.10986 | 63.1393 | -60.3287 | 62.915 | -59.935 | -60.3195 | -0.09613 | -0.091553 | 63.1119 | -60.1318 | 63.1302 | -60.054 | -60.1456 | -59.6878 | -0.27466 | 0.082397 | -0.14191 | 0.11902 | 59.9579 | -0.2655 | 60.2325 | 0.009155 | -0.07782 | 0.054931 | 0.073242 | 0 | 0.36621 | -0.091553 | 0.44403 | -0.013733 | 0.39368 | 123.2437 | 0.07782 | 123.262 | 123.468 | 123.2437 | 123.1934 | 123.1659 | -123.3856 | -123.1888 | 122.9691 | 123.1842 | 59.9442 | 59.9625
701.4844 | 123.4039 | -59.9991 | 63.0844 | -0.050049 | 0.00056187 | 0.064847 | 0.064331 | -1.486e-05 | 0.00049778 | 0.0013971 | 0.0072936 | -0.00053192 | 0.066635 | 0.065627 | -0.0002478 | -0.0014484 | -0.0022537 | -0.13733 | 63.1805 | -60.2509 | 62.9425 | -59.9533 | -60.1456 | 0.036621 | 0.11444 | 63.1485 | -60.1089 | 63.1989 | -59.967 | -60.0861 | -59.6603 | -0.25177 | 0.09613 | -0.14191 | 0.045776 | 60.0357 | -0.14648 | 60.2875 | 0.10528 | -0.10986 | 0.064087 | 0.11444 | 0.032043 | 0.33875 | -0.086976 | 0.44861 | 0.022888 | 0.29755 | 123.1934 | 0.14191 | 123.3078 | 123.4314 | 123.2574 | 123.1796 | 123.1476 | -123.3353 | -123.1934 | 122.9416 | 123.1979 | 59.8618 | 60.1135
702.4844 | 123.4268 | -59.9991 | 63.089 | -0.088196 | -7.913e-05 | 0.062284 | 0.064971 | -0.00065586 | -0.0014248 | -0.0045843 | 0.019501 | -0.00031832 | 0.065995 | 0.06285 | -0.0021704 | -0.0025164 | 0.00052346 | -0.059509 | 63.1622 | -60.2692 | 62.9471 | -59.8434 | -60.2005 | 0.050354 | 0.14648 | 63.1393 | -60.1089 | 63.2492 | -59.9442 | -60.0174 | -59.61 | -0.27008 | 0.073242 | -0.14191 | 0.15564 | 60.0494 | -0.20142 | 60.3195 | 0.068665 | -0.10986 | 0.050354 | 0.16022 | 0.054931 | 0.3891 | -0.018311 | 0.49896 | 0.091553 | 0.42572 | 123.2162 | 0.16479 | 123.3582 | 123.4314 | 123.2483 | 123.1613 | 123.1384 | -123.3582 | -123.1979 | 122.9462 | 123.2483 | 59.9396 | 60.1456
703.5 | 123.3032 | -60.0815 | 63.0707 | -0.088196 | -0.0026425 | 0.062498 | 0.064971 | -0.0021513 | 0.00049778 | 0.0013971 | -0.081207 | 0.0016043 | 0.068131 | 0.06755 | -0.001316 | -0.00059378 | -0.00011754 | -0.12817 | 63.1805 | -60.3424 | 62.8372 | -60.054 | -60.3928 | -0.17853 | -0.14191 | 63.1577 | -60.1685 | 63.1119 | -60.1089 | -60.2188 | -59.7336 | -0.26093 | 0.10986 | -0.23346 | 0.027466 | 59.903 | -0.31128 | 60.1639 | -0.050354 | -0.086975 | 0.086975 | 0.041198 | -0.027466 | 0.3479 | -0.13733 | 0.43487 | -0.050354 | 0.28839 | 123.1796 | 0.059509 | 123.2803 | 123.5229 | 123.3261 | 123.262 | 123.2391 | -123.4131 | -123.2391 | 122.9187 | 123.1934 | 59.9533 | 59.9396
704.5469 | 123.3765 | -60.0586 | 63.0569 | -0.095825 | 0.00056187 | 0.061857 | 0.062835 | -0.0010831 | 7.0582e-05 | 0.00011527 | 0.019501 | -0.00010472 | 0.06749 | 0.067763 | -0.003025 | -0.001662 | 0.00052346 | -0.15106 | 63.1485 | -60.3149 | 62.8876 | -59.9304 | -60.3058 | -0.082397 | -0.073242 | 63.1439 | -60.1501 | 63.1531 | -60.0449 | -60.1593 | -59.6878 | -0.25635 | 0.091553 | -0.16937 | 0.12817 | 59.9762 | -0.24719 | 60.2325 | 0.009155 | -0.091552 | 0.086975 | 0.09613 | 0.013733 | 0.37079 | -0.10071 | 0.46234 | -0.009156 | 0.38452 | 123.2025 | 0.10529 | 123.3032 | 123.4634 | 123.2941 | 123.2071 | 123.2025 | -123.3719 | -123.2071 | 122.9462 | 123.2117 | 59.9075 | 59.9854
705.5 | 123.23 | -60.0998 | 63.0753 | -0.03479 | 0.00056187 | 0.06442 | 0.066467 | -0.0015103 | -0.00078402 | 0.00054267 | -0.087311 | 0.0018179 | 0.068558 | 0.067336 | -0.0015296 | -0.0010212 | -0.0013991 | -0.12817 | 63.208 | -60.3653 | 62.8235 | -60.0632 | -60.4385 | -0.18768 | -0.17395 | 63.1851 | -60.1776 | 63.0615 | -60.1776 | -60.2966 | -59.7977 | -0.2655 | 0.13275 | -0.25177 | 0.036621 | 59.9121 | -0.33875 | 60.1776 | -0.073243 | -0.07782 | 0.10986 | -0.013733 | -0.07782 | 0.30212 | -0.19684 | 0.37994 | -0.11902 | 0.30212 | 123.1888 | 0 | 123.2391 | 123.5733 | 123.3627 | 123.3078 | 123.2849 | -123.4406 | -123.2529 | 122.9233 | 123.1613 | 59.9716 | 59.9258
706.4844 | 123.4131 | -60.0174 | 63.0707 | -0.042419 | -0.0013607 | 0.062284 | 0.06369 | -0.00022866 | 0.0015658 | -0.00052553 | 0.046967 | -0.00010472 | 0.066208 | 0.061141 | -0.000675 | -0.00080758 | 0.0039413 | -0.054932 | 63.1897 | -60.2875 | 62.9929 | -59.8068 | -60.173 | 0.068665 | 0.12817 | 63.1668 | -60.0906 | 63.2034 | -59.9579 | -60.0449 | -59.6237 | -0.27008 | 0.11902 | -0.07782 | 0.21057 | 60.0861 | -0.15564 | 60.3561 | 0.11444 | -0.073242 | 0.09613 | 0.13275 | 0.059509 | 0.39368 | -0.027466 | 0.46692 | 0.045776 | 0.48065 | 123.2803 | 0.13275 | 123.2941 | 123.4772 | 123.2574 | 123.2071 | 123.1842 | -123.3582 | -123.1613 | 123.0103 | 123.2208 | 59.9625 | 60.1456
707.4844 | 123.2941 | -60.0357 | 63.1348 | -0.011902 | -0.0011471 | 0.063566 | 0.065185 | 0.00019874 | -0.0014248 | -0.00031193 | -0.026276 | 0.0018179 | 0.068131 | 0.06755 | -0.0011022 | -0.00080758 | -0.0026809 | -0.07782 | 63.2126 | -60.3012 | 62.8876 | -59.9762 | -60.3058 | -0.032043 | 0.013733 | 63.2034 | -60.1318 | 63.1027 | -60.0723 | -60.1685 | -59.7382 | -0.2655 | 0.077819 | -0.24719 | 0.05951 | 60.0037 | -0.27008 | 60.2692 | -0.004578 | -0.09613 | 0.068664 | -0.032044 | -0.036621 | 0.29755 | -0.13275 | 0.39368 | -0.036621 | 0.32501 | 123.1888 | 0.059509 | 123.2346 | 123.5138 | 123.3353 | 123.2483 | 123.2391 | -123.436 | -123.2666 | 122.9233 | 123.1384 | 59.9579 | 60.0494
708.4844 | 123.2712 | -60.0723 | 63.121 | -0.080566 | 0.0014163 | 0.065916 | 0.067321 | 0.0012667 | -0.00014322 | 0.0011835 | -0.084259 | 0.0024589 | 0.066635 | 0.065627 | -0.0011022 | 0.001115 | -0.0026809 | -0.073242 | 63.2263 | -60.3149 | 62.8784 | -59.9854 | -60.3424 | -0.10986 | -0.073242 | 63.176 | -60.1501 | 63.1027 | -60.1181 | -60.2325 | -59.7519 | -0.24261 | 0.10529 | -0.24261 | 0.086975 | 59.9625 | -0.27008 | 60.2051 | -0.027466 | -0.077819 | 0.054931 | -0.018311 | -0.045776 | 0.32044 | -0.16022 | 0.39825 | -0.082398 | 0.32959 | 123.1934 | 0.032043 | 123.2529 | 123.5413 | 123.3261 | 123.2986 | 123.2483 | -123.436 | -123.2712 | 122.9507 | 123.175 | 59.9991 | 59.9991
709.5469 | 123.4177 | -60.0357 | 63.0844 | -0.03479 | -0.00071993 | 0.064634 | 0.061553 | -0.00065586 | -0.00057042 | -0.0018073 | 0.034759 | 0.0011771 | 0.067704 | 0.059218 | -0.0008886 | 0.00090142 | 0.0022323 | -0.11444 | 63.176 | -60.2829 | 62.9013 | -59.935 | -60.2875 | -0.045776 | -0.045776 | 63.1485 | -60.1318 | 63.1714 | -59.9808 | -60.0952 | -59.6649 | -0.24719 | 0.091552 | -0.18311 | 0.10071 | 59.9899 | -0.25177 | 60.2371 | -0.004578 | -0.09613 | 0.064087 | 0.086975 | 0.054932 | 0.37079 | -0.059509 | 0.46692 | 0.036621 | 0.3479 | 123.1842 | 0.15106 | 123.3032 | 123.4589 | 123.2803 | 123.2117 | 123.1842 | -123.3673 | -123.2162 | 122.937 | 123.2071 | 59.9213 | 59.9899
710.4844 | 123.3902 | -60.0174 | 63.0936 | -0.0042723 | -0.00050633 | 0.063138 | 0.063903 | -0.00065586 | 0.00071138 | -0.0026617 | 0.019501 | -0.00074552 | 0.065567 | 0.061141 | -0.0034522 | -0.0037982 | -0.0018265 | -0.036621 | 63.1577 | -60.2783 | 62.9608 | -59.6649 | -59.8892 | -0.086975 | 0.11902 | 63.1256 | -60.1044 | 63.2126 | -59.967 | -60.0723 | -59.6329 | -0.26093 | 0.064087 | -0.13275 | 0.35248 | 59.9304 | 0.12817 | 60.1913 | 0.3891 | -0.086975 | 0.032043 | 0.11902 | 0.050354 | 0.38452 | -0.054932 | 0.4715 | 0.032043 | 0.6134 | 123.2391 | 0.13733 | 123.317 | 123.436 | 123.23 | 123.175 | 123.143 | -123.3719 | -123.1979 | 122.9782 | 123.23 | 59.9808 | 60.1364
711.5625 | 123.4451 | -60.022 | 63.0798 | -0.011902 | -0.00029273 | 0.063352 | 0.064758 | -0.00086946 | -0.0027066 | -0.00073913 | 0.065277 | 0.00032248 | 0.067276 | 0.063277 | -0.002384 | -0.00016658 | -0.00097194 | -0.059509 | 63.1439 | -60.2921 | 62.9837 | -59.8572 | -60.1685 | 0.041199 | 0.11902 | 63.1531 | -60.1227 | 63.2172 | -59.9258 | -60.0174 | -59.6054 | -0.27008 | 0.064087 | -0.09613 | 0.1648 | 60.0632 | -0.14648 | 60.3333 | 0.1236 | -0.10071 | 0.073242 | 0.13733 | 0.096131 | 0.41657 | 0.004578 | 0.51727 | 0.10529 | 0.43488 | 123.2758 | 0.19684 | 123.3398 | 123.436 | 123.2758 | 123.1659 | 123.175 | -123.3719 | -123.2025 | 123.0057 | 123.2391 | 59.9625 | 60.141
712.4844 | 123.349 | -60.054 | 63.0753 | -0.072937 | -0.00093353 | 0.062498 | 0.064971 | -0.0021513 | -0.0016384 | -0.0011663 | 0.022552 | 0.0011771 | 0.065995 | 0.063705 | -0.0008886 | 4.7018e-05 | 0.00073706 | -0.13275 | 63.1485 | -60.3378 | 62.883 | -59.9533 | -60.3012 | -0.073242 | -0.07782 | 63.1577 | -60.1456 | 63.1485 | -60.0311 | -60.1501 | -59.7015 | -0.28381 | 0.073243 | -0.19226 | 0.10071 | 59.9808 | -0.24719 | 60.2646 | 0.036622 | -0.091553 | 0.082398 | 0.073243 | 0.022888 | 0.35248 | -0.09613 | 0.44403 | -0.004577 | 0.38452 | 123.2208 | 0.11444 | 123.2941 | 123.4863 | 123.3032 | 123.2025 | 123.2117 | -123.4131 | -123.2208 | 122.937 | 123.2025 | 59.9213 | 59.9762
713.4844 | 123.3765 | -60.022 | 63.0981 | -0.042419 | -0.00093353 | 0.063138 | 0.062835 | -0.00022866 | 0.00092498 | -0.0018073 | 0.040863 | 0.0018179 | 0.067276 | 0.068191 | -0.003025 | -0.0014484 | -0.00075834 | -0.09613 | 63.1577 | -60.3241 | 62.9471 | -59.8984 | -60.2371 | -0.004578 | 0.013733 | 63.1439 | -60.1135 | 63.1805 | -59.9625 | -60.0815 | -59.6558 | -0.30212 | 0.059509 | -0.15106 | 0.1236 | 60.0174 | -0.21515 | 60.3195 | 0.086975 | -0.091552 | 0.045776 | 0.082397 | 0.05951 | 0.36621 | -0.059509 | 0.45776 | 0.032043 | 0.42572 | 123.2712 | 0.15106 | 123.2941 | 123.4818 | 123.2574 | 123.1796 | 123.1659 | -123.4222 | -123.2117 | 122.9691 | 123.2025 | 59.9258 | 60.0357
714.4844 | 123.3215 | -60.0403 | 63.0707 | -0.088196 | 0.00034827 | 0.065061 | 0.064117 | -0.00022866 | -0.00099762 | -0.00052553 | -0.0049134 | 0.00032248 | 0.068131 | 0.068404 | -0.0025976 | 0.00068782 | -0.00097194 | -0.13275 | 63.1302 | -60.3516 | 62.8967 | -59.9304 | -60.3104 | -0.09613 | -0.082397 | 63.1348 | -60.1685 | 63.1531 | -60.0449 | -60.1364 | -59.7107 | -0.31128 | 0.059509 | -0.17395 | 0.10986 | 59.9442 | -0.27008 | 60.2554 | 0.041198 | -0.12817 | 0.064087 | 0.082397 | -0.004578 | 0.32959 | -0.096131 | 0.45776 | 0.032043 | 0.42114 | 123.2483 | 0.1236 | 123.3215 | 123.4818 | 123.3032 | 123.1705 | 123.175 | -123.4222 | -123.2391 | 122.937 | 123.1934 | 59.9075 | 59.9579
715.4844 | 123.4039 | -60.0174 | 63.0798 | -0.072937 | -7.913e-05 | 0.061857 | 0.064971 | 0.0025485 | -0.0012112 | -0.0018073 | 0.019501 | 0.0030997 | 0.066422 | 0.066482 | -0.001316 | -0.0012348 | -0.0035355 | -0.036621 | 63.1622 | -60.2875 | 62.9974 | -59.8206 | -60.173 | 0.064087 | 0.10529 | 63.1577 | -60.1135 | 63.2126 | -59.9396 | -60.0494 | -59.6146 | -0.27008 | 0.082397 | -0.082397 | 0.19684 | 60.0815 | -0.15564 | 60.3516 | 0.11444 | -0.09613 | 0.07782 | 0.13275 | 0.07782 | 0.40283 | -0.032043 | 0.49896 | 0.064087 | 0.46692 | 123.2849 | 0.17395 | 123.3261 | 123.4497 | 123.2712 | 123.1796 | 123.175 | -123.3673 | -123.1934 | 123.0148 | 123.23 | 59.9808 | 60.1227
716.4844 | 123.3673 | -60.0403 | 63.0661 | -0.088196 | 0.00077547 | 0.063138 | 0.06604 | -0.0019377 | -0.0020658 | -0.0026617 | -0.035431 | -0.00095912 | 0.067063 | 0.066054 | -0.0011022 | 0.00047422 | -0.0018265 | -0.09613 | 63.121 | -60.3058 | 62.9333 | -59.9075 | -60.2875 | -0.10071 | -0.036621 | 63.1393 | -60.1547 | 63.1851 | -60.0266 | -60.1227 | -59.6832 | -0.2655 | 0.054932 | -0.13275 | 0.13275 | 59.9396 | -0.24719 | 60.2051 | 0.01831 | -0.11444 | 0.073242 | 0.11902 | 0.013733 | 0.35706 | -0.082398 | 0.4715 | 0.032043 | 0.39825 | 123.2391 | 0.12817 | 123.3398 | 123.4268 | 123.2941 | 123.1613 | 123.1796 | -123.3719 | -123.2208 | 122.9736 | 123.2254 | 59.9442 | 60.0037
717.4844 | 123.381 | -60.0311 | 63.1027 | -0.095825 | -0.00050633 | 0.062284 | 0.064758 | -0.0032193 | 0.00071138 | -0.00073913 | 0.0011902 | -0.00010472 | 0.067063 | 0.068191 | -0.001316 | -0.00016658 | 0.0024461 | -0.13733 | 63.1577 | -60.3241 | 62.9013 | -59.9396 | -60.2875 | -0.082397 | -0.068665 | 63.1302 | -60.1364 | 63.1622 | -60.0403 | -60.141 | -59.697 | -0.29297 | 0.054932 | -0.20142 | 0.091553 | 59.9487 | -0.25635 | 60.2417 | 0.036621 | -0.10529 | 0.027466 | 0.059509 | -0.009155 | 0.33417 | -0.10986 | 0.43945 | -0.004577 | 0.38452 | 123.2254 | 0.096131 | 123.2986 | 123.4818 | 123.2666 | 123.1888 | 123.1613 | -123.4268 | -123.2391 | 122.9324 | 123.1934 | 59.8938 | 59.9625
718.5469 | 123.3948 | -60.0449 | 63.0569 | -0.050049 | -7.913e-05 | 0.063566 | 0.064544 | 0.0055393 | -0.00057042 | 0.00011527 | -0.059845 | 0.0016043 | 0.065354 | 0.068404 | -0.0019568 | -0.0018756 | -0.0031081 | -0.12817 | 63.1439 | -60.3333 | 62.9196 | -59.9213 | -60.2829 | -0.11902 | -0.07782 | 63.1256 | -60.1456 | 63.1897 | -60.0037 | -60.1227 | -59.6603 | -0.28839 | 0.086975 | -0.13733 | 0.1236 | 59.9258 | -0.23804 | 60.2142 | 0.050354 | -0.10071 | 0.068664 | 0.13275 | 0.041199 | 0.38452 | -0.07782 | 0.48523 | 0.022888 | 0.41199 | 123.2529 | 0.14191 | 123.3353 | 123.4772 | 123.2712 | 123.1888 | 123.1705 | -123.3902 | -123.2025 | 122.9645 | 123.2346 | 59.9167 | 59.967
719.5 | 123.2849 | -60.0586 | 63.1622 | -0.027161 | -7.913e-05 | 0.061216 | 0.066467 | -0.0025785 | -0.0020658 | -0.00073913 | -0.023224 | 0.00032248 | 0.065781 | 0.066695 | -0.0015296 | -0.00059378 | 0.0024461 | -0.09613 | 63.2309 | -60.3058 | 62.8738 | -59.9762 | -60.3104 | -0.054932 | -0.009155 | 63.2034 | -60.1456 | 63.1165 | -60.0769 | -60.1776 | -59.7519 | -0.24719 | 0.068665 | -0.28839 | 0.082398 | 60.0037 | -0.25177 | 60.2509 | -0.004578 | -0.086975 | 0.041199 | -0.045776 | -0.01831 | 0.3067 | -0.11902 | 0.39368 | -0.032043 | 0.32959 | 123.1796 | 0.068665 | 123.262 | 123.5367 | 123.349 | 123.2895 | 123.262 | -123.468 | -123.3078 | 122.9324 | 123.175 | 59.9625 | 60.0494
720.5469 | 123.4314 | -60.0174 | 63.0936 | 0.0033567 | -0.0015743 | 0.062498 | 0.064117 | -0.0012967 | 0.00092498 | 0.00075627 | 0.016449 | 0.00053628 | 0.06514 | 0.064986 | -0.0015296 | -0.0035846 | -0.00033114 | -0.082397 | 63.1668 | -60.2921 | 62.9608 | -59.8663 | -60.2234 | -0.004578 | 0.054932 | 63.1531 | -60.1089 | 63.2355 | -59.9533 | -60.054 | -59.6283 | -0.27466 | 0.073242 | -0.13275 | 0.15106 | 60.0128 | -0.20599 | 60.2875 | 0.068664 | -0.091553 | 0.059509 | 0.14191 | 0.064087 | 0.3891 | -0.036621 | 0.48065 | 0.054932 | 0.42572 | 123.2529 | 0.15564 | 123.3444 | 123.4589 | 123.262 | 123.1842 | 123.1705 | -123.3856 | -123.2025 | 122.9782 | 123.2529 | 59.935 | 60.0723
721.4844 | 123.3627 | -60.0403 | 63.0844 | -0.088196 | -0.00071993 | 0.063138 | 0.064331 | 0.00062594 | -0.0022794 | -0.00073913 | 0.031708 | 0.0018179 | 0.06514 | 0.0652 | -0.0017432 | -0.001662 | 0.00052346 | -0.13275 | 63.1531 | -60.3149 | 62.9883 | -60.0677 | -60.2875 | -0.082397 | -0.054932 | 63.1439 | -60.1318 | 63.1485 | -60.0174 | -60.1135 | -59.6786 | -0.27466 | 0.068664 | -0.096131 | -0.027466 | 59.9579 | -0.24719 | 60.2325 | 0.027465 | -0.091553 | 0.059509 | 0.064087 | 0.022888 | 0.36163 | -0.073242 | 0.45319 | 0.018311 | 0.24719 | 123.3032 | 0.11444 | 123.2803 | 123.468 | 123.2758 | 123.1934 | 123.1842 | -123.3994 | -123.2162 | 123.0286 | 123.1888 | 59.9075 | 59.9854
722.4844 | 123.3627 | -60.0586 | 63.0661 | -0.11108 | -0.0020017 | 0.063993 | 0.06668 | 0.0051119 | 0.0013522 | 0.0024653 | -0.020172 | 0.00096348 | 0.065354 | 0.066482 | -0.0025976 | -0.0010212 | -0.00033114 | -0.1236 | 63.1577 | -60.2829 | 62.9425 | -59.8846 | -60.2921 | -0.10071 | -0.064087 | 63.1393 | -60.1456 | 63.176 | -60.0403 | -60.1227 | -59.6741 | -0.2243 | 0.091553 | -0.1236 | 0.17395 | 59.9579 | -0.23346 | 60.1822 | -0.009155 | -0.086975 | 0.073242 | 0.10986 | 0.018311 | 0.38452 | -0.064087 | 0.4715 | 0.022888 | 0.39825 | 123.2254 | 0.10529 | 123.3215 | 123.4406 | 123.2849 | 123.2162 | 123.1979 | -123.349 | -123.2117 | 123.0011 | 123.2346 | 59.935 | 59.9945
723.5625 | 123.3353 | -60.054 | 63.0569 | -0.065308 | -0.0011471 | 0.063993 | 0.064758 | -0.00044226 | 0.00028418 | -0.00052553 | -0.01712 | 0.00053628 | 0.066635 | 0.067336 | -0.0025976 | -0.0018756 | 0.00095066 | -0.15564 | 63.121 | -60.3104 | 62.9059 | -59.9487 | -60.3104 | -0.10986 | -0.10071 | 63.1531 | -60.1501 | 63.1622 | -60.0357 | -60.1364 | -59.6878 | -0.25635 | 0.064087 | -0.15106 | 0.10529 | 59.9442 | -0.25635 | 60.2005 | 0 | -0.09613 | 0.09613 | 0.10528 | 0.01831 | 0.36621 | -0.082398 | 0.46234 | 0.013732 | 0.36163 | 123.2162 | 0.11444 | 123.3124 | 123.4314 | 123.3032 | 123.175 | 123.2071 | -123.3673 | -123.2071 | 122.9599 | 123.2162 | 59.8984 | 59.9533
724.4844 | 123.3902 | -60.0494 | 63.0707 | -0.10345 | 0.0031253 | 0.062284 | 0.065185 | 0.0014803 | -0.0014248 | -0.0020209 | 0.019501 | 0.00074988 | 0.065354 | 0.069686 | -0.002384 | -0.0010212 | -0.0013991 | -0.11902 | 63.1027 | -60.3241 | 62.9517 | -59.8206 | -60.5988 | -0.23346 | -0.091553 | 63.121 | -60.1273 | 63.1897 | -60.0174 | -60.1044 | -59.6603 | -0.27466 | 0.032043 | -0.11902 | 0.22888 | 59.816 | -0.54932 | 60.0906 | -0.27466 | -0.07782 | 0.050354 | 0.11902 | 0.032043 | 0.3891 | -0.054932 | 0.46692 | 0.022888 | 0.50354 | 123.2758 | 0.10986 | 123.317 | 123.4268 | 123.2483 | 123.1522 | 123.1705 | -123.3948 | -123.1979 | 123.0011 | 123.2391 | 59.9304 | 59.9579
725.4844 | 123.3673 | -60.0174 | 63.0753 | 0.033875 | 0.00013467 | 0.062498 | 0.064331 | 0.00019874 | 0.00049778 | -9.8328e-05 | 0.019501 | 0.00074988 | 0.066208 | 0.067123 | -0.0011022 | -0.00080758 | -0.0016129 | -0.10986 | 63.1485 | -60.3104 | 62.9517 | -59.8846 | -60.2554 | -0.009155 | 0.036621 | 63.1531 | -60.1273 | 63.2034 | -59.967 | -60.0815 | -59.6466 | -0.29297 | 0.073243 | -0.1236 | 0.13275 | 60.0082 | -0.23804 | 60.3012 | 0.054932 | -0.10986 | 0.07782 | 0.12817 | 0.050354 | 0.37079 | -0.064087 | 0.48065 | 0.045776 | 0.42572 | 123.262 | 0.16022 | 123.3307 | 123.4589 | 123.2803 | 123.1659 | 123.1705 | -123.3856 | -123.2025 | 122.9691 | 123.2208 | 59.9075 | 60.054
726.4844 | 123.317 | -60.0403 | 63.0524 | -0.065308 | -0.00029273 | 0.063779 | 0.062835 | -0.0012967 | -0.0031338 | -0.00095273 | -0.01712 | 0.0013907 | 0.064926 | 0.069045 | -0.0025976 | -0.00080758 | 0.0011643 | -0.16479 | 63.121 | -60.3287 | 62.8967 | -59.9625 | -60.3195 | -0.10986 | -0.09613 | 63.1165 | -60.141 | 63.1714 | -60.0403 | -60.1318 | -59.6786 | -0.28839 | 0.068665 | -0.15564 | 0.07782 | 59.9304 | -0.27924 | 60.2188 | 0.009155 | -0.10071 | 0.064087 | 0.11902 | 0 | 0.36163 | -0.091553 | 0.46234 | 0.009155 | 0.36621 | 123.2254 | 0.10071 | 123.3124 | 123.4497 | 123.2574 | 123.1613 | 123.1567 | -123.381 | -123.1934 | 122.937 | 123.2117 | 59.8755 | 59.9442
727.4844 | 123.4085 | -60.0266 | 63.0707 | -0.072937 | -0.0013607 | 0.062711 | 0.06668 | -0.0027921 | -0.00035682 | -0.0035163 | -0.0049134 | 0.00010888 | 0.06514 | 0.061782 | -0.0015296 | -0.0014484 | -0.00097194 | -0.073242 | 63.1393 | -60.3058 | 62.9654 | -59.8801 | -60.228 | 0.004578 | 0.10529 | 63.1531 | -60.1227 | 63.2355 | -59.9487 | -60.0311 | -59.6008 | -0.27924 | 0.068664 | -0.10529 | 0.14648 | 60.0311 | -0.20142 | 60.3104 | 0.07782 | -0.096131 | 0.082397 | 0.1648 | 0.07782 | 0.42572 | -0.004578 | 0.52185 | 0.091553 | 0.42572 | 123.2712 | 0.17395 | 123.3582 | 123.4451 | 123.2758 | 123.1659 | 123.1796 | -123.3765 | -123.1934 | 122.9919 | 123.262 | 59.9533 | 60.1318
728.5469 | 123.2758 | -60.0861 | 63.0615 | -0.042419 | 0.0014163 | 0.063993 | 0.065399 | 0.0014803 | -0.0020658 | -0.0013799 | -0.11783 | 0.0018179 | 0.066635 | 0.066268 | -0.001316 | -0.00038018 | 0.00095066 | -0.19226 | 63.1805 | -60.3653 | 62.8052 | -60.0998 | -60.4156 | -0.21515 | -0.20142 | 63.1851 | -60.1639 | 63.0753 | -60.1501 | -60.2509 | -59.7656 | -0.27923 | 0.11902 | -0.25635 | -0.013732 | 59.8709 | -0.32959 | 60.1501 | -0.050354 | -0.077819 | 0.1236 | 0.013733 | -0.064086 | 0.32044 | -0.16479 | 0.39825 | -0.086975 | 0.2655 | 123.1705 | 0.013733 | 123.2391 | 123.5458 | 123.349 | 123.2666 | 123.2712 | -123.4268 | -123.2254 | 122.8912 | 123.1613 | 59.8938 | 59.8846
729.4844 | 123.2803 | -60.0586 | 63.1393 | -0.050049 | 0.00034827 | 0.062925 | 0.063903 | 0.0016939 | 0.0015658 | -0.0013799 | -0.023224 | 0.00053628 | 0.066849 | 0.070113 | 0.000393 | 0.00047422 | 0.0020187 | -0.07782 | 63.2217 | -60.2921 | 62.9059 | -59.9442 | -60.2829 | -0.036621 | -0.036621 | 63.176 | -60.1501 | 63.1256 | -60.0815 | -60.173 | -59.7336 | -0.23346 | 0.082398 | -0.23346 | 0.11444 | 60.022 | -0.2243 | 60.2554 | 0.009155 | -0.091552 | 0.036621 | -0.013733 | -0.022888 | 0.32501 | -0.11444 | 0.41656 | -0.022889 | 0.3479 | 123.1979 | 0.068664 | 123.2758 | 123.5138 | 123.3261 | 123.2803 | 123.2346 | -123.4314 | -123.2895 | 122.9645 | 123.1842 | 59.9808 | 60.022
730.5469 | 123.2986 | -60.0723 | 63.1165 | -0.050049 | 0.00013467 | 0.063138 | 0.065399 | 0.0072481 | 0.0024204 | 0.0026789 | -0.05069 | 0.00074988 | 0.065781 | 0.070113 | -0.002384 | 0.00047422 | 0.0026597 | -0.19684 | 63.1439 | -60.379 | 62.709 | -59.7061 | -60.2921 | -0.22888 | -0.21973 | 63.1851 | -60.1639 | 63.1027 | -60.141 | -60.26 | -59.7794 | -0.3067 | 0.027466 | -0.40741 | 0.36621 | 59.8434 | -0.21973 | 60.1501 | 0.086975 | -0.091552 | 0.068665 | -0.013733 | -0.068664 | 0.29297 | -0.18768 | 0.38452 | -0.096131 | 0.67291 | 123.0881 | 0.022888 | 123.2666 | 123.5229 | 123.349 | 123.2162 | 123.2574 | -123.4955 | -123.2803 | 122.7814 | 123.175 | 59.8755 | 59.8526
731.4844 | 123.349 | -60.0586 | 63.0707 | -0.057678 | 0.0022709 | 0.06442 | 0.064758 | -0.0019377 | -0.00035682 | -0.00031193 | -0.0079652 | -0.00053192 | 0.068344 | 0.060927 | 0.0006066 | 0.00026062 | 0.0011643 | -0.17395 | 63.1165 | -60.3378 | 62.8876 | -59.9716 | -60.2875 | -0.10071 | -0.11902 | 63.1302 | -60.1456 | 63.1485 | -60.0174 | -60.1547 | -59.6878 | -0.27924 | 0.045776 | -0.18311 | 0.086975 | 59.9579 | -0.22888 | 60.2371 | 0.050354 | -0.086975 | 0.059509 | 0.07782 | 0.041199 | 0.37079 | -0.09613 | 0.45776 | -0.009155 | 0.36621 | 123.2254 | 0.12817 | 123.2941 | 123.4543 | 123.2758 | 123.175 | 123.1888 | -123.4085 | -123.2162 | 122.9462 | 123.2071 | 59.8846 | 59.9396
732.4844 | 123.3902 | -60.0449 | 63.0478 | -0.11871 | 0.0029117 | 0.066129 | 0.064331 | 0.0029757 | 0.00028418 | 0.00032907 | -0.044586 | -0.00074552 | 0.063858 | 0.06755 | -0.0028112 | -0.0012348 | -0.0020401 | -0.13275 | 63.1119 | -60.3287 | 62.9379 | -59.903 | -60.2829 | -0.11902 | -0.041199 | 63.1302 | -60.1501 | 63.208 | -59.9899 | -60.141 | -59.6466 | -0.28381 | 0.064086 | -0.10986 | 0.14191 | 59.9258 | -0.23804 | 60.2097 | 0.045776 | -0.10529 | 0.082397 | 0.16022 | 0.054932 | 0.39825 | -0.09613 | 0.50354 | 0.009155 | 0.42572 | 123.2666 | 0.16022 | 123.3582 | 123.4406 | 123.2803 | 123.1567 | 123.175 | -123.3765 | -123.1979 | 122.9828 | 123.2529 | 59.9121 | 60.0037
733.4844 | 123.3536 | -60.0494 | 63.0753 | -0.065308 | -7.913e-05 | 0.063138 | 0.064544 | -0.0042875 | -0.0014248 | -0.00052553 | -0.01712 | 0.0016043 | 0.066422 | 0.066482 | -0.003025 | -0.0012348 | -0.0011855 | -0.17395 | 63.1439 | -60.3104 | 62.8922 | -59.9396 | -60.3241 | -0.12817 | -0.11444 | 63.1531 | -60.1456 | 63.1577 | -60.0357 | -60.141 | -59.6832 | -0.26093 | 0.068665 | -0.18311 | 0.10986 | 59.9213 | -0.27466 | 60.1822 | -0.013733 | -0.096131 | 0.07782 | 0.082398 | 0.013732 | 0.36621 | -0.091553 | 0.46234 | 0.004578 | 0.37079 | 123.2025 | 0.10986 | 123.3032 | 123.4543 | 123.2986 | 123.1934 | 123.2025 | -123.3856 | -123.2208 | 122.9416 | 123.2071 | 59.8755 | 59.935
734.4844 | 123.4131 | -60.0449 | 63.0753 | -0.088196 | 0.0016299 | 0.065061 | 0.065612 | -0.0012967 | -0.0022794 | -0.0013799 | -0.059845 | 0.00032248 | 0.065354 | 0.068618 | -0.0017432 | -0.00080758 | -0.0046035 | -0.13733 | 63.0936 | -60.3241 | 62.9471 | -59.903 | -60.2737 | -0.13275 | -0.064087 | 63.1348 | -60.1273 | 63.1897 | -59.9762 | -60.0952 | -59.6741 | -0.27924 | 0.018311 | -0.12817 | 0.14191 | 59.9121 | -0.22888 | 60.1913 | 0.050354 | -0.082397 | 0.05951 | 0.11444 | 0.068665 | 0.37079 | -0.050354 | 0.45319 | 0.032043 | 0.42114 | 123.2712 | 0.15106 | 123.317 | 123.4177 | 123.262 | 123.1384 | 123.1796 | -123.3994 | -123.2025 | 122.9919 | 123.2346 | 59.9075 | 59.9808
735.4844 | 123.3444 | -60.0357 | 63.0753 | -0.095825 | 0.00056187 | 0.063779 | 0.064971 | -1.486e-05 | -0.0012112 | 0.0011835 | 0.022552 | -0.00031832 | 0.06514 | 0.059859 | -0.0017432 | -0.0012348 | 9.6064e-05 | -0.14648 | 63.1714 | -60.3149 | 62.9059 | -59.8663 | -60.1501 | -0.073242 | -0.09613 | 63.1256 | -60.1227 | 63.1485 | -60.0128 | -60.141 | -59.6695 | -0.27923 | 0.096131 | -0.16937 | 0.16937 | 59.9625 | -0.11444 | 60.2417 | 0.16479 | -0.086975 | 0.050354 | 0.073243 | 0.022889 | 0.36621 | -0.10529 | 0.45319 | -0.01831 | 0.44861 | 123.2208 | 0.10986 | 123.2712 | 123.4863 | 123.2483 | 123.2071 | 123.1613 | -123.3902 | -123.1979 | 122.9416 | 123.1842 | 59.8892 | 59.9396
736.4844 | 123.3948 | -60.0128 | 63.0432 | -0.080566 | 0.0012027 | 0.064207 | 0.065612 | -0.0010831 | 0.0013522 | 0.0013971 | -0.053741 | 0.00074988 | 0.067704 | 0.06755 | -0.0019568 | 0.00026062 | 0.0022323 | -0.13275 | 63.0981 | -60.2966 | 62.9471 | -59.9075 | -60.2921 | -0.11444 | -0.050354 | 63.1119 | -60.1547 | 63.1943 | -59.9854 | -60.1501 | -59.6832 | -0.28381 | 0.054932 | -0.09613 | 0.10528 | 59.8984 | -0.27924 | 60.1822 | 0.004578 | -0.14191 | 0.068664 | 0.15106 | 0.027465 | 0.32959 | -0.13733 | 0.4715 | 0.004578 | 0.3891 | 123.2437 | 0.16937 | 123.349 | 123.3948 | 123.2666 | 123.111 | 123.1247 | -123.3398 | -123.1979 | 122.9599 | 123.2071 | 59.8801 | 59.9625
737.5469 | 123.3948 | -60.0449 | 63.0615 | -0.11108 | 0.00013467 | 0.064634 | 0.064544 | 0.0019077 | -0.001852 | 0.00032907 | -0.026276 | 0.0013907 | 0.067063 | 0.064345 | -0.0032386 | -0.00016658 | -0.0013991 | -0.14191 | 63.1027 | -60.3012 | 63.0569 | -59.7656 | -60.3149 | -0.073242 | -0.059509 | 63.1302 | -60.141 | 63.1943 | -60.022 | -60.1318 | -59.6603 | -0.25635 | 0.041199 | -0.004577 | 0.27924 | 59.9716 | -0.27008 | 60.228 | -0.013733 | -0.09613 | 0.068665 | 0.13275 | 0.022888 | 0.38452 | -0.086975 | 0.48065 | 0.009155 | 0.53558 | 123.3582 | 0.11902 | 123.3353 | 123.4039 | 123.2712 | 123.1476 | 123.175 | -123.3627 | -123.2025 | 123.1018 | 123.2391 | 59.903 | 59.9854
738.4844 | 123.3627 | -60.0632 | 63.0569 | -0.088196 | 0.0012027 | 0.063993 | 0.065826 | -0.0017239 | -0.001852 | -0.0018073 | -0.029327 | 0.0018179 | 0.065354 | 0.067336 | -0.001316 | -0.0018756 | 0.0011643 | -0.14191 | 63.1439 | -60.3241 | 62.9196 | -59.8892 | -60.3012 | -0.1236 | -0.064087 | 63.121 | -60.1364 | 63.1622 | -60.0449 | -60.1273 | -59.6878 | -0.26093 | 0.086975 | -0.13733 | 0.17395 | 59.9396 | -0.23804 | 60.2005 | 0.022889 | -0.073243 | 0.064087 | 0.10528 | 0.01831 | 0.37537 | -0.064087 | 0.44861 | 0.009156 | 0.43488 | 123.2437 | 0.091553 | 123.2986 | 123.468 | 123.2574 | 123.2071 | 123.1842 | -123.381 | -123.1934 | 122.9828 | 123.2254 | 59.9213 | 59.9991
739.5625 | 123.381 | -60.0311 | 63.0798 | -0.042419 | 0.00034827 | 0.062284 | 0.065612 | -0.0025785 | 0.0022068 | -0.00095273 | -0.0079652 | 0.00096348 | 0.063217 | 0.063705 | -0.0017432 | -0.001662 | -0.0011855 | -0.17395 | 63.1439 | -60.3104 | 62.9059 | -59.9396 | -60.2875 | -0.082397 | -0.059509 | 63.1531 | -60.1364 | 63.1943 | -59.9899 | -60.0998 | -59.642 | -0.27924 | 0.064087 | -0.17395 | 0.091553 | 59.9487 | -0.25635 | 60.228 | 0.022888 | -0.10529 | 0.073242 | 0.11444 | 0.041199 | 0.3891 | -0.068664 | 0.49439 | 0.036622 | 0.37079 | 123.2162 | 0.14649 | 123.3307 | 123.4543 | 123.2895 | 123.175 | 123.1842 | -123.3902 | -123.2162 | 122.937 | 123.2254 | 59.8572 | 59.9716
740.4844 | 123.3444 | -60.0311 | 63.0753 | -0.019531 | -0.0011471 | 0.063566 | 0.064331 | 0.00041234 | 0.0019932 | 0.0031061 | 0.013397 | -0.00031832 | 0.06749 | 0.057296 | -0.0004614 | -0.0023028 | -0.00054474 | -0.15564 | 63.1622 | -60.3149 | 62.8555 | -59.7839 | -60.2051 | -0.11902 | -0.086975 | 63.1439 | -60.1501 | 63.176 | -60.022 | -60.1318 | -59.6878 | -0.28381 | 0.086975 | -0.21973 | 0.24719 | 59.9121 | -0.17395 | 60.1959 | 0.10986 | -0.11902 | 0.068665 | 0.10071 | 0.009155 | 0.34332 | -0.10071 | 0.46234 | 0.01831 | 0.53101 | 123.1705 | 0.12817 | 123.3261 | 123.4772 | 123.2941 | 123.1934 | 123.175 | -123.3902 | -123.2254 | 122.8867 | 123.2071 | 59.8755 | 59.9442
741.5469 | 123.3948 | -60.0586 | 63.0524 | -0.080566 | -0.00029273 | 0.063352 | 0.063903 | 0.0014803 | -0.00057042 | 0.00054267 | -0.062897 | 0.00096348 | 0.063004 | 0.067123 | -0.0045202 | -0.0025164 | -0.00011754 | -0.13275 | 63.1485 | -60.3287 | 62.9196 | -59.9121 | -60.2875 | -0.14191 | -0.09613 | 63.1485 | -60.1364 | 63.2034 | -60.0128 | -60.1227 | -59.6375 | -0.27008 | 0.096131 | -0.13275 | 0.14648 | 59.9167 | -0.22888 | 60.1868 | 0.041198 | -0.07782 | 0.096131 | 0.15106 | 0.045777 | 0.42114 | -0.064087 | 0.49896 | 0.013733 | 0.41656 | 123.2483 | 0.1236 | 123.3398 | 123.4772 | 123.2849 | 123.2071 | 123.2071 | -123.381 | -123.1888 | 122.9782 | 123.262 | 59.9258 | 59.9625
742.4844 | 123.3673 | -60.0403 | 63.0753 | -0.088196 | 0.0033389 | 0.063352 | 0.063262 | -0.00044226 | -0.00014322 | -0.00031193 | -0.023224 | -0.00053192 | 0.06749 | 0.0699 | -0.001316 | -0.00038018 | 0.0022323 | -0.19684 | 63.121 | -60.3104 | 62.9059 | -59.9396 | -60.3241 | -0.1236 | -0.11444 | 63.1668 | -60.1364 | 63.1668 | -60.0403 | -60.1318 | -59.6924 | -0.27008 | 0.045777 | -0.16937 | 0.10071 | 59.9167 | -0.28381 | 60.1868 | -0.013733 | -0.096131 | 0.091553 | 0.091553 | 0 | 0.3479 | -0.091553 | 0.44403 | 0.004578 | 0.37079 | 123.2162 | 0.096131 | 123.3032 | 123.4314 | 123.3032 | 123.1613 | 123.2071 | -123.3856 | -123.2117 | 122.9462 | 123.2071 | 59.8434 | 59.9258
743.5469 | 123.3856 | -60.0311 | 63.0615 | -0.065308 | -0.00029273 | 0.06207 | 0.063262 | 0.0014803 | -0.0022794 | -0.00073913 | 0.010345 | 0.00074988 | 0.066422 | 0.066909 | -0.0015296 | -0.00059378 | 0.00052346 | -0.18768 | 63.1577 | -60.3241 | 62.9105 | -59.935 | -60.3195 | -0.14648 | -0.10986 | 63.1577 | -60.1639 | 63.1439 | -60.0357 | -60.1364 | -59.697 | -0.29297 | 0.096131 | -0.15106 | 0.09613 | 59.8846 | -0.28839 | 60.1776 | 0.004578 | -0.13275 | 0.096131 | 0.082398 | -0.004578 | 0.33417 | -0.10529 | 0.46692 | 0.027465 | 0.3891 | 123.2346 | 0.12817 | 123.3078 | 123.4818 | 123.3215 | 123.1888 | 123.1888 | -123.3856 | -123.2254 | 122.9416 | 123.175 | 59.8434 | 59.9213
744.4844 | 123.3582 | -60.0357 | 63.0615 | -0.12634 | -0.0015743 | 0.062925 | 0.064971 | -0.0010831 | 0.0013522 | -0.0013799 | -0.023224 | 0.00032248 | 0.065995 | 0.065627 | -0.0028112 | -0.0023028 | -0.0011855 | -0.19226 | 63.1439 | -60.3424 | 62.9196 | -59.9808 | -60.3012 | -0.14191 | -0.11444 | 63.1485 | -60.1273 | 63.1622 | -60.0449 | -60.1318 | -59.6741 | -0.3067 | 0.082398 | -0.14191 | 0.054932 | 59.8938 | -0.2655 | 60.2005 | 0.041199 | -0.091552 | 0.086976 | 0.10071 | -0.009155 | 0.36163 | -0.09613 | 0.45319 | -0.004578 | 0.36163 | 123.262 | 0.082397 | 123.2895 | 123.4863 | 123.2758 | 123.1796 | 123.1842 | -123.4039 | -123.1888 | 122.9553 | 123.1979 | 59.8434 | 59.9213
745.5469 | 123.349 | -59.9945 | 63.1027 | -0.065308 | -0.00029273 | 0.061002 | 0.065399 | -0.0010831 | 0.0017794 | -0.0030889 | -0.044586 | 0.00074988 | 0.064286 | 0.064345 | -0.0025976 | -0.00038018 | -0.00097194 | -0.073242 | 63.1668 | -60.26 | 63.1577 | -59.9899 | -60.4843 | 0 | 0.086975 | 63.1577 | -60.1089 | 63.2126 | -59.9487 | -60.0403 | -59.6237 | -0.2655 | 0.064087 | 0.054932 | 0.004578 | 59.9945 | -0.48981 | 60.26 | -0.2243 | -0.11444 | 0.054932 | 0.10986 | 0.045777 | 0.37079 | -0.045776 | 0.48523 | 0.068665 | 0.27008 | 123.4177 | 0.16022 | 123.3215 | 123.4268 | 123.2666 | 123.1613 | 123.1522 | -123.3627 | -123.2117 | 123.1522 | 123.2071 | 59.9213 | 60.0815
746.4844 | 123.3994 | -60.0266 | 63.1027 | -0.050049 | 0.0016299 | 0.061857 | 0.063476 | 0.0010531 | 0.0017794 | -0.0024481 | 0.0011902 | -0.0011727 | 0.065354 | 0.064559 | -0.0011022 | 0.00047422 | -0.00075834 | -0.14648 | 63.1439 | -60.2875 | 62.9379 | -59.903 | -60.2463 | -0.045776 | 0 | 63.1622 | -60.1273 | 63.2126 | -59.9625 | -60.0677 | -59.642 | -0.26093 | 0.041199 | -0.16479 | 0.1236 | 59.9808 | -0.21973 | 60.2417 | 0.041199 | -0.10071 | 0.059509 | 0.10986 | 0.064087 | 0.38452 | -0.041199 | 0.48523 | 0.059509 | 0.38452 | 123.2254 | 0.16479 | 123.3398 | 123.4314 | 123.2895 | 123.1705 | 123.1888 | -123.3902 | -123.23 | 122.9645 | 123.2391 | 59.8801 | 60.0266
747.5469 | 123.3536 | -60.0494 | 63.089 | -0.03479 | 0.0018435 | 0.06442 | 0.064544 | 0.00041234 | 0.00028418 | -0.0011663 | -0.023224 | -0.0016001 | 0.065781 | 0.0652 | -0.0025976 | 0.001115 | -0.0018265 | -0.19226 | 63.1439 | -60.3012 | 62.9013 | -59.9442 | -60.2921 | -0.14191 | -0.11902 | 63.1439 | -60.1318 | 63.1485 | -60.0449 | -60.1364 | -59.6741 | -0.25177 | 0.054932 | -0.18768 | 0.10529 | 59.9075 | -0.24262 | 60.1593 | 0.009155 | -0.082398 | 0.054932 | 0.05951 | 0.004577 | 0.37537 | -0.086976 | 0.45776 | -0.004578 | 0.35706 | 123.2025 | 0.086975 | 123.2803 | 123.4451 | 123.2758 | 123.1934 | 123.1934 | -123.3902 | -123.2208 | 122.9507 | 123.1979 | 59.8572 | 59.9304
748.4844 | 123.3673 | -60.0494 | 63.0981 | -0.11108 | -7.913e-05 | 0.06143 | 0.063903 | 0.0029757 | 0.00092498 | -0.00073913 | -0.026276 | 0.0020315 | 0.064286 | 0.066268 | -0.0021704 | -0.0012348 | 0.00073706 | -0.18768 | 63.1256 | -60.3287 | 62.8967 | -59.9487 | -60.3058 | -0.14191 | -0.11902 | 63.1348 | -60.1364 | 63.1531 | -60.0174 | -60.1501 | -59.6924 | -0.27924 | 0.027465 | -0.20142 | 0.10071 | 59.9075 | -0.25635 | 60.1868 | 0.022888 | -0.086976 | 0.036621 | 0.054931 | 0.032043 | 0.35706 | -0.10071 | 0.44403 | -0.013732 | 0.37994 | 123.2254 | 0.11902 | 123.2895 | 123.4543 | 123.2712 | 123.175 | 123.1842 | -123.4268 | -123.2346 | 122.9462 | 123.2025 | 59.8618 | 59.9304
749.4844 | 123.4268 | -59.9899 | 63.0798 | -0.057678 | -0.00029273 | 0.062284 | 0.06369 | -1.486e-05 | -0.0020658 | -0.00095273 | 0.0072936 | 0.0024589 | 0.066635 | 0.065627 | -0.0038794 | -0.0025164 | -0.00075834 | -0.09613 | 63.1714 | -60.2966 | 62.9745 | -59.8572 | -60.2234 | -0.041199 | 0.10986 | 63.1668 | -60.1181 | 63.2492 | -59.9304 | -60.0357 | -59.61 | -0.3067 | 0.091553 | -0.10529 | 0.13275 | 59.9487 | -0.23346 | 60.2554 | 0.073242 | -0.12817 | 0.086975 | 0.16937 | 0.059509 | 0.37994 | -0.045777 | 0.50812 | 0.082397 | 0.43945 | 123.2712 | 0.18768 | 123.3673 | 123.468 | 123.2849 | 123.1613 | 123.1567 | -123.3765 | -123.1979 | 122.9645 | 123.2391 | 59.8938 | 60.0998
750.4844 | 123.3627 | -60.0494 | 63.0707 | -0.080566 | 0.0029117 | 0.062925 | 0.064971 | 0.0025485 | 0.00071138 | 0.00032907 | -0.053741 | 0.00074988 | 0.065567 | 0.067763 | -0.0004614 | -0.0018756 | -0.0031081 | -0.16937 | 63.1119 | -60.3149 | 62.915 | -59.935 | -60.3058 | -0.16937 | -0.11902 | 63.121 | -60.1593 | 63.1622 | -60.0586 | -60.1547 | -59.6786 | -0.2655 | 0.041198 | -0.15564 | 0.11444 | 59.8801 | -0.25635 | 60.1456 | 0.009155 | -0.10986 | 0.050354 | 0.091552 | -0.009156 | 0.37079 | -0.10529 | 0.48065 | 0.004578 | 0.37994 | 123.23 | 0.10071 | 123.3215 | 123.4268 | 123.2803 | 123.1613 | 123.1705 | -123.3856 | -123.23 | 122.9645 | 123.2117 | 59.8801 | 59.9304
751.5469 | 123.3673 | -60.054 | 63.0661 | -0.057678 | 0.00098907 | 0.062925 | 0.066467 | 0.00019874 | 7.0582e-05 | -0.0011663 | -0.093414 | -0.00095912 | 0.067276 | 0.066909 | -0.0011022 | 4.7018e-05 | 0.0020187 | -0.21515 | 63.1302 | -60.3607 | 62.883 | -59.9762 | -60.3333 | -0.21515 | -0.1236 | 63.1485 | -60.1456 | 63.2034 | -60.0586 | -60.173 | -59.6741 | -0.3067 | 0.064087 | -0.18311 | 0.07782 | 59.8389 | -0.27924 | 60.1456 | 0.027466 | -0.091553 | 0.082398 | 0.13733 | -0.004578 | 0.37994 | -0.11902 | 0.4715 | -0.027466 | 0.38452 | 123.2437 | 0.086975 | 123.349 | 123.4909 | 123.2941 | 123.1842 | 123.2025 | -123.4268 | -123.2117 | 122.937 | 123.2574 | 59.8389 | 59.9304
752.4844 | 123.3673 | -60.0266 | 63.0798 | 0.041504 | 0.0033389 | 0.060575 | 0.063476 | 0.00019874 | -0.0027066 | -0.0018073 | -0.0079652 | -0.00053192 | 0.066635 | 0.060287 | -0.0021704 | 0.00068782 | -0.0031081 | -0.13275 | 63.1805 | -60.3149 | 62.9059 | -59.9396 | -60.2921 | -0.11902 | -0.082397 | 63.1577 | -60.141 | 63.1851 | -59.9945 | -60.0861 | -59.6649 | -0.28839 | 0.10071 | -0.17395 | 0.086975 | 59.9075 | -0.2655 | 60.1959 | 0.022888 | -0.11444 | 0.07782 | 0.10529 | 0.032043 | 0.36163 | -0.05951 | 0.47607 | 0.054931 | 0.37537 | 123.2208 | 0.14648 | 123.3261 | 123.4955 | 123.2986 | 123.2071 | 123.1842 | -123.3948 | -123.2208 | 122.9324 | 123.2117 | 59.8938 | 59.9442
753.4844 | 123.4039 | -60.0082 | 63.121 | -0.057678 | -0.00093353 | 0.063352 | 0.064971 | -0.0015103 | -0.00078402 | -0.0050115 | -0.023224 | -0.00031832 | 0.066208 | 0.06285 | -0.0011022 | -0.00038018 | -0.00075834 | -0.091553 | 63.1668 | -60.2966 | 63.0112 | -59.7977 | -60.1639 | -0.013733 | 0.10071 | 63.1531 | -60.0998 | 63.2401 | -59.9579 | -60.0494 | -59.61 | -0.28839 | 0.045776 | -0.10986 | 0.21057 | 59.9945 | -0.15564 | 60.2829 | 0.13275 | -0.091552 | 0.032043 | 0.11902 | 0.050354 | 0.39825 | -0.041198 | 0.48981 | 0.050354 | 0.49896 | 123.3078 | 0.14191 | 123.3398 | 123.4634 | 123.2529 | 123.175 | 123.1613 | -123.4177 | -123.2208 | 123.0194 | 123.2483 | 59.9167 | 60.1089
754.5469 | 123.3765 | -60.054 | 63.0478 | -0.16449 | 0.0012027 | 0.063566 | 0.065399 | 0.00083954 | 0.00092498 | 0.00032907 | -0.059845 | 0.00010888 | 0.06514 | 0.068831 | -0.0015296 | 4.7018e-05 | -0.0037491 | -0.13733 | 63.0936 | -60.3241 | 62.9379 | -59.9304 | -60.2921 | -0.19226 | -0.07782 | 63.1256 | -60.1501 | 63.1897 | -60.0037 | -60.1135 | -59.642 | -0.27008 | 0.045776 | -0.10986 | 0.1236 | 59.8618 | -0.23804 | 60.1318 | 0.032044 | -0.09613 | 0.077819 | 0.14191 | 0.050354 | 0.41199 | -0.059509 | 0.50812 | 0.036621 | 0.39368 | 123.262 | 0.14648 | 123.3398 | 123.4177 | 123.2758 | 123.1476 | 123.1796 | -123.3719 | -123.1979 | 122.9919 | 123.2437 | 59.9167 | 59.9762
755.4844 | 123.4085 | -60.0586 | 63.0753 | 0.0033567 | 0.0026981 | 0.061857 | 0.066467 | -1.486e-05 | 0.0011386 | -0.00095273 | 0.004242 | 0.00096348 | 0.065354 | 0.062209 | -0.000675 | -0.001662 | 0.00030966 | -0.14191 | 63.1485 | -60.2829 | 62.9654 | -59.8801 | -60.228 | -0.073242 | 0 | 63.1439 | -60.0952 | 63.208 | -59.967 | -60.0632 | -59.6329 | -0.2243 | 0.073243 | -0.10986 | 0.17853 | 59.9854 | -0.16937 | 60.2097 | 0.054932 | -0.036621 | 0.068665 | 0.13275 | 0.091553 | 0.42572 | -0.004577 | 0.46234 | 0.032044 | 0.40283 | 123.2483 | 0.12817 | 123.3032 | 123.4314 | 123.2391 | 123.2071 | 123.2025 | -123.3582 | -123.1705 | 123.024 | 123.2666 | 59.9167 | 60.0586
756.4844 | 123.3902 | -60.022 | 63.0798 | -0.042419 | 0.00098907 | 0.06442 | 0.063476 | 0.0016939 | -0.0048428 | -0.0015935 | 0.0011902 | 0.0033133 | 0.067704 | 0.066909 | -0.001316 | -0.0012348 | 0.0026597 | -0.16937 | 63.1622 | -60.3149 | 62.9059 | -59.9945 | -60.2966 | -0.14191 | -0.082397 | 63.1485 | -60.1364 | 63.1805 | -60.0037 | -60.1089 | -59.6786 | -0.29297 | 0.082397 | -0.17395 | 0.027466 | 59.8801 | -0.27466 | 60.173 | 0.01831 | -0.11444 | 0.068665 | 0.10071 | 0.018311 | 0.34332 | -0.086975 | 0.45776 | 0.027466 | 0.32043 | 123.2208 | 0.13275 | 123.317 | 123.4772 | 123.2849 | 123.1842 | 123.1705 | -123.3948 | -123.2162 | 122.9279 | 123.2025 | 59.8526 | 59.9396
757.4844 | 123.3765 | -60.0403 | 63.0707 | -0.011902 | 0.00034827 | 0.06207 | 0.067108 | -0.0051419 | -0.0022794 | -0.0018073 | 0.022552 | 0.00010888 | 0.066208 | 0.063491 | -0.0015296 | -0.001662 | 0.00052346 | -0.14648 | 63.1393 | -60.3149 | 62.9654 | -59.8938 | -60.2417 | -0.054932 | 0 | 63.1668 | -60.1181 | 63.2263 | -59.967 | -60.0632 | -59.642 | -0.27466 | 0.068664 | -0.10529 | 0.14648 | 59.9854 | -0.20142 | 60.26 | 0.073242 | -0.07782 | 0.09613 | 0.15564 | 0.073242 | 0.39825 | -0.022888 | 0.47607 | 0.054932 | 0.42114 | 123.2803 | 0.15106 | 123.3444 | 123.4543 | 123.2849 | 123.1796 | 123.2071 | -123.3856 | -123.1888 | 123.0057 | 123.2666 | 59.8938 | 60.0403
758.5469 | 123.3536 | -60.022 | 63.0798 | -0.042419 | 0.00056187 | 0.063352 | 0.064758 | -0.0023649 | 0.00049778 | -0.0011663 | -0.072052 | 0.0022453 | 0.068344 | 0.067763 | -0.0004614 | -0.00016658 | -0.0020401 | -0.23804 | 63.1485 | -60.3561 | 62.851 | -60.0128 | -60.3745 | -0.25177 | -0.17395 | 63.1302 | -60.1822 | 63.1531 | -60.054 | -60.1776 | -59.7061 | -0.33417 | 0.068665 | -0.22888 | 0.009156 | 59.7702 | -0.35248 | 60.1044 | -0.018311 | -0.16022 | 0.050354 | 0.073242 | -0.032043 | 0.31586 | -0.15564 | 0.47607 | 0.004578 | 0.34332 | 123.2071 | 0.12817 | 123.3353 | 123.5046 | 123.3124 | 123.1705 | 123.1522 | -123.436 | -123.262 | 122.8729 | 123.175 | 59.7839 | 59.848
759.4844 | 123.4039 | -60.0494 | 63.0798 | -0.019531 | -0.0011471 | 0.063352 | 0.06369 | 0.00062594 | -0.00057042 | 0.0013971 | 0.004242 | 0.00032248 | 0.066208 | 0.066268 | -0.0008886 | -0.0018756 | -0.00033114 | -0.10071 | 63.1805 | -60.2646 | 63.0203 | -59.8068 | -60.1639 | -0.004578 | 0.091553 | 63.1668 | -60.0861 | 63.2263 | -59.967 | -60.0174 | -59.6237 | -0.21515 | 0.10071 | -0.059509 | 0.24261 | 60.0449 | -0.11444 | 60.26 | 0.10071 | -0.036622 | 0.086975 | 0.14648 | 0.082397 | 0.42572 | 0.032043 | 0.46234 | 0.068665 | 0.45776 | 123.2849 | 0.11902 | 123.3124 | 123.4451 | 123.2529 | 123.23 | 123.2162 | -123.3444 | -123.1659 | 123.0698 | 123.2758 | 59.9487 | 60.141
760.5469 | 123.2758 | -60.054 | 63.1714 | -0.0042723 | -0.0020017 | 0.063352 | 0.06604 | 0.0027621 | -0.00099762 | -0.0022345 | -0.044586 | -0.00031832 | 0.069412 | 0.066909 | -0.002384 | -0.00016658 | -0.0018265 | -0.16937 | 63.2309 | -60.3104 | 62.8738 | -59.9762 | -60.3012 | -0.11444 | -0.032043 | 63.1989 | -60.1364 | 63.121 | -60.0815 | -60.1776 | -59.7336 | -0.25635 | 0.059509 | -0.29755 | 0.07782 | 59.9396 | -0.24719 | 60.1959 | 0.009156 | -0.082398 | 0.027466 | -0.050354 | -0.027466 | 0.32043 | -0.1236 | 0.40283 | -0.041198 | 0.33417 | 123.1842 | 0.054932 | 123.2574 | 123.5413 | 123.3353 | 123.2849 | 123.2529 | -123.4818 | -123.3078 | 122.9279 | 123.175 | 59.8846 | 60.022
761.4844 | 123.436 | -60.0082 | 63.0981 | -0.057678 | 0.00034827 | 0.062925 | 0.065826 | 0.0019077 | -0.00078402 | -0.0037299 | 0.010345 | 0.00074988 | 0.06514 | 0.06755 | -0.0025976 | -0.00059378 | -0.00075834 | -0.11444 | 63.1805 | -60.2921 | 63.002 | -59.8251 | -60.1685 | -0.027466 | 0.082397 | 63.1531 | -60.1227 | 63.2172 | -59.9396 | -60.022 | -59.6375 | -0.28381 | 0.082397 | -0.096131 | 0.18311 | 59.9808 | -0.16022 | 60.2646 | 0.1236 | -0.11444 | 0.054931 | 0.11902 | 0.068665 | 0.37079 | -0.013733 | 0.48523 | 0.10071 | 0.46692 | 123.2941 | 0.18311 | 123.3398 | 123.4726 | 123.2758 | 123.1888 | 123.1613 | -123.3902 | -123.2208 | 123.0103 | 123.2254 | 59.8938 | 60.0906
762.4844 | 123.4131 | -60.0311 | 63.1027 | -0.03479 | 0.0014163 | 0.063779 | 0.064544 | 0.00062594 | -0.0027066 | -0.00073913 | -0.011017 | -0.0020273 | 0.067704 | 0.062209 | 0.0006066 | -0.0014484 | 0.0018051 | -0.16937 | 63.1622 | -60.2921 | 62.9425 | -59.8938 | -60.2463 | -0.073242 | -0.018311 | 63.1577 | -60.1135 | 63.1989 | -59.967 | -60.0723 | -59.6466 | -0.26093 | 0.059509 | -0.16022 | 0.13733 | 59.9579 | -0.21515 | 60.2188 | 0.045776 | -0.082397 | 0.054932 | 0.096131 | 0.064087 | 0.38452 | -0.041199 | 0.46692 | 0.041198 | 0.39825 | 123.2346 | 0.14648 | 123.3124 | 123.4543 | 123.2712 | 123.1934 | 123.1888 | -123.3948 | -123.2162 | 122.9736 | 123.23 | 59.8618 | 60.0128
763.5625 | 123.2574 | -60.054 | 63.1622 | -0.019531 | 0.0012027 | 0.061643 | 0.067748 | 0.0021213 | -0.00078402 | -0.0028753 | -0.069 | -0.00010472 | 0.066849 | 0.066909 | -3.4196e-05 | -0.0035846 | 0.00073706 | -0.15564 | 63.2126 | -60.2966 | 62.883 | -59.9762 | -60.3058 | -0.14191 | -0.045776 | 63.2034 | -60.141 | 63.2401 | -60.2783 | -60.3149 | -59.7107 | -0.24262 | 0.050354 | -0.27923 | 0.07782 | 59.9121 | -0.25177 | 60.1547 | -0.009155 | -0.086975 | 0.041199 | 0.07782 | -0.2243 | 0.34332 | -0.26093 | 0.4303 | -0.17395 | 0.32043 | 123.1796 | -0.13733 | 123.381 | 123.5092 | 123.3444 | 123.2666 | 123.2574 | -123.4589 | -123.3032 | 122.937 | 123.2941 | 59.8984 | 60.0082
764.4844 | 123.3582 | -60.0357 | 63.0798 | -0.072937 | 0.00056187 | 0.062925 | 0.065185 | 0.0019077 | 7.0582e-05 | -0.0033025 | 0.025604 | -0.00095912 | 0.06279 | 0.063491 | -0.0008886 | -0.00016658 | -0.0018265 | -0.19684 | 63.1668 | -60.3241 | 62.8967 | -59.9442 | -60.2829 | -0.16479 | -0.022888 | 63.1668 | -60.1273 | 63.176 | -60.0266 | -60.1135 | -59.6695 | -0.28839 | 0.086975 | -0.1831 | 0.091553 | 59.8709 | -0.24719 | 60.1593 | 0.041199 | -0.091552 | 0.086975 | 0.09613 | 0.009156 | 0.36621 | -0.077819 | 0.45776 | 0.013733 | 0.37994 | 123.2208 | 0.10071 | 123.3032 | 123.4909 | 123.2941 | 123.2025 | 123.2025 | -123.4039 | -123.2071 | 122.9324 | 123.2117 | 59.8389 | 60.0128
765.4844 | 123.4314 | -60.0128 | 63.1027 | -0.050049 | -0.00050633 | 0.062498 | 0.064331 | -0.00086946 | 0.00071138 | -0.0062933 | -0.0018616 | -0.0011727 | 0.068772 | 0.063064 | -0.0021704 | -0.0018756 | 0.00030966 | -0.13275 | 63.1805 | -60.3149 | 62.9929 | -59.8297 | -60.1868 | -0.027466 | 0.09613 | 63.1577 | -60.0952 | 63.2446 | -59.9304 | -60.0266 | -59.5917 | -0.30212 | 0.07782 | -0.10986 | 0.1831 | 59.9854 | -0.17395 | 60.2875 | 0.12817 | -0.082398 | 0.054932 | 0.14191 | 0.082397 | 0.42114 | -0.013733 | 0.50354 | 0.068665 | 0.48523 | 123.3078 | 0.1648 | 123.3398 | 123.4955 | 123.2529 | 123.1934 | 123.1705 | -123.4177 | -123.1979 | 123.0057 | 123.2574 | 59.8801 | 60.1089
766.5469 | 123.3398 | -60.0266 | 63.0844 | -0.10345 | -7.913e-05 | 0.062284 | 0.06369 | 0.00083954 | -0.0016384 | -0.0011663 | -0.011017 | -0.0022409 | 0.068985 | 0.064559 | -0.0017432 | -0.0020892 | -0.0016129 | -0.2243 | 63.1439 | -60.3333 | 62.9013 | -59.9533 | -60.2966 | -0.19684 | -0.14191 | 63.1714 | -60.1364 | 63.1577 | -60.0266 | -60.1456 | -59.6786 | -0.3067 | 0.059509 | -0.18311 | 0.073242 | 59.8297 | -0.27008 | 60.1364 | 0.036621 | -0.10986 | 0.086975 | 0.073242 | 0 | 0.3479 | -0.11902 | 0.45776 | -0.009155 | 0.37994 | 123.2346 | 0.10986 | 123.2941 | 123.4772 | 123.3078 | 123.1705 | 123.1979 | -123.4177 | -123.2208 | 122.9279 | 123.1842 | 59.8022 | 59.8846
767.4844 | 123.3444 | -60.0082 | 63.1165 | -0.072937 | 0.00098907 | 0.06442 | 0.06369 | -0.00086946 | 0.00049778 | 0.00096987 | -0.044586 | 0.0013907 | 0.065354 | 0.064132 | -0.001316 | -0.0010212 | 0.0013779 | -0.10986 | 63.1577 | -60.2966 | 62.97 | -59.8801 | -60.2005 | -0.059509 | 0.032043 | 63.1668 | -60.1044 | 63.176 | -60.0037 | -60.0952 | -59.6603 | -0.28839 | 0.041199 | -0.14648 | 0.12817 | 59.9487 | -0.19226 | 60.2371 | 0.096131 | -0.09613 | 0.050354 | 0.059509 | 0.004578 | 0.3479 | -0.086975 | 0.44403 | 0.009155 | 0.41656 | 123.2666 | 0.10071 | 123.2803 | 123.4543 | 123.2712 | 123.1659 | 123.175 | -123.4131 | -123.2208 | 122.9782 | 123.1842 | 59.8984 | 60.0403
768.5469 | 123.4268 | -60.0449 | 63.0524 | -0.11871 | 0.0022709 | 0.065061 | 0.063903 | 0.0019077 | -0.0016384 | 0.0043879 | -0.038483 | 0.00010888 | 0.065995 | 0.068191 | -0.0008886 | 0.00026062 | 0.00095066 | -0.19226 | 63.1256 | -60.3424 | 62.9471 | -59.9075 | -60.2875 | -0.20142 | -0.10986 | 63.1027 | -60.1273 | 63.2812 | -60.3149 | -60.0586 | -59.523 | -0.29755 | 0.073242 | -0.10529 | 0.13733 | 59.8434 | -0.24262 | 60.141 | 0.054931 | -0.082397 | 0.050354 | 0.22888 | -0.27008 | 0.52185 | -0.013733 | 0.60425 | 0.068664 | 0.43487 | 123.2895 | -0.18768 | 123.4085 | 123.468 | 123.23 | 123.1705 | 123.1476 | -123.3948 | -123.1796 | 122.9919 | 123.3261 | 59.8526 | 59.935
769.4844 | 123.3582 | -60.0174 | 63.1119 | -0.057678 | -0.00029273 | 0.062711 | 0.06604 | -0.0017239 | 0.00028418 | -0.0026617 | -0.0079652 | -0.0022409 | 0.066422 | 0.065841 | -0.0038794 | -0.0023028 | -0.00054474 | -0.091553 | 63.1805 | -60.2829 | 62.9745 | -59.8663 | -60.2097 | -0.064087 | 0.068665 | 63.1943 | -60.1227 | 63.1897 | -59.9899 | -60.0906 | -59.6466 | -0.2655 | 0.068665 | -0.13733 | 0.15106 | 59.9533 | -0.19226 | 60.2188 | 0.073242 | -0.10529 | 0.082398 | 0.07782 | 0.027466 | 0.37079 | -0.073242 | 0.47608 | 0.032044 | 0.41657 | 123.2574 | 0.13275 | 123.3124 | 123.4634 | 123.317 | 123.1979 | 123.2117 | -123.3948 | -123.2346 | 122.9919 | 123.2071 | 59.9258 | 60.0861
770.4844 | 123.436 | -60.0174 | 63.0753 | -0.080566 | 0.00056187 | 0.061857 | 0.065826 | -0.00065586 | -0.00014322 | -0.0035163 | 0.0072936 | -0.00095912 | 0.06514 | 0.0652 | -0.0021704 | -0.0014484 | -0.0022537 | -0.16479 | 63.1577 | -60.2966 | 62.9562 | -59.8755 | -60.2188 | -0.091553 | 0.018311 | 63.1485 | -60.1089 | 63.2126 | -59.9258 | -60.0494 | -59.6237 | -0.27924 | 0.082398 | -0.11902 | 0.14191 | 59.9258 | -0.20142 | 60.2051 | 0.07782 | -0.091553 | 0.073243 | 0.13733 | 0.091553 | 0.39368 | -0.032043 | 0.48523 | 0.05951 | 0.42114 | 123.2529 | 0.18311 | 123.3215 | 123.4543 | 123.2574 | 123.175 | 123.1659 | -123.3719 | -123.1842 | 122.9736 | 123.23 | 59.8526 | 60.0357
771.4844 | 123.3994 | -60.0037 | 63.1027 | -0.072937 | 0.0018435 | 0.062498 | 0.064971 | -0.00044226 | 7.0582e-05 | -0.00095273 | 0.004242 | 0.00053628 | 0.067276 | 0.062423 | -0.0043066 | -0.0010212 | 0.0037277 | -0.11444 | 63.1577 | -60.2737 | 63.002 | -59.7977 | -60.173 | -0.064087 | 0.068665 | 63.1622 | -60.0998 | 63.2126 | -59.9442 | -60.0449 | -59.6191 | -0.27008 | 0.054932 | -0.10071 | 0.20599 | 59.9396 | -0.16937 | 60.2097 | 0.10071 | -0.09613 | 0.059509 | 0.10986 | 0.059509 | 0.38452 | -0.041199 | 0.48065 | 0.054931 | 0.47608 | 123.2758 | 0.15564 | 123.3124 | 123.4314 | 123.262 | 123.1613 | 123.1659 | -123.3765 | -123.2025 | 123.0057 | 123.2162 | 59.8892 | 60.0723
772.5469 | 123.3902 | -60.0494 | 63.0936 | -0.088196 | -0.0011471 | 0.063352 | 0.063262 | -0.0012967 | -0.0027066 | -0.0022345 | 0.004242 | 0.00053628 | 0.066422 | 0.062636 | -0.0021704 | -0.0012348 | 0.0013779 | -0.20142 | 63.1439 | -60.3241 | 62.9288 | -59.935 | -60.2692 | -0.15564 | -0.07782 | 63.1348 | -60.1318 | 63.1943 | -59.9716 | -60.0861 | -59.6237 | -0.27466 | 0.050354 | -0.16479 | 0.11444 | 59.8938 | -0.21973 | 60.1685 | 0.054932 | -0.082398 | 0.041199 | 0.10071 | 0.077819 | 0.42572 | -0.036622 | 0.50812 | 0.045776 | 0.3891 | 123.2529 | 0.16022 | 123.3261 | 123.468 | 123.2666 | 123.1934 | 123.1842 | -123.4177 | -123.2254 | 122.9782 | 123.2437 | 59.848 | 59.9716
773.4844 | 123.2254 | -60.0403 | 63.176 | -0.042419 | -0.00093353 | 0.062284 | 0.065399 | 0.0029757 | 0.00071138 | 0.0022517 | -0.062897 | 0.00053628 | 0.064926 | 0.070754 | -0.0011022 | -0.0018756 | 0.0028733 | -0.17853 | 63.2538 | -60.3149 | 62.8876 | -59.9762 | -60.3104 | -0.14648 | -0.050354 | 63.2172 | -60.1318 | 63.1119 | -60.0677 | -60.1776 | -59.729 | -0.27466 | 0.07782 | -0.28839 | 0.064087 | 59.8938 | -0.27008 | 60.1685 | 0.004577 | -0.091553 | 0.041199 | -0.064087 | -0.027466 | 0.31128 | -0.13733 | 0.40283 | -0.045776 | 0.33874 | 123.2025 | 0.064087 | 123.2437 | 123.5687 | 123.349 | 123.2941 | 123.2574 | -123.4909 | -123.3078 | 122.9279 | 123.1522 | 59.8618 | 59.9899
774.5469 | 123.3353 | -60.0449 | 63.0798 | -0.095825 | 0.0012027 | 0.063352 | 0.065399 | 0.0014803 | 0.00092498 | -0.00073913 | -0.035431 | 0.00010888 | 0.065567 | 0.062423 | -0.001316 | -0.001662 | 0.00052346 | -0.21515 | 63.1439 | -60.3241 | 62.9196 | -59.9167 | -60.3104 | -0.21057 | -0.13733 | 63.1027 | -60.1685 | 63.1531 | -60.0403 | -60.1501 | -59.6741 | -0.27924 | 0.064087 | -0.16022 | 0.12817 | 59.8343 | -0.2655 | 60.1135 | 0.013733 | -0.1236 | 0.022888 | 0.073242 | 0.004578 | 0.37079 | -0.10529 | 0.49438 | 0.018311 | 0.40741 | 123.2437 | 0.12817 | 123.3215 | 123.468 | 123.2712 | 123.1888 | 123.1476 | -123.4039 | -123.2483 | 122.9645 | 123.1979 | 59.8297 | 59.9075
775.4844 | 123.3902 | -60.0174 | 63.0798 | -0.088196 | 0.00077547 | 0.062498 | 0.06369 | -0.0030057 | 0.0019932 | -0.0039435 | 0.056122 | 0.0018179 | 0.067704 | 0.0699 | -0.000675 | -0.0010212 | -0.0024673 | -0.14648 | 63.1851 | -60.2921 | 63.0386 | -59.523 | -60.2829 | -0.28381 | -0.045776 | 63.1714 | -60.0998 | 63.2217 | -59.967 | -60.0677 | -59.6146 | -0.27466 | 0.10529 | -0.041199 | 0.49439 | 59.7336 | -0.2655 | 60.0082 | 0.009155 | -0.082397 | 0.091553 | 0.14191 | 0.050354 | 0.40283 | -0.050354 | 0.48523 | 0.032043 | 0.76904 | 123.3307 | 0.13275 | 123.3215 | 123.4772 | 123.2712 | 123.2025 | 123.1888 | -123.3719 | -123.1796 | 123.056 | 123.2391 | 59.8709 | 59.9716
776.4844 | 123.4131 | -59.9808 | 63.0844 | -0.065308 | 0.00098907 | 0.06442 | 0.064758 | -0.0032193 | 7.0582e-05 | 0.00054267 | 0.004242 | -0.00010472 | 0.06749 | 0.064986 | -0.0017432 | -0.0010212 | -0.0016129 | -0.14648 | 63.176 | -60.2875 | 62.9745 | -59.8526 | -60.1913 | -0.068665 | 0.045776 | 63.1439 | -60.0952 | 63.2309 | -59.9075 | -60.022 | -59.5963 | -0.3067 | 0.091552 | -0.10986 | 0.12817 | 59.9121 | -0.21057 | 60.2188 | 0.096131 | -0.11444 | 0.059509 | 0.14648 | 0.073242 | 0.38452 | -0.041199 | 0.49896 | 0.073242 | 0.43488 | 123.262 | 0.18768 | 123.3261 | 123.4634 | 123.2391 | 123.1567 | 123.1247 | -123.3719 | -123.1796 | 122.9553 | 123.2117 | 59.8343 | 60.0265
777.5469 | 123.2803 | -60.0357 | 63.1302 | -0.011902 | 0.00098907 | 0.063779 | 0.067108 | -0.0012967 | -0.00099762 | -0.0015935 | -0.084259 | 0.00074988 | 0.067704 | 0.073745 | 0.0014612 | -0.00059378 | 0.00073706 | -0.19226 | 63.2217 | -60.3104 | 62.8555 | -59.8572 | -60.1044 | -0.28839 | -0.10071 | 63.2034 | -60.1456 | 63.121 | -60.0494 | -60.1913 | -59.7198 | -0.27466 | 0.091553 | -0.27466 | 0.17853 | 59.7473 | -0.068664 | 60.022 | 0.20599 | -0.10986 | 0.073242 | -0.009155 | -0.013732 | 0.31586 | -0.15564 | 0.42572 | -0.045776 | 0.45319 | 123.1659 | 0.096131 | 123.2666 | 123.5321 | 123.349 | 123.2574 | 123.2391 | -123.4406 | -123.2758 | 122.8912 | 123.1567 | 59.8434 | 59.935
778.4844 | 123.4222 | -60.0037 | 63.1073 | -0.0042723 | 0.0012027 | 0.062284 | 0.065826 | -0.0038603 | 0.00071138 | -0.0037299 | -0.0018616 | -0.00031832 | 0.068131 | 0.064559 | -0.0011022 | 4.7018e-05 | -0.00075834 | -0.16937 | 63.1714 | -60.3058 | 62.9654 | -59.8663 | -60.2142 | -0.11444 | 0.027466 | 63.1622 | -60.1044 | 63.2492 | -59.9304 | -60.0494 | -59.6146 | -0.30212 | 0.064087 | -0.14191 | 0.13733 | 59.8892 | -0.21057 | 60.1913 | 0.091553 | -0.10071 | 0.054931 | 0.14191 | 0.073242 | 0.3891 | -0.045776 | 0.48981 | 0.054932 | 0.43945 | 123.2712 | 0.17395 | 123.3536 | 123.4772 | 123.2666 | 123.175 | 123.1659 | -123.4131 | -123.2117 | 122.9691 | 123.2529 | 59.8343 | 60.0311
779.4844 | 123.3582 | -60.0357 | 63.1531 | -0.072937 | 0.00056187 | 0.065061 | 0.063476 | 0.00041234 | -0.00035682 | 0.00054267 | -0.011017 | -0.0013863 | 0.070908 | 0.070754 | -0.0047338 | -0.003371 | -0.0013991 | -0.15564 | 63.1531 | -60.2829 | 62.9883 | -59.8618 | -60.2005 | -0.091553 | 0.027466 | 63.1714 | -60.0998 | 63.1851 | -59.9808 | -60.0815 | -59.6466 | -0.24719 | 0 | -0.16479 | 0.17395 | 59.9442 | -0.16479 | 60.1913 | 0.082398 | -0.064086 | 0.018311 | 0.032044 | 0.054932 | 0.3891 | -0.045776 | 0.45319 | 0.01831 | 0.42114 | 123.2712 | 0.11902 | 123.2849 | 123.436 | 123.2712 | 123.1888 | 123.2071 | -123.436 | -123.2529 | 123.024 | 123.2208 | 59.8801 | 60.0632
780.5469 | 123.3673 | -60.0128 | 63.0844 | -0.065308 | 0.00098907 | 0.062711 | 0.066467 | -0.0025785 | 0.00049778 | 0.0018243 | -0.0079652 | 0.0016043 | 0.069199 | 0.061355 | -0.0015296 | -0.001662 | 9.6064e-05 | -0.26093 | 63.1439 | -60.3287 | 62.9105 | -59.9487 | -60.2966 | -0.21057 | -0.15106 | 63.1668 | -60.1364 | 63.1531 | -60.0403 | -60.1273 | -59.5642 | -0.31586 | 0.059509 | -0.17395 | 0.064087 | 59.8022 | -0.28381 | 60.1181 | 0.032043 | -0.1236 | 0.082397 | 0.068664 | -0.027466 | 0.44861 | -0.11444 | 0.57221 | 0.009156 | 0.37994 | 123.2391 | 0.096131 | 123.2895 | 123.4726 | 123.3032 | 123.1567 | 123.1796 | -123.4131 | -123.2208 | 122.9233 | 123.1659 | 59.7519 | 59.8618
781.4844 | 123.1522 | -60.022 | 63.1348 | 0.018616 | -0.00050633 | 0.062925 | 0.06604 | 0.0010531 | -0.0022794 | 0.0018243 | -0.05069 | -0.00053192 | 0.066635 | 0.064773 | -0.0011022 | -0.001662 | -0.0043899 | -0.21057 | 63.2263 | -60.3241 | 62.8784 | -59.9762 | -60.3058 | -0.1831 | -0.09613 | 63.2263 | -60.1044 | 63.1027 | -60.0815 | -59.8801 | -59.6741 | -0.30212 | 0.091552 | -0.25635 | 0.045777 | 59.8389 | -0.28381 | 60.141 | 0.018311 | -0.082397 | 0.091552 | -0.032044 | -0.059509 | 0.3479 | 0.14191 | 0.4303 | 0.2243 | 0.3479 | 123.2025 | 0.022888 | 123.2071 | 123.5504 | 123.3307 | 123.2483 | 123.2483 | -123.4589 | -123.2391 | 122.9004 | 123.1247 | 59.8114 | 59.9258
782.5469 | 123.3627 | -60.0449 | 63.0478 | -0.095825 | 0.00034827 | 0.065061 | 0.065612 | -1.486e-05 | 0.00092498 | -0.0011663 | -0.023224 | 0.00053628 | 0.067917 | 0.074386 | -0.000675 | -0.001662 | 0.00052346 | -0.25177 | 63.121 | -60.3241 | 62.8922 | -59.848 | -60.2554 | -0.22888 | -0.12817 | 63.1439 | -60.1227 | 63.1805 | -60.0128 | -60.1044 | -59.6375 | -0.27924 | 0.073242 | -0.15564 | 0.19684 | 59.816 | -0.21057 | 60.0952 | 0.068665 | -0.07782 | 0.09613 | 0.13275 | 0.032044 | 0.40741 | -0.059509 | 0.48523 | 0.018311 | 0.47608 | 123.2162 | 0.10986 | 123.3032 | 123.4451 | 123.2666 | 123.1659 | 123.1888 | -123.3719 | -123.1705 | 122.937 | 123.2254 | 59.7931 | 59.9167
783.4844 | 123.2803 | -60.0494 | 63.1439 | -0.011902 | -7.913e-05 | 0.065916 | 0.06369 | -0.00065586 | 7.0582e-05 | -0.0013799 | -0.01712 | 0.0016043 | 0.065354 | 0.065841 | -0.0015296 | -0.00016658 | -0.0011855 | -0.19226 | 63.2263 | -60.2829 | 62.9196 | -59.9075 | -60.2371 | -0.14191 | -0.018311 | 63.1989 | -60.1273 | 63.1256 | -60.0266 | -60.0998 | -59.6878 | -0.23346 | 0.082397 | -0.2243 | 0.14191 | 59.9075 | -0.18768 | 60.141 | 0.045776 | -0.07782 | 0.054932 | -0.018311 | 0.022888 | 0.36163 | -0.050354 | 0.43945 | 0.027466 | 0.37537 | 123.2025 | 0.10071 | 123.2529 | 123.5092 | 123.3261 | 123.2758 | 123.2483 | -123.4268 | -123.2712 | 122.9691 | 123.175 | 59.8572 | 60.0311
784.4844 | 123.2803 | -60.0906 | 63.1165 | -0.33997 | 0.00077547 | 0.064634 | 0.065612 | 0.00062594 | -0.00078402 | 0.00054267 | -0.096466 | 0.0018179 | 0.068131 | 0.071609 | -0.001316 | 0.0015424 | -0.0016129 | -0.18768 | 63.1851 | -60.3607 | 62.883 | -59.9487 | -60.3058 | -0.21515 | -0.07782 | 63.2034 | -60.141 | 63.1165 | -60.0861 | -60.1959 | -59.7244 | -0.27008 | 0.068665 | -0.23346 | 0.14191 | 59.8755 | -0.21515 | 60.1456 | 0.054932 | -0.050354 | 0.086975 | 0 | 0.004577 | 0.36621 | -0.10529 | 0.41656 | -0.054932 | 0.41199 | 123.2437 | 0.054931 | 123.2574 | 123.5458 | 123.3444 | 123.2758 | 123.2941 | -123.4772 | -123.2574 | 122.9736 | 123.2071 | 59.903 | 60.0128
785.4844 | 123.4177 | -59.9899 | 63.0798 | -0.011902 | 0.00013467 | 0.062711 | 0.066467 | -0.0036465 | 7.0582e-05 | -0.0018073 | 0.028656 | 0.00032248 | 0.067276 | 0.062636 | -0.001316 | -0.0020892 | 0.0013779 | -0.18768 | 63.176 | -60.2829 | 62.9837 | -59.7885 | -60.1776 | -0.073242 | 0.027466 | 63.1714 | -60.1227 | 63.2263 | -59.935 | -60.0266 | -59.6329 | -0.29297 | 0.09613 | -0.09613 | 0.20142 | 59.9167 | -0.18768 | 60.2097 | 0.10529 | -0.13275 | 0.091553 | 0.14648 | 0.054931 | 0.35705 | -0.036621 | 0.48981 | 0.096131 | 0.49439 | 123.2666 | 0.18768 | 123.349 | 123.4589 | 123.2941 | 123.1659 | 123.1613 | -123.3627 | -123.2025 | 122.9736 | 123.2162 | 59.8022 | 60.0174
786.4844 | 123.4131 | -60.0037 | 63.1027 | -0.072937 | -7.913e-05 | 0.063352 | 0.064544 | -0.00086946 | 0.00049778 | -0.0018073 | 0.025604 | -0.0016001 | 0.067704 | 0.067977 | -0.0017432 | -0.0020892 | -0.00033114 | -0.19684 | 63.121 | -60.2875 | 62.9745 | -59.816 | -60.1868 | -0.082397 | 0.064087 | 63.1577 | -60.1089 | 63.2172 | -59.9304 | -60.0128 | -59.6146 | -0.28381 | 0.018311 | -0.12817 | 0.18768 | 59.9213 | -0.18311 | 60.2051 | 0.10071 | -0.10529 | 0.054932 | 0.11444 | 0.073242 | 0.3891 | -0.009155 | 0.49439 | 0.096131 | 0.4715 | 123.262 | 0.17853 | 123.3261 | 123.4085 | 123.2666 | 123.1247 | 123.1613 | -123.3902 | -123.2117 | 122.9782 | 123.2208 | 59.8068 | 60.0677
787.5469 | 123.4222 | -60.0082 | 63.1165 | -0.03479 | 0.00098907 | 0.062711 | 0.066894 | 0.00019874 | 0.0017794 | -0.0011663 | 0.016449 | 0.0011771 | 0.06749 | 0.067763 | -0.0017432 | -0.00038018 | -0.00033114 | -0.17853 | 63.1851 | -60.2737 | 62.9974 | -59.816 | -60.1868 | -0.10986 | 0.045776 | 63.1485 | -60.0952 | 63.2126 | -59.9396 | -60.0357 | -59.61 | -0.2655 | 0.068665 | -0.11902 | 0.19226 | 59.8984 | -0.17853 | 60.1639 | 0.086975 | -0.086975 | 0.032044 | 0.09613 | 0.068665 | 0.39825 | -0.027466 | 0.48523 | 0.059509 | 0.45776 | 123.2712 | 0.15564 | 123.3078 | 123.4589 | 123.2437 | 123.1934 | 123.1567 | -123.3902 | -123.2117 | 123.0057 | 123.2208 | 59.8297 | 60.054
788.4844 | 123.3902 | -60.022 | 63.089 | -0.057678 | 0.0026981 | 0.061002 | 0.065399 | -0.0051419 | 0.00092498 | -9.8328e-05 | -0.029327 | -0.00095912 | 0.064926 | 0.068618 | -0.001316 | -0.00038018 | -0.00011754 | -0.19226 | 63.1622 | -60.2829 | 62.8052 | -60.0632 | -60.1364 | -0.13275 | 0.050354 | 63.1439 | -60.1181 | 63.2034 | -59.9533 | -60.0357 | -59.6191 | -0.26093 | 0.073242 | -0.28381 | -0.041198 | 59.8892 | -0.11444 | 60.1501 | 0.14648 | -0.09613 | 0.054932 | 0.11444 | 0.068665 | 0.40283 | -0.013733 | 0.49896 | 0.082397 | 0.21973 | 123.0881 | 0.16479 | 123.3215 | 123.4451 | 123.262 | 123.1842 | 123.1659 | -123.3719 | -123.2071 | 122.8271 | 123.2254 | 59.8297 | 60.0723
789.5625 | 123.2574 | -60.0723 | 63.1027 | -0.065308 | 0.0016299 | 0.06442 | 0.065826 | 0.0023349 | 0.00071138 | 0.0013971 | -0.10257 | 0.0013907 | 0.066635 | 0.071395 | -0.000675 | -0.00038018 | 9.6064e-05 | -0.33417 | 63.1897 | -60.3607 | 62.8281 | -60.0586 | -60.4065 | -0.37994 | -0.3067 | 63.176 | -60.1593 | 63.0844 | -60.1273 | -60.2646 | -59.761 | -0.28839 | 0.086975 | -0.27466 | 0.013733 | 59.6924 | -0.33417 | 59.9808 | -0.045776 | -0.086975 | 0.073242 | -0.01831 | -0.054931 | 0.31128 | -0.19226 | 0.39825 | -0.10529 | 0.30212 | 123.1888 | 0.032044 | 123.2437 | 123.5504 | 123.3353 | 123.262 | 123.2483 | -123.4634 | -123.262 | 122.9004 | 123.1567 | 59.7382 | 59.7656
790.4844 | 123.3948 | -60.0128 | 63.0798 | -0.027161 | -0.00071993 | 0.06442 | 0.064331 | -0.00022866 | 0.0015658 | -0.0022345 | 0.034759 | -0.0011727 | 0.064499 | 0.067763 | -0.003025 | -0.00059378 | 9.6064e-05 | -0.21057 | 63.1943 | -60.2921 | 62.9974 | -59.8068 | -60.1913 | -0.10529 | 0.045776 | 63.1531 | -60.0952 | 63.2172 | -59.9396 | -60.0128 | -59.6054 | -0.27924 | 0.11444 | -0.082397 | 0.20599 | 59.9075 | -0.17853 | 60.1868 | 0.10071 | -0.082398 | 0.073242 | 0.13733 | 0.073242 | 0.40741 | 0 | 0.48981 | 0.082398 | 0.48523 | 123.2895 | 0.15564 | 123.3124 | 123.4863 | 123.2483 | 123.2071 | 123.1659 | -123.3719 | -123.175 | 123.0103 | 123.23 | 59.8022 | 60.0586
791.4844 | 123.3078 | -60.0449 | 63.1348 | -0.011902 | 0.00013467 | 0.063566 | 0.065185 | -0.0040739 | 0.00071138 | 0.00075627 | -0.0018616 | -0.00010472 | 0.069412 | 0.064986 | -0.0028112 | 0.0021832 | 0.0020187 | -0.19684 | 63.1897 | -60.3058 | 62.9471 | -59.8984 | -60.2371 | -0.15106 | -0.032043 | 63.2034 | -60.1089 | 63.1348 | -60.022 | -60.1364 | -59.7061 | -0.26093 | 0.054931 | -0.18768 | 0.14648 | 59.8938 | -0.19226 | 60.1547 | 0.068664 | -0.064087 | 0.068664 | 0 | 0.022888 | 0.33874 | -0.091553 | 0.40283 | -0.027466 | 0.40741 | 123.2529 | 0.086975 | 123.2437 | 123.4955 | 123.3124 | 123.2346 | 123.2483 | -123.4406 | -123.2437 | 122.9919 | 123.1796 | 59.848 | 60.0128
792.4844 | 123.4131 | -60.022 | 63.1073 | -0.057678 | 0.00077547 | 0.063566 | 0.063903 | -0.0030057 | -0.00014322 | 0.0026789 | 0.022552 | -0.00074552 | 0.065567 | 0.0652 | -0.0025976 | -0.00016658 | 0.0026597 | -0.19684 | 63.1714 | -60.2554 | 62.9974 | -59.7931 | -60.1822 | -0.11444 | 0.045776 | 63.1577 | -60.0998 | 63.2217 | -59.9213 | -60.0403 | -59.6191 | -0.23346 | 0.064087 | -0.10986 | 0.22888 | 59.9075 | -0.16022 | 60.141 | 0.073242 | -0.077819 | 0.050354 | 0.11444 | 0.10071 | 0.40283 | -0.01831 | 0.48065 | 0.059509 | 0.46234 | 123.2529 | 0.17853 | 123.3215 | 123.4268 | 123.2574 | 123.1934 | 123.1796 | -123.3627 | -123.2071 | 123.0194 | 123.2437 | 59.8251 | 60.0677
793.4844 | 123.2529 | -60.0403 | 63.1668 | -0.0042723 | -0.00071993 | 0.062925 | 0.064331 | -0.0021513 | -0.00099762 | 0.00054267 | -0.026276 | 0.0011771 | 0.067063 | 0.063491 | -0.0017432 | -0.0027302 | 0.0041551 | -0.27466 | 63.2172 | -60.3149 | 62.8738 | -59.9899 | -60.2875 | -0.21515 | -0.10071 | 63.2172 | -60.1135 | 63.121 | -60.0632 | -60.1776 | -59.7519 | -0.27466 | 0.050354 | -0.29297 | 0.050354 | 59.8251 | -0.24719 | 60.0998 | 0.027465 | -0.073242 | 0.050354 | -0.045776 | -0.022888 | 0.28839 | -0.13733 | 0.36163 | -0.064087 | 0.32501 | 123.1888 | 0.050354 | 123.2346 | 123.5321 | 123.3307 | 123.2574 | 123.2574 | -123.4818 | -123.2803 | 122.9141 | 123.1613 | 59.7656 | 59.9396
794.5625 | 123.3261 | -60.0449 | 63.1027 | -0.042419 | 0.0014163 | 0.065061 | 0.065826 | 0.0014803 | 0.00092498 | -0.00095273 | -0.10562 | -0.00074552 | 0.06749 | 0.069045 | 0.0006066 | -0.0014484 | 0.00073706 | -0.24261 | 63.1897 | -60.3333 | 62.9013 | -59.9396 | -60.3012 | -0.26093 | -0.091553 | 63.1943 | -60.1501 | 63.1851 | -60.0723 | -60.1318 | -59.6786 | -0.28839 | 0.086975 | -0.20142 | 0.10529 | 59.7839 | -0.25635 | 60.0723 | 0.032044 | -0.10529 | 0.091553 | 0.082398 | -0.027466 | 0.36621 | -0.086975 | 0.4715 | 0.01831 | 0.39368 | 123.2346 | 0.077819 | 123.3353 | 123.5229 | 123.3444 | 123.2346 | 123.2391 | -123.436 | -123.2529 | 122.9462 | 123.23 | 59.8022 | 59.9533
795.4844 | 123.2712 | -60.0311 | 63.1439 | -0.072937 | -0.00029273 | 0.063138 | 0.066253 | -0.0040739 | -0.0029202 | 0.00032907 | -0.056793 | 0.00010888 | 0.066208 | 0.065414 | 0.0006066 | 0.00026062 | -0.0020401 | -0.25177 | 63.2309 | -60.3149 | 62.8052 | -60.1501 | -60.2646 | -0.2655 | -0.14191 | 63.1989 | -60.1318 | 63.1302 | -60.0769 | -60.1593 | -59.7336 | -0.28381 | 0.086975 | -0.33874 | -0.11902 | 59.7656 | -0.23346 | 60.0494 | 0.050354 | -0.10071 | 0.054932 | -0.013733 | -0.045776 | 0.29755 | -0.12817 | 0.39825 | -0.027466 | 0.16479 | 123.1201 | 0.054932 | 123.262 | 123.5458 | 123.3307 | 123.262 | 123.23 | -123.4589 | -123.2758 | 122.8363 | 123.1613 | 59.7794 | 59.8892
796.5469 | 123.3627 | -60.0037 | 63.0798 | -0.050049 | -0.00050633 | 0.065916 | 0.063262 | -0.0034329 | -0.0014248 | -0.0022345 | 0.0072936 | -0.00010472 | 0.067917 | 0.060927 | -0.000675 | -0.0023028 | 0.00030966 | -0.32044 | 63.1714 | -60.2875 | 62.9013 | -59.935 | -60.2783 | -0.26093 | -0.14648 | 63.176 | -60.1364 | 63.1668 | -60.022 | -60.1227 | -59.6695 | -0.28381 | 0.091553 | -0.17853 | 0.068664 | 59.7427 | -0.27466 | 60.0266 | 0.009156 | -0.13275 | 0.09613 | 0.086975 | -0.018311 | 0.33417 | -0.11902 | 0.46692 | 0.013733 | 0.35248 | 123.1888 | 0.11444 | 123.3032 | 123.4589 | 123.3124 | 123.175 | 123.1796 | -123.3673 | -123.2162 | 122.905 | 123.1705 | 59.6832 | 59.8572
797.4844 | 123.2758 | -60.0449 | 63.1714 | -0.019531 | 0.0012027 | 0.06143 | 0.066467 | 0.00083954 | -0.00014322 | 0.00054267 | 0.028656 | 0.0026725 | 0.067704 | 0.065841 | -0.0025976 | -0.0023028 | -0.00011754 | -0.2655 | 63.2492 | -60.3287 | 62.8784 | -59.9899 | -60.3012 | -0.17853 | -0.31586 | 63.2172 | -60.1318 | 63.0844 | -60.054 | -60.1822 | -59.7244 | -0.28381 | 0.07782 | -0.29297 | 0.054932 | 59.8663 | -0.25635 | 60.1501 | 0.027466 | -0.086975 | 0.045776 | -0.086975 | -0.009155 | 0.32043 | -0.13733 | 0.40741 | -0.050354 | 0.33875 | 123.2071 | 0.07782 | 123.2162 | 123.5779 | 123.349 | 123.2941 | 123.262 | -123.5001 | -123.3032 | 122.9233 | 123.1293 | 59.7794 | 59.729
798.4844 | 123.4222 | -60.022 | 63.0981 | -0.095825 | 0.00077547 | 0.062284 | 0.063903 | -0.0017239 | -0.00014322 | 0.0011835 | 0.025604 | -0.0018137 | 0.067063 | 0.064132 | -0.002384 | 0.00026062 | 0.0013779 | -0.20599 | 63.176 | -60.26 | 62.9883 | -59.8068 | -60.1776 | -0.14648 | 0.018311 | 63.1805 | -60.0677 | 63.2812 | -59.7015 | -60.3012 | -59.8709 | -0.23804 | 0.077819 | -0.10986 | 0.21515 | 59.8755 | -0.15564 | 60.1135 | 0.082398 | -0.045776 | 0.082397 | 0.1831 | 0.32044 | 0.15106 | -0.27923 | 0.19684 | -0.23346 | 0.45319 | 123.2483 | 0.36621 | 123.349 | 123.436 | 123.2483 | 123.1979 | 123.2025 | -123.3582 | -123.1659 | 123.0103 | 123.3032 | 59.816 | 60.0403
799.5 | 123.2712 | -60.0906 | 63.121 | -0.10345 | 0.0014163 | 0.064847 | 0.066253 | 0.00019874 | 0.00071138 | 0.0031061 | -0.093414 | 0.0041679 | 0.068344 | 0.064986 | -0.0015296 | -0.00016658 | 0.0050095 | -0.33875 | 63.1851 | -60.3653 | 62.8006 | -60.0357 | -60.4065 | -0.39825 | -0.32044 | 63.1805 | -60.1547 | 63.0936 | -60.1501 | -60.2509 | -59.7702 | -0.27466 | 0.064087 | -0.32043 | 0.054931 | 59.6924 | -0.31586 | 59.967 | -0.041199 | -0.064087 | 0.059509 | -0.027466 | -0.059509 | 0.32043 | -0.16022 | 0.38452 | -0.09613 | 0.32959 | 123.1659 | 0.004578 | 123.2483 | 123.5504 | 123.3353 | 123.2758 | 123.2712 | -123.4863 | -123.2758 | 122.8912 | 123.1842 | 59.7519 | 59.7702
800.5469 | 123.3673 | -60.0266 | 63.0981 | -0.0042723 | 0.00077547 | 0.063566 | 0.064758 | 0.00019874 | 0.00092498 | -0.0020209 | 0.028656 | 0.0011771 | 0.065354 | 0.059646 | -3.4196e-05 | -0.0014484 | 0.00095066 | -0.32959 | 63.1851 | -60.2783 | 62.9059 | -59.9213 | -60.2737 | -0.25635 | -0.15106 | 63.1577 | -60.1273 | 63.1851 | -59.9579 | -60.054 | -59.6329 | -0.25177 | 0.086975 | -0.19226 | 0.10529 | 59.7702 | -0.24719 | 60.022 | 0.004577 | -0.10071 | 0.059509 | 0.086975 | 0.068664 | 0.39368 | -0.027466 | 0.49438 | 0.073242 | 0.35706 | 123.1842 | 0.16937 | 123.3124 | 123.4634 | 123.2849 | 123.2117 | 123.1842 | -123.3765 | -123.2254 | 122.9324 | 123.2117 | 59.697 | 59.8755
801.4844 | 123.2849 | -60.022 | 63.1622 | -0.019531 | 0.0020573 | 0.062711 | 0.065399 | -0.0017239 | 7.0582e-05 | -0.0026617 | -0.044586 | 0.0018179 | 0.067704 | 0.066482 | -0.0025976 | 0.00068782 | 0.0024461 | -0.27924 | 63.2401 | -60.3287 | 62.883 | -59.9899 | -60.3104 | -0.25635 | -0.13275 | 63.2309 | -60.1135 | 63.121 | -60.0403 | -60.1593 | -59.7198 | -0.3067 | 0.07782 | -0.27923 | 0.032044 | 59.7656 | -0.28839 | 60.0723 | 0.01831 | -0.091552 | 0.068665 | -0.041198 | -0.01831 | 0.30212 | -0.13733 | 0.39368 | -0.045777 | 0.33875 | 123.2117 | 0.073242 | 123.2346 | 123.5687 | 123.3444 | 123.262 | 123.2529 | -123.4909 | -123.2758 | 122.905 | 123.143 | 59.7427 | 59.8892
802.4844 | 123.3627 | -60.0174 | 63.121 | -0.080566 | 0.0018435 | 0.061643 | 0.064758 | -0.00065586 | 0.0015658 | -0.00073913 | 0.037811 | -0.0016001 | 0.064713 | 0.065414 | -0.0002478 | -0.0018756 | 0.0060777 | -0.23346 | 63.1943 | -60.2692 | 62.8052 | -59.8022 | -60.2371 | -0.25635 | -0.059509 | 63.1348 | -60.1181 | 63.1989 | -59.9625 | -60.0266 | -59.6283 | -0.25177 | 0.073242 | -0.31586 | 0.21515 | 59.761 | -0.21973 | 60.0128 | 0.032043 | -0.10071 | 0.013733 | 0.07782 | 0.054932 | 0.3891 | -0.009155 | 0.48981 | 0.091553 | 0.46692 | 123.0743 | 0.15564 | 123.317 | 123.4634 | 123.2529 | 123.2117 | 123.1522 | -123.3902 | -123.2391 | 122.8226 | 123.2162 | 59.7839 | 59.9579
803.4844 | 123.2803 | -60.0403 | 63.1302 | 0.018616 | -0.00093353 | 0.061643 | 0.066467 | -0.0015103 | -0.00057042 | 0.00011527 | -0.029327 | 0.0022453 | 0.068344 | 0.069472 | -0.0017432 | -0.0012348 | -0.00054474 | -0.31586 | 63.2309 | -60.2921 | 62.8372 | -60.0357 | -60.2829 | -0.27924 | -0.1236 | 63.2309 | -60.1547 | 63.1165 | -60.0586 | -60.1822 | -59.7061 | -0.25177 | 0.10071 | -0.29297 | 0.004577 | 59.761 | -0.24262 | 60.0128 | 0.009155 | -0.11444 | 0.10071 | -0.013733 | -0.018311 | 0.33417 | -0.14191 | 0.44861 | -0.027466 | 0.25635 | 123.1293 | 0.09613 | 123.2712 | 123.5229 | 123.3856 | 123.2712 | 123.2712 | -123.4222 | -123.2849 | 122.8775 | 123.1567 | 59.7244 | 59.9167
804.4844 | 123.2254 | -60.0906 | 63.1073 | -0.057678 | 0.0014163 | 0.063993 | 0.065612 | 0.0040439 | -0.00035682 | -9.8328e-05 | -0.053741 | 0.0024589 | 0.068344 | 0.072463 | -0.0011022 | 0.001756 | -0.0035355 | -0.37079 | 63.1805 | -60.3699 | 62.8326 | -60.054 | -60.4111 | -0.43488 | -0.33875 | 63.1897 | -60.1593 | 63.0844 | -60.1318 | -60.2509 | -59.761 | -0.27924 | 0.073242 | -0.27466 | 0.036621 | 59.6558 | -0.32043 | 59.935 | -0.041199 | -0.068665 | 0.082397 | -0.022888 | -0.041199 | 0.32959 | -0.16022 | 0.39825 | -0.091552 | 0.31586 | 123.2025 | 0.027466 | 123.2437 | 123.5504 | 123.349 | 123.2712 | 123.2803 | -123.4772 | -123.2666 | 122.9233 | 123.175 | 59.7198 | 59.7519
805.5469 | 123.381 | -60.022 | 63.089 | -0.057678 | 0.0016299 | 0.063566 | 0.062622 | -0.00086946 | 0.00071138 | 0.0016107 | 0.016449 | -0.0022409 | 0.066422 | 0.056655 | -0.0011022 | -0.0018756 | -0.0028945 | -0.27008 | 63.1851 | -60.2921 | 62.9608 | -59.6603 | -59.8709 | -0.31128 | -0.009155 | 63.1622 | -60.1135 | 63.2217 | -59.9442 | -60.0677 | -59.61 | -0.27008 | 0.096131 | -0.12817 | 0.36163 | 59.7107 | 0.15106 | 59.9808 | 0.42114 | -0.091552 | 0.073242 | 0.13275 | 0.07782 | 0.41199 | -0.045776 | 0.50354 | 0.045776 | 0.63171 | 123.2529 | 0.16937 | 123.3353 | 123.4772 | 123.2758 | 123.2071 | 123.1842 | -123.381 | -123.2025 | 122.9828 | 123.2437 | 59.7519 | 60.0128
806.4844 | 123.4406 | -59.9762 | 63.1348 | -0.03479 | -7.913e-05 | 0.061643 | 0.063262 | -0.00086946 | 0.002634 | 0.0026789 | 0.043915 | -0.00095912 | 0.066849 | 0.063064 | -0.000675 | 4.7018e-05 | 0.0020187 | -0.27008 | 63.1851 | -60.26 | 62.9974 | -59.816 | -60.1822 | -0.1831 | 0 | 63.1577 | -60.1135 | 63.2263 | -59.9258 | -59.9854 | -59.4589 | -0.28381 | 0.050354 | -0.13733 | 0.16022 | 59.7931 | -0.20599 | 60.0769 | 0.07782 | -0.13733 | 0.022888 | 0.091552 | 0.050354 | 0.51727 | -0.009156 | 0.6546 | 0.12817 | 0.44403 | 123.2574 | 0.18768 | 123.3398 | 123.4451 | 123.2712 | 123.1613 | 123.1338 | -123.3948 | -123.2483 | 122.9736 | 123.2025 | 59.7061 | 59.9762
807.5469 | 123.4268 | -60.0082 | 63.0981 | -0.042419 | 0.0012027 | 0.063138 | 0.063262 | -0.0025785 | 0.0015658 | -0.0013799 | 0.028656 | 0.00096348 | 0.067276 | 0.058791 | -0.0015296 | -0.0018756 | -0.0018265 | -0.30212 | 63.1805 | -60.26 | 62.9654 | -59.8572 | -60.2005 | -0.21515 | -0.050354 | 63.1622 | -60.0861 | 63.2309 | -59.9213 | -60.0266 | -59.5963 | -0.25177 | 0.082397 | -0.13275 | 0.15106 | 59.7931 | -0.19226 | 60.0449 | 0.05951 | -0.07782 | 0.064086 | 0.13275 | 0.086975 | 0.41199 | -0.01831 | 0.48981 | 0.05951 | 0.40283 | 123.2254 | 0.1648 | 123.317 | 123.4406 | 123.2483 | 123.1888 | 123.1705 | -123.3582 | -123.1842 | 122.9736 | 123.2391 | 59.7061 | 59.9579
808.4844 | 123.349 | -60.0082 | 63.1256 | -0.057678 | 0.0033389 | 0.05908 | 0.064971 | -0.0034329 | 0.0015658 | 0.00011527 | 0.019501 | -0.00031832 | 0.067704 | 0.057296 | -0.0015296 | -0.00080758 | -0.00075834 | 0.018311 | 63.2584 | -60.228 | 62.97 | -59.8068 | -60.2371 | -0.23804 | -0.032043 | 63.176 | -60.1044 | 63.208 | -59.9579 | -60.0403 | -59.6375 | -0.21973 | 0.13275 | -0.15564 | 0.20142 | 59.7702 | -0.22888 | 59.9899 | -0.009156 | -0.09613 | 0.050354 | 0.082398 | 0.050354 | 0.37079 | -0.032043 | 0.46692 | 0.064087 | 0.42114 | 123.1979 | 0.14648 | 123.3124 | 123.4863 | 123.2803 | 123.2666 | 123.1842 | -123.3536 | -123.23 | 122.9782 | 123.2162 | 60.0266 | 59.9762
809.4844 | 123.2758 | -60.0311 | 63.1485 | 0.08728 | 0.0020573 | 0.064847 | 0.064758 | 0.0036165 | -0.00035682 | 0.00096987 | -0.053741 | 0.0016043 | 0.068558 | 0.066909 | -0.0019568 | -0.00059378 | 0.0041551 | -0.48523 | 63.2446 | -60.3195 | 62.8555 | -59.9808 | -60.2646 | -0.29297 | -0.13733 | 63.208 | -60.1135 | 63.1393 | -60.0586 | -60.1639 | -59.697 | -0.28839 | 0.09613 | -0.29297 | 0.050354 | 59.7382 | -0.23346 | 60.0266 | 0.054932 | -0.082397 | 0.059509 | -0.009156 | -0.027466 | 0.33417 | -0.13275 | 0.41657 | -0.050354 | 0.33875 | 123.175 | 0.054931 | 123.2529 | 123.5641 | 123.3215 | 123.2758 | 123.2391 | -123.468 | -123.262 | 122.8867 | 123.1705 | 59.5459 | 59.8938
810.5469 | 123.3948 | -59.9762 | 63.1027 | -0.0042723 | 0.00077547 | 0.064634 | 0.063476 | -0.0012967 | 0.00071138 | -0.0037299 | 0.025604 | 0.00053628 | 0.06514 | 0.069045 | -0.0017432 | -0.0020892 | -0.00097194 | -0.30212 | 63.1897 | -60.3012 | 62.9974 | -59.816 | -60.1547 | -0.17853 | -0.027466 | 63.1531 | -60.1273 | 63.2309 | -59.9213 | -60.0311 | -59.5963 | -0.32501 | 0.086975 | -0.10529 | 0.16022 | 59.7977 | -0.17853 | 60.1227 | 0.14648 | -0.15106 | 0.050354 | 0.12817 | 0.054931 | 0.37994 | -0.054932 | 0.53101 | 0.09613 | 0.48523 | 123.2986 | 0.20599 | 123.3582 | 123.4909 | 123.2803 | 123.1659 | 123.1293 | -123.4039 | -123.23 | 122.9736 | 123.2071 | 59.6741 | 59.9487
811.4844 | 123.2666 | -60.0449 | 63.1531 | -0.027161 | -7.913e-05 | 0.062925 | 0.064544 | -0.00022866 | -0.0016384 | -0.00073913 | -0.044586 | 0.00074988 | 0.066849 | 0.066268 | -0.0015296 | -0.00038018 | -0.0018265 | -0.35248 | 63.2355 | -60.3104 | 62.8326 | -59.7153 | -60.2417 | -0.4303 | -0.1831 | 63.2126 | -60.1227 | 63.1256 | -60.0586 | -60.173 | -59.6924 | -0.2655 | 0.082398 | -0.32043 | 0.32959 | 59.6146 | -0.19684 | 59.8801 | 0.068665 | -0.07782 | 0.059509 | -0.027466 | -0.013733 | 0.35248 | -0.12817 | 0.4303 | -0.050354 | 0.59509 | 123.143 | 0.064087 | 123.2483 | 123.5458 | 123.3353 | 123.2803 | 123.2574 | -123.4634 | -123.2758 | 122.8775 | 123.1705 | 59.6924 | 59.8618
812.5469 | 123.381 | -60.0174 | 63.0936 | -0.080566 | 0.0012027 | 0.062711 | 0.064331 | 0.0025485 | -0.0016384 | -0.0041571 | 0.031708 | 0.0016043 | 0.066849 | 0.064986 | -0.0011022 | -0.0018756 | 0.0013779 | -0.37994 | 63.1805 | -60.2692 | 62.9242 | -59.9075 | -60.2371 | -0.27924 | -0.14648 | 63.1714 | -60.1181 | 63.2126 | -59.9579 | -60.0677 | -59.6329 | -0.25177 | 0.086975 | -0.16937 | 0.10986 | 59.7382 | -0.21973 | 59.9899 | 0.032043 | -0.10071 | 0.07782 | 0.11902 | 0.059509 | 0.38452 | -0.050354 | 0.48523 | 0.050354 | 0.36163 | 123.1934 | 0.16022 | 123.3307 | 123.4497 | 123.2895 | 123.1979 | 123.1888 | -123.3627 | -123.2117 | 122.9416 | 123.23 | 59.6375 | 59.8709
813.4844 | 123.2849 | -60.0677 | 63.1485 | -0.03479 | 0.00034827 | 0.063566 | 0.065185 | -0.0045011 | 0.0017794 | 0.0018243 | -0.01712 | 0.0026725 | 0.066208 | 0.063918 | -0.0011022 | -0.00016658 | -0.00054474 | -0.37537 | 63.2401 | -60.3104 | 62.8876 | -59.967 | -60.2783 | -0.32501 | -0.16937 | 63.2401 | -60.1227 | 63.0157 | -59.9854 | -60.2371 | -59.7427 | -0.24262 | 0.091552 | -0.26093 | 0.10071 | 59.7427 | -0.21057 | 59.9854 | 0.032044 | -0.054932 | 0.091552 | -0.13275 | 0.082397 | 0.32501 | -0.16937 | 0.37994 | -0.11444 | 0.34332 | 123.1979 | 0.13733 | 123.1384 | 123.5504 | 123.3627 | 123.3078 | 123.3078 | -123.4589 | -123.2712 | 122.9553 | 123.0835 | 59.6924 | 59.8984
814.5469 | 123.3765 | -60.0311 | 63.1027 | -0.03479 | 0.0014163 | 0.062498 | 0.063903 | -0.0017239 | 0.0030612 | 0.0026789 | 0.0072936 | 0.0013907 | 0.064286 | 0.060287 | -0.001316 | -0.0029438 | 0.0033005 | -0.42572 | 63.1943 | -60.3104 | 62.9288 | -59.9304 | -60.2737 | -0.35706 | -0.23804 | 63.1577 | -60.1456 | 63.1485 | -59.9991 | -59.9808 | -59.5779 | -0.27924 | 0.091553 | -0.17395 | 0.10071 | 59.6741 | -0.24262 | 59.9533 | 0.036621 | -0.11444 | 0.054932 | 0.045777 | 0.032044 | 0.45319 | 0.050354 | 0.56763 | 0.1648 | 0.37994 | 123.2391 | 0.14648 | 123.2941 | 123.5046 | 123.3032 | 123.2254 | 123.1888 | -123.4131 | -123.2483 | 122.9599 | 123.1796 | 59.6054 | 59.7931
815.4844 | 123.3032 | -60.0082 | 63.1805 | -0.019531 | -0.00071993 | 0.062711 | 0.06604 | -0.0049283 | 0.00071138 | -0.00095273 | -0.029327 | 0.0011771 | 0.065354 | 0.065841 | -0.0021704 | -0.00016658 | -0.0050307 | -0.38452 | 63.2538 | -60.3058 | 62.8647 | -59.9762 | -60.2829 | -0.3067 | -0.16022 | 63.2263 | -60.1181 | 63.121 | -60.0357 | -60.173 | -59.5779 | -0.29755 | 0.073242 | -0.31586 | 0.032044 | 59.7015 | -0.27466 | 59.9991 | 0.022888 | -0.10986 | 0.045776 | -0.059509 | -0.027466 | 0.4303 | -0.16479 | 0.54016 | -0.054932 | 0.32959 | 123.1705 | 0.082397 | 123.2391 | 123.5596 | 123.3444 | 123.262 | 123.2346 | -123.4863 | -123.2986 | 122.8729 | 123.1293 | 59.6237 | 59.848
816.4844 | 123.3719 | -60.0037 | 63.1165 | -0.072937 | -0.00050633 | 0.061002 | 0.063049 | -0.0012967 | -0.0014248 | 0.00075627 | 0.028656 | -0.0011727 | 0.064072 | 0.061996 | -0.0019568 | -0.00080758 | -0.00011754 | -0.25177 | 63.2126 | -60.2097 | 62.9059 | -59.848 | -60.141 | -0.27008 | -0.064087 | 63.1714 | -60.1089 | 63.2172 | -59.9442 | -60.0403 | -59.6191 | -0.20599 | 0.09613 | -0.21057 | 0.15564 | 59.7336 | -0.13733 | 59.9396 | 0.068665 | -0.10529 | 0.054932 | 0.10071 | 0.059509 | 0.38452 | -0.036621 | 0.48981 | 0.068665 | 0.36163 | 123.1155 | 0.16479 | 123.3261 | 123.4222 | 123.2803 | 123.2162 | 123.175 | -123.3261 | -123.2254 | 122.9095 | 123.2208 | 59.7519 | 59.9396
817.4844 | 123.3261 | -60.0311 | 63.1256 | 0.0033567 | 0.00098907 | 0.062284 | 0.065612 | 0.00062594 | -0.0016384 | -0.0011663 | -0.062897 | 0.0016043 | 0.067063 | 0.07054 | -0.0017432 | -0.0020892 | 0.00073706 | -0.35706 | 63.2355 | -60.3012 | 62.9013 | -59.9258 | -60.2646 | -0.30212 | -0.14648 | 63.1897 | -60.0998 | 63.1943 | -60.0174 | -60.1501 | -59.6695 | -0.27008 | 0.10986 | -0.2243 | 0.10529 | 59.729 | -0.23346 | 59.9991 | 0.036621 | -0.068664 | 0.064087 | 0.068665 | 0.013733 | 0.36163 | -0.11902 | 0.4303 | -0.050354 | 0.37537 | 123.2025 | 0.082397 | 123.2941 | 123.5367 | 123.2895 | 123.2666 | 123.2208 | -123.4268 | -123.2254 | 122.9324 | 123.2254 | 59.6741 | 59.8846
818.5469 | 123.3902 | -60.0037 | 63.0981 | -0.065308 | 0.00056187 | 0.062711 | 0.062408 | -0.0042875 | -0.00057042 | -9.8328e-05 | 0.074432 | 0.00032248 | 0.066635 | 0.0652 | -0.0002478 | -0.00038018 | 0.0020187 | -0.31586 | 63.1805 | -60.26 | 63.0112 | -59.7977 | -60.1456 | -0.23804 | -0.036621 | 63.176 | -60.0906 | 63.2309 | -59.9258 | -60.0311 | -59.5963 | -0.25635 | 0.082397 | -0.086976 | 0.20599 | 59.7656 | -0.14191 | 60.022 | 0.11444 | -0.086975 | 0.077819 | 0.13275 | 0.07782 | 0.40741 | -0.027466 | 0.49439 | 0.059509 | 0.46234 | 123.2712 | 0.16479 | 123.3215 | 123.4406 | 123.2666 | 123.1842 | 123.1796 | -123.3582 | -123.1888 | 123.0148 | 123.2346 | 59.6878 | 59.967
819.4844 | 123.2712 | -60.0632 | 63.1622 | -0.019531 | -0.0028561 | 0.061643 | 0.067962 | -0.0019377 | -0.00035682 | -0.0015935 | -0.032379 | 0.00053628 | 0.067063 | 0.065414 | -0.0021704 | -0.00016658 | 0.0022323 | -0.44861 | 63.2401 | -60.2646 | 62.8235 | -60.0128 | -60.2829 | -0.37079 | -0.17853 | 63.2309 | -60.1135 | 63.121 | -60.0449 | -60.1547 | -59.7107 | -0.20142 | 0.07782 | -0.33874 | 0.050354 | 59.6924 | -0.21973 | 59.8938 | -0.018311 | -0.050354 | 0.068665 | -0.041198 | 0.01831 | 0.35248 | -0.091553 | 0.40283 | -0.041199 | 0.25177 | 123.0881 | 0.068664 | 123.2346 | 123.5046 | 123.3444 | 123.3032 | 123.2941 | -123.4268 | -123.2758 | 122.8867 | 123.1842 | 59.6146 | 59.8846
820.4844 | 123.2758 | -60.0266 | 63.1119 | -0.042419 | 0.0024845 | 0.062925 | 0.064544 | -0.0040739 | 0.0017794 | 0.00075627 | 0.004242 | 0.0018179 | 0.066208 | 0.061782 | -0.003025 | -0.0027302 | -0.0026809 | -0.35248 | 63.1851 | -60.2875 | 62.9608 | -59.8572 | -60.2051 | -0.27008 | -0.086975 | 63.2034 | -60.0998 | 63.1851 | -59.9991 | -60.1044 | -59.6512 | -0.26093 | 0.073243 | -0.15106 | 0.16937 | 59.7565 | -0.17853 | 60.0174 | 0.082398 | -0.073242 | 0.091553 | 0.073243 | 0.027466 | 0.37537 | -0.07782 | 0.44861 | -0.004578 | 0.4303 | 123.2483 | 0.10071 | 123.2849 | 123.4726 | 123.3032 | 123.2117 | 123.23 | -123.3994 | -123.2117 | 122.9874 | 123.2117 | 59.6741 | 59.9396
821.5469 | 123.381 | -59.9899 | 63.121 | 0.010986 | 0.00013467 | 0.064847 | 0.06668 | -1.486e-05 | 0.00028418 | -0.0015935 | 0.050018 | -0.0011727 | 0.067063 | 0.066695 | -0.004093 | -0.0025164 | -0.0018265 | -0.35706 | 63.1851 | -60.2463 | 63.0066 | -59.7977 | -60.1456 | -0.23346 | -0.054932 | 63.1805 | -60.0815 | 63.2309 | -59.9167 | -60.022 | -59.5917 | -0.25635 | 0.064087 | -0.11444 | 0.19226 | 59.7565 | -0.15564 | 60.0128 | 0.10071 | -0.091553 | 0.059509 | 0.10986 | 0.073242 | 0.39825 | -0.032044 | 0.48981 | 0.059509 | 0.44861 | 123.2529 | 0.16479 | 123.3124 | 123.4314 | 123.262 | 123.175 | 123.1705 | -123.3673 | -123.2025 | 122.9965 | 123.2208 | 59.6329 | 59.935
822.4844 | 123.3307 | -60.0266 | 63.1531 | -0.072937 | 0.00013467 | 0.062925 | 0.063476 | 0.00062594 | 7.0582e-05 | -0.0022345 | -0.014069 | 0.00096348 | 0.06514 | 0.063918 | -0.0004614 | -0.0010212 | -0.0041763 | -0.34332 | 63.2172 | -60.2783 | 62.9745 | -59.8618 | -60.1913 | -0.25177 | -0.10986 | 63.2126 | -60.0952 | 63.1897 | -59.9808 | -60.0861 | -59.6558 | -0.25177 | 0.064087 | -0.17853 | 0.16479 | 59.7748 | -0.16479 | 60.0266 | 0.086975 | -0.068665 | 0.059509 | 0.036621 | 0.045776 | 0.37079 | -0.05951 | 0.43945 | 0.009155 | 0.41656 | 123.2529 | 0.11444 | 123.2849 | 123.4955 | 123.3078 | 123.2437 | 123.2391 | -123.4314 | -123.2483 | 123.0011 | 123.2162 | 59.6832 | 59.9167
823.4844 | 123.2803 | -60.0082 | 63.1485 | 0.0033567 | 0.0016299 | 0.062498 | 0.065399 | 0.0025485 | -0.00078402 | 0.00075627 | -0.023224 | 0.0016043 | 0.068131 | 0.066909 | -0.002384 | -0.0014484 | -0.0033219 | -0.41199 | 63.2675 | -60.2966 | 62.8372 | -59.6558 | -60.3699 | -0.48065 | -0.23804 | 63.2217 | -60.1364 | 63.1256 | -60.0357 | -60.1639 | -59.6878 | -0.28839 | 0.11902 | -0.31128 | 0.35248 | 59.5276 | -0.36163 | 59.816 | -0.073242 | -0.12817 | 0.073242 | -0.022889 | -0.027466 | 0.32044 | -0.15564 | 0.44861 | -0.027465 | 0.64087 | 123.1338 | 0.10071 | 123.262 | 123.5641 | 123.3582 | 123.2758 | 123.23 | -123.4451 | -123.2849 | 122.8455 | 123.1338 | 59.5963 | 59.7702
824.5469 | 123.4039 | -59.9854 | 63.1165 | -0.03479 | 0.00077547 | 0.062711 | 0.062835 | 0.0042575 | -0.00057042 | -0.00031193 | 0.025604 | -0.00053192 | 0.066422 | 0.060287 | -0.0008886 | -0.0023028 | 0.00073706 | -0.37994 | 63.1805 | -60.2692 | 63.0066 | -59.7885 | -60.1547 | -0.26093 | -0.050354 | 63.1622 | -60.0723 | 63.2446 | -59.9075 | -60.0128 | -59.5963 | -0.28381 | 0.064087 | -0.10986 | 0.19684 | 59.7244 | -0.16937 | 60.0082 | 0.11444 | -0.086975 | 0.045776 | 0.12817 | 0.07782 | 0.3891 | -0.027465 | 0.47608 | 0.05951 | 0.48065 | 123.2758 | 0.16479 | 123.317 | 123.4497 | 123.2346 | 123.1659 | 123.1476 | -123.3856 | -123.1888 | 122.9919 | 123.23 | 59.6054 | 59.935
825.4844 | 123.3032 | -59.9991 | 63.1577 | -0.088196 | -7.913e-05 | 0.061643 | 0.06668 | 0.0021213 | -0.0029202 | 0.0022517 | -0.078156 | 0.00032248 | 0.067704 | 0.068191 | -0.0017432 | -0.0010212 | -0.00033114 | -0.41657 | 63.2309 | -60.3241 | 62.8967 | -59.9579 | -60.2646 | -0.37079 | -0.20599 | 63.2355 | -60.1044 | 63.1531 | -60.022 | -60.1364 | -59.6741 | -0.32501 | 0.073242 | -0.26093 | 0.041198 | 59.6283 | -0.2655 | 59.9533 | 0.05951 | -0.10529 | 0.07782 | -0.004578 | -0.022889 | 0.32501 | -0.13733 | 0.4303 | -0.032044 | 0.36621 | 123.2208 | 0.082397 | 123.2574 | 123.555 | 123.3398 | 123.23 | 123.2346 | -123.4818 | -123.262 | 122.8958 | 123.1522 | 59.5825 | 59.7931
826.4844 | 123.3215 | -60.0082 | 63.121 | -0.065308 | 0.00013467 | 0.063352 | 0.064758 | -0.0023649 | -0.001852 | 0.00054267 | -0.011017 | -0.00053192 | 0.065781 | 0.059859 | -0.0008886 | -0.003371 | 0.00073706 | -0.35706 | 63.2034 | -60.2646 | 62.97 | -59.8434 | -60.1822 | -0.28839 | -0.091553 | 63.2172 | -60.0815 | 63.1897 | -59.9625 | -60.0632 | -59.6375 | -0.25635 | 0.082397 | -0.15106 | 0.16479 | 59.7198 | -0.17395 | 59.9762 | 0.082397 | -0.073242 | 0.09613 | 0.068664 | 0.045777 | 0.37079 | -0.054931 | 0.44403 | 0.018311 | 0.42114 | 123.2346 | 0.11902 | 123.2712 | 123.468 | 123.2986 | 123.2117 | 123.2254 | -123.3856 | -123.2025 | 122.9782 | 123.1979 | 59.6512 | 59.9167
827.4844 | 123.3124 | -60.0449 | 63.1622 | -0.065308 | 0.0012027 | 0.062284 | 0.064971 | 0.0023349 | 0.00092498 | -0.00095273 | -0.032379 | 0.0018179 | 0.064926 | 0.073531 | 0.0001794 | 0.00090142 | -0.00011754 | -0.41657 | 63.2355 | -60.3241 | 62.8784 | -59.9716 | -60.2737 | -0.37079 | -0.21973 | 63.2355 | -60.1135 | 63.1668 | -60.0266 | -60.141 | -59.6878 | -0.27924 | 0.073243 | -0.28381 | 0.073242 | 59.6741 | -0.22888 | 59.9533 | 0.050354 | -0.068664 | 0.073243 | 0.004578 | 0.018311 | 0.35706 | -0.09613 | 0.42572 | -0.027466 | 0.35248 | 123.2025 | 0.086975 | 123.2803 | 123.5596 | 123.349 | 123.2803 | 123.2803 | -123.4863 | -123.2758 | 122.9233 | 123.2117 | 59.6283 | 59.8251
828.4844 | 123.2666 | -60.0357 | 63.1485 | -0.057678 | 0.00056187 | 0.06143 | 0.06369 | -0.00044226 | 0.00028418 | 0.0020379 | 0.0011902 | 0.0024589 | 0.067063 | 0.061568 | -0.0004614 | 0.00026062 | -0.0026809 | -0.4303 | 63.2401 | -60.2692 | 62.8601 | -59.9533 | -60.2875 | -0.35706 | -0.2243 | 63.2446 | -60.1181 | 63.002 | -59.9762 | -60.2234 | -59.7244 | -0.23346 | 0.091552 | -0.28839 | 0.082398 | 59.6786 | -0.25177 | 59.9121 | -0.018311 | -0.082397 | 0.09613 | -0.14648 | 0.05951 | 0.31128 | -0.18768 | 0.39368 | -0.10529 | 0.31586 | 123.1293 | 0.14191 | 123.1201 | 123.5092 | 123.3627 | 123.2758 | 123.2803 | -123.4177 | -123.2666 | 122.8958 | 123.0377 | 59.6054 | 59.8114
829.5469 | 123.4177 | -59.9945 | 63.0844 | -0.072937 | -0.0020017 | 0.061643 | 0.062194 | 0.0023349 | -0.00014322 | -0.0011663 | 0.05307 | 0.00032248 | 0.066849 | 0.057723 | 0.0006066 | -0.0018756 | 0.0028733 | -0.42572 | 63.2172 | -60.2921 | 62.9791 | -59.8434 | -60.173 | -0.29755 | -0.12817 | 63.1668 | -60.0998 | 63.2446 | -59.9075 | -59.9991 | -59.5779 | -0.29755 | 0.13275 | -0.10529 | 0.15106 | 59.697 | -0.17853 | 59.9945 | 0.11902 | -0.10529 | 0.082397 | 0.16022 | 0.086975 | 0.41656 | -0.004577 | 0.52185 | 0.10071 | 0.44861 | 123.2712 | 0.19226 | 123.3444 | 123.5092 | 123.2666 | 123.2117 | 123.1613 | -123.3765 | -123.1842 | 122.9736 | 123.2391 | 59.5688 | 59.8663
830.4844 | 123.2574 | -60.0082 | 63.1348 | -0.0042723 | -0.00071993 | 0.063779 | 0.065612 | 0.00019874 | -0.0029202 | -0.0011663 | -0.014069 | -0.00074552 | 0.065781 | 0.056441 | -0.0017432 | -0.0023028 | -0.0037491 | -0.39368 | 63.2355 | -60.2921 | 62.9288 | -59.9213 | -60.2463 | -0.33875 | -0.19684 | 63.2126 | -60.0861 | 63.121 | -60.0403 | -60.1364 | -59.6924 | -0.28381 | 0.10071 | -0.20599 | 0.086975 | 59.6695 | -0.23804 | 59.9533 | 0.045776 | -0.07782 | 0.077819 | -0.013733 | -0.032043 | 0.31586 | -0.12817 | 0.39368 | -0.050354 | 0.37079 | 123.2208 | 0.045777 | 123.2071 | 123.5275 | 123.2986 | 123.2437 | 123.2208 | -123.4268 | -123.2208 | 122.937 | 123.1293 | 59.6146 | 59.8114
831.4844 | 123.3032 | -60.0311 | 63.1256 | 0.026245 | 0.00056187 | 0.063779 | 0.065826 | 0.0019077 | 7.0582e-05 | -0.0018073 | -0.090363 | 0.0013907 | 0.066849 | 0.072036 | -0.0021704 | -0.001662 | -0.0024673 | -0.4303 | 63.2263 | -60.3149 | 62.9242 | -59.9258 | -60.2783 | -0.40283 | -0.25177 | 63.2172 | -60.1044 | 63.1531 | -60.0403 | -60.1501 | -59.6832 | -0.28381 | 0.10071 | -0.20142 | 0.10529 | 59.6283 | -0.24719 | 59.9121 | 0.036621 | -0.073242 | 0.091553 | 0.027466 | -0.009155 | 0.3479 | -0.11902 | 0.42114 | -0.045776 | 0.3891 | 123.2391 | 0.064087 | 123.2574 | 123.5413 | 123.3215 | 123.2574 | 123.2483 | -123.4406 | -123.23 | 122.9553 | 123.1842 | 59.6008 | 59.7794
832.5469 | 123.3536 | -60.0266 | 63.1073 | -0.065308 | 0.0024845 | 0.062925 | 0.064758 | -0.0010831 | 7.0582e-05 | -0.0018073 | 0.019501 | 0.00074988 | 0.066422 | 0.064345 | -0.0021704 | -0.0023028 | -0.0011855 | -0.52185 | 63.176 | -60.3012 | 62.9059 | -59.9213 | -60.2646 | -0.42572 | -0.31586 | 63.1577 | -60.1181 | 63.1668 | -59.9945 | -60.1227 | -59.6558 | -0.27466 | 0.068664 | -0.20142 | 0.10529 | 59.6008 | -0.23804 | 59.8755 | 0.036621 | -0.091553 | 0.050354 | 0.059509 | 0.032043 | 0.37079 | -0.096131 | 0.46234 | -0.004578 | 0.37994 | 123.2071 | 0.1236 | 123.2849 | 123.4772 | 123.2758 | 123.2025 | 123.1842 | -123.4085 | -123.2254 | 122.9324 | 123.1934 | 59.5047 | 59.7107
833.4844 | 123.3032 | -60.0311 | 63.1302 | -0.0042723 | 0.00056187 | 0.062925 | 0.065612 | -0.00044226 | -0.00099762 | -0.0011663 | -0.053741 | 0.00074988 | 0.066635 | 0.068191 | -0.0004614 | -0.00059378 | 0.0024461 | -0.58594 | 63.2538 | -60.3195 | 62.8601 | -59.9396 | -60.2875 | -0.3891 | -0.27466 | 63.2263 | -60.1227 | 63.1302 | -60.0494 | -60.1364 | -59.6786 | -0.28839 | 0.1236 | -0.27008 | 0.091553 | 59.642 | -0.25635 | 59.9304 | 0.032043 | -0.091553 | 0.09613 | 0 | -0.01831 | 0.35248 | -0.10529 | 0.44403 | -0.013733 | 0.37994 | 123.1796 | 0.073243 | 123.2529 | 123.5733 | 123.349 | 123.2849 | 123.2574 | -123.4497 | -123.2529 | 122.8912 | 123.1613 | 59.4452 | 59.7565
834.4844 | 123.2666 | -60.0266 | 63.1622 | -0.019531 | 0.00098907 | 0.061216 | 0.064971 | 0.0010531 | -0.0012112 | -0.0013799 | -0.0018616 | -0.00053192 | 0.070694 | 0.064559 | -0.0034522 | 0.00090142 | -0.00054474 | -0.46692 | 63.2446 | -60.3012 | 62.8693 | -59.9442 | -60.2829 | -0.37079 | -0.25177 | 63.2172 | -60.1089 | 63.1302 | -60.0403 | -60.1593 | -59.7107 | -0.27466 | 0.082398 | -0.29297 | 0.082397 | 59.6558 | -0.25635 | 59.9304 | 0.01831 | -0.082398 | 0.054932 | -0.032043 | -0.013733 | 0.31586 | -0.13275 | 0.39825 | -0.050354 | 0.35706 | 123.1705 | 0.068665 | 123.2391 | 123.5458 | 123.3261 | 123.2712 | 123.2437 | -123.4634 | -123.2712 | 122.8958 | 123.1567 | 59.5596 | 59.7748
835.4844 | 123.317 | -60.0357 | 63.1485 | -0.011902 | 0.00013467 | 0.063779 | 0.066253 | -0.0010831 | 0.00071138 | -0.0011663 | -0.053741 | 0.0011771 | 0.068344 | 0.066268 | 0.001034 | -0.0012348 | 0.00095066 | -0.45776 | 63.2492 | -60.3058 | 62.915 | -59.9213 | -60.2371 | -0.40741 | -0.22888 | 63.2309 | -60.1044 | 63.1851 | -59.9991 | -60.1364 | -59.6603 | -0.27008 | 0.10071 | -0.23346 | 0.11444 | 59.6283 | -0.20142 | 59.8984 | 0.068664 | -0.068664 | 0.082397 | 0.036621 | 0.036622 | 0.37537 | -0.10071 | 0.44403 | -0.032044 | 0.38452 | 123.2208 | 0.10529 | 123.2895 | 123.555 | 123.3353 | 123.2849 | 123.2666 | -123.4543 | -123.2529 | 122.9507 | 123.2208 | 59.5779 | 59.8068
836.5469 | 123.3902 | -60.0174 | 63.1073 | -0.080566 | 0.00098907 | 0.062498 | 0.064331 | -0.0025785 | 0.00092498 | -0.0013799 | 0.056122 | -0.0011727 | 0.064286 | 0.063277 | -0.0019568 | -0.0010212 | -0.00033114 | -0.48523 | 63.1851 | -60.2829 | 62.9654 | -59.8297 | -60.1913 | -0.35248 | -0.23346 | 63.1668 | -60.0769 | 63.2217 | -59.9121 | -60.0266 | -59.6054 | -0.2655 | 0.07782 | -0.14191 | 0.18768 | 59.6649 | -0.17395 | 59.9304 | 0.091553 | -0.059509 | 0.059509 | 0.11444 | 0.10529 | 0.41199 | -0.009155 | 0.4715 | 0.050354 | 0.45319 | 123.2483 | 0.16479 | 123.2986 | 123.468 | 123.2437 | 123.2025 | 123.1842 | -123.3902 | -123.1842 | 122.9828 | 123.2391 | 59.5322 | 59.7839
837.4844 | 123.3124 | -60.0174 | 63.1622 | -0.027161 | -0.00050633 | 0.063566 | 0.065612 | 0.0010531 | 0.00028418 | 0.0022517 | -0.05069 | 0.0018179 | 0.067917 | 0.063705 | -0.0036658 | -0.0014484 | -0.0020401 | -0.47607 | 63.2584 | -60.3104 | 62.9059 | -59.9396 | -60.2554 | -0.40741 | -0.25177 | 63.2446 | -60.1135 | 63.1622 | -59.9991 | -60.1318 | -59.6649 | -0.29297 | 0.096131 | -0.25635 | 0.07782 | 59.61 | -0.23804 | 59.903 | 0.054932 | -0.09613 | 0.082398 | 0 | 0.018311 | 0.35248 | -0.11444 | 0.44861 | -0.018311 | 0.37079 | 123.2162 | 0.11444 | 123.2758 | 123.5687 | 123.3582 | 123.2758 | 123.262 | -123.4726 | -123.2758 | 122.9233 | 123.1796 | 59.5413 | 59.7656
838.5469 | 123.3765 | -60.0082 | 63.089 | -0.019531 | 0.0012027 | 0.062711 | 0.064544 | -0.0015103 | -0.0020658 | 0.00011527 | 0.025604 | -0.0011727 | 0.069412 | 0.061782 | 0.000393 | 0.00068782 | 0.0015915 | -0.53558 | 63.1943 | -60.3058 | 62.9242 | -59.9167 | -60.2692 | -0.40283 | -0.41657 | 63.1897 | -60.0861 | 63.1668 | -59.9945 | -60.0906 | -59.6558 | -0.29755 | 0.10529 | -0.16479 | 0.091553 | 59.6054 | -0.26093 | 59.903 | 0.036621 | -0.07782 | 0.10071 | 0.07782 | 0.013733 | 0.35248 | -0.082397 | 0.4303 | -0.004577 | 0.3891 | 123.23 | 0.091553 | 123.2529 | 123.5001 | 123.2758 | 123.2025 | 123.1979 | -123.3948 | -123.175 | 122.9324 | 123.175 | 59.4727 | 59.5917
839.4844 | 123.3353 | -60.0082 | 63.1302 | 0.010986 | 0.00034827 | 0.063779 | 0.066467 | 0.00019874 | 0.0022068 | 0.00032907 | -0.053741 | 0.00032248 | 0.063431 | 0.064773 | -0.0015296 | 4.7018e-05 | 0.00095066 | -0.48981 | 63.2538 | -60.2966 | 62.9059 | -59.935 | -60.2737 | -0.41199 | -0.28381 | 63.2401 | -60.1089 | 63.1668 | -60.0174 | -60.1181 | -59.6603 | -0.28839 | 0.1236 | -0.2243 | 0.073242 | 59.5963 | -0.2655 | 59.8846 | 0.022888 | -0.10071 | 0.10986 | 0.036621 | -0.009155 | 0.3479 | -0.10986 | 0.44861 | -0.009155 | 0.36163 | 123.2025 | 0.091553 | 123.2758 | 123.5504 | 123.349 | 123.262 | 123.2483 | -123.4268 | -123.2391 | 122.9141 | 123.175 | 59.5184 | 59.7244
840.5469 | 123.2941 | -60.0174 | 63.1485 | -0.072937 | 0.00056187 | 0.06442 | 0.064971 | -1.486e-05 | -0.0012112 | -0.0030889 | 0.013397 | -0.00031832 | 0.066422 | 0.065627 | -0.0015296 | -0.00080758 | -0.0018265 | -0.45319 | 63.2355 | -60.2692 | 62.9471 | -59.848 | -60.2051 | -0.33875 | -0.21057 | 63.2355 | -60.0998 | 63.1805 | -59.9991 | -60.1044 | -59.6649 | -0.25177 | 0.086975 | -0.20142 | 0.16937 | 59.6786 | -0.18768 | 59.9304 | 0.064087 | -0.082397 | 0.086975 | 0.032043 | 0.018311 | 0.35248 | -0.086975 | 0.43487 | -0.004578 | 0.42114 | 123.2162 | 0.10071 | 123.2803 | 123.5046 | 123.3353 | 123.2529 | 123.2529 | -123.4177 | -123.2483 | 122.9645 | 123.1979 | 59.5642 | 59.8068
841.4844 | 123.317 | -59.9991 | 63.1165 | -0.057678 | 0.0024845 | 0.063566 | 0.065185 | 0.0036165 | 0.0013522 | -0.0020209 | -0.069 | 0.0018179 | 0.064499 | 0.066909 | -0.0028112 | 4.7018e-05 | -0.0022537 | -0.48981 | 63.2492 | -60.3058 | 62.9288 | -59.9121 | -60.2692 | -0.4303 | -0.25635 | 63.2217 | -60.0998 | 63.1714 | -60.0357 | -60.1318 | -59.6741 | -0.3067 | 0.13275 | -0.18768 | 0.086975 | 59.5688 | -0.27008 | 59.8755 | 0.036621 | -0.10071 | 0.10529 | 0.054932 | -0.036622 | 0.32501 | -0.13275 | 0.42572 | -0.032044 | 0.39368 | 123.2346 | 0.064086 | 123.2712 | 123.555 | 123.3215 | 123.2483 | 123.2208 | -123.4222 | -123.2162 | 122.9279 | 123.1705 | 59.5093 | 59.7427
842.5469 | 123.3124 | -60.0266 | 63.1439 | -0.065308 | 0.00077547 | 0.062284 | 0.064758 | -0.00044226 | -0.0016384 | 0.00075627 | 0.037811 | 0.00096348 | 0.066422 | 0.058364 | -0.0017432 | -0.0035846 | 9.6064e-05 | -0.46692 | 63.1897 | -60.26 | 62.9654 | -59.8389 | -60.1868 | -0.34332 | -0.2243 | 63.2172 | -60.0769 | 63.1714 | -59.9899 | -60.0769 | -59.6558 | -0.23346 | 0.045776 | -0.17853 | 0.18768 | 59.6832 | -0.16022 | 59.9167 | 0.073242 | -0.050354 | 0.073242 | 0.027466 | 0.036621 | 0.37079 | -0.050354 | 0.42114 | 0 | 0.42114 | 123.2254 | 0.086975 | 123.2483 | 123.4497 | 123.2941 | 123.2162 | 123.2437 | -123.4039 | -123.2208 | 122.9919 | 123.1979 | 59.5596 | 59.8022
843.4844 | 123.3078 | -60.0266 | 63.1439 | -0.042419 | 0.0018435 | 0.063566 | 0.067535 | 0.00041234 | 0.0013522 | -0.0022345 | -0.035431 | 0.0028861 | 0.066208 | 0.071609 | -0.0008886 | 0.00068782 | -0.0013991 | -0.50812 | 63.208 | -60.2966 | 62.8967 | -59.903 | -60.466 | -0.50354 | -0.28839 | 63.2034 | -60.0952 | 63.176 | -60.0311 | -60.1318 | -59.6603 | -0.27008 | 0.064087 | -0.24719 | 0.1236 | 59.523 | -0.43945 | 59.7931 | -0.16937 | -0.068665 | 0.059509 | 0.032043 | -0.004578 | 0.36621 | -0.10529 | 0.43488 | -0.036621 | 0.39368 | 123.1934 | 0.064087 | 123.2712 | 123.5046 | 123.2986 | 123.2346 | 123.23 | -123.4406 | -123.2391 | 122.9233 | 123.2025 | 59.5184 | 59.7382
844.5469 | 123.3353 | -59.9899 | 63.0844 | -0.072937 | 0.0022709 | 0.063993 | 0.063049 | 0.0034029 | -0.0022794 | -9.8328e-05 | 0.013397 | -0.00031832 | 0.065781 | 0.063277 | -0.0008886 | -0.0010212 | 0.00073706 | -0.57678 | 63.176 | -60.2737 | 62.9013 | -59.9121 | -60.2829 | -0.48523 | -0.39825 | 63.1622 | -60.1089 | 63.1668 | -60.0037 | -60.1044 | -59.6558 | -0.28381 | 0.091552 | -0.18311 | 0.07782 | 59.5047 | -0.29297 | 59.7885 | -0.009155 | -0.11902 | 0.077819 | 0.082397 | -0.013733 | 0.33417 | -0.11444 | 0.45319 | 0.004578 | 0.36163 | 123.175 | 0.10529 | 123.2758 | 123.4497 | 123.2712 | 123.1659 | 123.1522 | -123.3582 | -123.1934 | 122.8912 | 123.1567 | 59.4131 | 59.5917
845.4844 | 123.2849 | -60.022 | 63.1393 | -0.03479 | 0.0012027 | 0.065061 | 0.067962 | 0.00041234 | -0.00014322 | 0.00096987 | -0.035431 | 0.0020315 | 0.067917 | 0.068831 | -0.0025976 | -0.00016658 | 0.00073706 | -0.5127 | 63.2217 | -60.3058 | 62.9105 | -59.9121 | -60.5026 | -0.53101 | -0.31128 | 63.2263 | -60.0998 | 63.1531 | -60.0311 | -60.1364 | -59.6603 | -0.28381 | 0.082398 | -0.22888 | 0.10986 | 59.491 | -0.48065 | 59.7748 | -0.19684 | -0.077819 | 0.086975 | 0.013733 | -0.009155 | 0.36163 | -0.11444 | 0.43945 | -0.036622 | 0.39368 | 123.2162 | 0.068664 | 123.2529 | 123.5275 | 123.3261 | 123.2437 | 123.2483 | -123.4451 | -123.2391 | 122.9324 | 123.175 | 59.5093 | 59.7107
846.4844 | 123.262 | -60.0311 | 63.1531 | -0.0042723 | -7.913e-05 | 0.062925 | 0.06369 | 0.0014803 | -0.00078402 | -0.00095273 | -0.014069 | -0.00010472 | 0.069199 | 0.061355 | 0.0006066 | 0.00026062 | 9.6064e-05 | -0.54016 | 63.2721 | -60.2737 | 62.8784 | -59.9396 | -60.2875 | -0.4303 | -0.3479 | 63.2446 | -60.0861 | 63.0524 | -60.0037 | -60.2142 | -59.7153 | -0.24262 | 0.11902 | -0.27466 | 0.091553 | 59.6008 | -0.25635 | 59.8434 | -0.013733 | -0.054932 | 0.091553 | -0.10071 | 0.027466 | 0.31586 | -0.1831 | 0.37079 | -0.12817 | 0.33417 | 123.1522 | 0.082398 | 123.1384 | 123.5458 | 123.3307 | 123.3032 | 123.2758 | -123.4268 | -123.2391 | 122.9095 | 123.0835 | 59.491 | 59.6832
847.5469 | 123.3353 | -60.022 | 63.1119 | -0.019531 | -0.00071993 | 0.062711 | 0.061767 | 0.00062594 | -0.0012112 | -0.00031193 | 0.028656 | -0.0016001 | 0.068344 | 0.062209 | -0.000675 | -0.0052936 | -0.0026809 | -0.57678 | 63.1989 | -60.2737 | 62.9196 | -59.903 | -60.2554 | -0.48523 | -0.40283 | 63.1851 | -60.1089 | 63.2355 | -59.9442 | -60.1593 | -59.6283 | -0.25177 | 0.086976 | -0.19226 | 0.11902 | 59.5367 | -0.23346 | 59.7885 | 0.018311 | -0.086975 | 0.073243 | 0.1236 | 0.07782 | 0.39368 | -0.13733 | 0.48065 | -0.050354 | 0.37079 | 123.1934 | 0.16479 | 123.3444 | 123.4726 | 123.2941 | 123.2208 | 123.2071 | -123.3856 | -123.2208 | 122.9416 | 123.2574 | 59.4452 | 59.6191
848.4844 | 123.2712 | -59.9899 | 63.1439 | -0.019531 | 0.00098907 | 0.063352 | 0.065826 | 0.00062594 | 7.0582e-05 | -0.00095273 | -0.075104 | 0.00053628 | 0.068558 | 0.067763 | -0.0025976 | 0.00068782 | -0.0018265 | -0.52185 | 63.2263 | -60.2829 | 62.883 | -59.9396 | -60.3973 | -0.49439 | -0.31128 | 63.208 | -60.0815 | 63.1531 | -60.0311 | -60.1318 | -59.6695 | -0.29297 | 0.082397 | -0.26093 | 0.050354 | 59.4955 | -0.40741 | 59.7885 | -0.11444 | -0.091553 | 0.064087 | 0.009155 | -0.041199 | 0.32043 | -0.14191 | 0.41199 | -0.050354 | 0.34332 | 123.1659 | 0.050354 | 123.2346 | 123.5092 | 123.2895 | 123.2162 | 123.1979 | -123.4268 | -123.2254 | 122.8729 | 123.143 | 59.4681 | 59.6786
849.5469 | 123.317 | -60.022 | 63.1485 | 0.0033567 | 0.00056187 | 0.062711 | 0.064117 | 0.0023349 | 0.00071138 | 0.00032907 | -0.038483 | 0.0022453 | 0.066422 | 0.071609 | -0.0028112 | -0.00080758 | -0.00054474 | -0.52643 | 63.2263 | -60.2829 | 62.8967 | -59.9121 | -60.2463 | -0.44861 | -0.32959 | 63.208 | -60.1089 | 63.176 | -60.0174 | -60.1181 | -59.6512 | -0.26093 | 0.077819 | -0.25177 | 0.10986 | 59.5734 | -0.2243 | 59.8343 | 0.036621 | -0.086975 | 0.059509 | 0.027465 | 0.004578 | 0.37079 | -0.09613 | 0.45776 | -0.009155 | 0.37079 | 123.1796 | 0.091553 | 123.2849 | 123.5092 | 123.317 | 123.2483 | 123.23 | -123.4314 | -123.2574 | 122.9187 | 123.1979 | 59.4955 | 59.6924
850.4844 | 123.3032 | -59.9991 | 63.1485 | -0.050049 | 0.00013467 | 0.06207 | 0.06604 | -0.00022866 | -0.001852 | -0.0018073 | -0.041534 | 0.00010888 | 0.065567 | 0.06285 | -0.0028112 | -0.00059378 | -0.00033114 | -0.53558 | 63.2675 | -60.2737 | 62.8922 | -59.9442 | -60.2417 | -0.44861 | -0.35248 | 63.2263 | -60.1089 | 63.176 | -59.9899 | -60.1181 | -59.6649 | -0.27466 | 0.11902 | -0.25635 | 0.054931 | 59.5505 | -0.24261 | 59.8251 | 0.032044 | -0.10986 | 0.077819 | 0.027465 | 0.009155 | 0.33417 | -0.11902 | 0.44403 | -0.009155 | 0.32959 | 123.1659 | 0.11902 | 123.2849 | 123.5413 | 123.3353 | 123.2666 | 123.2254 | -123.4222 | -123.2574 | 122.8912 | 123.175 | 59.4635 | 59.6466
851.4844 | 123.2483 | -60.0494 | 63.1027 | -0.03479 | 0.0012027 | 0.062498 | 0.06604 | -0.00065586 | -0.00035682 | 0.0028925 | -0.099518 | 0.00010888 | 0.066849 | 0.070327 | -0.0021704 | -0.00038018 | -0.0041763 | -0.63629 | 63.2172 | -60.3333 | 62.8326 | -60.0449 | -60.3928 | -0.60425 | -0.54016 | 63.2217 | -60.1364 | 63.1027 | -60.1089 | -60.2188 | -59.729 | -0.28381 | 0.11444 | -0.27008 | 0.004577 | 59.4452 | -0.34332 | 59.729 | -0.059509 | -0.086976 | 0.11902 | 0 | -0.05951 | 0.32043 | -0.16937 | 0.40741 | -0.082397 | 0.28839 | 123.1659 | 0.027466 | 123.2391 | 123.5504 | 123.3582 | 123.2666 | 123.2712 | -123.436 | -123.2391 | 122.8821 | 123.1522 | 59.4131 | 59.5093
852.4844 | 123.317 | -60.0128 | 63.1531 | -0.027161 | 0.00013467 | 0.063779 | 0.066467 | 0.0034029 | -0.00078402 | 0.0013971 | -0.053741 | -0.00010472 | 0.065781 | 0.065627 | -0.0032386 | 0.0013288 | 0.0015915 | -0.53558 | 63.2492 | -60.2692 | 62.915 | -59.8892 | -60.2509 | -0.48065 | -0.3479 | 63.2172 | -60.1044 | 63.1805 | -60.0266 | -60.1318 | -59.6558 | -0.25635 | 0.096131 | -0.23804 | 0.1236 | 59.5322 | -0.23804 | 59.7885 | 0.018311 | -0.091553 | 0.064087 | 0.027466 | -0.013733 | 0.35705 | -0.11902 | 0.44861 | -0.027466 | 0.37994 | 123.1842 | 0.07782 | 123.2849 | 123.5184 | 123.3215 | 123.262 | 123.23 | -123.4222 | -123.2574 | 122.9279 | 123.1934 | 59.4772 | 59.6649
853.5469 | 123.2574 | -59.9991 | 63.1851 | -0.011902 | -7.913e-05 | 0.063779 | 0.063476 | 0.0012667 | 0.00092498 | -0.00095273 | -0.0018616 | 0.00096348 | 0.06749 | 0.060927 | -0.0004614 | -0.001662 | 0.0018051 | -0.57678 | 63.2538 | -60.2554 | 62.8876 | -59.935 | -60.2737 | -0.45776 | -0.37079 | 63.2446 | -60.0906 | 63.1256 | -60.0357 | -60.1318 | -59.6832 | -0.25635 | 0.068664 | -0.29755 | 0.064086 | 59.5413 | -0.27466 | 59.7977 | -0.018311 | -0.091553 | 0.059509 | -0.05951 | -0.036622 | 0.31586 | -0.13275 | 0.40741 | -0.041199 | 0.32043 | 123.143 | 0.054931 | 123.2162 | 123.5092 | 123.3353 | 123.2529 | 123.2437 | -123.4406 | -123.2758 | 122.8867 | 123.1247 | 59.4223 | 59.6283
854.4844 | 123.3215 | -60.0403 | 63.1577 | 0.0033567 | 0.00077547 | 0.063566 | 0.065826 | -1.486e-05 | -0.00099762 | -0.0015935 | -0.032379 | 0.0013907 | 0.06749 | 0.068404 | -0.003025 | -0.0010212 | 0.0018051 | -0.54474 | 63.208 | -60.3012 | 62.915 | -59.9167 | -60.2509 | -0.48523 | -0.3479 | 63.1943 | -60.0952 | 63.1805 | -60.0174 | -60.1273 | -59.6649 | -0.26093 | 0.050354 | -0.24262 | 0.1236 | 59.5551 | -0.21057 | 59.816 | 0.050354 | -0.054932 | 0.036621 | 0.022888 | 0.022888 | 0.37537 | -0.086975 | 0.4303 | -0.032043 | 0.38452 | 123.2162 | 0.07782 | 123.2758 | 123.5092 | 123.2895 | 123.2483 | 123.2346 | -123.4589 | -123.2529 | 122.9553 | 123.2208 | 59.4955 | 59.6924
855.5469 | 123.2849 | -59.9991 | 63.1622 | -0.072937 | 0.00034827 | 0.061857 | 0.064331 | -0.0025785 | 0.00028418 | -0.00095273 | -0.011017 | 0.00074988 | 0.066422 | 0.063918 | -0.0017432 | -0.00016658 | -0.0016129 | -0.59052 | 63.2309 | -60.2875 | 62.9059 | -59.9487 | -60.2646 | -0.47607 | -0.40741 | 63.2675 | -60.0723 | 63.1714 | -60.0128 | -60.1273 | -59.6558 | -0.28839 | 0.068665 | -0.25635 | 0.050354 | 59.523 | -0.2655 | 59.8114 | 0.022889 | -0.073243 | 0.10529 | 0.009156 | -0.013733 | 0.34332 | -0.12817 | 0.41656 | -0.054931 | 0.33875 | 123.1934 | 0.05951 | 123.2437 | 123.5184 | 123.3398 | 123.23 | 123.2666 | -123.4497 | -123.2346 | 122.905 | 123.1705 | 59.4086 | 59.5917
856.4844 | 123.2803 | -60.0357 | 63.1531 | -0.042419 | 0.0018435 | 0.063566 | 0.066894 | -1.486e-05 | 0.0032748 | 0.00011527 | -0.059845 | 0.0011771 | 0.067276 | 0.067763 | -0.0017432 | -0.00059378 | 0.0018051 | -0.59052 | 63.2355 | -60.2966 | 62.915 | -59.9075 | -60.2646 | -0.55847 | -0.40741 | 63.2217 | -60.1227 | 63.1256 | -60.0677 | -60.1776 | -59.6878 | -0.26093 | 0.082398 | -0.23804 | 0.12817 | 59.4772 | -0.22888 | 59.7382 | 0.032044 | -0.086975 | 0.068665 | -0.027466 | -0.032043 | 0.3479 | -0.14191 | 0.43488 | -0.054931 | 0.3891 | 123.2117 | 0.054932 | 123.2483 | 123.5321 | 123.3444 | 123.2712 | 123.2574 | -123.4497 | -123.2758 | 122.9507 | 123.1613 | 59.4452 | 59.6283
857.5469 | 123.3353 | -60.0037 | 63.1805 | -0.03479 | 0.0018435 | 0.063138 | 0.06604 | 0.0016939 | 0.00028418 | -0.0024481 | -0.0018616 | 0.00010888 | 0.067276 | 0.064345 | -0.0021704 | 4.7018e-05 | 0.00030966 | -0.55847 | 63.2538 | -60.2417 | 62.9425 | -59.8434 | -60.2097 | -0.48523 | -0.37079 | 63.2263 | -60.0769 | 63.1989 | -59.9854 | -60.0952 | -59.6237 | -0.23804 | 0.073242 | -0.23804 | 0.16022 | 59.5184 | -0.20599 | 59.7565 | 0.032043 | -0.073242 | 0.045776 | 0.018311 | 0.01831 | 0.37994 | -0.091553 | 0.45319 | -0.018311 | 0.39825 | 123.1842 | 0.091552 | 123.2758 | 123.4955 | 123.3032 | 123.2574 | 123.23 | -123.4222 | -123.2574 | 122.9462 | 123.2025 | 59.4452 | 59.6329
858.4844 | 123.2803 | -60.0128 | 63.1393 | -0.072937 | 0.011243 | 0.063993 | 0.053863 | 0.0036165 | -0.0012112 | 0.00011527 | -0.023224 | 0.0026725 | 0.066422 | 0.060927 | -0.0002478 | 0.00026062 | -0.0020401 | -0.59509 | 63.2584 | -60.2875 | 62.9242 | -59.903 | -60.2692 | -0.55389 | -0.4715 | 63.2401 | -60.0906 | 63.1393 | -60.0357 | -60.1456 | -59.6878 | -0.27466 | 0.11902 | -0.21515 | 0.10986 | 59.4589 | -0.25635 | 59.7336 | 0.018311 | -0.07782 | 0.10071 | 0 | -0.022889 | 0.32501 | -0.13275 | 0.40283 | -0.054932 | 0.38452 | 123.2117 | 0.054931 | 123.23 | 123.5458 | 123.3307 | 123.2712 | 123.2529 | -123.4268 | -123.23 | 122.937 | 123.1522 | 59.4177 | 59.5413
859.4844 | 123.2574 | -60.0082 | 63.1439 | -0.072937 | 0.011457 | 0.063779 | 0.059417 | 0.0010531 | 0.0017794 | -9.8328e-05 | -0.023224 | 0.0035269 | 0.064713 | 0.070327 | -0.0028112 | -0.0010212 | -0.00054474 | -0.6958 | 63.2401 | -60.3058 | 62.8464 | -59.967 | -60.3424 | -0.65918 | -0.83771 | 63.1577 | -60.1181 | 63.1119 | -60.0311 | -60.173 | -59.6924 | -0.29755 | 0.09613 | -0.29755 | 0.041199 | 59.3491 | -0.33417 | 59.6466 | -0.036621 | -0.10986 | 0.013733 | -0.032044 | -0.022888 | 0.31586 | -0.16479 | 0.42572 | -0.054932 | 0.33874 | 123.1522 | 0.086975 | 123.23 | 123.5458 | 123.2758 | 123.2483 | 123.1659 | -123.4497 | -123.262 | 122.8546 | 123.1201 | 59.3124 | 59.1705
860.5469 | 123.3261 | -59.9762 | 63.1851 | -0.065308 | 0.011884 | 0.063566 | 0.055572 | -0.0019377 | -0.0022794 | 0.0026789 | -0.026276 | 0.0016043 | 0.069412 | 0.069472 | -0.0028112 | -0.00016658 | 0.0045823 | -0.6134 | 63.3041 | -60.26 | 62.9242 | -59.967 | -60.173 | -0.52185 | -0.4303 | 63.2584 | -60.0586 | 63.2126 | -59.9899 | -60.0815 | -59.6329 | -0.28381 | 0.11902 | -0.26093 | 0.009155 | 59.4543 | -0.19684 | 59.7382 | 0.086975 | -0.082398 | 0.073242 | 0.027465 | -0.013733 | 0.34332 | -0.10529 | 0.42572 | -0.022888 | 0.29297 | 123.1842 | 0.068665 | 123.2712 | 123.5641 | 123.317 | 123.2803 | 123.2346 | -123.4451 | -123.2437 | 122.9004 | 123.1888 | 59.3628 | 59.5459
861.4844 | 123.2849 | -60.0449 | 63.1073 | -0.080566 | 0.022138 | 0.06143 | 0.04425 | -0.0015103 | -0.0012112 | -0.0030889 | 0.004242 | 0.00010888 | 0.067063 | 0.061141 | -0.002384 | -0.0014484 | 0.0030869 | -0.71869 | 63.2263 | -60.3058 | 62.8555 | -59.9991 | -60.4156 | -0.94757 | -0.52185 | 63.2034 | -60.1135 | 63.1302 | -60.1135 | -60.1822 | -59.6878 | -0.26093 | 0.11902 | -0.25177 | 0.045777 | 59.0973 | -0.37079 | 59.3582 | -0.10986 | -0.068664 | 0.09613 | 0.022888 | -0.068664 | 0.35706 | -0.13733 | 0.42572 | -0.068665 | 0.3067 | 123.1613 | 0 | 123.2437 | 123.5321 | 123.317 | 123.2712 | 123.2483 | -123.4131 | -123.2208 | 122.9004 | 123.175 | 59.3262 | 59.523
862.4844 | 123.2895 | -59.9945 | 63.1805 | -0.050049 | 0.024488 | 0.062498 | 0.03955 | 0.0023349 | -0.00057042 | 0.00032907 | -0.047638 | -0.00031832 | 0.067917 | 0.064986 | -0.001316 | 0.00068782 | 0.0039413 | -0.64087 | 63.295 | -60.2554 | 62.9013 | -59.903 | -60.2646 | -0.6134 | -0.51727 | 63.2492 | -60.0906 | 63.1577 | -60.0357 | -60.1456 | -59.6786 | -0.26093 | 0.11444 | -0.27924 | 0.091553 | 59.3811 | -0.27008 | 59.642 | -0.009155 | -0.09613 | 0.068665 | -0.022888 | -0.041199 | 0.31586 | -0.15106 | 0.41199 | -0.054932 | 0.35248 | 123.1567 | 0.054931 | 123.2483 | 123.5504 | 123.3398 | 123.2895 | 123.2437 | -123.436 | -123.2712 | 122.8958 | 123.1522 | 59.3536 | 59.4772
863.4844 | 123.2437 | -60.9741 | 62.146 | -0.81299 | 0.82728 | 0.06207 | 0.0030207 | 0.0031893 | 0.76505 | 0.0065241 | -0.084259 | 0.0018179 | 0.068131 | 0.056441 | -0.0017432 | -0.0012348 | 0.0022323 | -0.086975 | 62.1826 | -61.1847 | 61.6562 | -61.1435 | 61.9308 | -0.091553 | -0.53101 | 62.2513 | -61.0474 | 62.1323 | -61.0153 | -61.1481 | -60.6491 | -0.21057 | 0.036621 | -0.48981 | -0.16937 | 60.8826 | 122.905 | 61.0931 | 123.1155 | -0.073242 | 0.10529 | -0.013733 | -0.041199 | 0.32501 | -0.17395 | 0.39825 | -0.10071 | 0.041198 | 122.8409 | 0.032043 | 123.1796 | 123.3673 | 123.2986 | 123.1567 | 123.2254 | -123.3307 | -123.1934 | 122.6303 | 123.1064 | 60.8871 | 60.4431
864.4844 | 123.2025 | -60.9283 | 62.1597 | -0.85114 | 0.82429 | 0.06442 | 0.0032343 | 0.0027621 | 0.76292 | 0.0039607 | -0.032379 | 0.0028861 | 0.068985 | 0.070113 | -0.0025976 | -0.0012348 | -0.00075834 | -0.013733 | 62.178 | -61.1206 | 61.7752 | -60.7727 | 61.7752 | -0.21515 | -0.53101 | 62.2604 | -61.0153 | 62.1735 | -60.9467 | -61.0886 | -60.5896 | -0.19226 | 0.018311 | -0.38452 | 0.15564 | 60.7132 | 122.7036 | 60.9055 | 122.8958 | -0.086975 | 0.10071 | 0.013733 | -0.01831 | 0.33875 | -0.16022 | 0.42572 | -0.073242 | 0.3479 | 122.8958 | 0.068665 | 123.1888 | 123.2986 | 123.2758 | 123.1064 | 123.1888 | -123.2803 | -123.175 | 122.7036 | 123.1018 | 60.9146 | 60.3973
865.5469 | 123.1842 | -60.9558 | 62.146 | -0.80536 | 0.82152 | 0.062498 | 0.0013117 | 0.0010531 | 0.7563 | 0.00011527 | -0.035431 | 0.0026725 | 0.06749 | 0.0652 | -0.0002478 | -0.0020892 | -0.00075834 | -0.050354 | 62.1323 | -61.1298 | 61.734 | -60.8093 | 61.7477 | -0.24261 | -0.58594 | 62.2101 | -61.0291 | 62.0956 | -61.0153 | -61.1023 | -60.6171 | -0.17395 | -0.013733 | -0.41199 | 0.14648 | 60.7132 | 122.7036 | 60.8871 | 122.8775 | -0.073242 | 0.064087 | -0.050354 | -0.059509 | 0.33875 | -0.14648 | 0.41199 | -0.073242 | 0.32044 | 122.8638 | 0.013733 | 123.1247 | 123.262 | 123.2391 | 123.0881 | 123.1659 | -123.2758 | -123.175 | 122.6898 | 123.0515 | 60.9055 | 60.3699
866.4844 | 123.2071 | -60.8139 | 62.2284 | -0.80536 | 0.81917 | 0.063993 | -0.00039728 | -0.00086946 | 0.75266 | 0.0035333 | -0.01712 | 0.0013907 | 0.068985 | 0.0652 | -3.4196e-05 | -0.0018756 | 0.0011643 | -0.086975 | 62.2742 | -61.0016 | 61.8347 | -60.6491 | 61.9904 | -0.27008 | -0.60883 | 62.3199 | -60.8643 | 62.2375 | -60.8459 | -60.9741 | -60.4477 | -0.18768 | 0.045776 | -0.39368 | 0.16479 | 60.5438 | 122.8043 | 60.7315 | 122.9919 | -0.050354 | 0.091552 | 0.009155 | -0.032043 | 0.36621 | -0.16022 | 0.41656 | -0.10986 | 0.35248 | 122.8363 | 0.018311 | 123.1018 | 123.2758 | 123.1842 | 123.0881 | 123.1338 | -123.23 | -123.0927 | 122.6486 | 123.0515 | 60.7269 | 60.2051
867.4844 | 123.2391 | -60.8231 | 62.1643 | -0.82062 | 0.81489 | 0.062711 | -0.00018368 | -0.00086946 | 0.7501 | 0.0020379 | 0.0011902 | 0.0016043 | 0.066422 | 0.066268 | -0.002384 | 0.00047422 | 0.00073706 | -0.086975 | 62.2421 | -61.0474 | 61.8301 | -60.6354 | 61.821 | -0.25177 | -0.59967 | 62.2375 | -60.9146 | 62.2604 | -60.791 | -60.9421 | -60.4248 | -0.2243 | 0.077819 | -0.33417 | 0.18768 | 60.5713 | 122.644 | 60.7956 | 122.8683 | -0.091553 | 0.073242 | 0.09613 | 0.032043 | 0.39825 | -0.11902 | 0.48981 | -0.027466 | 0.41199 | 122.8775 | 0.1236 | 123.175 | 123.2895 | 123.1522 | 123.0652 | 123.0606 | -123.2117 | -123.0789 | 122.6532 | 123.0835 | 60.7361 | 60.2234
868.5469 | 123.1705 | -60.8597 | 62.1506 | -0.79773 | 0.81126 | 0.063138 | 0.0030207 | 0.0034029 | 0.7516 | -9.8328e-05 | -0.0018616 | 0.0037405 | 0.065567 | 0.065841 | -0.0015296 | 4.7018e-05 | 0.00030966 | 0.009155 | 62.178 | -61.0748 | 61.7981 | -60.6491 | 61.8301 | -0.21973 | -0.5127 | 62.2513 | -60.9604 | 62.178 | -60.8871 | -61.0153 | -60.5347 | -0.21515 | 0.027466 | -0.35248 | 0.21057 | 60.64 | 122.6898 | 60.8551 | 122.905 | -0.10071 | 0.10071 | 0.027466 | -0.027466 | 0.32501 | -0.15564 | 0.42572 | -0.054932 | 0.42572 | 122.8729 | 0.073242 | 123.1384 | 123.2529 | 123.2117 | 123.0377 | 123.111 | -123.2254 | -123.111 | 122.6578 | 123.0377 | 60.8688 | 60.347
869.4844 | 123.2117 | -60.8688 | 62.0728 | -0.7901 | 0.81041 | 0.063779 | 0.00067072 | 0.0016939 | 0.74732 | 0.0028925 | 0.016449 | 0.0035269 | 0.067276 | 0.063918 | -0.0002478 | -0.0010212 | -0.00033114 | -0.091553 | 62.1323 | -61.0748 | 61.7477 | -60.6995 | 61.7569 | -0.26093 | -0.6134 | 62.1735 | -60.9833 | 62.1872 | -60.8643 | -60.9604 | -60.4385 | -0.20599 | 0.059509 | -0.32501 | 0.16937 | 60.6079 | 122.6257 | 60.8139 | 122.8317 | -0.11444 | 0.10071 | 0.11444 | 0.004577 | 0.4303 | -0.091553 | 0.54474 | 0.022888 | 0.37537 | 122.8226 | 0.11902 | 123.1705 | 123.2071 | 123.1567 | 123.0011 | 123.0423 | -123.1476 | -123.056 | 122.6166 | 123.056 | 60.7773 | 60.2554
870.5469 | 123.175 | -60.6125 | 62.3749 | -0.77484 | 0.80656 | 0.062498 | 0.0023797 | -0.00022866 | 0.74412 | -0.0013799 | -0.014069 | 0.0020315 | 0.068344 | 0.0699 | -0.0021704 | -0.0012348 | -0.0050307 | 0.004578 | 62.3795 | -60.8093 | 62.0316 | -60.3241 | 62.0361 | -0.17395 | -0.47607 | 62.4481 | -60.7086 | 62.4069 | -60.6079 | -60.7269 | -60.26 | -0.19684 | 0.004578 | -0.34332 | 0.28839 | 60.4385 | 122.6486 | 60.6354 | 122.8455 | -0.09613 | 0.073242 | 0.032043 | 0.004578 | 0.35248 | -0.11444 | 0.44861 | -0.018311 | 0.48523 | 122.8409 | 0.10071 | 123.1155 | 123.1888 | 123.1567 | 122.9919 | 123.0606 | -123.1842 | -123.0835 | 122.644 | 123.0194 | 60.6171 | 60.1364
871.4844 | 123.2208 | -60.6949 | 62.2009 | -0.80536 | 0.80549 | 0.063352 | 0.00088432 | 0.0021213 | 0.7422 | -0.0013799 | -0.0018616 | 0.0028861 | 0.068772 | 0.067336 | -0.0011022 | -0.0031574 | 0.00073706 | -0.054932 | 62.2467 | -60.9421 | 61.8713 | -60.5072 | 61.8896 | -0.25177 | -0.60883 | 62.2925 | -60.8276 | 62.3016 | -60.7086 | -60.8093 | -60.3424 | -0.24719 | 0.045776 | -0.32959 | 0.18768 | 60.4431 | 122.5845 | 60.6903 | 122.8317 | -0.13275 | 0.091552 | 0.10071 | -0.013733 | 0.35248 | -0.11444 | 0.48523 | 0.018311 | 0.43488 | 122.8134 | 0.11902 | 123.1293 | 123.1888 | 123.1201 | 122.9416 | 122.9874 | -123.143 | -123.0286 | 122.5662 | 122.9965 | 60.64 | 60.0861
872.4844 | 123.1293 | -60.585 | 62.4069 | -0.75195 | 0.80037 | 0.063566 | 0.0055841 | 0.00019874 | 0.73643 | -0.00073913 | -0.029327 | 0.0018179 | 0.066635 | 0.066268 | -0.001316 | -0.0012348 | 0.00073706 | -0.082397 | 62.4023 | -60.8322 | 62.0316 | -60.4111 | 62.0865 | -0.21515 | -0.62256 | 62.4893 | -60.6537 | 62.4161 | -60.6354 | -60.759 | -60.2509 | -0.24719 | -0.004577 | -0.37537 | 0.17395 | 60.3699 | 122.6715 | 60.6171 | 122.9187 | -0.068665 | 0.082398 | 0.009156 | -0.050354 | 0.33417 | -0.17395 | 0.40283 | -0.10529 | 0.42114 | 122.8638 | 0.018311 | 123.0698 | 123.2346 | 123.143 | 122.9874 | 123.0743 | -123.2391 | -123.0606 | 122.6166 | 123.0011 | 60.5026 | 59.9625
873.5469 | 123.1155 | -60.4843 | 62.4481 | -0.72906 | 0.80122 | 0.062284 | 0.0028069 | 0.00083954 | 0.73814 | 0.0026789 | -0.014069 | 0.0050223 | 0.065567 | 0.068618 | -0.0036658 | 0.0015424 | 0.00030966 | 0.018311 | 62.4756 | -60.7269 | 62.027 | -60.1639 | 62.1277 | -0.20142 | -0.52185 | 62.5259 | -60.6125 | 62.4985 | -60.5118 | -60.6354 | -60.1456 | -0.24262 | 0.027466 | -0.42114 | 0.32043 | 60.2829 | 122.612 | 60.5255 | 122.8546 | -0.12817 | 0.07782 | 0.050354 | -0.027466 | 0.33874 | -0.15106 | 0.46692 | -0.022888 | 0.56305 | 122.7539 | 0.10071 | 123.111 | 123.2025 | 123.1384 | 122.9599 | 123.0103 | -123.175 | -123.0606 | 122.5113 | 122.9828 | 60.5026 | 59.9625
874.4844 | 123.0515 | -60.8734 | 62.0911 | -0.7901 | 0.79844 | 0.064634 | 0.0036615 | 0.0014803 | 0.73258 | 0.0031061 | -0.038483 | 0.0030997 | 0.066635 | 0.066909 | -0.0019568 | 0.00026062 | 0.0030869 | -0.068665 | 62.146 | -61.0977 | 61.6196 | -60.7361 | 61.7157 | -0.29755 | -0.72327 | 62.178 | -60.965 | 62.0636 | -60.9467 | -61.0748 | -60.5392 | -0.2243 | 0.054932 | -0.4715 | 0.13733 | 60.5759 | 122.5891 | 60.8002 | 122.8134 | -0.091553 | 0.086976 | -0.027465 | -0.073242 | 0.33417 | -0.20142 | 0.42572 | -0.10986 | 0.36163 | 122.7173 | 0.018311 | 123.0286 | 123.2437 | 123.143 | 123.0194 | 123.0515 | -123.1888 | -123.056 | 122.493 | 122.937 | 60.8047 | 60.1501
875.5625 | 123.1705 | -60.4568 | 62.4344 | -0.82825 | 0.79652 | 0.062925 | -0.00082468 | -0.0027921 | 0.73023 | 0.00054267 | 0.004242 | 0.0028861 | 0.063004 | 0.070113 | -0.0019568 | 4.7018e-05 | 0.0011643 | -0.013733 | 62.4573 | -60.6583 | 62.1185 | -60.022 | 62.2009 | -0.21057 | -0.58594 | 62.5168 | -60.5347 | 62.5854 | -60.3973 | -60.5164 | -60.0449 | -0.20142 | 0.022888 | -0.31586 | 0.43487 | 60.2463 | 122.6578 | 60.4477 | 122.8592 | -0.07782 | 0.082398 | 0.15106 | 0.059509 | 0.41199 | -0.059509 | 0.48981 | 0.018311 | 0.63629 | 122.7768 | 0.13733 | 123.1201 | 123.1155 | 123.0515 | 122.9141 | 122.9736 | -123.0927 | -122.9691 | 122.5754 | 123.0423 | 60.4431 | 59.8709
876.4844 | 123.0789 | -60.6308 | 62.3474 | -0.81299 | 0.7931 | 0.06207 | 0.0032343 | 0.00041234 | 0.72874 | 0.0024653 | -0.032379 | 0.0041679 | 0.068344 | 0.070327 | 0.0001794 | 0.0023968 | -0.00054474 | -0.086975 | 62.3703 | -60.8505 | 61.9171 | -60.4248 | 61.9263 | -0.31128 | -0.73242 | 62.4161 | -60.7315 | 62.2696 | -60.4065 | -60.791 | -60.3745 | -0.21973 | 0.022888 | -0.4303 | 0.20599 | 60.3195 | 122.5571 | 60.5392 | 122.7768 | -0.10071 | 0.068665 | -0.07782 | 0.2243 | 0.25635 | -0.16022 | 0.35706 | -0.05951 | 0.42572 | 122.7676 | 0.32501 | 123.0011 | 123.2208 | 123.1476 | 123.0011 | 123.0469 | -123.1979 | -123.0789 | 122.5479 | 122.9004 | 60.5438 | 59.8984
877.5469 | 123.0377 | -60.6766 | 62.3108 | -0.78247 | 0.79118 | 0.06207 | 0.0025933 | 0.00041234 | 0.72874 | 0.0026789 | -0.038483 | 0.0016043 | 0.065995 | 0.068191 | -0.001316 | 4.7018e-05 | 0.00073706 | -0.045776 | 62.3337 | -60.8688 | 61.8896 | -60.4294 | 61.9354 | -0.30212 | -0.71869 | 62.3749 | -60.7407 | 62.265 | -60.7086 | -60.8414 | -60.3516 | -0.19226 | 0.022888 | -0.42114 | 0.24719 | 60.3745 | 122.612 | 60.5667 | 122.8043 | -0.064087 | 0.064087 | -0.045776 | -0.032043 | 0.32501 | -0.16479 | 0.3891 | -0.10071 | 0.43945 | 122.7585 | 0.032044 | 123.0057 | 123.2025 | 123.1155 | 123.0103 | 123.0515 | -123.1796 | -123.0515 | 122.5662 | 122.9416 | 60.6308 | 59.9579
878.4844 | 123.0789 | -60.8597 | 62.0636 | -0.7901 | 0.78691 | 0.063566 | 0.0025933 | 0.0019077 | 0.72511 | 0.00096987 | -0.011017 | 0.0043815 | 0.065781 | 0.065414 | -0.0011022 | -0.00059378 | 0.0045823 | 0.050354 | 62.1368 | -61.0291 | 61.6882 | -60.7407 | 61.6882 | -0.31128 | -0.72327 | 62.1689 | -60.9329 | 62.0956 | -60.8917 | -61.0199 | -60.5164 | -0.16937 | 0.073242 | -0.37537 | 0.11902 | 60.5484 | 122.5479 | 60.7178 | 122.7173 | -0.073242 | 0.10528 | 0.032043 | -0.032044 | 0.34332 | -0.16022 | 0.41656 | -0.086975 | 0.28839 | 122.7173 | 0.041198 | 123.0286 | 123.1659 | 123.1018 | 122.9965 | 123.0286 | -123.0927 | -122.9965 | 122.5479 | 122.9553 | 60.91 | 60.1364
879.5469 | 123.056 | -60.7773 | 62.2009 | -0.76721 | 0.78627 | 0.064207 | 0.0021661 | 0.0021213 | 0.72361 | 0.0013971 | -0.062897 | 0.0026725 | 0.064926 | 0.066695 | -0.0019568 | -0.00080758 | 0.0024461 | -0.027466 | 62.2284 | -60.9558 | 61.734 | -60.5621 | 61.8164 | -0.27008 | -0.67749 | 62.2696 | -60.8597 | 62.1689 | -60.8139 | -60.9558 | -60.466 | -0.17853 | 0.027466 | -0.46692 | 0.21515 | 60.5072 | 122.5937 | 60.6857 | 122.7722 | -0.082397 | 0.068664 | -0.032044 | -0.036621 | 0.31128 | -0.17853 | 0.39368 | -0.096131 | 0.39368 | 122.6898 | 0.045776 | 123.0286 | 123.1842 | 123.1293 | 123.0057 | 123.0469 | -123.1567 | -123.0606 | 122.5113 | 122.9462 | 60.7498 | 60.0998
880.4844 | 123.1842 | -60.7178 | 62.1597 | -0.74432 | 0.78413 | 0.061002 | -0.00082468 | -0.0045011 | 0.7187 | -0.0011663 | 0.083588 | 0.0024589 | 0.065567 | 0.061355 | -0.0008886 | -0.001662 | 0.0018051 | 0.013733 | 62.1964 | -60.9055 | 61.8713 | -60.4431 | 61.9583 | -0.10529 | -0.53101 | 62.2147 | -60.8185 | 62.2742 | -60.6445 | -60.7498 | -60.3195 | -0.18768 | 0.036621 | -0.28839 | 0.27466 | 60.6125 | 122.6761 | 60.8002 | 122.8638 | -0.10071 | 0.054932 | 0.11444 | 0.073242 | 0.39825 | -0.032044 | 0.49896 | 0.068664 | 0.46234 | 122.7768 | 0.17395 | 123.0927 | 123.1018 | 123.0331 | 122.9141 | 122.9324 | -123.0652 | -122.9782 | 122.5891 | 122.9919 | 60.7315 | 60.1868
881.4844 | 123.0423 | -60.4019 | 62.5671 | -0.76721 | 0.78328 | 0.063352 | 0.0023797 | 0.00083954 | 0.72062 | 0.00096987 | -0.038483 | 0.0039541 | 0.068985 | 0.063277 | -0.0021704 | -0.0010212 | 0.00073706 | -0.059509 | 62.5534 | -60.6583 | 62.0865 | -60.0998 | 62.146 | -0.28839 | -0.98419 | 62.5626 | -60.5072 | 62.59 | -60.4614 | -60.5896 | -60.0494 | -0.25635 | -0.013733 | -0.48065 | 0.30212 | 60.1135 | 122.5479 | 60.3699 | 122.8043 | -0.10529 | -0.004578 | 0.022888 | -0.059509 | 0.35248 | -0.18768 | 0.45776 | -0.082398 | 0.55847 | 122.7448 | 0.045776 | 123.0972 | 123.2117 | 123.0698 | 122.9553 | 122.9645 | -123.2254 | -123.0743 | 122.4884 | 122.9919 | 60.3424 | 59.4177
882.5469 | 123.111 | -60.6491 | 62.2787 | -0.71381 | 0.78178 | 0.063779 | 0.0034479 | -0.0012967 | 0.71784 | 0.0018243 | 0.0072936 | 0.0016043 | 0.067704 | 0.070327 | -0.0034522 | 0.001115 | -0.0020401 | 0.032043 | 62.3291 | -60.8505 | 61.9171 | -60.3745 | 61.9766 | -0.16479 | -0.53558 | 62.3611 | -60.7269 | 62.3016 | -60.6491 | -60.7452 | -60.2966 | -0.20142 | 0.050354 | -0.36163 | 0.27466 | 60.4843 | 122.6257 | 60.6857 | 122.8271 | -0.07782 | 0.082397 | 0.022888 | 0 | 0.35248 | -0.09613 | 0.4303 | -0.01831 | 0.47607 | 122.7676 | 0.07782 | 123.0286 | 123.1796 | 123.0881 | 122.9782 | 123.0103 | -123.1293 | -123.0057 | 122.5662 | 122.9507 | 60.6812 | 60.1135
883.4844 | 123.1476 | -60.5255 | 62.3291 | -0.76721 | 0.779 | 0.063993 | 0.00088432 | -1.486e-05 | 0.71528 | -0.0011663 | 0.016449 | 0.0011771 | 0.066208 | 0.066482 | -0.0015296 | -0.0012348 | 0.00095066 | -0.032043 | 62.3291 | -60.7224 | 62.0682 | -60.1685 | 62.0682 | -0.21973 | -0.61798 | 62.3749 | -60.6308 | 62.4115 | -60.5209 | -60.6171 | -60.141 | -0.19684 | 0 | -0.26093 | 0.35706 | 60.3058 | 122.5937 | 60.5026 | 122.7905 | -0.10529 | 0.045776 | 0.082397 | 0.004578 | 0.38452 | -0.091552 | 0.48981 | 0.013733 | 0.55389 | 122.7905 | 0.10986 | 123.0423 | 123.0515 | 123.0057 | 122.8546 | 122.9004 | -123.0515 | -122.9599 | 122.5937 | 122.937 | 60.4935 | 59.9075
884.5469 | 123.0377 | -60.5438 | 62.4573 | -0.72906 | 0.77473 | 0.061002 | -0.00061088 | 0.0021213 | 0.71507 | -0.0011663 | 0.013397 | 0.0013907 | 0.065781 | 0.065414 | -0.004093 | -0.0014484 | 0.0035141 | 0.036621 | 62.4252 | -60.7361 | 62.0361 | -60.2325 | 62.0636 | -0.15564 | -0.56305 | 62.5031 | -60.6125 | 62.3749 | -60.5484 | -60.6491 | -60.1959 | -0.19226 | -0.032043 | -0.42114 | 0.31128 | 60.3882 | 122.6074 | 60.5804 | 122.7997 | -0.068665 | 0.045777 | -0.082397 | -0.004578 | 0.3479 | -0.10529 | 0.41656 | -0.036621 | 0.50354 | 122.7722 | 0.064087 | 122.9874 | 123.1613 | 123.1155 | 122.9691 | 123.0469 | -123.1934 | -123.0698 | 122.58 | 122.9187 | 60.5804 | 59.9808
885.5 | 123.1705 | -60.2829 | 62.6404 | -0.72906 | 0.77559 | 0.061216 | -0.00039728 | 0.00041234 | 0.70866 | -0.00073913 | 0.083588 | 0.0026725 | 0.066635 | 0.059218 | 0.0008204 | 0.00047422 | -0.0013991 | 0.09613 | 62.6175 | -60.4843 | 62.3657 | -59.7519 | 62.4115 | -0.073242 | -0.46234 | 62.6862 | -60.3378 | 62.558 | -60.1639 | -60.3058 | -59.9075 | -0.20142 | -0.022888 | -0.27466 | 0.53101 | 60.2097 | 122.6944 | 60.4111 | 122.8958 | -0.054932 | 0.045776 | -0.082398 | 0.11902 | 0.37537 | -0.022888 | 0.4303 | 0.032044 | 0.73242 | 122.85 | 0.17395 | 122.8958 | 123.1018 | 123.024 | 122.9004 | 122.9691 | -123.1247 | -122.9782 | 122.6486 | 122.8409 | 60.379 | 59.8206
886.5469 | 123.0789 | -60.5484 | 62.3978 | -0.7901 | 0.77388 | 0.061643 | 0.0015253 | 0.0014803 | 0.71165 | -0.0033025 | 0.028656 | 0.00096348 | 0.064499 | 0.068618 | -0.0034522 | -0.00059378 | -0.0028945 | 0.032043 | 62.352 | -60.7773 | 62.0316 | -60.2463 | 61.9125 | -0.33417 | -0.59509 | 62.4619 | -60.6262 | 62.4115 | -60.553 | -60.6674 | -60.173 | -0.22888 | -0.045776 | -0.36621 | 0.30212 | 60.2142 | 122.4609 | 60.4431 | 122.6898 | -0.07782 | 0.064087 | 0.013733 | -0.004578 | 0.37537 | -0.11902 | 0.45319 | -0.041198 | 0.53101 | 122.8088 | 0.073242 | 123.0377 | 123.1293 | 123.0881 | 122.9004 | 123.0103 | -123.175 | -123.024 | 122.58 | 122.9599 | 60.5804 | 59.9533
887.4844 | 123.1476 | -60.5118 | 62.3245 | -0.78247 | 0.77281 | 0.06207 | 0.00067072 | 0.0012667 | 0.71101 | 0.0028925 | -0.0049134 | 0.0045951 | 0.070053 | 0.063491 | -0.0034522 | -0.0010212 | -0.00054474 | -0.004578 | 62.3154 | -60.7361 | 62.0773 | -60.1639 | 62.0773 | -0.2243 | -0.86517 | 62.3795 | -60.6308 | 62.439 | -60.4477 | -60.5713 | -60.0998 | -0.2243 | -0.009155 | -0.24719 | 0.3479 | 60.2875 | 122.5891 | 60.5118 | 122.8134 | -0.11902 | 0.054932 | 0.11444 | 0.064087 | 0.41199 | -0.059509 | 0.53101 | 0.059509 | 0.5722 | 122.8134 | 0.1831 | 123.0698 | 123.0515 | 123.0103 | 122.8271 | 122.8912 | -123.0606 | -122.9553 | 122.5891 | 122.9507 | 60.5072 | 59.6466
888.5469 | 123.0515 | -60.498 | 62.4161 | -0.72906 | 0.76875 | 0.061002 | 0.00088432 | 0.0029757 | 0.7046 | 0.0016107 | -0.0079652 | 0.0037405 | 0.068558 | 0.070754 | -0.0015296 | -0.0027302 | 0.0022323 | 0.027466 | 62.4893 | -60.7178 | 62.0224 | -60.3104 | 62.059 | -0.18768 | -0.60883 | 62.4847 | -60.6262 | 62.384 | -60.5438 | -60.6583 | -60.1776 | -0.21973 | 0.073242 | -0.39368 | 0.18768 | 60.3104 | 122.5571 | 60.5301 | 122.7768 | -0.12817 | 0.068664 | -0.032044 | -0.045776 | 0.32043 | -0.16022 | 0.44861 | -0.032043 | 0.40741 | 122.7402 | 0.082398 | 123.0103 | 123.2071 | 123.111 | 122.9874 | 122.9828 | -123.1338 | -123.0423 | 122.5204 | 122.8821 | 60.5255 | 59.8892
889.4844 | 123.1338 | -60.3745 | 62.4802 | -0.83588 | 0.76854 | 0.063566 | 0.00024352 | 0.0040439 | 0.70353 | -0.0011663 | -0.026276 | 0.00053628 | 0.064072 | 0.066268 | -0.003025 | -0.0031574 | 0.00030966 | 0.013733 | 62.4527 | -60.64 | 62.2101 | -59.9762 | 62.1872 | -0.20599 | -0.64545 | 62.5305 | -60.4843 | 62.5717 | -60.347 | -60.4706 | -59.9899 | -0.2655 | -0.027466 | -0.27008 | 0.39825 | 60.1685 | 122.5616 | 60.434 | 122.8271 | -0.10986 | 0.050354 | 0.091552 | 0.027466 | 0.38452 | -0.09613 | 0.49439 | 0.013733 | 0.66376 | 122.85 | 0.13733 | 123.056 | 123.0927 | 123.0148 | 122.8271 | 122.905 | -123.1201 | -122.9645 | 122.5845 | 122.9462 | 60.3882 | 59.729
890.5 | 123.1155 | -60.4385 | 62.4664 | -0.72144 | 0.76768 | 0.062284 | -0.00018368 | 0.0010531 | 0.7031 | 0.00096987 | 0.022552 | 0.00032248 | 0.066422 | 0.061996 | -0.0002478 | -0.0029438 | -0.0018265 | -0.027466 | 62.4481 | -60.64 | 62.1552 | -60.0494 | 62.1689 | -0.18768 | -0.63629 | 62.5122 | -60.5164 | 62.5442 | -60.3607 | -60.4706 | -60.054 | -0.20142 | -0.018311 | -0.31128 | 0.3891 | 60.2509 | 122.6074 | 60.4523 | 122.8088 | -0.077819 | 0.045776 | 0.077819 | 0.07782 | 0.38452 | -0.032043 | 0.46234 | 0.045776 | 0.59052 | 122.7951 | 0.15564 | 123.0606 | 123.0881 | 123.0286 | 122.8867 | 122.9507 | -123.1064 | -122.9828 | 122.5937 | 122.9828 | 60.4111 | 59.8022
891.5469 | 123.0148 | -60.6766 | 62.265 | -0.72906 | 0.76533 | 0.06207 | 0.0040887 | 0.00019874 | 0.70075 | 0.0022517 | -0.087311 | 0.0013907 | 0.065354 | 0.072677 | -0.0025976 | 0.001115 | 0.0022323 | 0 | 62.2604 | -60.8871 | 61.8805 | -60.4431 | 61.8851 | -0.28381 | -0.71869 | 62.3199 | -60.759 | 62.2467 | -60.7086 | -60.8322 | -60.3378 | -0.21057 | -0.004578 | -0.38452 | 0.23346 | 60.3928 | 122.5616 | 60.6033 | 122.7722 | -0.082397 | 0.054931 | -0.018311 | -0.032043 | 0.33875 | -0.15564 | 0.42114 | -0.073242 | 0.44403 | 122.7676 | 0.050354 | 123.0057 | 123.1476 | 123.0789 | 122.937 | 122.9965 | -123.1522 | -123.024 | 122.5571 | 122.9233 | 60.6766 | 59.9579
892.4844 | 123.1201 | -60.4935 | 62.4527 | -0.71381 | 0.76426 | 0.066129 | 0.0023797 | 0.0025485 | 0.69883 | -0.0011663 | -0.062897 | 0.00096348 | 0.066422 | 0.06755 | -0.0045202 | 0.00026062 | 0.0011643 | -0.086975 | 62.4481 | -60.6995 | 62.059 | -60.1959 | 62.0407 | -0.32959 | -0.82855 | 62.5488 | -60.5896 | 62.4298 | -60.434 | -61.0474 | -60.3699 | -0.20599 | -0.004578 | -0.39368 | 0.29755 | 60.1639 | 122.5342 | 60.3699 | 122.7402 | -0.096131 | 0.09613 | -0.022888 | 0.059509 | 0.1236 | -0.55389 | 0.21973 | -0.45776 | 0.50354 | 122.7585 | 0.15564 | 123.0194 | 123.1476 | 123.1384 | 122.9416 | 123.0423 | -123.1522 | -123.0423 | 122.5525 | 122.9233 | 60.4065 | 59.6649
893.5469 | 123.0469 | -60.2737 | 62.645 | -0.78247 | 0.76085 | 0.063779 | 0.0021661 | 0.0036165 | 0.69947 | 0.0020379 | -0.05069 | -0.00010472 | 0.066422 | 0.067763 | -0.0011022 | -0.0020892 | -0.0020401 | 0.009155 | 62.6358 | -60.466 | 62.2742 | -59.8389 | 62.2879 | -0.2243 | -0.67291 | 62.7136 | -60.3745 | 62.6495 | -60.3104 | -60.4156 | -59.9304 | -0.19226 | -0.009155 | -0.37079 | 0.43488 | 60.0494 | 122.5616 | 60.2417 | 122.7539 | -0.10071 | 0.068665 | 0.004578 | -0.036621 | 0.34332 | -0.14191 | 0.44403 | -0.041198 | 0.62714 | 122.7402 | 0.064087 | 123.024 | 123.1018 | 123.0881 | 122.9095 | 122.9874 | -123.111 | -123.0194 | 122.5479 | 122.9233 | 60.2829 | 59.6008
894.4844 | 123.0103 | -60.2142 | 62.709 | -0.70618 | 0.76021 | 0.061857 | 0.0025933 | 0.0036165 | 0.69755 | -9.8328e-05 | -0.072052 | 0.0022453 | 0.065995 | 0.0652 | -0.0015296 | -0.0014484 | 0.0024461 | 0.004578 | 62.7319 | -60.4065 | 62.3291 | -59.7702 | 62.3337 | -0.25635 | -0.737 | 62.7869 | -60.2921 | 62.6724 | -60.2463 | -60.3607 | -59.8801 | -0.19226 | 0.022889 | -0.37994 | 0.44403 | 59.9579 | 122.5479 | 60.1501 | 122.7402 | -0.07782 | 0.07782 | -0.036621 | -0.032044 | 0.33417 | -0.14648 | 0.41199 | -0.068665 | 0.63629 | 122.7356 | 0.045776 | 122.9645 | 123.1384 | 123.0789 | 122.9462 | 123.0011 | -123.1155 | -123.0011 | 122.5433 | 122.8867 | 60.2188 | 59.4772
895.4844 | 123.1293 | -60.2417 | 62.5809 | -0.79773 | 0.75914 | 0.06442 | 0.0025933 | -0.00022866 | 0.69563 | -0.0011663 | -0.01712 | 0.00074988 | 0.066849 | 0.063064 | -0.0034522 | -0.00059378 | -0.0033219 | 0 | 62.6221 | -60.4614 | 62.3428 | -59.7519 | 62.3383 | -0.23346 | -0.71411 | 62.6495 | -60.347 | 62.7182 | -60.2097 | -60.3104 | -59.8434 | -0.21973 | 0.041198 | -0.23804 | 0.48981 | 60.0082 | 122.58 | 60.228 | 122.7997 | -0.10529 | 0.068664 | 0.13733 | 0.032043 | 0.39825 | -0.068665 | 0.50354 | 0.036621 | 0.70953 | 122.8043 | 0.13733 | 123.0652 | 123.0835 | 122.9965 | 122.8638 | 122.8912 | -123.0423 | -122.9279 | 122.5845 | 122.9599 | 60.2417 | 59.5276
896.4844 | 122.9919 | -60.4202 | 62.4893 | -0.75195 | 0.75679 | 0.062284 | 0.00088432 | 0.0025485 | 0.69499 | 0.00096987 | -0.056793 | 0.0048087 | 0.066635 | 0.067123 | -0.0019568 | 0.00090142 | -0.00054474 | -0.036621 | 62.5214 | -60.6171 | 62.1277 | -60.0861 | 62.0773 | -0.34332 | -0.85144 | 62.5854 | -60.5026 | 62.4664 | -60.4706 | -60.6125 | -60.0769 | -0.19684 | 0.032043 | -0.36163 | 0.33417 | 60.0769 | 122.4976 | 60.2737 | 122.6944 | -0.082398 | 0.09613 | -0.022888 | -0.050354 | 0.34332 | -0.19226 | 0.42572 | -0.10986 | 0.531 | 122.7448 | 0.032044 | 122.9691 | 123.1384 | 123.0881 | 122.9416 | 123.0057 | -123.1064 | -122.9919 | 122.5479 | 122.8867 | 60.3836 | 59.5688
897.4844 | 123.1018 | -60.6812 | 62.146 | -0.76721 | 0.75444 | 0.064207 | 0.00024352 | -0.00086946 | 0.69178 | 0.00075627 | -0.020172 | 0.0022453 | 0.065567 | 0.068831 | -0.001316 | 0.001115 | 0.0015915 | 59.4864 | 62.1872 | -60.9009 | 61.8576 | -60.26 | 61.8713 | -0.11902 | -0.75531 | 62.2101 | -60.8002 | 62.2604 | -60.6445 | -60.7727 | -60.2737 | -0.21973 | 0.041199 | -0.28839 | 0.42114 | 60.5621 | 122.5525 | 60.7819 | 122.7722 | -0.11902 | 0.064087 | 0.11444 | 0.036621 | 0.40741 | -0.091553 | 0.52643 | 0.027466 | 0.64087 | 122.7585 | 0.15564 | 123.0606 | 123.0881 | 123.0103 | 122.8683 | 122.8912 | -123.0469 | -122.9462 | 122.5388 | 122.9416 | 120.1675 | 59.9258
898.5469 | 122.9965 | -60.6812 | 62.1964 | -0.69855 | 0.75316 | 0.061002 | -0.00039728 | -0.0040739 | 0.69093 | 0.0031061 | 0.043915 | 0.0035269 | 0.067276 | 0.061141 | -0.0015296 | -0.0031574 | -0.00011754 | 61.8301 | 62.233 | -60.9375 | 61.8073 | -60.2737 | 61.8484 | -0.041199 | -0.70496 | 62.2604 | -60.7864 | 62.1735 | -60.7224 | -60.8459 | -60.3882 | -0.25635 | 0.036621 | -0.3891 | 0.40741 | 60.64 | 122.5296 | 60.8963 | 122.7859 | -0.10529 | 0.064087 | -0.022888 | -0.041199 | 0.29297 | -0.1648 | 0.39825 | -0.059509 | 0.66376 | 122.7448 | 0.064087 | 122.9599 | 123.1705 | 123.0469 | 122.9141 | 122.9416 | -123.1338 | -122.9828 | 122.4884 | 122.8546 | 122.5113 | 59.9762
899.4844 | 123.0515 | -60.9283 | 61.9034 | -0.73669 | 0.75166 | 0.062925 | 0.00067072 | 0.0016939 | 0.68794 | 0.0024653 | 0.0011902 | 0.00074988 | 0.067063 | 0.063491 | -0.001316 | -0.00059378 | 0.0011643 | 61.615 | 61.8622 | -61.1938 | 61.6379 | -60.5896 | 61.6241 | -0.14191 | -0.76446 | 61.9217 | -61.0519 | 61.8393 | -60.9879 | -60.7636 | -60.3424 | -0.2655 | -0.041198 | -0.2655 | 0.33875 | 60.7864 | 122.5525 | 61.0519 | 122.818 | -0.1236 | 0.018311 | -0.064087 | -0.059509 | 0.58594 | 0.16479 | 0.70953 | 0.28839 | 0.60425 | 122.8317 | 0.064087 | 122.8912 | 123.056 | 122.9736 | 122.7905 | 122.85 | -123.0972 | -122.9553 | 122.5662 | 122.7676 | 122.5433 | 60.1639
900.5469 | 123.056 | -60.9421 | 61.9583 | -0.74432 | 0.75017 | 0.06143 | 0.0028069 | -0.0021513 | 0.6858 | -0.0013799 | -0.047638 | 0.0043815 | 0.067063 | 0.071181 | -0.002384 | -0.0020892 | 0.0011643 | 61.6653 | 61.9492 | -61.1526 | 61.615 | -60.585 | 61.6425 | -0.091553 | -0.70038 | 62.0544 | -61.0382 | 61.9812 | -60.9375 | -61.0428 | -60.5759 | -0.21057 | -0.009155 | -0.34332 | 0.35706 | 60.8505 | 122.5845 | 61.0611 | 122.7951 | -0.09613 | 0.09613 | 0.022888 | 0.004578 | 0.36621 | -0.10071 | 0.46234 | -0.004578 | 0.56763 | 122.7676 | 0.10071 | 123.0194 | 123.1018 | 123.0927 | 122.8912 | 122.9965 | -123.111 | -122.9965 | 122.5571 | 122.9233 | 122.6074 | 60.2417
901.4844 | 123.0148 | -60.7269 | 62.1597 | -0.79773 | 0.74803 | 0.062284 | 0.0021661 | 0.0019077 | 0.68601 | -0.00095273 | -0.01712 | 0.00053628 | 0.066635 | 0.0652 | -0.001316 | -0.00038018 | 0.00052346 | 61.821 | 62.178 | -60.9558 | 61.7889 | -60.2051 | 61.7935 | -0.20599 | -0.89722 | 62.2696 | -60.8276 | 62.1643 | -60.759 | -60.8826 | -60.379 | -0.22888 | 0.018311 | -0.37079 | 0.52185 | 60.5209 | 122.5204 | 60.7498 | 122.7493 | -0.10071 | 0.10986 | 0.004578 | -0.032043 | 0.3479 | -0.15564 | 0.44861 | -0.054931 | 0.75073 | 122.7448 | 0.068665 | 122.9919 | 123.1339 | 123.0972 | 122.905 | 122.9965 | -123.1155 | -122.9874 | 122.5159 | 122.8912 | 122.5479 | 59.8297
902.4844 | 123.0011 | -60.7132 | 62.1964 | -0.69092 | 0.74717 | 0.062711 | 0.0032343 | 0.0021213 | 0.68751 | 0.0016107 | -0.047638 | 0.0026725 | 0.066635 | 0.068618 | -0.0019568 | 0.00068782 | -0.0031081 | 61.8622 | 62.2055 | -60.9238 | 61.8118 | -60.2737 | 61.8118 | -0.15106 | -0.8194 | 62.2696 | -60.8139 | 62.1735 | -60.7452 | -60.8688 | -60.379 | -0.21057 | 0.009155 | -0.38452 | 0.43945 | 60.5621 | 122.525 | 60.7727 | 122.7356 | -0.10071 | 0.073242 | -0.022888 | -0.032043 | 0.33417 | -0.15564 | 0.43488 | -0.054931 | 0.65002 | 122.7356 | 0.068665 | 122.9874 | 123.1293 | 123.0835 | 122.9187 | 122.9828 | -123.1201 | -123.0103 | 122.525 | 122.8867 | 122.5754 | 59.8938
903.5469 | 122.9782 | -60.672 | 62.233 | -0.71381 | 0.74803 | 0.062925 | 0.0019525 | 0.0023349 | 0.68452 | 0.0037469 | -0.035431 | 0.0033133 | 0.065354 | 0.063064 | -0.002384 | -0.00038018 | -0.0037491 | 61.8942 | 62.2284 | -60.8963 | 61.8439 | -60.228 | 61.8393 | -0.19226 | -0.83771 | 62.2742 | -60.7819 | 62.1964 | -60.7315 | -60.8368 | -60.347 | -0.2243 | -0.004577 | -0.3891 | 0.44403 | 60.4797 | 122.5113 | 60.704 | 122.7356 | -0.10986 | 0.041199 | -0.036621 | -0.059509 | 0.32501 | -0.1648 | 0.43488 | -0.054932 | 0.66833 | 122.7402 | 0.050354 | 122.9782 | 123.1247 | 123.056 | 122.9004 | 122.9462 | -123.1293 | -123.0148 | 122.5159 | 122.8683 | 122.5662 | 59.8343
904.4844 | 122.9553 | -60.7178 | 62.1826 | -0.72144 | 0.74611 | 0.063993 | 0.0023797 | 0.0027621 | 0.6826 | 0.0013971 | -0.038483 | 0.0039541 | 0.065567 | 0.064986 | -0.001316 | 0.00026062 | 0.0013779 | 61.8347 | 62.2147 | -60.9375 | 61.7981 | -60.3516 | 61.7569 | -0.18768 | -0.9201 | 62.2604 | -60.8139 | 62.1231 | -60.7956 | -60.9375 | -60.3928 | -0.21973 | 0.032044 | -0.38452 | 0.36621 | 60.5301 | 122.4747 | 60.7498 | 122.6944 | -0.096131 | 0.07782 | -0.059509 | -0.07782 | 0.32501 | -0.21973 | 0.42114 | -0.1236 | 0.58594 | 122.7356 | 0.018311 | 122.937 | 123.1522 | 123.0743 | 122.9324 | 122.9782 | -123.1201 | -122.9965 | 122.5159 | 122.8409 | 122.5525 | 59.7977
905.4844 | 123.0972 | -60.6445 | 62.1643 | -0.80536 | 0.74461 | 0.064847 | -0.0014655 | 0.0066073 | 0.68388 | 0.0016107 | 0.010345 | 0.0013907 | 0.066635 | 0.061355 | 0.0001794 | -0.0037982 | 0.0026597 | 61.94 | 62.1918 | -60.8643 | 62.059 | -60.0174 | 61.8942 | -0.068665 | -0.78278 | 62.2284 | -60.7361 | 62.2787 | -60.5896 | -60.704 | -60.2509 | -0.21973 | 0.027465 | -0.10529 | 0.62714 | 60.5759 | 122.5388 | 60.7956 | 122.7585 | -0.091553 | 0.064087 | 0.11444 | 0.054931 | 0.39368 | -0.05951 | 0.48523 | 0.032043 | 0.84686 | 122.9233 | 0.14648 | 123.0148 | 123.056 | 122.9645 | 122.8363 | 122.8729 | -123.0286 | -122.9004 | 122.7036 | 122.9233 | 122.5845 | 59.8618
906.5469 | 122.9736 | -60.6903 | 62.2147 | -0.72144 | 0.74333 | 0.062498 | 0.0028069 | -0.0027921 | 0.67704 | -0.0033025 | 0.025604 | 0.0013907 | 0.065995 | 0.069472 | -0.0028112 | -0.0031574 | 0.0028733 | 61.908 | 62.2009 | -60.8734 | 61.8439 | -60.2325 | 61.8851 | -0.032043 | -0.71411 | 62.2787 | -60.7727 | 62.1689 | -60.6949 | -60.7956 | -60.3516 | -0.1831 | -0.013733 | -0.37079 | 0.45776 | 60.6583 | 122.5754 | 60.8414 | 122.7585 | -0.082397 | 0.064087 | -0.045777 | -0.004577 | 0.33875 | -0.10528 | 0.42114 | -0.022888 | 0.64087 | 122.7173 | 0.07782 | 122.9416 | 123.0743 | 123.0515 | 122.8912 | 122.9691 | -123.0881 | -122.9874 | 122.5342 | 122.8592 | 122.5983 | 59.9762
907.4844 | 123.1201 | -60.6583 | 62.1643 | -0.74432 | 0.74269 | 0.063993 | 0.0021661 | 0.00083954 | 0.68025 | 0.00054267 | 0.0072936 | 0.00074988 | 0.065781 | 0.066909 | -0.003025 | 0.00068782 | -0.00097194 | 61.9125 | 62.1872 | -60.878 | 61.908 | -60.1685 | 61.9125 | -0.17853 | -0.87891 | 62.2147 | -60.7452 | 62.2604 | -60.6537 | -60.7681 | -60.26 | -0.21973 | 0.022888 | -0.25635 | 0.48981 | 60.4797 | 122.5708 | 60.6995 | 122.7905 | -0.086975 | 0.050354 | 0.09613 | 0.004577 | 0.39825 | -0.10986 | 0.48523 | -0.022888 | 0.70953 | 122.7859 | 0.091552 | 123.0057 | 123.0652 | 122.9599 | 122.8455 | 122.8729 | -123.0423 | -122.9095 | 122.5662 | 122.9187 | 122.5708 | 59.7794
908.4844 | 122.9736 | -59.9533 | 62.9288 | -0.68329 | 0.73991 | 0.062711 | 0.0013117 | 0.0021213 | 0.67469 | 0.0026789 | -0.056793 | 0.0024589 | 0.065995 | 0.067336 | -0.0011022 | -0.0014484 | -0.00033114 | 62.3154 | 62.5763 | -60.5118 | 62.2742 | -59.4727 | 62.3474 | -0.10986 | -0.76446 | 62.9013 | -60.1685 | 63.0157 | -60.0449 | -60.1685 | -59.6512 | -0.55847 | -0.35248 | -0.6546 | 0.48065 | 59.8434 | 122.3007 | 60.4019 | 122.8592 | -0.21515 | -0.027466 | 0.086975 | -0.091553 | 0.30212 | -0.21515 | 0.51727 | 0 | 1.0391 | 122.7859 | 0.1236 | 123.1842 | 123.0881 | 123.0698 | 122.5296 | 122.8546 | -123.4406 | -123.0972 | 122.2275 | 122.9691 | 122.2687 | 59.1888
909.4844 | 122.9691 | -24.8383 | 98.0942 | -0.69855 | 0.74012 | 0.072965 | 0.0023797 | 0.00041234 | 0.67491 | -0.0020209 | -0.026276 | 0.0022453 | 0.066208 | 0.06285 | -0.0032386 | -0.0031574 | -0.00075834 | 97.6456 | 98.0667 | -25.058 | 97.6364 | -7.5256 | 97.6776 | 1.1536 | -0.3891 | 98.1857 | -24.9115 | 98.1125 | -24.9298 | -25.0305 | -24.7833 | -0.21973 | -0.027466 | -0.45776 | 17.3126 | 25.9918 | 122.5159 | 26.2115 | 122.7356 | -0.073242 | 0.091553 | 0.018311 | -0.091553 | 0.054932 | -0.19226 | 0.12817 | -0.11902 | 17.5323 | 122.6944 | -0.018311 | 123.024 | 123.1247 | 123.0972 | 122.905 | 123.024 | -123.1522 | -123.0057 | 122.4747 | 122.9507 | 122.4838 | 24.4492
910.5469 | 122.9691 | -24.5636 | 98.3551 | -0.67566 | 0.73777 | 0.071683 | -0.0010383 | 0.0021213 | 0.67362 | 0.00011527 | -0.038483 | 0.0030997 | 0.066208 | 0.064986 | -0.002384 | -0.00059378 | 0.00095066 | 98.0301 | 98.3826 | -24.7192 | 97.9523 | -7.1182 | 97.9706 | 1.2497 | -0.23346 | 98.4467 | -24.678 | 98.3643 | -24.6506 | -24.7742 | -24.5453 | -0.15564 | 0.027465 | -0.40283 | 17.4454 | 25.8133 | 122.5342 | 25.9689 | 122.6898 | -0.11444 | 0.091552 | 0.009155 | -0.086975 | 0.018311 | -0.21057 | 0.13275 | -0.09613 | 17.601 | 122.6715 | 0.027466 | 123.0423 | 123.1018 | 123.1247 | 122.9462 | 123.0103 | -123.0743 | -123.0331 | 122.5159 | 122.9279 | 122.5937 | 24.3301
911.4844 | 123.0652 | -24.7467 | 98.085 | -0.73669 | 0.73863 | 0.072324 | 0.0030207 | 0.0021213 | 0.67277 | 0.0031061 | -0.011017 | 0.00010888 | 0.063645 | 0.061568 | -0.0008886 | -0.0023028 | -0.00011754 | 97.7829 | 98.0942 | -24.9481 | 97.7325 | -7.4387 | 97.7554 | 1.1856 | -0.35706 | 98.1628 | -24.8932 | 98.1949 | -24.8199 | -24.9344 | -24.7009 | -0.20142 | 0.009155 | -0.35248 | 17.308 | 25.9323 | 122.5021 | 26.1337 | 122.7036 | -0.14648 | 0.07782 | 0.10986 | -0.073242 | 0.045776 | -0.18768 | 0.19226 | -0.041199 | 17.5095 | 122.6807 | 0.073242 | 123.0881 | 123.0423 | 123.056 | 122.8409 | 122.9095 | -123.0331 | -122.9782 | 122.4792 | 122.9416 | 122.5296 | 24.3896
912.5469 | 122.9919 | -25.9277 | 96.9727 | -0.68329 | 0.73478 | 0.073606 | 0.0025933 | 0.0010531 | 0.67149 | 0.0018243 | -0.16055 | 0.0013907 | 0.065354 | 0.061568 | -0.0017432 | -0.0014484 | -0.00075834 | 96.5836 | 96.9589 | -26.152 | 96.5195 | -9.2239 | 96.5744 | 1.181 | -0.21515 | 97.0963 | -26.0422 | 97.0276 | -26.0605 | -26.1749 | -25.9094 | -0.2243 | -0.013733 | -0.45319 | 16.7038 | 27.1088 | 122.5021 | 27.3331 | 122.7264 | -0.11444 | 0.1236 | 0.054932 | -0.13275 | 0.01831 | -0.24719 | 0.13275 | -0.13275 | 16.9281 | 122.6715 | -0.018311 | 123.0698 | 123.111 | 123.1384 | 122.8867 | 123.024 | -123.1247 | -123.0148 | 122.4472 | 122.9553 | 122.5113 | 25.7126
913.4844 | 123.0881 | -26.3351 | 96.492 | -0.75958 | 0.73393 | 0.073179 | 2.9918e-05 | 0.00041234 | 0.67042 | -0.00073913 | 0.0011902 | 0.0022453 | 0.06984 | 0.062209 | -0.0011022 | -0.0014484 | -0.00033114 | 96.1807 | 96.5103 | -26.5457 | 96.199 | -9.9747 | 96.1029 | 1.2863 | -0.37079 | 96.5424 | -26.4908 | 96.5973 | -26.4221 | -26.5091 | -26.2665 | -0.21057 | 0.018311 | -0.29297 | 16.3605 | 27.6215 | 122.438 | 27.832 | 122.6486 | -0.15564 | 0.050354 | 0.10529 | -0.086975 | 0.068665 | -0.17395 | 0.22431 | -0.01831 | 16.571 | 122.7448 | 0.068665 | 123.0881 | 123.056 | 123.0331 | 122.8455 | 122.8775 | -123.0377 | -122.9828 | 122.5342 | 122.9324 | 122.5159 | 25.9644
914.4844 | 123.0469 | -26.2894 | 96.6019 | -0.79773 | 0.73329 | 0.071897 | 0.00088432 | 0.0012667 | 0.67085 | -0.0033025 | 0.108 | 0.00010888 | 0.06749 | 0.063705 | -0.0019568 | 4.7018e-05 | 0.0030869 | 96.2769 | 96.6064 | -26.4679 | 96.2448 | -9.6771 | 95.9061 | 1.1215 | -0.39368 | 96.6431 | -26.3947 | 96.6797 | -26.3397 | -26.4175 | -26.1932 | -0.17853 | 0.004577 | -0.35706 | 16.6122 | 27.4109 | 122.1954 | 27.5894 | 122.374 | -0.10529 | 0.041198 | 0.077819 | -0.050354 | 0.096131 | -0.12817 | 0.20142 | -0.022889 | 16.7908 | 122.7127 | 0.054931 | 123.0743 | 123.0743 | 123.0377 | 122.8958 | 122.9324 | -123.0698 | -122.9965 | 122.5342 | 122.9691 | 122.5662 | 25.8957
915.4844 | 123.0743 | -26.4954 | 96.3547 | -0.69855 | 0.73393 | 0.072324 | 0.0023797 | -0.0045011 | 0.67063 | 0.0018243 | -0.032379 | 0.00053628 | 0.065995 | 0.07054 | -0.004093 | 0.00047422 | -0.0043899 | 96.0342 | 96.405 | -26.683 | 96.0068 | -9.993 | 96.0342 | 1.1353 | -0.40283 | 96.4325 | -26.6006 | 96.4737 | -26.5503 | -26.6693 | -26.413 | -0.18768 | 0.050354 | -0.3479 | 16.5024 | 27.6306 | 122.5296 | 27.8183 | 122.7173 | -0.10529 | 0.07782 | 0.11902 | -0.054932 | 0.082397 | -0.17395 | 0.18768 | -0.068665 | 16.6901 | 122.6898 | 0.050354 | 123.0743 | 123.0881 | 123.0331 | 122.9004 | 122.9279 | -123.0377 | -122.9553 | 122.5021 | 122.9691 | 122.5296 | 26.0925
916.5469 | 122.9507 | -26.4084 | 96.5469 | -0.66803 | 0.72966 | 0.071897 | -0.00082468 | -0.00044226 | 0.66828 | 0.0016107 | 0.034759 | 0.00074988 | 0.066849 | 0.062209 | -0.0019568 | -0.0029438 | 0.0018051 | 96.2173 | 96.6019 | -26.4771 | 96.1166 | -9.8099 | 96.1899 | 1.2497 | -0.29755 | 96.6431 | -26.4725 | 96.4874 | -26.4862 | -26.5778 | -26.3718 | -0.068665 | 0.054932 | -0.4303 | 16.5985 | 27.6581 | 122.5983 | 27.7267 | 122.6669 | -0.064087 | 0.09613 | -0.059509 | -0.07782 | 0.036621 | -0.16937 | 0.10071 | -0.10529 | 16.6672 | 122.5937 | -0.013733 | 122.9599 | 123.0789 | 123.1155 | 123.0103 | 123.0515 | -123.024 | -123.0194 | 122.525 | 122.8958 | 122.6257 | 26.1108
917.4844 | 123.0469 | -26.2299 | 96.5881 | -0.79773 | 0.72902 | 0.070615 | 0.00067072 | 0.0012667 | 0.66422 | -0.0020209 | 0.022552 | -0.00031832 | 0.065781 | 0.069472 | -0.0028112 | -0.0020892 | -0.00054474 | 96.2723 | 96.5973 | -26.4542 | 96.2494 | -9.6222 | 96.286 | 1.2085 | -0.65002 | 96.6248 | -26.3947 | 96.6797 | -26.3306 | -26.4084 | -26.1475 | -0.22431 | 0.009155 | -0.33874 | 16.6077 | 27.4384 | 122.5159 | 27.6627 | 122.7402 | -0.1648 | 0.036621 | 0.091552 | -0.10071 | 0.082397 | -0.17853 | 0.24719 | -0.013733 | 16.832 | 122.7036 | 0.064087 | 123.0743 | 123.0515 | 123.0194 | 122.8271 | 122.8546 | -123.0423 | -122.9828 | 122.4792 | 122.9095 | 122.5021 | 25.5798
918.4844 | 122.9874 | -26.6006 | 96.2906 | -0.78247 | 0.72688 | 0.071256 | 0.0017389 | 0.00041234 | 0.66294 | 0.0020379 | -0.044586 | 0.0033133 | 0.066422 | 0.066695 | -0.0011022 | -0.001662 | -0.0013991 | 95.9198 | 96.3135 | -26.7975 | 95.8328 | -10.2402 | 95.8603 | 1.1032 | -0.47607 | 96.3776 | -26.7242 | 96.2952 | -26.7334 | -26.8295 | -26.5915 | -0.19684 | 0.022889 | -0.45776 | 16.3605 | 27.7039 | 122.4609 | 27.9007 | 122.6578 | -0.1236 | 0.086975 | 0.004578 | -0.13275 | 0.009155 | -0.22888 | 0.13275 | -0.10529 | 16.5573 | 122.6303 | -0.009155 | 123.0194 | 123.111 | 123.1018 | 122.9141 | 122.9782 | -123.0881 | -123.0148 | 122.4335 | 122.8958 | 122.5204 | 26.1246
919.4844 | 123.0652 | -26.3489 | 96.46 | -0.79773 | 0.72603 | 0.071256 | 0.0017389 | -0.00065586 | 0.66401 | 0.00096987 | -0.014069 | 0.0022453 | 0.068344 | 0.067336 | -0.000675 | 4.7018e-05 | 0.0022323 | 96.1716 | 96.4828 | -26.5457 | 96.1395 | -9.787 | 96.1578 | 1.2039 | -0.38452 | 96.5836 | -26.4771 | 96.4828 | -26.2115 | -26.4404 | -26.3123 | -0.19684 | 0.022888 | -0.32044 | 16.5619 | 27.5528 | 122.5067 | 27.7496 | 122.7036 | -0.12817 | 0.1236 | 0.022888 | 0.13733 | 0.036621 | -0.091553 | 0.16479 | 0.036621 | 16.7587 | 122.6852 | 0.2655 | 122.9599 | 123.0286 | 123.0606 | 122.8317 | 122.9324 | -123.0057 | -122.937 | 122.4884 | 122.8317 | 122.5204 | 25.9644
920.5469 | 122.9782 | -26.5366 | 96.3547 | -0.70618 | 0.72496 | 0.069547 | 0.0023797 | -0.00022866 | 0.66017 | 0.00011527 | -0.0079652 | 0.0022453 | 0.066849 | 0.067336 | -0.0008886 | -0.00080758 | -0.0024673 | 95.9839 | 96.4188 | -26.7014 | 95.8603 | -10.1624 | 95.9473 | 1.2085 | -0.37537 | 96.4645 | -26.6739 | 96.3089 | -26.6785 | -26.7975 | -26.5686 | -0.16479 | 0.064087 | -0.49438 | 16.3742 | 27.7451 | 122.4838 | 27.9099 | 122.6486 | -0.13733 | 0.10986 | -0.045776 | -0.14191 | -0.032044 | -0.26093 | 0.10528 | -0.1236 | 16.539 | 122.5616 | -0.004578 | 122.9828 | 123.1201 | 123.1384 | 122.9553 | 123.0011 | -123.056 | -123.0286 | 122.3969 | 122.8455 | 122.5204 | 26.1612
921.4844 | 123.0057 | -26.6739 | 96.1761 | -0.78247 | 0.72325 | 0.071043 | 0.00088432 | -1.486e-05 | 0.66102 | 0.0026789 | 0.028656 | 0.0020315 | 0.066422 | 0.071395 | -0.000675 | -0.0020892 | 0.00095066 | 95.9015 | 96.2082 | -26.8524 | 95.8191 | -10.231 | 95.8557 | 1.1948 | -0.41199 | 96.2448 | -26.7883 | 96.2494 | -26.7426 | -26.8387 | -26.5915 | -0.17853 | 0.032044 | -0.35706 | 16.4429 | 27.8687 | 122.5296 | 28.0472 | 122.7081 | -0.11444 | 0.068665 | 0.073243 | -0.068665 | 0.082397 | -0.1648 | 0.19684 | -0.050354 | 16.6214 | 122.6715 | 0.045776 | 123.0377 | 123.0606 | 123.0331 | 122.8821 | 122.9187 | -123.0286 | -122.9645 | 122.493 | 122.9233 | 122.5754 | 26.2619
922.5469 | 123.0148 | -26.7105 | 96.1578 | -0.67566 | 0.72261 | 0.070829 | 0.0010981 | -0.0021513 | 0.65888 | -0.0026617 | 0.050018 | 0.0016043 | 0.067917 | 0.064132 | -0.0015296 | -0.0027302 | 9.6064e-05 | 95.842 | 96.1716 | -26.8524 | 95.8099 | -10.2814 | 95.8923 | 1.2955 | -0.28839 | 96.2402 | -26.825 | 96.1578 | -26.8066 | -26.9211 | -26.6876 | -0.14191 | 0.013733 | -0.3479 | 16.4291 | 28.006 | 122.6028 | 28.1479 | 122.7448 | -0.11444 | 0.082397 | 0 | -0.096131 | 0.022888 | -0.21057 | 0.13733 | -0.096131 | 16.571 | 122.6624 | 0.01831 | 122.9828 | 123.024 | 123.0652 | 122.8821 | 122.9507 | -123.0103 | -122.9828 | 122.5204 | 122.8683 | 122.5525 | 26.4221
923.4844 | 123.0377 | -26.9989 | 95.8603 | -0.74432 | 0.72303 | 0.071897 | 0.0040887 | 0.0042575 | 0.65931 | 0.0022517 | 0.022552 | 0.0022453 | 0.06749 | 0.070113 | -0.004093 | -0.0012348 | -0.0013991 | 95.5307 | 95.8511 | -27.182 | 95.4437 | -10.6979 | 95.549 | 1.1993 | -0.41657 | 95.9473 | -27.1225 | 95.9564 | -27.0538 | -27.1591 | -26.9073 | -0.18311 | -0.009156 | -0.41657 | 16.301 | 28.1982 | 122.5479 | 28.3813 | 122.731 | -0.1236 | 0.086975 | 0.09613 | -0.054932 | 0.091552 | -0.16022 | 0.21515 | -0.036621 | 16.4841 | 122.6257 | 0.068665 | 123.0789 | 123.0331 | 123.0698 | 122.85 | 122.9462 | -123.0423 | -122.9828 | 122.4426 | 122.9553 | 122.5296 | 26.5823
924.5469 | 122.9233 | -26.3718 | 96.5149 | -0.70618 | 0.72069 | 0.073606 | 0.0028069 | 0.00041234 | 0.65589 | -0.00073913 | -0.065949 | 0.0048087 | 0.066849 | 0.0699 | -0.004093 | -0.0012348 | 0.0011643 | 96.0892 | 96.524 | -26.6006 | 96.0251 | -9.9655 | 96.0251 | 1.1444 | -0.58594 | 96.5973 | -26.5366 | 96.4966 | -26.5228 | -26.6556 | -26.3855 | -0.22888 | 0.009155 | -0.48981 | 16.4062 | 27.5162 | 122.3969 | 27.7451 | 122.6257 | -0.1648 | 0.082397 | -0.018311 | -0.15106 | -0.013733 | -0.28381 | 0.15106 | -0.11902 | 16.6351 | 122.6257 | 0.013733 | 123.0331 | 123.1247 | 123.1338 | 122.8958 | 122.9691 | -123.1155 | -123.0515 | 122.3969 | 122.8683 | 122.4609 | 25.7858
925.4844 | 122.9919 | -26.152 | 96.698 | -0.69092 | 0.72004 | 0.072538 | 0.0010981 | -0.0030057 | 0.65782 | 0.00096987 | 0.010345 | 0.0011771 | 0.068772 | 0.066482 | -0.0021704 | -0.0023028 | 0.0018051 | 96.3776 | 96.7392 | -26.3077 | 96.3409 | -9.4299 | 96.3776 | 1.2589 | -0.42572 | 96.7712 | -26.2573 | 96.7667 | -26.2253 | -26.326 | -26.1017 | -0.15564 | 0.041199 | -0.35706 | 16.7221 | 27.4109 | 122.5296 | 27.5665 | 122.6852 | -0.10529 | 0.073242 | 0.068665 | -0.073242 | 0.050354 | -0.17395 | 0.15564 | -0.068665 | 16.8777 | 122.6486 | 0.032043 | 123.024 | 123.0469 | 123.0286 | 122.8912 | 122.9233 | -123.0057 | -122.9553 | 122.493 | 122.9187 | 122.5296 | 25.7263
926.4844 | 122.9691 | -26.3031 | 96.6019 | -0.62988 | 0.7194 | 0.071043 | 0.0036615 | 0.0038303 | 0.65248 | 0.0018243 | -0.062897 | 0.0024589 | 0.06749 | 0.059646 | -0.0019568 | -0.0014484 | -0.0022537 | 96.2265 | 96.6202 | -26.4679 | 96.1349 | -9.7549 | 96.1578 | 1.181 | -0.53558 | 96.7026 | -26.413 | 96.5836 | -26.4313 | -26.5411 | -26.2802 | -0.16479 | 0.01831 | -0.46692 | 16.5482 | 27.4841 | 122.4609 | 27.6489 | 122.6257 | -0.10986 | 0.10071 | -0.018311 | -0.12817 | 0.022889 | -0.23804 | 0.13275 | -0.12817 | 16.713 | 122.6028 | -0.01831 | 122.9965 | 123.0881 | 123.1155 | 122.9233 | 123.0057 | -123.0698 | -123.0148 | 122.4381 | 122.8867 | 122.5296 | 25.7675
927.4844 | 123.0194 | -26.3443 | 96.5057 | -0.82825 | 0.71834 | 0.071683 | 0.00088432 | -0.0025785 | 0.65675 | -0.00031193 | -0.01712 | 0.0016043 | 0.066422 | 0.068191 | -0.0017432 | -0.00080758 | -0.0011855 | 96.1761 | 96.5378 | -26.5091 | 96.1578 | -9.7412 | 96.1945 | 1.2589 | -0.42114 | 96.579 | -26.4404 | 96.5881 | -26.3992 | -26.5091 | -26.2619 | -0.1648 | 0.032044 | -0.3479 | 16.6031 | 27.6031 | 122.5388 | 27.7679 | 122.7036 | -0.096131 | 0.073242 | 0.082398 | -0.054932 | 0.082397 | -0.1648 | 0.17853 | -0.068664 | 16.7679 | 122.6669 | 0.041199 | 123.0286 | 123.0469 | 123.0194 | 122.8821 | 122.9233 | -123.0148 | -122.9462 | 122.5021 | 122.9324 | 122.5204 | 25.9232
928.4844 | 123.024 | -58.5159 | 64.3021 | -0.69855 | 0.71663 | 0.062925 | 0.0021661 | 0.00041234 | 0.64884 | 0.00032907 | -0.084259 | 0.0024589 | 0.067704 | 0.069259 | 0.0008204 | -0.00038018 | 9.6064e-05 | 64.8376 | 64.9658 | -58.2275 | 63.4735 | -56.781 | 64.5264 | 0.16937 | -1.9684 | 64.2151 | -58.8959 | 64.5676 | -58.7906 | -59.0286 | -58.3649 | 0.28839 | 0.66376 | -0.82855 | 1.7349 | 58.6853 | 123.0423 | 58.3969 | 122.7539 | -0.37994 | -0.086975 | 0.2655 | -0.27466 | 0.15106 | -0.5127 | 0.53101 | -0.13275 | 1.4465 | 121.7011 | 0.10529 | 123.4634 | 123.1934 | 123.111 | 123.4817 | 122.731 | -122.5296 | -123.1979 | 121.9894 | 123.0835 | 123.3536 | 56.5475
929.5469 | 122.9095 | -26.2665 | 96.6476 | -0.70618 | 0.71556 | 0.072538 | 0.0025933 | 0.0010531 | 0.65205 | 0.0026789 | -0.065949 | 0.0033133 | 0.065781 | 0.063705 | -0.0002478 | -0.00016658 | 0.00095066 | 96.2357 | 96.7255 | -26.4221 | 96.1487 | -9.7412 | 96.1716 | 1.1719 | -0.55847 | 96.7621 | -26.3672 | 96.6156 | -26.3992 | -26.532 | -26.239 | -0.15564 | 0.07782 | -0.49896 | 16.5253 | 27.4384 | 122.438 | 27.594 | 122.5937 | -0.10071 | 0.11444 | -0.032043 | -0.13275 | 0.027465 | -0.2655 | 0.12817 | -0.16479 | 16.6809 | 122.5708 | -0.032044 | 122.9828 | 123.1476 | 123.1293 | 122.9919 | 123.0286 | -123.0698 | -123.0148 | 122.4152 | 122.8821 | 122.5021 | 25.708
930.4844 | 122.9919 | -25.9048 | 96.9406 | -0.69092 | 0.71705 | 0.069334 | 0.0019525 | 0.0051119 | 0.65055 | 0.00054267 | -0.026276 | 0.0037405 | 0.067704 | 0.064986 | -3.4196e-05 | 0.00090142 | -0.0011855 | 96.5836 | 97.0001 | -26.1063 | 96.4828 | -9.1919 | 96.5149 | 1.1993 | -0.55847 | 97.0367 | -26.033 | 96.9818 | -26.0193 | -26.1337 | -25.8957 | -0.20142 | 0.059509 | -0.45776 | 16.713 | 27.1042 | 122.4197 | 27.3056 | 122.6212 | -0.12817 | 0.09613 | 0.041199 | -0.11444 | 0.009155 | -0.22888 | 0.13733 | -0.10071 | 16.9144 | 122.5891 | 0.013733 | 123.0148 | 123.1064 | 123.0698 | 122.905 | 122.9416 | -123.0469 | -122.9736 | 122.3877 | 122.8867 | 122.4884 | 25.3464
931.4844 | 123.0057 | -26.3763 | 96.4325 | -0.72144 | 0.71577 | 0.071683 | 0.0021661 | -0.00044226 | 0.64991 | 0.0035333 | -0.011017 | 0.0033133 | 0.063645 | 0.065841 | -0.0025976 | -0.00016658 | -0.0035355 | 96.1533 | 96.4828 | -26.5778 | 96.1029 | -9.7733 | 96.167 | 1.3138 | -0.66834 | 96.4828 | -26.5182 | 96.5424 | -26.3992 | -26.5182 | -26.2665 | -0.20142 | 0.050354 | -0.32959 | 16.6031 | 27.6901 | 122.5433 | 27.8915 | 122.7448 | -0.14191 | 0.050354 | 0.10986 | -0.022888 | 0.10986 | -0.14191 | 0.25177 | 0 | 16.8045 | 122.6807 | 0.11902 | 123.0606 | 123.0606 | 123.0011 | 122.8592 | 122.8592 | -123.0103 | -122.9507 | 122.4792 | 122.9187 | 122.5296 | 25.708
932.5469 | 123.0011 | -26.6556 | 96.2128 | -0.61462 | 0.71214 | 0.072324 | 0.0015253 | -1.486e-05 | 0.6482 | -0.00095273 | -0.038483 | 0.0028861 | 0.066208 | 0.068191 | 0.0001794 | -0.0014484 | -0.0022537 | 95.8282 | 96.2723 | -26.8524 | 95.7642 | -10.3455 | 95.8328 | 1.2817 | -0.40283 | 96.3135 | -26.7975 | 96.2036 | -26.7471 | -26.8707 | -26.6373 | -0.19684 | 0.059509 | -0.44861 | 16.3101 | 27.9373 | 122.4884 | 28.1342 | 122.6852 | -0.14191 | 0.10071 | -0.009156 | -0.091552 | 0.018311 | -0.21515 | 0.16022 | -0.073243 | 16.507 | 122.6166 | 0.050354 | 123.0011 | 123.1247 | 123.111 | 122.9279 | 122.9691 | -123.0652 | -123.0103 | 122.4197 | 122.8592 | 122.4838 | 26.2527
933.4844 | 123.0103 | -26.3214 | 96.524 | -0.72144 | 0.70915 | 0.071683 | 2.9918e-05 | -0.0012967 | 0.64607 | 0.00054267 | 0.031708 | 0.00074988 | 0.065995 | 0.061141 | -0.0019568 | -0.0025164 | 0.0020187 | 96.199 | 96.5469 | -26.4816 | 96.1578 | -9.6771 | 96.2265 | 1.3275 | -0.43488 | 96.6019 | -26.4175 | 96.6064 | -26.358 | -26.4633 | -26.239 | -0.16022 | 0.022888 | -0.36621 | 16.6443 | 27.6489 | 122.5479 | 27.8091 | 122.7081 | -0.096131 | 0.07782 | 0.082397 | -0.036621 | 0.082397 | -0.14191 | 0.17853 | -0.045776 | 16.8045 | 122.6395 | 0.05951 | 123.024 | 123.0286 | 123.0194 | 122.8683 | 122.9233 | -123.0057 | -122.9416 | 122.4792 | 122.9279 | 122.5204 | 25.8865
934.5469 | 122.9141 | -26.8341 | 96.0434 | -0.70618 | 0.71257 | 0.069761 | 0.00088432 | 0.0010531 | 0.64543 | 0.0011835 | 0.010345 | 0.0011771 | 0.067063 | 0.068404 | -0.001316 | -0.0014484 | 0.0013779 | 95.6268 | 95.9976 | -27.0767 | 95.6451 | -10.5469 | 95.668 | 1.3321 | -0.41199 | 96.1487 | -26.9394 | 96.0388 | -26.9669 | -27.1042 | -26.8616 | -0.24262 | -0.045776 | -0.39825 | 16.2872 | 28.1662 | 122.5021 | 28.4088 | 122.7448 | -0.10529 | 0.10529 | -0.004578 | -0.13275 | -0.027466 | -0.27008 | 0.07782 | -0.16479 | 16.5298 | 122.7219 | -0.027466 | 122.9782 | 123.0743 | 123.0881 | 122.8317 | 122.9828 | -123.1201 | -122.9828 | 122.4792 | 122.8729 | 122.4609 | 26.4221
935.4844 | 123.0286 | -26.3947 | 96.4005 | -0.71381 | 0.71043 | 0.073179 | 0.0015253 | -1.486e-05 | 0.64607 | 0.0037469 | -0.014069 | 0.0013907 | 0.067063 | 0.066268 | -3.4196e-05 | -0.0018756 | 0.0011643 | 96.0846 | 96.3821 | -26.6464 | 96.0388 | -9.8923 | 96.0983 | 1.3321 | -0.46234 | 96.492 | -26.5366 | 96.5012 | -26.4679 | -26.5778 | -26.3031 | -0.25177 | -0.018311 | -0.36163 | 16.5024 | 27.7267 | 122.493 | 27.9785 | 122.7448 | -0.14191 | 0.091552 | 0.10071 | -0.073243 | 0.091552 | -0.18311 | 0.23346 | -0.041199 | 16.7541 | 122.6852 | 0.068664 | 123.0377 | 123.0286 | 123.0286 | 122.7768 | 122.8867 | -123.0469 | -122.937 | 122.4335 | 122.8958 | 122.4792 | 25.9323
936.4844 | 122.905 | -26.6418 | 96.286 | -0.71381 | 0.70851 | 0.071043 | 0.0028069 | 0.0027621 | 0.64115 | -0.0022345 | -0.041534 | -0.00010472 | 0.068558 | 0.063491 | -0.0036658 | 0.001115 | -0.0035355 | 95.842 | 96.3043 | -26.8204 | 95.8054 | -10.2631 | 95.8054 | 1.2131 | -0.60425 | 96.3913 | -26.7105 | 96.199 | -26.7746 | -26.8295 | -26.6327 | -0.17853 | 0.01831 | -0.48065 | 16.3788 | 27.8549 | 122.4472 | 28.0334 | 122.6257 | -0.068664 | 0.10528 | -0.086975 | -0.13275 | 0.009156 | -0.18768 | 0.07782 | -0.11902 | 16.5573 | 122.6257 | -0.064087 | 122.9095 | 123.1247 | 123.1018 | 122.9462 | 123.0331 | -123.1064 | -122.9965 | 122.4472 | 122.8409 | 122.4838 | 26.0376
937.4844 | 123.1338 | -60.9146 | 61.7477 | -0.72144 | 0.7083 | 0.066556 | 0.0015253 | -0.0015103 | 0.64478 | 0.00011527 | -0.011017 | 0.0028861 | 0.067063 | 0.060714 | -0.0049476 | -0.0014484 | 0.00073706 | 61.528 | 61.8256 | -61.1984 | 61.5784 | -60.6033 | 61.5509 | -0.34332 | -1.268 | 61.8301 | -61.0748 | 61.8393 | -60.9512 | -61.1114 | -60.6583 | -0.28381 | 0.07782 | -0.16937 | 0.31128 | 60.5713 | 122.4655 | 60.8551 | 122.7493 | -0.16022 | 0.082397 | 0.091552 | -0.036621 | 0.25635 | -0.19684 | 0.41656 | -0.036621 | 0.59509 | 122.7768 | 0.1236 | 122.9141 | 123.024 | 122.905 | 122.7402 | 122.7448 | -122.9462 | -122.8226 | 122.493 | 122.7539 | 122.4426 | 59.6466
938.4844 | 122.9004 | -27.2461 | 95.6635 | -0.90454 | 0.70915 | 0.070829 | 0.0013117 | -0.00065586 | 0.64179 | -0.0020209 | -0.075104 | 0.0033133 | 0.066208 | 0.063491 | -0.0025976 | -0.0018756 | 0.0022323 | 95.3796 | 95.7138 | -27.3743 | 95.1691 | -11.1191 | 95.224 | 1.2222 | -0.60883 | 95.7367 | -27.3422 | 95.668 | -27.3514 | -27.4612 | -27.2095 | -0.12817 | 0.050354 | -0.49439 | 16.127 | 28.4683 | 122.4701 | 28.5965 | 122.5983 | -0.09613 | 0.073242 | 0.004578 | -0.10529 | 0.036621 | -0.21515 | 0.13275 | -0.11902 | 16.2552 | 122.5433 | -0.009155 | 123.0103 | 123.0881 | 123.0789 | 122.9599 | 122.9828 | -123.0377 | -123.0057 | 122.4152 | 122.9141 | 122.6257 | 26.6373
939.5469 | 122.9416 | -27.3834 | 95.5261 | -0.72906 | 0.70744 | 0.071043 | 0.0021661 | 0.0040439 | 0.64372 | 0.0011835 | -0.044586 | 0.0039541 | 0.064713 | 0.07054 | -0.0017432 | -0.0012348 | 0.0013779 | 94.8532 | 95.1828 | -27.9236 | 94.7525 | -11.8011 | 94.7983 | 1.3 | -0.21973 | 95.4117 | -27.6443 | 95.4849 | -27.4704 | -27.5894 | -27.3239 | -0.54016 | -0.34332 | -0.77362 | 15.5823 | 28.6835 | 122.1817 | 29.2236 | 122.7219 | -0.26093 | -0.11444 | -0.041199 | -0.086975 | 0.059509 | -0.20599 | 0.32043 | 0.054931 | 16.1224 | 122.6761 | 0.17395 | 123.1293 | 123.1064 | 123.056 | 122.5662 | 122.7951 | -123.4497 | -123.1705 | 122.1359 | 122.8683 | 122.2366 | 27.1637
940.4844 | 122.9416 | -27.3468 | 95.4803 | -0.69855 | 0.70509 | 0.071256 | 0.0013117 | 0.00019874 | 0.64222 | -0.00031193 | -0.032379 | 0.0026725 | 0.067063 | 0.069045 | -0.0019568 | -0.00080758 | 0.0039413 | 95.0958 | 95.5536 | -27.5436 | 95.0088 | -11.3525 | 95.0775 | 1.2589 | -0.57678 | 95.5627 | -27.4658 | 95.5353 | -27.4521 | -27.5848 | -27.301 | -0.19684 | 0.073242 | -0.4715 | 15.9943 | 28.6057 | 122.4243 | 28.8025 | 122.6212 | -0.11902 | 0.082397 | 0.054931 | -0.10528 | 0.045777 | -0.23804 | 0.1648 | -0.11902 | 16.1911 | 122.5525 | 0.013733 | 123.0011 | 123.0972 | 123.0286 | 122.9004 | 122.9095 | -123.024 | -122.9462 | 122.3557 | 122.8821 | 122.4426 | 26.77
941.4844 | 123.0286 | -28.0243 | 94.725 | -0.75958 | 0.7053 | 0.072538 | -0.00039728 | -1.486e-05 | 0.63966 | 0.00011527 | 0.0011902 | -0.00053192 | 0.065781 | 0.063705 | -0.0017432 | -0.0025164 | 0.00095066 | 94.5007 | 94.8166 | -28.1937 | 94.4321 | -12.3093 | 94.4595 | 1.2314 | -0.5127 | 94.7937 | -28.1754 | 94.8807 | -28.1021 | -28.2715 | -28.0106 | -0.16937 | 0.091552 | -0.29297 | 15.715 | 29.2557 | 122.4838 | 29.425 | 122.6532 | -0.15106 | 0.068664 | 0.15564 | -0.07782 | 0.013733 | -0.24719 | 0.16479 | -0.09613 | 15.8844 | 122.6257 | 0.073242 | 123.056 | 123.0103 | 122.9691 | 122.8409 | 122.818 | -122.9187 | -122.9004 | 122.4564 | 122.905 | 122.525 | 27.5116
942.4844 | 122.9095 | -27.5024 | 95.3384 | -0.63751 | 0.70317 | 0.070402 | 0.0036615 | -0.00044226 | 0.63923 | -0.00052553 | -0.072052 | 0.0035269 | 0.066635 | 0.063705 | -0.0008886 | -0.0023028 | -0.00033114 | 94.9493 | 95.3979 | -27.7039 | 94.8486 | -11.6226 | 94.899 | 1.1948 | -0.68207 | 95.4346 | -27.6306 | 95.3201 | -27.6718 | -27.8 | -27.5208 | -0.20142 | 0.059509 | -0.48981 | 15.8798 | 28.6972 | 122.4014 | 28.8986 | 122.6028 | -0.12817 | 0.09613 | -0.018311 | -0.16937 | -0.018311 | -0.29755 | 0.10986 | -0.16937 | 16.0812 | 122.5525 | -0.041199 | 122.9507 | 123.1018 | 123.0652 | 122.9004 | 122.937 | -123.0423 | -122.9691 | 122.3511 | 122.8226 | 122.4518 | 26.8204
943.5469 | 122.9553 | -27.8 | 95.0546 | -0.66803 | 0.70231 | 0.072752 | 0.0030207 | -0.0012967 | 0.63944 | 0.0024653 | -0.044586 | 0.0024589 | 0.066422 | 0.064559 | -0.0034522 | -0.00059378 | -0.00033114 | 94.6976 | 95.0958 | -27.9968 | 94.6289 | -11.998 | 94.6793 | 1.3092 | -0.48981 | 95.1279 | -27.9099 | 95.0546 | -27.9099 | -28.0289 | -27.7634 | -0.19684 | 0.041199 | -0.42572 | 15.802 | 29.1092 | 122.4792 | 29.306 | 122.6761 | -0.10986 | 0.073243 | 0 | -0.10986 | 0.036621 | -0.22888 | 0.14648 | -0.11902 | 15.9988 | 122.6257 | 0 | 122.9645 | 123.0927 | 123.0377 | 122.8958 | 122.9279 | -123.0515 | -122.9645 | 122.4289 | 122.8546 | 122.4976 | 27.3102
944.4844 | 122.937 | -27.7359 | 95.1324 | -0.69092 | 0.70125 | 0.072324 | 0.0013117 | 0.0034029 | 0.64094 | 0.00096987 | -0.038483 | 0.0024589 | 0.065567 | 0.066268 | 0.0008204 | -0.0020892 | 0.0011643 | 94.6838 | 95.1645 | -27.9419 | 94.6335 | -11.9614 | 94.6701 | 1.3184 | -0.8194 | 95.2103 | -27.8458 | 95.1233 | -27.9099 | -28.0655 | -27.7267 | -0.20599 | 0.032044 | -0.49896 | 15.7745 | 29.0543 | 122.406 | 29.2603 | 122.612 | -0.10986 | 0.07782 | -0.009155 | -0.17395 | 0.009155 | -0.32959 | 0.11902 | -0.21973 | 15.9805 | 122.5754 | -0.064087 | 122.9691 | 123.1064 | 123.056 | 122.9004 | 122.9462 | -123.0743 | -122.9782 | 122.3694 | 122.8592 | 122.4197 | 26.9165
945.5469 | 122.9095 | -27.6947 | 95.1416 | -0.68329 | 0.70146 | 0.070402 | 0.0032343 | 0.0010531 | 0.63731 | -0.00052553 | -0.023224 | 0.0030997 | 0.067917 | 0.0652 | -0.0019568 | -0.00038018 | 0.0024461 | 94.7525 | 95.1828 | -27.8915 | 94.6655 | -11.4807 | 94.7067 | 94.9814 | -0.94757 | 95.2286 | -27.8412 | 95.1279 | -27.8961 | -27.9968 | -27.6901 | -0.19684 | 0.041198 | -0.47608 | 16.214 | 122.6761 | 122.4014 | 122.8729 | 122.5983 | -0.14649 | 0.086975 | -0.013733 | -0.20142 | 0.004577 | -0.30212 | 0.15106 | -0.15564 | 16.4108 | 122.5571 | -0.054931 | 122.9691 | 123.0743 | 123.0698 | 122.8775 | 122.9233 | -123.0331 | -122.9828 | 122.3602 | 122.8226 | 122.4472 | 26.7471
946.4844 | 122.9141 | -27.1317 | 95.7138 | -0.69092 | 0.69954 | 0.07147 | 0.0023797 | 0.0023349 | 0.63624 | -0.00052553 | -0.026276 | 0.0024589 | 0.066208 | 0.061568 | -0.000675 | -0.00016658 | 0.0041551 | 95.0912 | 95.5261 | -27.5757 | 95.1736 | -10.7071 | 95.224 | 95.4987 | -0.53101 | 95.8145 | -27.2644 | 95.7001 | -27.2827 | -27.4063 | -27.1179 | -0.44403 | -0.18768 | -0.54016 | 16.4246 | 122.6303 | 122.3557 | 123.0743 | 122.7997 | -0.13275 | 0.10071 | -0.013733 | -0.15106 | 0.013733 | -0.27466 | 0.14648 | -0.14191 | 16.8686 | 122.7493 | -0.018311 | 122.9645 | 123.1018 | 123.0789 | 122.6578 | 122.9462 | -123.2895 | -122.9782 | 122.3053 | 122.8317 | 122.2229 | 26.6006
947.4844 | 123.0377 | -27.7863 | 94.9951 | -0.72144 | 0.70039 | 0.07147 | 0.0019525 | 0.00041234 | 0.63453 | -0.0018073 | 0.0072936 | 0.0013907 | 0.065995 | 0.065627 | -0.0025976 | -0.0014484 | -0.0024673 | 94.7067 | 95.0134 | -28.0106 | 94.6518 | -11.4761 | 94.6884 | 94.9493 | -0.59967 | 95.0958 | -27.9419 | 95.1141 | -27.8595 | -27.9968 | -27.713 | -0.2243 | 0.018311 | -0.34332 | 16.3101 | 122.7356 | 122.4747 | 122.9599 | 122.699 | -0.15564 | 0.10071 | 0.11902 | -0.073242 | 0.073242 | -0.21057 | 0.22888 | -0.054931 | 16.5344 | 122.6624 | 0.082398 | 123.056 | 123.024 | 123.0377 | 122.7997 | 122.8821 | -123.0057 | -122.937 | 122.438 | 122.9004 | 122.493 | 27.1866
948.4844 | 122.8958 | -28.0609 | 94.8257 | -0.72144 | 0.69911 | 0.072111 | 0.0028069 | -0.0017239 | 0.6356 | -0.0022345 | -0.047638 | 0.0033133 | 0.06984 | 0.066482 | -0.0021704 | -0.0012348 | -0.0016129 | 94.4 | 94.8715 | -28.2211 | 94.3359 | -11.9522 | 94.4 | 94.6426 | -0.71869 | 94.9081 | -28.1479 | 94.7205 | -28.1296 | -28.299 | -28.0838 | -0.16022 | 0.045776 | -0.48981 | 16.1087 | 122.7036 | 122.4609 | 122.8638 | 122.6212 | -0.086975 | 0.082397 | -0.10529 | -0.068665 | -0.022888 | -0.23804 | 0.064087 | -0.15106 | 16.2689 | 122.5571 | 0.01831 | 122.8683 | 123.0927 | 123.056 | 122.9324 | 122.9691 | -123.0469 | -122.9736 | 122.3969 | 122.7814 | 122.4609 | 27.3422
949.5469 | 122.905 | -28.1067 | 94.7754 | -0.69092 | 0.6974 | 0.071256 | 0.0038751 | -0.0015103 | 0.63239 | 0.00011527 | -0.05069 | 0.0030997 | 0.06984 | 0.069045 | -0.003025 | -0.00080758 | 0.00073706 | 94.3542 | 94.812 | -28.2898 | 94.2673 | -12.0392 | 94.3176 | 94.5786 | -0.71869 | 94.8486 | -28.2257 | 94.7571 | -28.244 | -28.4409 | -28.1204 | -0.18311 | 0.036621 | -0.50812 | 16.0675 | 122.6852 | 122.4243 | 122.8683 | 122.6074 | -0.11902 | 0.073242 | -0.018311 | -0.13733 | -0.013733 | -0.33417 | 0.10529 | -0.21515 | 16.2506 | 122.5571 | -0.018311 | 122.9828 | 123.1018 | 123.0743 | 122.9187 | 122.9553 | -123.0652 | -123.0011 | 122.374 | 122.8638 | 122.4609 | 27.388
950.4844 | 122.9004 | -27.7451 | 95.1324 | -0.69092 | 0.69783 | 0.073606 | 0.0017389 | 0.00062594 | 0.63218 | 0.00054267 | -0.020172 | 0.0033133 | 0.070267 | 0.070113 | -0.001316 | 0.00090142 | 9.6064e-05 | 94.7525 | 95.1599 | -27.9236 | 94.6426 | -11.4532 | 94.6976 | 94.9402 | -0.65002 | 95.2423 | -27.832 | 95.0958 | -27.887 | -28.0106 | -27.7176 | -0.17853 | 0.027466 | -0.48981 | 16.2918 | 122.6852 | 122.4426 | 122.8638 | 122.6212 | -0.086975 | 0.10986 | -0.036621 | -0.14191 | 0.027466 | -0.2655 | 0.11444 | -0.17853 | 16.4703 | 122.5662 | -0.054932 | 122.9279 | 123.0835 | 123.0743 | 122.905 | 122.9874 | -123.056 | -122.9645 | 122.3877 | 122.8409 | 122.4976 | 27.095
951.5469 | 122.9416 | -27.5986 | 95.2515 | -0.74432 | 0.69655 | 0.07147 | 0.0015253 | 0.0010531 | 0.63304 | 0.00075627 | -0.038483 | 0.0016043 | 0.065567 | 0.068191 | -0.0025976 | -0.001662 | 0.00095066 | 94.8395 | 95.2881 | -27.7634 | 94.8212 | -11.2335 | 94.8807 | 95.1187 | -0.59509 | 95.3568 | -27.7267 | 95.224 | -27.7176 | -27.8412 | -27.5711 | -0.16479 | 0.036621 | -0.4303 | 16.3651 | 122.7173 | 122.4792 | 122.8821 | 122.644 | -0.12817 | 0.10529 | -0.027466 | -0.11902 | 0.027466 | -0.24262 | 0.15564 | -0.11444 | 16.5298 | 122.5845 | 0.009156 | 122.9507 | 123.0515 | 123.0835 | 122.8867 | 122.9553 | -123.0148 | -122.9782 | 122.4197 | 122.8226 | 122.4381 | 27.0035
952.4844 | 122.8775 | -27.6215 | 95.2286 | -0.68329 | 0.69569 | 0.071683 | 0.0021661 | -0.0019377 | 0.63154 | 0.0013971 | -0.062897 | 0.0013907 | 0.067276 | 0.071822 | -0.0011022 | -0.00016658 | 0.00052346 | 94.8303 | 95.2652 | -27.8137 | 94.7388 | -11.3434 | 94.7571 | 95.05 | -0.74158 | 95.3476 | -27.7588 | 95.1599 | -27.8183 | -27.9282 | -27.6489 | -0.19226 | 0.036621 | -0.48981 | 16.2781 | 122.6715 | 122.3785 | 122.8638 | 122.5708 | -0.13733 | 0.11902 | -0.068665 | -0.19684 | -0.027466 | -0.3067 | 0.10986 | -0.16937 | 16.4703 | 122.5525 | -0.059509 | 122.9187 | 123.0789 | 123.1064 | 122.8867 | 122.9691 | -123.0423 | -122.9874 | 122.3602 | 122.7814 | 122.4518 | 26.8799
953.4844 | 122.9599 | -27.8412 | 94.9768 | -0.65277 | 0.69505 | 0.072324 | 2.9918e-05 | -0.0015103 | 0.63069 | -0.0028753 | -0.020172 | 0.0018179 | 0.067063 | 0.066909 | -0.0004614 | 0.00068782 | -0.00075834 | 94.6014 | 95.0455 | -28.0197 | 94.519 | -11.6364 | 94.5694 | 94.8441 | -0.71869 | 95.1004 | -27.9556 | 94.9951 | -27.9648 | -28.0701 | -27.7954 | -0.17853 | 0.068664 | -0.45776 | 16.2048 | 122.6852 | 122.4106 | 122.8638 | 122.5891 | -0.11444 | 0.1236 | 0.01831 | -0.1236 | 0.045777 | -0.22888 | 0.16022 | -0.11444 | 16.3834 | 122.5388 | -0.009156 | 122.9507 | 123.0652 | 123.056 | 122.8867 | 122.9416 | -122.9965 | -122.9324 | 122.3602 | 122.8363 | 122.4426 | 27.1225
954.5469 | 123.0057 | -27.9648 | 94.8257 | -0.66803 | 0.69484 | 0.071683 | 0.00045712 | -0.0010831 | 0.63026 | -0.00031193 | 0.059174 | 0.00096348 | 0.067276 | 0.0605 | -0.0015296 | -0.0035846 | -0.00011754 | 94.5419 | 94.8853 | -28.1204 | 94.5648 | -11.7462 | 94.5236 | 94.8532 | -0.46234 | 94.9036 | -28.0655 | 94.9173 | -28.0151 | -28.1067 | -27.8961 | -0.15564 | 0.059509 | -0.26093 | 16.2186 | 122.818 | 122.4884 | 122.9736 | 122.644 | -0.10071 | 0.077819 | 0.091552 | -0.050354 | 0.068665 | -0.14191 | 0.16937 | -0.041198 | 16.3742 | 122.6852 | 0.050354 | 122.9828 | 123.0057 | 122.9691 | 122.85 | 122.8683 | -122.9462 | -122.8912 | 122.5296 | 122.8821 | 122.5067 | 27.5024
955.4844 | 123.0148 | -27.8183 | 94.9493 | -0.75195 | 0.69142 | 0.072324 | 0.0036615 | 0.00083954 | 0.62769 | -0.00073913 | 0.0072936 | 0.0028861 | 0.065995 | 0.063705 | -0.0036658 | 0.00090142 | -0.0043899 | 94.6014 | 94.9905 | -28.0518 | 94.5465 | -11.6364 | 94.5831 | 94.8578 | -0.67291 | 95.0272 | -27.9785 | 95.0134 | -27.919 | -28.0151 | -27.7634 | -0.23346 | 0.041199 | -0.40283 | 16.1819 | 122.6761 | 122.4014 | 122.9095 | 122.6349 | -0.16022 | 0.07782 | 0.064087 | -0.10071 | 0.054931 | -0.19684 | 0.21515 | -0.036621 | 16.4154 | 122.5983 | 0.05951 | 122.9919 | 123.0423 | 123.0057 | 122.8088 | 122.8455 | -123.0011 | -122.9279 | 122.3648 | 122.8317 | 122.4197 | 27.1454
956.4844 | 122.9141 | -27.8915 | 94.9493 | -0.64514 | 0.69313 | 0.072538 | 0.0025933 | 0.0038303 | 0.62428 | 0.0022517 | -0.032379 | 0.0013907 | 0.066635 | 0.067763 | -0.0025976 | -0.001662 | -0.00097194 | 94.5877 | 94.9905 | -28.0655 | 94.5007 | -11.6776 | 94.5465 | 94.7891 | -0.68665 | 95.0363 | -28.0243 | 94.931 | -28.0563 | -28.1616 | -27.887 | -0.17395 | 0.041199 | -0.44861 | 16.214 | 122.6807 | 122.4381 | 122.8546 | 122.612 | -0.13275 | 0.086975 | -0.018311 | -0.16479 | 0.004578 | -0.27008 | 0.13733 | -0.13733 | 16.3879 | 122.5662 | -0.032043 | 122.9553 | 123.056 | 123.0606 | 122.8821 | 122.9279 | -123.0148 | -122.9736 | 122.3923 | 122.8226 | 122.4792 | 27.2049
957.5469 | 122.8867 | -28.2532 | 94.6106 | -0.69855 | 0.69163 | 0.072752 | 0.0025933 | -0.0015103 | 0.62513 | 0.0011835 | -0.053741 | 0.0028861 | 0.065354 | 0.069045 | -0.0032386 | -0.00016658 | 9.6064e-05 | 94.2032 | 94.6335 | -28.4546 | 94.1162 | -12.2452 | 94.162 | 94.4138 | -0.71411 | 94.6884 | -28.3768 | 94.5374 | -28.4317 | -28.5416 | -28.2623 | -0.20142 | 0.022888 | -0.49438 | 16.008 | 122.6669 | 122.4152 | 122.8683 | 122.6166 | -0.1236 | 0.07782 | -0.073242 | -0.17853 | -0.009155 | -0.28839 | 0.11444 | -0.16479 | 16.2094 | 122.5708 | -0.054932 | 122.9141 | 123.0881 | 123.0652 | 122.8867 | 122.9416 | -123.0652 | -122.9874 | 122.3694 | 122.7905 | 122.4564 | 27.5391
958.4844 | 122.8775 | -28.2211 | 94.6564 | -0.6604 | 0.69099 | 0.072324 | 0.0023797 | 0.00041234 | 0.62705 | -0.00095273 | -0.056793 | 0.0043815 | 0.066422 | 0.064559 | -0.0002478 | -0.001662 | 0.00095066 | 94.2764 | 94.6838 | -28.3768 | 94.1528 | -12.1902 | 94.2032 | 94.4504 | -0.78278 | 94.7617 | -28.3127 | 94.6152 | -28.3768 | -28.4775 | -28.1982 | -0.15564 | 0.027466 | -0.50354 | 16.0309 | 122.6715 | 122.4243 | 122.8271 | 122.58 | -0.091553 | 0.10529 | -0.041199 | -0.15564 | 0.022888 | -0.25635 | 0.11444 | -0.1648 | 16.1865 | 122.5296 | -0.064087 | 122.9279 | 123.0606 | 123.0743 | 122.905 | 122.9828 | -123.0331 | -122.9691 | 122.374 | 122.8363 | 122.4976 | 27.4384
959.4844 | 122.937 | -28.3035 | 94.5099 | -0.70618 | 0.6895 | 0.072324 | 0.0023797 | 0.0025485 | 0.6247 | 0.0028925 | -0.029327 | 0.0035269 | 0.066849 | 0.066909 | -0.0011022 | -0.0020892 | -0.0028945 | 94.1391 | 94.574 | -28.5141 | 94.0475 | -12.3047 | 94.1025 | 94.3726 | -0.77362 | 94.6289 | -28.4134 | 94.5465 | -28.418 | -28.537 | -28.2852 | -0.21057 | 0.064087 | -0.46234 | 15.9988 | 122.6761 | 122.406 | 122.8867 | 122.6166 | -0.10986 | 0.11902 | 0.036621 | -0.11444 | 0.018311 | -0.23346 | 0.12817 | -0.1236 | 16.2094 | 122.5616 | -0.004578 | 122.9599 | 123.0881 | 123.0423 | 122.8775 | 122.9324 | -123.024 | -122.9233 | 122.3511 | 122.85 | 122.4426 | 27.5299
960.4844 | 122.8867 | -28.2486 | 94.6198 | -0.67566 | 0.68715 | 0.072324 | 0.00045712 | 0.0059665 | 0.6247 | 0.00011527 | -0.0049134 | 0.0018179 | 0.064926 | 0.068191 | 0.001034 | -0.00059378 | -0.00097194 | 94.2032 | 94.6518 | -28.4363 | 94.1162 | -12.2177 | 94.1803 | 94.4229 | -0.71869 | 94.693 | -28.3447 | 94.5374 | -28.3768 | -28.537 | -28.2486 | -0.18768 | 0.032043 | -0.50354 | 16.0309 | 122.6715 | 122.4289 | 122.8592 | 122.6166 | -0.096131 | 0.073242 | -0.082397 | -0.12817 | 0 | -0.28839 | 0.096131 | -0.19226 | 16.2186 | 122.5525 | -0.032043 | 122.8821 | 123.0881 | 123.0377 | 122.9004 | 122.9416 | -123.056 | -122.9645 | 122.3648 | 122.7859 | 122.4518 | 27.5299
961.5469 | 122.8912 | -27.9694 | 94.8761 | -0.65277 | 0.68886 | 0.072752 | 0.0023797 | 0.0014803 | 0.6247 | 0.00032907 | -0.029327 | 0.0035269 | 0.067917 | 0.064345 | -0.002384 | -0.0018756 | -0.0031081 | 94.487 | 94.9036 | -28.1799 | 94.3771 | -11.7966 | 94.4366 | 94.6793 | -0.75531 | 94.9631 | -28.0838 | 94.812 | -28.1433 | -28.2578 | -27.9785 | -0.21057 | 0.027465 | -0.49896 | 16.1728 | 122.6486 | 122.406 | 122.8592 | 122.6166 | -0.11444 | 0.086975 | -0.064087 | -0.17395 | -0.009156 | -0.28839 | 0.10529 | -0.17395 | 16.3834 | 122.5571 | -0.05951 | 122.8958 | 123.0835 | 123.0469 | 122.8729 | 122.9324 | -123.056 | -122.9599 | 122.3465 | 122.7814 | 122.4564 | 27.2141
962.4844 | 122.8912 | -28.2303 | 94.6198 | -0.72144 | 0.68629 | 0.073606 | 0.0025933 | 0.0059665 | 0.62257 | -0.0013799 | 0.004242 | 0.0016043 | 0.067063 | 0.067123 | -0.0008886 | -0.00059378 | 0.00052346 | 94.2673 | 94.7159 | -28.3768 | 94.4275 | -11.9888 | 94.1116 | 94.5557 | -0.83313 | 94.7525 | -28.2669 | 94.5923 | -28.3768 | -28.5278 | -28.2303 | -0.14648 | 0.09613 | -0.19226 | 16.2415 | 122.7859 | 122.3419 | 122.9324 | 122.4884 | -0.036621 | 0.13275 | -0.027466 | -0.14648 | 0 | -0.29755 | 0.036621 | -0.26093 | 16.3879 | 122.8043 | -0.10986 | 122.8592 | 123.0927 | 123.0194 | 122.9462 | 122.9828 | -122.9965 | -122.8867 | 122.6578 | 122.8226 | 122.4976 | 27.3972
963.5469 | 122.9095 | -28.3813 | 94.4412 | -0.68329 | 0.688 | 0.069547 | 0.0034479 | 0.0036165 | 0.62043 | 0.0018243 | -0.026276 | 0.0024589 | 0.065995 | 0.063705 | -0.0019568 | -0.0012348 | 0.0018051 | 94.1162 | 94.5007 | -28.5553 | 94.0109 | -12.291 | 94.1757 | 94.4183 | -0.65002 | 94.5511 | -28.4866 | 94.4412 | -28.5095 | -28.6148 | -28.3539 | -0.17395 | 0.059509 | -0.4303 | 16.0904 | 122.7997 | 122.5571 | 122.9736 | 122.731 | -0.10529 | 0.10986 | 0 | -0.12817 | 0.027466 | -0.23346 | 0.13275 | -0.12817 | 16.2643 | 122.5662 | -0.022888 | 122.9279 | 123.056 | 123.0377 | 122.8821 | 122.9324 | -122.9965 | -122.9279 | 122.3923 | 122.8226 | 122.4976 | 27.7313
964.4844 | 122.8821 | -27.8 | 95.0272 | -0.63751 | 0.68522 | 0.070188 | 0.0043023 | 0.0038303 | 0.62171 | 0.0018243 | -0.035431 | 0.0018179 | 0.066422 | 0.067977 | -0.0019568 | 0.00047422 | 0.0011643 | 94.6564 | 95.0821 | -27.9877 | 94.5602 | -11.554 | 94.5969 | 94.8624 | -0.72784 | 95.1141 | -27.9373 | 94.9539 | -27.9739 | -28.1021 | -27.8183 | -0.18768 | 0.054931 | -0.46692 | 16.246 | 122.6624 | 122.3969 | 122.85 | 122.5845 | -0.13733 | 0.086975 | -0.073243 | -0.17395 | -0.01831 | -0.30212 | 0.11902 | -0.1648 | 16.4337 | 122.5479 | -0.036621 | 122.8912 | 123.0698 | 123.0515 | 122.8821 | 122.9141 | -123.0148 | -122.9645 | 122.3602 | 122.7539 | 122.4564 | 27.0721
965.4844 | 123.0011 | -28.006 | 94.7433 | -0.71381 | 0.68651 | 0.072538 | 0.0030207 | -0.0010831 | 0.62022 | -9.8328e-05 | 0.062225 | 0.0018179 | 0.064926 | 0.070327 | -0.0004614 | -0.0012348 | 9.6064e-05 | 94.4778 | 94.7845 | -28.1799 | 94.4092 | -11.7416 | 94.4687 | 94.725 | -0.70038 | 94.8212 | -28.1525 | 94.931 | -28.1708 | -28.1525 | -27.919 | -0.17395 | 0.041199 | -0.33417 | 16.2643 | 122.731 | 122.4747 | 122.905 | 122.6486 | -0.14649 | 0.07782 | 0.18768 | -0.1648 | 0.086975 | -0.14649 | 0.23346 | 0 | 16.4383 | 122.5891 | -0.01831 | 123.0835 | 122.9645 | 122.9736 | 122.7905 | 122.8271 | -122.9233 | -122.8958 | 122.4152 | 122.937 | 122.4838 | 27.3056
966.5469 | 122.9324 | -27.9968 | 94.8166 | -0.6604 | 0.68437 | 0.069761 | 0.0021661 | -0.0019377 | 0.62342 | 0.00032907 | 0.0011902 | 0.0037405 | 0.066422 | 0.066054 | -0.0011022 | -0.0010212 | 0.0013779 | 94.4733 | 94.9036 | -28.1708 | 94.368 | -11.8057 | 94.4687 | 94.7113 | -0.6546 | 94.9265 | -28.1204 | 94.8212 | -28.1113 | -28.2257 | -27.9694 | -0.17395 | 0.086975 | -0.44861 | 16.1911 | 122.7081 | 122.4655 | 122.8821 | 122.6395 | -0.1236 | 0.10986 | 0.004578 | -0.11444 | 0.027466 | -0.22888 | 0.15106 | -0.10529 | 16.3651 | 122.5388 | 0.009155 | 122.9416 | 123.0743 | 123.0469 | 122.9004 | 122.9233 | -122.9874 | -122.937 | 122.3648 | 122.818 | 122.4701 | 27.3422
967.4844 | 123.0103 | -27.9785 | 94.8074 | -0.68329 | 0.6833 | 0.07147 | 0.0019525 | -0.0010831 | 0.623 | -0.0011663 | 0.004242 | 0.00074988 | 0.066422 | 0.063918 | -0.0021704 | -0.0012348 | 0.0011643 | 94.4778 | 94.8166 | -28.1708 | 94.4366 | -11.7233 | 94.4641 | 94.7388 | -0.70496 | 94.8349 | -28.125 | 94.8715 | -28.0609 | -28.1708 | -27.9236 | -0.19226 | 0.009155 | -0.37079 | 16.2552 | 122.7173 | 122.4426 | 122.9095 | 122.6349 | -0.14648 | 0.027466 | 0.064087 | -0.082397 | 0.054932 | -0.19226 | 0.20142 | -0.045776 | 16.4474 | 122.6074 | 0.064087 | 122.9965 | 122.9874 | 122.9599 | 122.7951 | 122.8134 | -122.9782 | -122.9324 | 122.4152 | 122.85 | 122.4564 | 27.2736
968.4844 | 122.8775 | -28.1342 | 94.7296 | -0.71381 | 0.68437 | 0.070615 | 0.00088432 | 0.0036165 | 0.61701 | 0.0020379 | -0.05069 | 0.0052359 | 0.065354 | 0.066695 | -0.004093 | -0.00080758 | -0.00033114 | 94.3222 | 94.7571 | -28.3127 | 94.2352 | -11.9934 | 94.281 | 94.5557 | -1.0757 | 94.7983 | -28.2211 | 94.6655 | -28.2578 | -28.3951 | -28.0975 | -0.17853 | 0.027466 | -0.49438 | 16.1407 | 122.6898 | 122.4152 | 122.8683 | 122.5937 | -0.086975 | 0.068665 | -0.064087 | -0.1236 | 0.036621 | -0.26093 | 0.1236 | -0.17395 | 16.3193 | 122.5479 | -0.036621 | 122.8867 | 123.0698 | 123.0194 | 122.8912 | 122.9324 | -123.0423 | -122.9507 | 122.3694 | 122.7997 | 122.4564 | 27.0584
969.5469 | 122.8592 | -27.919 | 94.9448 | -0.63751 | 0.68266 | 0.069761 | 0.0019525 | -0.00022866 | 0.61936 | 0.00075627 | -0.056793 | 0.0037405 | 0.065781 | 0.068831 | -0.003025 | -0.0018756 | 0.0026597 | 94.5557 | 94.9905 | -28.0884 | 94.4595 | -11.6638 | 94.4733 | 94.7662 | -0.8606 | 95.0775 | -28.0106 | 94.8807 | -28.0655 | -28.1845 | -27.8961 | -0.16937 | 0.045777 | -0.48523 | 16.2552 | 122.6852 | 122.3923 | 122.8546 | 122.5616 | -0.091553 | 0.13275 | -0.064087 | -0.14649 | 0.022888 | -0.2655 | 0.11444 | -0.17395 | 16.4246 | 122.5479 | -0.054932 | 122.8912 | 123.0789 | 123.0881 | 122.9095 | 122.9965 | -123.0331 | -122.9553 | 122.3785 | 122.7997 | 122.4747 | 27.0584
970.4844 | 122.8729 | -27.8275 | 95.0272 | -0.65277 | 0.68223 | 0.071043 | 2.9918e-05 | 0.0025485 | 0.6153 | 0.0020379 | -0.038483 | 0.0024589 | 0.065995 | 0.066268 | -0.0032386 | 0.00047422 | 0.0013779 | 94.6198 | 95.0638 | -28.0197 | 94.5328 | -11.5402 | 94.574 | 94.8074 | -0.80566 | 95.0958 | -27.9373 | 94.9493 | -28.0106 | -28.1113 | -27.8549 | -0.19226 | 0.036621 | -0.49439 | 16.2872 | 122.6349 | 122.4014 | 122.8271 | 122.5937 | -0.10986 | 0.068664 | -0.07782 | -0.18311 | -0.027465 | -0.28381 | 0.082398 | -0.17395 | 16.4795 | 122.5525 | -0.073242 | 122.8867 | 123.0835 | 123.0331 | 122.8912 | 122.9233 | -123.0469 | -122.9645 | 122.3602 | 122.7768 | 122.4472 | 27.0218
971.5 | 122.9736 | -27.7588 | 95.0088 | -0.6604 | 0.68052 | 0.071897 | -0.0014655 | -0.00086946 | 0.61723 | -0.0035163 | 0.05307 | 0.00096348 | 0.064286 | 0.066909 | -0.0025976 | -0.0012348 | 0.0020187 | 94.7021 | 95.0546 | -27.9144 | 94.812 | -11.2839 | 94.3542 | 95.0226 | -0.59052 | 95.0592 | -27.8687 | 95.0775 | -27.8046 | -27.8915 | -27.6627 | -0.15564 | 0.045776 | -0.19684 | 16.4749 | 122.7814 | 122.113 | 122.937 | 122.2687 | -0.10986 | 0.050354 | 0.068665 | -0.045776 | 0.09613 | -0.13275 | 0.20599 | -0.022889 | 16.6306 | 122.7264 | 0.064087 | 122.9462 | 122.9691 | 122.9279 | 122.8134 | 122.818 | -122.9233 | -122.8775 | 122.5708 | 122.8363 | 122.4609 | 27.1683
972.4844 | 122.85 | -27.8046 | 95.0409 | -0.69092 | 0.68287 | 0.072538 | 0.00024352 | -0.00065586 | 0.61723 | 0.0046015 | -0.065949 | 0.0030997 | 0.068344 | 0.068191 | -0.0015296 | 0.00047422 | -0.0046035 | 94.6243 | 95.0958 | -27.9785 | 94.5465 | -11.4899 | 94.5831 | 94.8486 | -0.86975 | 95.1508 | -27.8915 | 94.9768 | -27.951 | -28.0792 | -27.7817 | -0.17395 | 0.054931 | -0.49438 | 16.3147 | 122.6532 | 122.3877 | 122.8271 | 122.5616 | -0.086976 | 0.10986 | -0.064087 | -0.14648 | 0.022888 | -0.27466 | 0.10986 | -0.18768 | 16.4886 | 122.525 | -0.059509 | 122.8683 | 123.0743 | 123.0423 | 122.9004 | 122.9553 | -123.0194 | -122.9324 | 122.3511 | 122.7814 | 122.4289 | 26.9348
973.5469 | 122.905 | -27.8091 | 95.0317 | -0.65277 | 0.67946 | 0.070188 | 0.0015253 | 0.00019874 | 0.61488 | -0.00073913 | -0.0079652 | 0.0013907 | 0.06749 | 0.065841 | -0.0028112 | -0.0014484 | -0.0031081 | 94.6335 | 95.0958 | -27.9785 | 94.574 | -11.4853 | 94.6518 | 94.9081 | -0.70953 | 95.1096 | -27.9144 | 95.0043 | -27.9099 | -28.0243 | -27.7817 | -0.16937 | 0.064087 | -0.45776 | 16.3239 | 122.7173 | 122.4609 | 122.8867 | 122.6303 | -0.10529 | 0.07782 | -0.027466 | -0.10071 | 0.027466 | -0.21515 | 0.13275 | -0.10986 | 16.4932 | 122.5525 | 0.004578 | 122.9187 | 123.0743 | 123.024 | 122.905 | 122.9187 | -123.0103 | -122.9462 | 122.3831 | 122.8134 | 122.4426 | 27.0996
974.4844 | 122.8638 | -27.8229 | 95.0043 | -0.68329 | 0.67967 | 0.072538 | 0.0021661 | 0.00041234 | 0.6153 | -0.00073913 | -0.023224 | 0.0020315 | 0.066635 | 0.066909 | -0.001316 | -0.001662 | -0.00097194 | 94.6106 | 95.0546 | -28.0151 | 94.5374 | -11.5036 | 94.5648 | 94.8212 | -0.86517 | 95.1233 | -27.9236 | 94.9768 | -27.9831 | -28.1113 | -27.8275 | -0.19226 | 0.050354 | -0.46692 | 16.3193 | 122.644 | 122.3877 | 122.8363 | 122.58 | -0.10071 | 0.11902 | -0.027465 | -0.16022 | -0.004578 | -0.28839 | 0.09613 | -0.18768 | 16.5115 | 122.5525 | -0.059509 | 122.9004 | 123.0698 | 123.0469 | 122.8775 | 122.9462 | -123.0194 | -122.9279 | 122.3602 | 122.7997 | 122.4335 | 26.9577
975.4844 | 123.0148 | -27.5482 | 95.2103 | -0.67566 | 0.67903 | 0.071683 | 0.0013117 | 0.00083954 | 0.61466 | -0.0028753 | 0.004242 | 0.0022453 | 0.066849 | 0.067336 | -0.0015296 | -0.0014484 | 0.0018051 | 94.8669 | 95.2606 | -27.7496 | 94.8395 | -11.0092 | 94.8395 | 95.1187 | -0.75989 | 95.2835 | -27.6764 | 95.311 | -27.6215 | -27.7405 | -27.475 | -0.20142 | 0.050354 | -0.37079 | 16.539 | 122.6669 | 122.3877 | 122.8683 | 122.5891 | -0.12817 | 0.073242 | 0.10071 | -0.073242 | 0.073242 | -0.19226 | 0.20142 | -0.064087 | 16.7404 | 122.5891 | 0.054932 | 122.9874 | 123.0103 | 122.9599 | 122.8088 | 122.8317 | -122.9599 | -122.8867 | 122.3877 | 122.8592 | 122.4152 | 26.7883
976.4844 | 122.9324 | -27.6352 | 95.1324 | -0.68329 | 0.67668 | 0.069761 | -0.00018368 | -0.0021513 | 0.61253 | 0.0013971 | 0.037811 | 0.00032248 | 0.067063 | 0.063277 | -0.0025976 | -0.0025164 | -0.0011855 | 94.8349 | 95.2286 | -27.7771 | 94.7845 | -11.0733 | 94.8669 | 95.1279 | -0.7782 | 95.2515 | -27.6993 | 95.2194 | -27.6764 | -27.8046 | -27.6031 | -0.14191 | 0.096131 | -0.3479 | 16.5619 | 122.7631 | 122.5021 | 122.905 | 122.644 | -0.064087 | 0.11902 | 0.086975 | -0.041199 | 0.032044 | -0.16937 | 0.096131 | -0.10528 | 16.7038 | 122.5616 | 0.022888 | 122.9187 | 123.0057 | 122.9507 | 122.8638 | 122.8867 | -122.9095 | -122.8317 | 122.4197 | 122.8546 | 122.4701 | 26.857
977.5469 | 122.9187 | -28.4683 | 94.3359 | -0.66803 | 0.67796 | 0.070188 | 0.0030207 | 0.0027621 | 0.61317 | 0.00032907 | -0.044586 | 0.0033133 | 0.068131 | 0.068404 | -0.0034522 | 0.00047422 | -0.00075834 | 93.9743 | 94.3954 | -28.6606 | 93.9148 | -12.3596 | 93.9743 | 94.2123 | -0.74158 | 94.4458 | -28.5828 | 94.3268 | -28.5965 | -28.7384 | -28.4546 | -0.19226 | 0.05951 | -0.42114 | 16.1087 | 122.6807 | 122.4426 | 122.8729 | 122.6349 | -0.11444 | 0.10986 | -0.009155 | -0.12817 | 0.013733 | -0.27008 | 0.12817 | -0.15564 | 16.301 | 122.5754 | -0.013733 | 122.9095 | 123.056 | 123.0286 | 122.8638 | 122.9141 | -122.9965 | -122.9187 | 122.3831 | 122.7951 | 122.4426 | 27.7267
978.4844 | 122.8592 | -27.1683 | 95.6543 | -0.65277 | 0.67604 | 0.07382 | 0.0015253 | 0.00083954 | 0.61295 | 0.0022517 | -0.05069 | 0.0020315 | 0.066422 | 0.067336 | -0.0021704 | -0.00038018 | 0.0028733 | 95.2606 | 95.7047 | -27.3788 | 95.1508 | -10.5057 | 95.1874 | 95.4849 | -0.86517 | 95.7504 | -27.301 | 95.5811 | -27.3605 | -27.4841 | -27.2003 | -0.21057 | 0.050354 | -0.50354 | 16.6626 | 122.6532 | 122.3557 | 122.8638 | 122.5662 | -0.13275 | 0.09613 | -0.073242 | -0.19226 | -0.032043 | -0.31586 | 0.10071 | -0.18311 | 16.8732 | 122.5296 | -0.05951 | 122.8821 | 123.0835 | 123.0515 | 122.8729 | 122.9187 | -123.0331 | -122.9553 | 122.319 | 122.7493 | 122.4289 | 26.3031
979.4844 | 122.9187 | -27.6169 | 95.1645 | -0.65277 | 0.67476 | 0.071897 | 0.0023797 | 0.00062594 | 0.61146 | -0.0018073 | -0.041534 | 0.0022453 | 0.06749 | 0.067763 | -0.0015296 | -0.0014484 | 0.00052346 | 94.7891 | 95.2515 | -27.832 | 94.7113 | -11.1008 | 94.7754 | 95.0546 | -0.86975 | 95.3064 | -27.7451 | 95.2011 | -27.7451 | -27.8595 | -27.5803 | -0.21515 | 0.086975 | -0.45319 | 16.5161 | 122.6715 | 122.3923 | 122.8867 | 122.6074 | -0.12817 | 0.14191 | 0.036621 | -0.12817 | 0.036621 | -0.24262 | 0.1648 | -0.11444 | 16.7313 | 122.5433 | 0 | 122.9462 | 123.0835 | 123.0515 | 122.8683 | 122.9233 | -122.9965 | -122.9095 | 122.3282 | 122.818 | 122.406 | 26.7471
980.5469 | 122.9919 | -27.6306 | 95.137 | -0.6604 | 0.67604 | 0.071683 | -0.00061088 | -0.0057829 | 0.60954 | 0.0031061 | -0.0079652 | 0.0013907 | 0.065567 | 0.068404 | -0.0036658 | -0.0035846 | -0.00097194 | 94.8166 | 95.1828 | -27.8183 | 94.6289 | -11.2335 | 95.018 | 95.1004 | -0.58594 | 95.2148 | -27.7451 | 95.2011 | -27.6672 | -27.7542 | -27.5528 | -0.18768 | 0.045776 | -0.50812 | 16.3971 | 122.731 | 122.6486 | 122.9187 | 122.8363 | -0.11444 | 0.07782 | 0.064087 | -0.036621 | 0.07782 | -0.1236 | 0.19226 | -0.009155 | 16.5848 | 122.4472 | 0.07782 | 122.9462 | 123.0011 | 122.9599 | 122.8134 | 122.8455 | -122.9553 | -122.8821 | 122.2595 | 122.8317 | 122.4472 | 27.0447
981.5 | 122.9553 | -27.3468 | 95.43 | -0.67566 | 0.67497 | 0.071897 | 0.0015253 | 0.0016939 | 0.60996 | -9.8328e-05 | 0.034759 | 0.00053628 | 0.06749 | 0.062636 | -0.003025 | -0.0020892 | -0.00075834 | 95.0684 | 95.4437 | -27.5299 | 95.0363 | -10.6476 | 95.0729 | 95.3659 | -0.79193 | 95.5215 | -27.4658 | 95.4666 | -27.4521 | -27.5574 | -27.3102 | -0.18311 | 0.013733 | -0.39368 | 16.6992 | 122.7127 | 122.4197 | 122.8958 | 122.6028 | -0.11902 | 0.091552 | 0.036621 | -0.10528 | 0.036621 | -0.21057 | 0.15564 | -0.091553 | 16.8823 | 122.5662 | 0.013733 | 122.9324 | 122.9736 | 122.9874 | 122.7905 | 122.8683 | -122.9599 | -122.8958 | 122.3831 | 122.8134 | 122.4152 | 26.5549
982.5469 | 122.8912 | -27.5482 | 95.2789 | -0.60699 | 0.6754 | 0.07147 | 0.0013117 | -0.0021513 | 0.60847 | 0.00054267 | -0.020172 | 0.0016043 | 0.06749 | 0.063491 | -0.0032386 | -0.00059378 | -0.0050307 | 94.8761 | 95.3384 | -27.7634 | 94.8029 | -11.0321 | 94.8349 | 95.105 | -0.76446 | 95.3568 | -27.6718 | 95.1691 | -27.7176 | -27.7863 | -27.507 | -0.21515 | 0.059509 | -0.47607 | 16.5161 | 122.6532 | 122.3831 | 122.8683 | 122.5983 | -0.1236 | 0.077819 | -0.10986 | -0.16937 | 0.041199 | -0.23804 | 0.1648 | -0.11444 | 16.7313 | 122.5662 | -0.045776 | 122.8409 | 123.1018 | 123.0286 | 122.8867 | 122.905 | -123.0423 | -122.9507 | 122.3511 | 122.7173 | 122.4243 | 26.7838
983.4844 | 122.9279 | -27.6398 | 95.2286 | -0.68329 | 0.67326 | 0.072111 | 0.0038751 | 0.0046847 | 0.60911 | 0.0013971 | -0.062897 | 0.0037405 | 0.069199 | 0.069259 | -0.0043066 | -0.0010212 | -0.0022537 | 94.7388 | 95.1599 | -27.8641 | 94.6289 | -11.1923 | 94.6884 | 94.9722 | -0.92926 | 95.2103 | -27.8091 | 95.1828 | -28.0701 | -28.0655 | -27.5665 | -0.2243 | -0.068665 | -0.59967 | 16.4474 | 122.612 | 122.3282 | 122.8363 | 122.5525 | -0.16937 | -0.018311 | -0.045777 | -0.4303 | 0.073243 | -0.42572 | 0.24261 | -0.25635 | 16.6718 | 122.493 | -0.26093 | 122.9919 | 123.024 | 123.0194 | 122.7997 | 122.85 | -123.0927 | -123.0377 | 122.2687 | 122.8226 | 122.3785 | 26.7105
984.5469 | 122.9004 | -27.5803 | 95.1645 | -0.59174 | 0.67305 | 0.071043 | 0.0025933 | 0.00019874 | 0.60932 | 0.0016107 | -0.032379 | 0.0016043 | 0.065995 | 0.0652 | -0.0015296 | -0.0018756 | -0.0026809 | 94.8349 | 95.2744 | -27.7908 | 94.7571 | -11.0275 | 94.8349 | 95.0729 | -0.75073 | 95.3064 | -27.713 | 95.192 | -27.713 | -27.8458 | -27.5848 | -0.21057 | 0.10986 | -0.40741 | 16.5527 | 122.6532 | 122.4152 | 122.8638 | 122.6257 | -0.13275 | 0.14191 | 0.027466 | -0.13275 | -0.004578 | -0.2655 | 0.12817 | -0.13275 | 16.7633 | 122.5479 | 0 | 122.905 | 123.0652 | 123.0194 | 122.8546 | 122.8867 | -122.9553 | -122.8775 | 122.3373 | 122.7722 | 122.4152 | 26.8295
985.4844 | 122.8455 | -27.0264 | 95.8054 | -0.63751 | 0.67198 | 0.071256 | 0.0030207 | 0.0042575 | 0.60697 | 0.0026789 | -0.044586 | 0.0033133 | 0.064286 | 0.066482 | -0.0017432 | 4.7018e-05 | -0.00033114 | 95.4163 | 95.8511 | -27.2141 | 95.3064 | -10.144 | 95.3659 | 95.6177 | -0.88806 | 95.9061 | -27.1317 | 95.7321 | -27.2095 | -27.3422 | -27.0584 | -0.18768 | 0.045776 | -0.49896 | 16.8823 | 122.644 | 122.3923 | 122.8317 | 122.58 | -0.10529 | 0.10071 | -0.073242 | -0.18311 | -0.032044 | -0.31586 | 0.073242 | -0.21057 | 17.07 | 122.5204 | -0.07782 | 122.8638 | 123.0652 | 123.0377 | 122.8775 | 122.9324 | -123.0194 | -122.937 | 122.3328 | 122.7585 | 122.4426 | 26.1383
986.5 | 122.9416 | -28.7292 | 94.043 | -0.63751 | 0.67283 | 0.069547 | -0.00018368 | -0.0010831 | 0.60847 | -0.0011663 | 0.040863 | 0.00032248 | 0.06749 | 0.060714 | -0.0002478 | -0.0018756 | 0.00073706 | 93.7042 | 94.0887 | -28.9124 | 93.5898 | -12.7121 | 93.5303 | 93.9377 | -0.8606 | 94.075 | -28.8666 | 94.0842 | -28.7933 | -28.9169 | -28.656 | -0.18311 | 0.045776 | -0.45319 | 16.0172 | 122.6669 | 122.2595 | 122.85 | 122.4426 | -0.13733 | 0.032043 | 0.041198 | -0.064087 | 0.073242 | -0.18768 | 0.21057 | -0.050354 | 16.2003 | 122.5021 | 0.073242 | 122.9507 | 123.0011 | 122.9416 | 122.818 | 122.8043 | -122.9553 | -122.9095 | 122.319 | 122.8134 | 122.4335 | 27.8687
987.4844 | 122.8363 | -27.301 | 95.5124 | -0.71381 | 0.66984 | 0.068693 | 0.0023797 | 0.00083954 | 0.60591 | 0.00011527 | -0.053741 | 0.0011771 | 0.065567 | 0.06755 | -0.0038794 | 4.7018e-05 | -0.00075834 | 95.1599 | 95.5994 | -27.4658 | 95.0729 | -10.4691 | 95.105 | 95.3568 | -0.8606 | 95.5994 | -27.3972 | 95.462 | -27.4612 | -27.5848 | -27.3102 | -0.1648 | 0.086975 | -0.43945 | 16.832 | 122.6578 | 122.406 | 122.8226 | 122.5708 | -0.096131 | 0.086975 | -0.050354 | -0.16022 | -0.009156 | -0.28381 | 0.086975 | -0.18768 | 16.9968 | 122.5388 | -0.064087 | 122.8592 | 123.0652 | 122.9965 | 122.9004 | 122.9004 | -122.9782 | -122.9095 | 122.374 | 122.7631 | 122.4609 | 26.4404
988.5469 | 122.9095 | -27.269 | 95.4483 | -0.64514 | 0.67006 | 0.072111 | -0.00018368 | -0.0010831 | 0.60697 | -9.8328e-05 | 0.056122 | 0.0026725 | 0.06514 | 0.062636 | -0.0028112 | -0.0020892 | 0.0013779 | 95.1324 | 95.5261 | -27.4658 | 95.0958 | -10.4324 | 95.137 | 95.4025 | -0.82398 | 95.549 | -27.4109 | 95.4941 | -27.3697 | -27.4841 | -27.2507 | -0.19684 | 0.07782 | -0.35248 | 16.8365 | 122.6715 | 122.406 | 122.8683 | 122.6028 | -0.14191 | 0.10071 | 0.045777 | -0.10071 | 0.018311 | -0.21515 | 0.16022 | -0.073242 | 17.0334 | 122.5616 | 0.041199 | 122.905 | 122.9919 | 122.9599 | 122.7951 | 122.818 | -122.9141 | -122.8592 | 122.3648 | 122.7631 | 122.4014 | 26.445
989.4844 | 122.8455 | -27.3788 | 95.43 | -0.60699 | 0.66984 | 0.073392 | 0.0036615 | 0.0027621 | 0.60569 | 0.00096987 | -0.062897 | 0.0033133 | 0.06749 | 0.071395 | -0.0038794 | -0.00080758 | 0.00030966 | 95.0409 | 95.4849 | -27.5574 | 94.9219 | -10.3592 | 95.0088 | 95.2515 | -0.92926 | 95.5307 | -27.4979 | 95.3842 | -27.5528 | -27.7084 | -27.4017 | -0.17853 | 0.054931 | -0.50812 | 17.0197 | 122.6303 | 122.3877 | 122.8088 | 122.5662 | -0.11902 | 0.10071 | -0.045777 | -0.17395 | -0.022888 | -0.32959 | 0.096131 | -0.21057 | 17.1982 | 122.4792 | -0.054931 | 122.8821 | 123.0423 | 123.0286 | 122.8638 | 122.9095 | -122.9874 | -122.9279 | 122.3007 | 122.7631 | 122.4197 | 26.4496
990.4844 | 123.0194 | -116.7755 | 5.9509 | -0.69092 | 0.68181 | 0.071683 | 0.0051569 | 0.00062594 | 0.60633 | -0.00095273 | -0.020172 | 0.0024589 | 0.066422 | 0.068404 | -0.002384 | 0.00068782 | -0.00033114 | 6.1111 | 6.1523 | -116.8304 | 5.7816 | -114.7705 | 5.7129 | 5.9006 | -4.0054 | 6.2805 | -116.7664 | 5.777 | -116.5695 | -116.7847 | -115.9149 | -0.054931 | 0.20142 | -0.16937 | 2.005 | 122.6761 | 122.4884 | 122.731 | 122.5433 | 0.009156 | 0.32959 | -0.17395 | 0.20599 | 0.8606 | -0.009155 | 0.85144 | -0.018311 | 2.0599 | 122.612 | 0.19684 | 122.5433 | 122.9828 | 123.0469 | 122.9279 | 123.056 | -122.7814 | -122.7173 | 122.5571 | 122.5525 | 122.8867 | 112.7701
991.4844 | 123.024 | -116.3864 | 6.3629 | -0.69092 | 0.68095 | 0.066129 | 0.00088432 | 0.0023349 | 0.60334 | -0.0013799 | 0.059174 | 0.0022453 | 0.067276 | 0.063918 | -0.001316 | -0.0023028 | -0.0018265 | 6.5964 | 6.8298 | -116.2857 | 6.2622 | -113.0356 | 6.2164 | 6.4636 | -4.1107 | 6.6925 | -116.4459 | 6.1752 | -115.947 | -116.0431 | -115.5258 | 0.10071 | 0.46692 | -0.10071 | 3.3508 | 122.85 | 122.6028 | 122.7493 | 122.5021 | -0.059509 | 0.32959 | -0.18768 | 0.43945 | 0.8606 | 0.34332 | 0.9201 | 0.40283 | 3.2501 | 122.5479 | 0.49896 | 122.6212 | 123.1155 | 123.1384 | 123.2162 | 123.0789 | -122.6486 | -122.8088 | 122.6486 | 122.5616 | 122.9828 | 112.2757
992.5469 | 122.9828 | -119.6686 | 3.1769 | -0.70618 | 0.68138 | 0.063352 | 0.0017389 | -0.0025785 | 0.60035 | 0.00054267 | 0.016449 | 0.00053628 | 0.06749 | 0.065627 | -0.000675 | 0.00026062 | 0.0013779 | 2.8519 | 3.2135 | -119.8654 | 2.7557 | -118.3823 | 2.7512 | 2.8793 | -3.8406 | 3.2547 | -119.7418 | 2.9205 | -119.4168 | -119.6136 | -118.7622 | -0.19684 | 0.036621 | -0.42114 | 1.2863 | 122.5479 | 122.4197 | 122.7447 | 122.6166 | -0.073242 | 0.07782 | -0.25635 | 0.25177 | 0.90637 | 0.054932 | 0.97961 | 0.12817 | 1.4832 | 122.6212 | 0.32501 | 122.6624 | 123.0789 | 122.9965 | 122.8821 | 122.9233 | -123.0423 | -122.9187 | 122.4243 | 122.5891 | 122.5204 | 115.8279
993.4844 | 122.9553 | -119.8837 | 2.948 | -0.72144 | 0.68309 | 0.064207 | 0.0013117 | -0.00044226 | 0.60249 | 0.00075627 | -0.059845 | -0.00031832 | 0.066422 | 0.063705 | -0.0028112 | 0.00068782 | 0.00095066 | 2.5909 | 3.0029 | -120.1401 | 2.5269 | -118.3319 | 2.504 | 2.655 | -3.8223 | 3.1128 | -119.8883 | 2.7512 | -119.6548 | -119.8517 | -118.9453 | -0.25635 | 0.054932 | -0.42114 | 1.5518 | 122.5388 | 122.3877 | 122.7951 | 122.644 | -0.004578 | 0.16479 | -0.19684 | 0.22888 | 0.93842 | 0.032043 | 0.94299 | 0.036621 | 1.8082 | 122.6669 | 0.23346 | 122.6395 | 123.143 | 123.0011 | 122.8867 | 122.9965 | -123.0881 | -122.8363 | 122.4106 | 122.6349 | 122.4747 | 116.0614
994.4844 | 122.9324 | -120.0806 | 2.8336 | -0.64514 | 0.68779 | 0.062284 | 0.0021661 | 0.00062594 | 0.6027 | 0.00032907 | -0.0049134 | 0.00074988 | 0.067063 | 0.063277 | -0.0008886 | -0.00059378 | -0.00033114 | 2.417 | 3.0304 | -120.2499 | 2.5635 | -117.0685 | 2.417 | 3.0716 | -3.8956 | 3.1082 | -120.0165 | 2.4948 | -119.8654 | -119.989 | -119.133 | -0.16937 | 0.19684 | -0.27008 | 3.0121 | 123.1522 | 122.4976 | 123.3215 | 122.6669 | 0.064087 | 0.27466 | -0.33874 | 0.21515 | 0.94757 | 0.091552 | 0.88348 | 0.027465 | 3.1815 | 122.8134 | 0.15106 | 122.5113 | 123.2803 | 123.1247 | 123.111 | 123.1888 | -123.0835 | -122.85 | 122.644 | 122.5754 | 122.4976 | 116.185
995.4844 | 122.8912 | -120.1172 | 2.7969 | -0.62988 | 0.68052 | 0.065702 | 0.0032343 | 0.00019874 | 0.60227 | 0.00075627 | -0.075104 | 0.00074988 | 0.065995 | 0.064773 | -0.0011022 | -0.00080758 | -0.00033114 | 2.3392 | 2.7832 | -120.3644 | 2.2614 | -118.5699 | 2.2247 | 2.3529 | -3.9185 | 2.8519 | -120.1492 | 2.4857 | -119.8654 | -120.0989 | -119.2017 | -0.24719 | -0.013733 | -0.53558 | 1.5472 | 122.4701 | 122.3419 | 122.7173 | 122.5891 | -0.032044 | 0.054932 | -0.31128 | 0.25177 | 0.91553 | 0.01831 | 0.94757 | 0.050354 | 1.7944 | 122.6257 | 0.28381 | 122.6349 | 123.1476 | 123.0011 | 122.9004 | 122.9691 | -123.1613 | -122.9462 | 122.3785 | 122.6028 | 122.4564 | 116.1987
996.4844 | 122.9324 | -118.2861 | 4.5547 | -0.65277 | 0.74077 | 0.12701 | 0.0023797 | 0.00083954 | 0.60099 | -0.00095273 | -0.020172 | 0.0013907 | 0.069626 | 0.070968 | -0.003025 | -0.00038018 | -0.0022537 | 4.1473 | 4.5914 | -118.5104 | 4.0741 | -5.1682 | 4.0558 | 4.1748 | -3.717 | 4.628 | -118.3411 | 4.335 | -118.0069 | -118.2358 | -117.366 | -0.2243 | 0.036621 | -0.48065 | 113.118 | 122.4609 | 122.3419 | 122.6852 | 122.5662 | -0.054931 | 0.073242 | -0.21973 | 0.27924 | 0.92011 | 0.050354 | 0.97504 | 0.10529 | 113.3423 | 122.5845 | 0.33417 | 122.6761 | 123.1018 | 122.9691 | 122.8775 | 122.9141 | -123.0652 | -122.8958 | 122.3602 | 122.6212 | 122.4335 | 114.5691
997.5469 | 122.9599 | -118.4601 | 4.3854 | -0.73669 | 0.74012 | 0.12594 | 0.0013117 | 0.0025485 | 0.59843 | 0.00096987 | 0.050018 | 0.00032248 | 0.065354 | 0.064559 | -0.001316 | -0.0037982 | 0.00030966 | 4.0558 | 4.39 | -118.6523 | 4.0009 | -4.6967 | 4.0237 | 4.1245 | -3.5797 | 4.4449 | -118.483 | 4.1977 | -118.1305 | -118.3319 | -117.4896 | -0.19226 | 0.004578 | -0.38452 | 113.7634 | 122.5845 | 122.4838 | 122.7768 | 122.6761 | -0.022888 | 0.059509 | -0.18768 | 0.32959 | 0.97046 | 0.12817 | 0.99335 | 0.15106 | 113.9557 | 122.6532 | 0.35248 | 122.6807 | 123.0423 | 122.9279 | 122.85 | 122.905 | -123.0377 | -122.8683 | 122.4609 | 122.6578 | 122.5159 | 114.8804
998.4844 | 122.8775 | -118.6295 | 4.2252 | -0.63751 | 0.73927 | 0.12488 | -0.00039728 | -0.0012967 | 0.5995 | 0.00032907 | -0.020172 | 0.0022453 | 0.066635 | 0.064559 | -0.0004614 | -0.0014484 | 0.00073706 | 3.8544 | 4.2847 | -118.808 | 3.7308 | -4.921 | 3.7308 | 3.8544 | -3.6804 | 4.335 | -118.689 | 3.9734 | -118.3685 | -118.6066 | -117.7048 | -0.17853 | 0.059509 | -0.49438 | 113.7085 | 122.4838 | 122.3602 | 122.6624 | 122.5388 | -0.059509 | 0.10986 | -0.25177 | 0.26093 | 0.92468 | 0.022889 | 0.98419 | 0.082398 | 113.887 | 122.5388 | 0.32043 | 122.6624 | 123.0927 | 123.024 | 122.9141 | 122.9645 | -123.0331 | -122.9141 | 122.3602 | 122.6028 | 122.4838 | 114.949
999.5469 | 122.8683 | -118.5699 | 4.3259 | -0.69092 | 0.73948 | 0.12701 | 0.0021661 | 0.0014803 | 0.59779 | 0.0018243 | 0.004242 | 0.00032248 | 0.06749 | 0.064345 | -0.0002478 | -0.00016658 | -0.00033114 | 3.9185 | 4.3533 | -118.7347 | 3.8223 | -4.8431 | 3.8132 | 3.9459 | -3.6438 | 4.39 | -118.5883 | 4.0375 | -118.2999 | -118.5059 | -117.6361 | -0.16479 | 0.027466 | -0.50354 | 113.7268 | 122.5159 | 122.3831 | 122.6807 | 122.5479 | -0.018311 | 0.064087 | -0.28839 | 0.27008 | 0.93384 | 0.064087 | 0.95215 | 0.082398 | 113.8916 | 122.5571 | 0.28839 | 122.6257 | 123.0881 | 122.9782 | 122.9233 | 122.9599 | -123.0606 | -122.9141 | 122.3923 | 122.6074 | 122.4884 | 114.9261
1000.4844 | 122.8683 | -118.6203 | 4.2572 | -0.68329 | 0.7382 | 0.12509 | 0.00067072 | 0.0031893 | 0.59821 | -0.0013799 | -0.011017 | 0.00074988 | 0.066849 | 0.06285 | -0.0015296 | -0.0025164 | 0.0011643 | 3.7994 | 4.2755 | -118.8629 | 3.7308 | -4.6829 | 3.7033 | 3.8589 | -3.6346 | 4.2984 | -118.6661 | 3.9185 | -118.2907 | -118.6203 | -117.6865 | -0.24262 | 0.018311 | -0.52643 | 113.9374 | 122.4792 | 122.3236 | 122.7219 | 122.5662 | -0.045777 | 0.041199 | -0.33875 | 0.32959 | 0.93384 | 0 | 0.97961 | 0.045777 | 114.18 | 122.5937 | 0.37537 | 122.5845 | 123.1384 | 122.9645 | 122.8958 | 122.9187 | -123.1201 | -122.9233 | 122.3511 | 122.5388 | 122.4197 | 114.9857
1001.4844 | 122.9187 | -118.5425 | 4.3076 | -0.70618 | 0.74055 | 0.12295 | 0.0017389 | 0.0014803 | 0.59928 | -0.00052553 | -0.05069 | 0.00032248 | 0.067917 | 0.066909 | -0.0032386 | -0.00080758 | -0.00075834 | 3.8956 | 4.2664 | -118.8034 | 3.8498 | -4.5227 | 3.7903 | 3.9093 | -3.5934 | 4.3396 | -118.6432 | 4.0741 | -118.2724 | -118.4875 | -117.6086 | -0.26093 | -0.041199 | -0.45776 | 114.0198 | 122.4518 | 122.3328 | 122.7127 | 122.5937 | -0.10071 | 0.032044 | -0.23346 | 0.27008 | 0.93384 | 0.054931 | 1.0345 | 0.15564 | 114.2807 | 122.6532 | 0.37079 | 122.7173 | 123.0698 | 122.9828 | 122.8088 | 122.8821 | -123.111 | -122.9507 | 122.3923 | 122.6166 | 122.438 | 114.949
1002.4844 | 122.8821 | -118.4921 | 4.3671 | -0.69855 | 0.74119 | 0.12701 | 0.0036615 | -0.0023649 | 0.59757 | -0.0013799 | -0.0049134 | 0.0026725 | 0.066208 | 0.059005 | -0.001316 | -0.00059378 | -0.0028945 | 3.9047 | 4.4128 | -118.6935 | 3.8635 | -4.6921 | 3.8498 | 3.9688 | -3.6209 | 4.4266 | -118.5287 | 4.0878 | -118.2266 | -118.4372 | -117.5629 | -0.20142 | 0.045777 | -0.50354 | 113.8 | 122.4609 | 122.3419 | 122.6624 | 122.5433 | -0.036622 | 0.05951 | -0.27923 | 0.2655 | 0.92926 | 0.054931 | 0.96588 | 0.091553 | 114.0015 | 122.5571 | 0.30212 | 122.6166 | 123.1064 | 122.9553 | 122.905 | 122.9187 | -123.0606 | -122.8958 | 122.3557 | 122.58 | 122.3969 | 114.8712
1003.5469 | 122.7631 | -118.6203 | 4.2206 | -0.70618 | 0.73842 | 0.12573 | 0.00088432 | -0.00065586 | 0.59458 | -0.0022345 | 0.013397 | 0.0024589 | 0.068344 | 0.066482 | -0.0011022 | 4.7018e-05 | -0.00097194 | 3.7674 | 4.2206 | -118.8858 | 3.685 | -4.6692 | 3.6713 | 3.8132 | -3.6209 | 4.248 | -118.7164 | 3.9047 | -118.4235 | -118.2907 | -117.5903 | -0.2655 | 0 | -0.53558 | 113.9511 | 122.4335 | 122.2916 | 122.699 | 122.5571 | -0.096131 | 0.027466 | -0.31586 | 0.19684 | 1.03 | 0.32959 | 1.1261 | 0.42572 | 114.2166 | 122.5708 | 0.29297 | 122.6212 | 123.1064 | 122.9645 | 122.8409 | 122.8683 | -123.1064 | -122.937 | 122.3053 | 122.525 | 122.3877 | 114.9994
1004.4844 | 122.8271 | -118.6798 | 4.1702 | -0.75958 | 0.73692 | 0.12423 | 0.00024352 | -0.0012967 | 0.5948 | -0.0013799 | 0.025604 | 0.00032248 | 0.070908 | 0.066695 | 0.0008204 | -0.00059378 | 0.00052346 | 3.7491 | 4.184 | -118.8766 | 3.6942 | -4.3762 | 3.6667 | 3.8132 | -3.598 | 4.2572 | -118.721 | 3.8956 | -118.4052 | -118.634 | -117.746 | -0.19684 | 0.013733 | -0.47607 | 114.3036 | 122.493 | 122.3465 | 122.6898 | 122.5433 | -0.041198 | 0.086975 | -0.27466 | 0.27466 | 0.93384 | 0.045777 | 0.97504 | 0.086975 | 114.5004 | 122.5708 | 0.31586 | 122.6166 | 123.0606 | 122.9782 | 122.8638 | 122.937 | -123.0469 | -122.8912 | 122.374 | 122.5754 | 122.4289 | 115.0818
1005.5469 | 122.8546 | -118.6478 | 4.2068 | -0.72144 | 0.73628 | 0.12423 | 0.0028069 | 0.0012667 | 0.59458 | 0.00054267 | 0.004242 | 0.0022453 | 0.068772 | 0.066268 | -0.0011022 | -0.00059378 | -0.0020401 | 3.7674 | 4.2114 | -118.8995 | 3.717 | -4.7287 | 3.6896 | 3.8177 | -3.5934 | 4.2938 | -118.7256 | 3.9185 | -118.3914 | -118.5974 | -117.746 | -0.25177 | 0.004578 | -0.48981 | 113.9191 | 122.4655 | 122.3373 | 122.7173 | 122.5891 | -0.07782 | 0.086975 | -0.28839 | 0.25635 | 0.90179 | 0.050354 | 0.97961 | 0.12817 | 114.1708 | 122.6166 | 0.33417 | 122.644 | 123.111 | 123.0194 | 122.8592 | 122.9416 | -123.1064 | -122.9324 | 122.3648 | 122.5662 | 122.4152 | 115.0543
1006.4844 | 122.905 | -118.7576 | 4.0741 | -0.71381 | 0.73564 | 0.12509 | 0.0015253 | -1.486e-05 | 0.59565 | 0.0020379 | -0.053741 | 0.0013907 | 0.066849 | 0.063491 | -0.0025976 | 0.00047422 | -0.0024673 | 3.6987 | 4.0649 | -118.9957 | 3.6346 | -4.4586 | 3.5934 | 3.7216 | -3.5431 | 4.1382 | -118.7988 | 3.8681 | -118.4692 | -118.6798 | -117.7917 | -0.23804 | -0.009156 | -0.43945 | 114.299 | 122.4792 | 122.3511 | 122.7173 | 122.5891 | -0.041199 | 0.064087 | -0.20599 | 0.28839 | 0.96588 | 0.077819 | 1.0071 | 0.11902 | 114.537 | 122.6303 | 0.32959 | 122.6669 | 123.0606 | 122.937 | 122.8226 | 122.8958 | -123.0698 | -122.8729 | 122.3923 | 122.6257 | 122.4564 | 115.2145
1007.4844 | 122.8912 | -118.6111 | 4.1931 | -0.72144 | 0.73649 | 0.12509 | 0.0017389 | -0.00065586 | 0.59394 | -0.0011663 | -0.01712 | -0.00010472 | 0.068558 | 0.061782 | -0.0015296 | -0.0025164 | -0.0011855 | 3.8177 | 4.1931 | -118.8904 | 3.7537 | -4.6371 | 3.7216 | 3.8452 | -3.5431 | 4.2618 | -118.6432 | 4.0009 | -118.3411 | -118.5562 | -117.6865 | -0.27924 | 0 | -0.43945 | 113.974 | 122.4564 | 122.3328 | 122.7356 | 122.612 | -0.032043 | 0.068665 | -0.19226 | 0.27008 | 0.92468 | 0.054932 | 0.95673 | 0.086975 | 114.2532 | 122.644 | 0.30212 | 122.644 | 123.0835 | 122.905 | 122.8043 | 122.8729 | -123.0835 | -122.8363 | 122.3648 | 122.612 | 122.4289 | 115.0681
1008.5469 | 122.9874 | -118.6432 | 4.1153 | -0.69092 | 0.73692 | 0.12658 | 2.9918e-05 | -0.0021513 | 0.59672 | 0.00075627 | 0.068329 | 0.00010888 | 0.066849 | 0.056441 | -0.0004614 | -0.0012348 | -0.00033114 | 3.8086 | 4.1382 | -118.8538 | 3.7903 | -4.8569 | 3.7674 | 3.9139 | -3.4927 | 4.1977 | -118.6798 | 4.01 | -118.2816 | -118.483 | -117.6361 | -0.21057 | 0.022889 | -0.32501 | 113.7863 | 122.5571 | 122.4106 | 122.7676 | 122.6212 | -0.036622 | 0.082398 | -0.10528 | 0.36163 | 1.0071 | 0.16022 | 1.0437 | 0.19684 | 113.9969 | 122.644 | 0.39826 | 122.6898 | 122.9919 | 122.8775 | 122.7814 | 122.8409 | -122.9691 | -122.7951 | 122.4335 | 122.6532 | 122.4518 | 115.1505
1009.4844 | 122.8912 | -118.5745 | 4.2435 | -0.73669 | 0.7335 | 0.12637 | 0.0036615 | 0.0027621 | 0.59416 | -0.00095273 | -0.062897 | 0.0013907 | 0.069199 | 0.066482 | -0.0021704 | 0.001756 | -0.00011754 | 3.8635 | 4.2572 | -118.8126 | 3.7811 | -4.7836 | 3.7491 | 3.8773 | -3.4515 | 4.3488 | -118.515 | 4.0283 | -118.2953 | -118.5471 | -117.6361 | -0.23804 | 0.013733 | -0.46234 | 113.7909 | 122.4518 | 122.3236 | 122.6898 | 122.5616 | 0.059509 | 0.10529 | -0.21515 | 0.27924 | 0.93842 | 0.027466 | 0.87891 | -0.032043 | 114.0289 | 122.5937 | 0.21973 | 122.5433 | 123.0698 | 122.8638 | 122.8317 | 122.9233 | -123.056 | -122.7585 | 122.3557 | 122.6028 | 122.438 | 115.123
1010.5469 | 122.9279 | -118.6981 | 4.0924 | -0.67566 | 0.73414 | 0.12552 | 0.0010981 | 0.00019874 | 0.58988 | -0.00031193 | 0.071381 | 0.00010888 | 0.065995 | 0.057723 | -0.0043066 | 0.00047422 | -0.00097194 | 3.7125 | 4.0283 | -118.959 | 3.6713 | -4.7791 | 3.6713 | 3.7811 | -3.4287 | 4.0878 | -118.7851 | 3.7994 | -118.1259 | -118.5745 | -117.7917 | -0.26093 | -0.064087 | -0.42114 | 113.9191 | 122.4792 | 122.3694 | 122.7402 | 122.6303 | -0.086975 | -0.004577 | -0.29297 | 0.5722 | 0.90637 | 0.1236 | 0.99335 | 0.21057 | 114.18 | 122.6303 | 0.65918 | 122.5845 | 122.9874 | 122.8729 | 122.7264 | 122.7859 | -123.0515 | -122.8775 | 122.3694 | 122.4976 | 122.4106 | 115.2695
1011.4844 | 122.8958 | -118.7622 | 4.0421 | -0.67566 | 0.73073 | 0.12637 | 0.0021661 | 0.0016939 | 0.59437 | 0.0013971 | -0.053741 | -0.00074552 | 0.069626 | 0.061782 | -0.003025 | 0.00026062 | -0.0018265 | 3.6621 | 4.0787 | -119.0094 | 3.6255 | -4.9347 | 3.5934 | 3.6987 | -3.6118 | 4.1336 | -118.8263 | 3.8544 | -118.4692 | -118.6981 | -117.7917 | -0.24719 | 0.036621 | -0.41657 | 113.8275 | 122.4609 | 122.3557 | 122.7081 | 122.6028 | -0.064087 | 0.091553 | -0.18768 | 0.29297 | 0.97046 | 0.064087 | 1.0345 | 0.12817 | 114.0747 | 122.6349 | 0.35706 | 122.6807 | 123.0881 | 122.9599 | 122.8409 | 122.8958 | -123.0515 | -122.8683 | 122.3877 | 122.6166 | 122.4243 | 115.1505
1012.4844 | 122.8363 | -118.7393 | 4.1107 | -0.64514 | 0.73051 | 0.12552 | 0.0028069 | 0.0016939 | 0.58924 | 0.0013971 | 0.022552 | -0.00031832 | 0.066208 | 0.066268 | -0.0019568 | -0.001662 | -0.00075834 | 3.653 | 4.1473 | -118.8904 | 3.6301 | -4.5731 | 3.6118 | 3.7033 | -3.653 | 4.1885 | -118.7759 | 3.8361 | -118.4601 | -118.6981 | -117.8055 | -0.15106 | 0.036621 | -0.48065 | 114.1663 | 122.4426 | 122.3511 | 122.5937 | 122.5021 | -0.036621 | 0.07782 | -0.27466 | 0.27924 | 0.93384 | 0.041199 | 0.97046 | 0.07782 | 114.3173 | 122.5204 | 0.31586 | 122.612 | 123.0377 | 122.9645 | 122.8867 | 122.9279 | -123.0011 | -122.8867 | 122.3694 | 122.5754 | 122.3923 | 115.0864
1013.5469 | 122.937 | -118.959 | 3.8361 | -0.73669 | 0.73308 | 0.12509 | 0.0010981 | 0.0057529 | 0.59394 | 0.00096987 | 0.068329 | 0.0016043 | 0.068344 | 0.061355 | -0.0028112 | -0.0014484 | 0.0022323 | 3.4744 | 3.8498 | -119.1513 | 3.4882 | -4.8065 | 3.4607 | 3.5889 | -3.598 | 3.9139 | -118.9682 | 3.7216 | -118.5699 | -118.7988 | -117.9291 | -0.19226 | 0.013732 | -0.3479 | 114.1525 | 122.5479 | 122.4197 | 122.7402 | 122.612 | -0.009156 | 0.077819 | -0.11444 | 0.3891 | 1.03 | 0.16022 | 1.0391 | 0.16937 | 114.3448 | 122.6395 | 0.39825 | 122.6898 | 123.0011 | 122.8821 | 122.8088 | 122.8729 | -122.9874 | -122.8043 | 122.4472 | 122.6807 | 122.4335 | 115.361
1014.4844 | 122.8271 | -119.0002 | 3.8132 | -0.61462 | 0.73179 | 0.12488 | 0.0013117 | 0.0019077 | 0.5933 | -9.8328e-05 | 0.062225 | 0.0030997 | 0.067276 | 0.069045 | -0.0062292 | -0.0020892 | 0.0013779 | 3.4241 | 3.8452 | -119.2245 | 3.3508 | -4.5593 | 3.3188 | 3.447 | -3.7857 | 3.9505 | -119.0186 | 3.5614 | -118.7622 | -118.9819 | -118.0893 | -0.2243 | 0.032044 | -0.46234 | 114.4409 | 122.4472 | 122.319 | 122.6715 | 122.5433 | -0.018311 | 0.13733 | -0.25177 | 0.23804 | 0.91095 | 0.01831 | 0.92926 | 0.036621 | 114.6652 | 122.5754 | 0.25635 | 122.58 | 123.0698 | 122.9691 | 122.8455 | 122.9507 | -123.0377 | -122.8317 | 122.3511 | 122.5616 | 122.4243 | 115.2145
1015.5469 | 122.8867 | -119.0186 | 3.804 | -0.75195 | 0.73073 | 0.12466 | 0.00045712 | 0.0027621 | 0.59138 | -0.0018073 | 0.016449 | -0.00010472 | 0.068131 | 0.061355 | -0.0025976 | -0.0025164 | 0.0026597 | 3.4653 | 3.7903 | -119.2291 | 3.4378 | -4.7699 | 3.392 | 3.5156 | -3.598 | 3.8452 | -119.046 | 3.598 | -118.6752 | -118.9133 | -118.0389 | -0.21057 | -0.013733 | -0.36621 | 114.2487 | 122.5342 | 122.4106 | 122.7448 | 122.6212 | -0.027466 | 0.041199 | -0.20599 | 0.34332 | 0.97962 | 0.10529 | 1.0071 | 0.13275 | 114.4592 | 122.6669 | 0.37079 | 122.644 | 123.0194 | 122.8912 | 122.8088 | 122.8638 | -123.0331 | -122.85 | 122.4564 | 122.6166 | 122.4838 | 115.4205
1016.4844 | 122.8821 | -119.0323 | 3.7949 | -0.65277 | 0.7303 | 0.12616 | 0.0028069 | 0.0025485 | 0.5901 | 0.0016107 | -0.01712 | 0.0020315 | 0.06514 | 0.0699 | -0.0034522 | -0.0012348 | -0.0013991 | 3.3875 | 3.8452 | -119.3024 | 3.3188 | -4.8065 | 3.2776 | 3.4195 | -3.7308 | 3.8498 | -119.0918 | 3.511 | -118.7439 | -118.9957 | -118.0847 | -0.27008 | 0.050354 | -0.47607 | 114.2258 | 122.4518 | 122.3099 | 122.7219 | 122.58 | -0.059509 | 0.054931 | -0.28381 | 0.28839 | 0.94757 | 0.036621 | 1.0071 | 0.09613 | 114.4958 | 122.6212 | 0.3479 | 122.6028 | 123.1476 | 122.9416 | 122.8775 | 122.8821 | -123.0972 | -122.8867 | 122.3511 | 122.5433 | 122.4197 | 115.3015
1017.5469 | 122.8043 | -119.0506 | 3.804 | -0.71381 | 0.72987 | 0.12381 | 0.0017389 | -0.0017239 | 0.58882 | -0.0018073 | -0.011017 | 0.0022453 | 0.06749 | 0.057937 | -0.0025976 | 4.7018e-05 | 0.0037277 | 3.3234 | 3.7491 | -119.339 | 3.2639 | -5.0354 | 3.2318 | 3.3966 | -3.7079 | 3.8361 | -119.0872 | 3.4882 | -118.8263 | -119.014 | -118.1259 | -0.28839 | -0.054932 | -0.54016 | 114.0152 | 122.4472 | 122.2824 | 122.7356 | 122.5708 | -0.036621 | 0.032044 | -0.31586 | 0.2243 | 0.92468 | 0.036621 | 0.9613 | 0.073242 | 114.3036 | 122.6028 | 0.26093 | 122.5754 | 123.0881 | 122.9233 | 122.7997 | 122.8867 | -123.143 | -122.8912 | 122.3145 | 122.5388 | 122.374 | 115.3427
1018.4844 | 122.8363 | -118.8217 | 4.0009 | -0.56885 | 0.72688 | 0.12552 | 0.00088432 | -0.0015103 | 0.58775 | -0.00031193 | 0.0072936 | 0.0022453 | 0.066635 | 0.062209 | -0.0011022 | -0.0018756 | 0.0026597 | 3.5889 | 4.0421 | -119.0643 | 3.5477 | -4.8157 | 3.5202 | 3.6667 | -3.7399 | 4.1153 | -118.8583 | 3.7399 | -118.5654 | -118.8034 | -117.9337 | -0.24262 | 0.041199 | -0.45319 | 114.006 | 122.4884 | 122.3419 | 122.731 | 122.5845 | -0.036621 | 0.11444 | -0.26093 | 0.25635 | 0.88806 | 0.01831 | 0.92468 | 0.054931 | 114.2487 | 122.612 | 0.29297 | 122.5983 | 123.1064 | 122.9736 | 122.8638 | 122.937 | -123.0652 | -122.8592 | 122.3694 | 122.5616 | 122.4106 | 115.0818
1019.4844 | 122.8729 | -119.0231 | 3.7949 | -0.72144 | 0.72966 | 0.12466 | 0.0030207 | 0.0036165 | 0.58711 | -0.0015935 | -0.01712 | 0.00074988 | 0.067704 | 0.0652 | -0.001316 | -0.0020892 | -0.00097194 | 3.4058 | 3.8177 | -119.2612 | 3.3463 | -4.6829 | 3.3325 | 3.4424 | -3.7445 | 3.9047 | -119.0277 | 3.5706 | -118.7027 | -118.9453 | -118.0573 | -0.23804 | 0.022888 | -0.44861 | 114.3402 | 122.4655 | 122.3557 | 122.7036 | 122.5937 | -0.004578 | 0.10986 | -0.2243 | 0.32043 | 0.96588 | 0.07782 | 0.97046 | 0.082398 | 114.5782 | 122.6074 | 0.32501 | 122.5983 | 123.0789 | 122.9324 | 122.8409 | 122.9279 | -123.056 | -122.8226 | 122.3694 | 122.5937 | 122.4289 | 115.2786
1020.4844 | 122.818 | -119.0186 | 3.8361 | -0.71381 | 0.72731 | 0.12274 | 0.0015253 | -0.0012967 | 0.58839 | -0.0011663 | -0.072052 | 0.0041679 | 0.067276 | 0.064132 | -0.0004614 | -0.00080758 | 0.00052346 | 3.4012 | 3.8269 | -119.2612 | 3.3325 | -4.9118 | 3.4515 | 3.7582 | -3.7857 | 3.9551 | -119.0277 | 3.5248 | -118.7347 | -118.9957 | -118.071 | -0.24261 | -0.009156 | -0.50354 | 114.1068 | 122.7768 | 122.4701 | 123.0194 | 122.7127 | -0.009155 | 0.11902 | -0.31128 | 0.28381 | 0.94757 | 0.022888 | 0.95673 | 0.032043 | 114.3494 | 122.5937 | 0.29297 | 122.5525 | 123.0881 | 122.9828 | 122.8455 | 122.9736 | -123.0972 | -122.8638 | 122.3511 | 122.5433 | 122.4197 | 115.2328
1021.5469 | 122.9095 | -119.0735 | 3.6942 | -0.7901 | 0.73137 | 0.12573 | 0.0015253 | 0.0029757 | 0.58903 | 0.0016107 | 0.016449 | -0.00053192 | 0.066422 | 0.067977 | -0.0019568 | -0.00016658 | 0.00095066 | 3.3417 | 3.6484 | -119.3436 | 3.3371 | -4.7882 | 3.2684 | 3.4287 | -3.7994 | 3.7399 | -119.1284 | 3.5614 | -118.7531 | -118.9819 | -118.0939 | -0.27008 | -0.045777 | -0.35706 | 114.2853 | 122.5021 | 122.3419 | 122.7722 | 122.612 | -0.054932 | 0.045776 | -0.13275 | 0.32043 | 0.97961 | 0.091552 | 1.0345 | 0.14648 | 114.5554 | 122.6807 | 0.37537 | 122.6898 | 122.9919 | 122.8683 | 122.7219 | 122.8134 | -123.0377 | -122.8226 | 122.4106 | 122.6349 | 122.4152 | 115.274
1022.4844 | 122.8729 | -119.0735 | 3.7033 | -0.67566 | 0.72752 | 0.1253 | 0.0010981 | 0.00083954 | 0.58668 | 0.0024653 | -0.053741 | 0.0013907 | 0.067704 | 0.065841 | -0.0019568 | 0.00068782 | -0.00011754 | 3.3371 | 3.7033 | -119.3619 | 3.2867 | -4.8203 | 3.2455 | 3.3646 | -3.7582 | 3.7949 | -119.1238 | 3.5065 | -118.7988 | -119.0231 | -118.1168 | -0.28839 | 0 | -0.41656 | 114.2532 | 122.438 | 122.319 | 122.7264 | 122.6074 | -0.050354 | 0.091553 | -0.19684 | 0.27466 | 0.95673 | 0.050354 | 1.0071 | 0.10071 | 114.5416 | 122.6486 | 0.32501 | 122.6303 | 123.0652 | 122.9187 | 122.7768 | 122.8683 | -123.0652 | -122.8271 | 122.3602 | 122.58 | 122.4106 | 115.3152
1023.4844 | 122.8729 | -119.1834 | 3.653 | -0.70618 | 0.72816 | 0.12616 | 0.0023797 | 0.0048983 | 0.58839 | 0.00011527 | -0.090363 | 0.0052359 | 0.065354 | 0.068191 | -0.0025976 | 4.7018e-05 | 0.00030966 | 3.2822 | 3.6438 | -119.3893 | 3.1998 | -5.0079 | 3.1677 | 3.2913 | -3.772 | 3.772 | -119.1559 | 3.4287 | -118.8858 | -119.101 | -118.1808 | -0.20599 | -0.009155 | -0.45319 | 114.1754 | 122.4747 | 122.3511 | 122.6807 | 122.5571 | 0.027466 | 0.11902 | -0.2243 | 0.29755 | 1.0025 | 0.082398 | 0.97504 | 0.054932 | 114.3814 | 122.5891 | 0.27008 | 122.5845 | 123.0331 | 122.9279 | 122.8271 | 122.9553 | -123.0423 | -122.8088 | 122.3831 | 122.612 | 122.4655 | 115.4114
1024.5469 | 122.9279 | -119.1742 | 3.5934 | -0.72144 | 0.72838 | 0.12488 | 0.0013117 | -0.0038603 | 0.58839 | -0.0033025 | 0.037811 | 0.0016043 | 0.065781 | 0.059646 | -0.0036658 | -0.00038018 | -0.0043899 | 3.3188 | 3.653 | -119.3527 | 3.2776 | -4.4357 | 3.2776 | 3.4103 | -3.717 | 3.6896 | -119.1925 | 3.3875 | -118.6844 | -119.0414 | -118.1717 | -0.17853 | 0.059509 | -0.31586 | 114.7385 | 122.5845 | 122.4518 | 122.7631 | 122.6303 | -0.018311 | 0.09613 | -0.20599 | 0.48981 | 1.0025 | 0.13275 | 1.0208 | 0.15106 | 114.917 | 122.6303 | 0.50812 | 122.58 | 123.0057 | 122.8821 | 122.8271 | 122.8638 | -122.9462 | -122.7859 | 122.4518 | 122.5616 | 122.493 | 115.4572
1025.4844 | 122.8775 | -119.1834 | 3.6209 | -0.70618 | 0.7256 | 0.12381 | 0.00067072 | 0.0036165 | 0.58689 | -9.8328e-05 | -0.044586 | 0.00010888 | 0.066635 | 0.064986 | -0.0036658 | -0.00038018 | -0.0020401 | 3.2455 | 3.6209 | -119.458 | 3.1815 | -4.7791 | 3.1311 | 3.2822 | -3.8132 | 3.6942 | -119.2429 | 3.4012 | -118.8766 | -119.1101 | -118.2083 | -0.27466 | 0 | -0.43945 | 114.4043 | 122.4655 | 122.3145 | 122.7402 | 122.5891 | -0.059509 | 0.073242 | -0.21973 | 0.3067 | 0.97504 | 0.073243 | 1.0345 | 0.13275 | 114.679 | 122.6395 | 0.36621 | 122.644 | 123.0789 | 122.937 | 122.8043 | 122.8775 | -123.0789 | -122.8638 | 122.3648 | 122.5845 | 122.4289 | 115.3702
1026.4844 | 122.8455 | -119.2474 | 3.566 | -0.65277 | 0.72517 | 0.12509 | 0.0053705 | 0.0016939 | 0.5839 | -0.0013799 | -0.0079652 | 0.00053628 | 0.069412 | 0.060073 | -0.0011022 | -0.0029438 | -0.0013991 | 3.2089 | 3.6209 | -119.4855 | 3.1036 | -4.7791 | 3.0945 | 3.2227 | -3.923 | 3.6667 | -119.2841 | 3.3234 | -118.9499 | -119.1925 | -118.2816 | -0.23804 | 0.054932 | -0.46234 | 114.4684 | 122.4701 | 122.3419 | 122.7081 | 122.58 | -0.036621 | 0.10071 | -0.24261 | 0.29755 | 0.96588 | 0.054932 | 1.0025 | 0.091553 | 114.7064 | 122.5891 | 0.33417 | 122.6074 | 123.1064 | 122.9507 | 122.8683 | 122.9141 | -123.0515 | -122.85 | 122.3511 | 122.5708 | 122.4564 | 115.3244
1027.4844 | 122.8775 | -119.2337 | 3.5934 | -0.71381 | 0.72282 | 0.12552 | 0.0030207 | 0.00062594 | 0.58476 | 0.00054267 | -0.053741 | 0.00053628 | 0.067276 | 0.064559 | -0.0021704 | -0.001662 | 0.0013779 | 3.1723 | 3.5477 | -119.5221 | 3.0991 | -4.7699 | 3.0716 | 3.1906 | -3.8773 | 3.6209 | -119.2612 | 3.3463 | -118.9453 | -119.2108 | -118.2999 | -0.28839 | -0.045777 | -0.49438 | 114.4638 | 122.4243 | 122.3053 | 122.7127 | 122.5937 | -0.027465 | 0.027466 | -0.24719 | 0.28839 | 0.93384 | 0.022889 | 0.9613 | 0.050354 | 114.7522 | 122.6212 | 0.31586 | 122.6074 | 123.0698 | 122.8821 | 122.7814 | 122.8546 | -123.1155 | -122.8546 | 122.3328 | 122.58 | 122.406 | 115.3564
1028.5469 | 122.9645 | -119.2474 | 3.5202 | -0.72906 | 0.72325 | 0.12509 | -0.0010383 | 0.00019874 | 0.58412 | -9.8328e-05 | 0.077484 | 0.0016043 | 0.067063 | 0.06285 | -0.002384 | -0.0027302 | -0.0028945 | 3.2684 | 3.5843 | -119.4214 | 3.241 | -4.66 | 3.2181 | 3.3279 | -3.8223 | 3.6209 | -119.2383 | 3.3142 | -118.7714 | -119.4031 | -118.4052 | -0.17395 | 0.064087 | -0.27924 | 114.5874 | 122.5754 | 122.4655 | 122.7493 | 122.6395 | 0.009156 | 0.10071 | -0.20599 | 0.47608 | 0.84229 | -0.15564 | 0.83313 | -0.16479 | 114.7614 | 122.6624 | 0.46692 | 122.5525 | 123.0057 | 122.8592 | 122.8317 | 122.8683 | -122.9416 | -122.7585 | 122.4884 | 122.5616 | 122.5159 | 115.4251
1029.4844 | 122.8409 | -119.1788 | 3.6255 | -0.69855 | 0.72368 | 0.12723 | 0.0032343 | 0.00062594 | 0.58625 | -0.00073913 | -0.069 | 0.0024589 | 0.069412 | 0.061568 | -0.0032386 | 0.0026104 | 0.00052346 | 3.2776 | 3.6621 | -119.4122 | 3.1769 | -4.7974 | 3.1174 | 3.2684 | -3.9871 | 3.717 | -119.2017 | 3.4012 | -118.9316 | -119.165 | -118.2266 | -0.23346 | 0.036621 | -0.44861 | 114.3814 | 122.4472 | 122.2961 | 122.6807 | 122.5296 | -0.022888 | 0.091553 | -0.2243 | 0.24719 | 0.95215 | 0.013733 | 0.97504 | 0.036621 | 114.6149 | 122.5891 | 0.27008 | 122.6028 | 123.0743 | 122.9187 | 122.8409 | 122.8958 | -123.0377 | -122.8271 | 122.3557 | 122.58 | 122.4564 | 115.1916
1030.4844 | 122.8409 | -119.1284 | 3.6621 | -0.69855 | 0.72368 | 0.12658 | 0.0025933 | 0.0014803 | 0.58262 | 0.00075627 | -0.041534 | -0.00074552 | 0.068344 | 0.064986 | -0.0021704 | 0.0015424 | 0.0015915 | 3.2822 | 3.653 | -119.3848 | 3.2089 | -4.6921 | 3.1723 | 3.2913 | -3.9413 | 3.7216 | -119.2062 | 3.4607 | -118.8309 | -119.0735 | -118.1717 | -0.25635 | -0.009155 | -0.45319 | 114.4363 | 122.4197 | 122.3007 | 122.6761 | 122.5571 | -0.07782 | 0.05951 | -0.20142 | 0.29755 | 0.95673 | 0.054932 | 1.0345 | 0.13275 | 114.6927 | 122.5937 | 0.37537 | 122.6669 | 123.0377 | 122.9279 | 122.7814 | 122.85 | -123.0469 | -122.8683 | 122.3373 | 122.5891 | 122.4106 | 115.1871
1031.4844 | 122.8729 | -119.1055 | 3.6942 | -0.68329 | 0.72239 | 0.12616 | 0.0015253 | 0.0027621 | 0.58134 | -0.00031193 | -0.041534 | 0.0022453 | 0.068131 | 0.063705 | -0.0025976 | -0.0010212 | -0.00075834 | 3.2639 | 3.6118 | -119.4214 | 3.2043 | -4.6692 | 3.186 | 3.3279 | -3.9551 | 3.7216 | -119.1925 | 3.5751 | -118.7347 | -119.0643 | -118.1396 | -0.31586 | -0.082398 | -0.48981 | 114.4363 | 122.4335 | 122.2916 | 122.7493 | 122.6074 | -0.086975 | 0.027466 | -0.11902 | 0.37079 | 0.96588 | 0.041199 | 1.0529 | 0.12817 | 114.7522 | 122.6257 | 0.45776 | 122.7676 | 123.0331 | 122.9141 | 122.7173 | 122.8271 | -123.1155 | -122.8867 | 122.3099 | 122.6807 | 122.3694 | 115.1505
1032.5469 | 122.9416 | -119.3115 | 3.4149 | -0.67566 | 0.72282 | 0.12359 | -0.0012519 | 0.00041234 | 0.58326 | -0.00052553 | 0.068329 | 0.0018179 | 0.06749 | 0.059859 | -0.0021704 | -0.0042254 | 0.0047959 | 3.1082 | 3.4195 | -119.5633 | 3.0624 | -4.66 | 3.067 | 3.1769 | -3.9001 | 3.479 | -119.3802 | 3.2822 | -118.9499 | -119.165 | -118.309 | -0.25177 | 0.004578 | -0.35248 | 114.6515 | 122.4884 | 122.3785 | 122.7402 | 122.6303 | -0.068665 | 0.064087 | -0.13275 | 0.36163 | 1.0025 | 0.14648 | 1.0712 | 0.21515 | 114.9033 | 122.6257 | 0.4303 | 122.6624 | 122.9828 | 122.8592 | 122.731 | 122.7905 | -122.9782 | -122.7951 | 122.374 | 122.5937 | 122.4197 | 115.4114
1033.4844 | 122.8409 | -119.4168 | 3.3875 | -0.70618 | 0.72303 | 0.12723 | 0.0036615 | 0.00041234 | 0.58113 | 0.00032907 | -0.053741 | -0.00010472 | 0.067063 | 0.069045 | -0.0032386 | 0.00068782 | -0.00075834 | 3.0212 | 3.4332 | -119.632 | 2.9434 | -4.8019 | 2.8976 | 3.0304 | -4.0787 | 3.4607 | -119.4489 | 3.1403 | -119.1834 | -119.4077 | -118.4784 | -0.21515 | 0.045777 | -0.44403 | 114.6149 | 122.4472 | 122.3145 | 122.6624 | 122.5296 | -0.032044 | 0.073242 | -0.24719 | 0.23346 | 0.93842 | 0.009155 | 0.97046 | 0.041199 | 114.83 | 122.5754 | 0.2655 | 122.5891 | 123.0652 | 122.9095 | 122.85 | 122.8775 | -123.0194 | -122.8363 | 122.3602 | 122.5571 | 122.438 | 115.3381
1034.4844 | 122.8546 | -119.4397 | 3.3554 | -0.72144 | 0.72303 | 0.12637 | 0.00088432 | -1.486e-05 | 0.5839 | 0.00011527 | -0.035431 | 0.0016043 | 0.065354 | 0.067763 | -3.4196e-05 | -0.00080758 | 0.0018051 | 3.0075 | 3.36 | -119.6777 | 2.9205 | -4.7882 | 2.8885 | 3.0121 | -4.0466 | 3.4287 | -119.4763 | 3.1677 | -119.1376 | -119.371 | -118.4601 | -0.23804 | 0.004577 | -0.43488 | 114.6515 | 122.4518 | 122.3282 | 122.6898 | 122.5662 | -0.036621 | 0.073242 | -0.18768 | 0.30212 | 0.97961 | 0.068664 | 1.0162 | 0.10529 | 114.8895 | 122.5983 | 0.33875 | 122.644 | 123.0377 | 122.905 | 122.7997 | 122.8683 | -123.0331 | -122.8317 | 122.3602 | 122.6074 | 122.4472 | 115.3931
1035.5469 | 122.9279 | -119.4168 | 3.3096 | -0.7901 | 0.72175 | 0.12359 | -0.0018927 | 0.00083954 | 0.58283 | -0.0013799 | 0.086639 | 0.0016043 | 0.069626 | 0.05815 | -0.0017432 | -0.0020892 | 0.0011643 | 3.0121 | 3.3325 | -119.6457 | 2.9892 | -4.6921 | 2.9846 | 3.1082 | -3.9642 | 3.3783 | -119.4717 | 3.186 | -119.046 | -119.2566 | -118.3914 | -0.22888 | 0.022889 | -0.32043 | 114.7247 | 122.525 | 122.4014 | 122.7539 | 122.6303 | -0.054932 | 0.068665 | -0.1236 | 0.37079 | 1.0254 | 0.16022 | 1.0803 | 0.21515 | 114.9536 | 122.6349 | 0.42572 | 122.6578 | 122.9782 | 122.85 | 122.7493 | 122.7951 | -122.9553 | -122.7814 | 122.406 | 122.6028 | 122.4289 | 115.4526
1036.4844 | 122.85 | -119.4534 | 3.3646 | -0.66803 | 0.72111 | 0.12488 | 0.0013117 | 0.0010531 | 0.58027 | 0.0013971 | -0.041534 | 0.0045951 | 0.067917 | 0.0605 | -0.0032386 | 0.0013288 | -0.0011855 | 3.0075 | 3.3646 | -119.696 | 2.9114 | -4.7653 | 2.8885 | 3.0075 | -4.0741 | 3.4195 | -119.4626 | 3.1448 | -119.1193 | -119.3848 | -118.4509 | -0.24262 | 0 | -0.45319 | 114.6881 | 122.4609 | 122.3419 | 122.7036 | 122.5845 | -0.009155 | 0.054932 | -0.21973 | 0.33417 | 1.0025 | 0.068664 | 1.0117 | 0.077819 | 114.9307 | 122.6074 | 0.34332 | 122.6074 | 123.0606 | 122.8821 | 122.818 | 122.8729 | -123.0606 | -122.8271 | 122.3648 | 122.5983 | 122.4609 | 115.3793
1037.4844 | 122.7859 | -119.3939 | 3.3829 | -0.72144 | 0.72133 | 0.12637 | 0.0028069 | 0.00083954 | 0.58027 | -0.0011663 | -0.035431 | 0.0018179 | 0.065995 | 0.069045 | -0.0034522 | -0.00059378 | 0.00095066 | 3.0029 | 3.4012 | -119.664 | 2.9205 | -4.8065 | 2.8656 | 2.98 | -4.2572 | 3.4561 | -119.4443 | 3.1403 | -119.1605 | -119.4031 | -118.4647 | -0.27008 | 0.01831 | -0.46234 | 114.5874 | 122.374 | 122.2595 | 122.644 | 122.5296 | -0.050354 | 0.073242 | -0.24262 | 0.23346 | 0.92926 | -0.009155 | 0.97961 | 0.041199 | 114.8575 | 122.5845 | 0.28381 | 122.5845 | 123.0652 | 122.9004 | 122.7951 | 122.85 | -123.0469 | -122.8271 | 122.3145 | 122.5342 | 122.3969 | 115.1367
1038.4844 | 122.8455 | -119.4214 | 3.3875 | -0.68329 | 0.71748 | 0.12295 | 0.0040887 | 0.00019874 | 0.57942 | 0.00032907 | -0.020172 | 0.00074988 | 0.065995 | 0.064345 | -0.0025976 | -0.00059378 | 0.0011643 | 2.9938 | 3.4332 | -119.6594 | 2.9114 | -4.7974 | 2.8976 | 3.0167 | -4.2068 | 3.4698 | -119.4443 | 3.1311 | -119.1101 | -119.3481 | -118.4189 | -0.23804 | 0.045777 | -0.47607 | 114.624 | 122.438 | 122.319 | 122.6761 | 122.5571 | -0.022888 | 0.082398 | -0.25635 | 0.31128 | 1.0025 | 0.073242 | 1.0254 | 0.09613 | 114.8621 | 122.5708 | 0.33417 | 122.5754 | 123.0927 | 122.9141 | 122.8546 | 122.8912 | -123.0469 | -122.8317 | 122.3328 | 122.5525 | 122.4152 | 115.2145
1039.4844 | 122.8592 | -119.3893 | 3.4058 | -0.65277 | 0.71898 | 0.12637 | 0.0030207 | 0.0048983 | 0.58091 | -0.0015935 | -0.05069 | 0.0020315 | 0.068344 | 0.0652 | -0.003025 | -0.00016658 | 0.0084275 | 2.9846 | 3.3646 | -119.6686 | 2.9205 | -4.7104 | 2.9114 | 3.0075 | -4.1977 | 3.4287 | -119.4489 | 3.3142 | -119.0781 | -119.2795 | -118.4235 | -0.27924 | -0.041199 | -0.48523 | 114.679 | 122.3969 | 122.3007 | 122.6761 | 122.58 | -0.05951 | 0.022888 | -0.091553 | 0.31128 | 0.96588 | 0.10986 | 1.0254 | 0.16937 | 114.9582 | 122.5891 | 0.37079 | 122.7631 | 123.0331 | 122.8775 | 122.7539 | 122.818 | -123.0743 | -122.8546 | 122.3099 | 122.7036 | 122.374 | 115.1916
1040.5469 | 122.8271 | -119.4855 | 3.3417 | -0.69092 | 0.72154 | 0.12488 | 0.0015253 | 0.00041234 | 0.58006 | -0.0013799 | 0.043915 | 0.0016043 | 0.066849 | 0.069045 | -0.0011022 | -0.00016658 | 0.0035141 | 2.9617 | 3.3096 | -119.6869 | 2.8885 | -4.9255 | 2.8793 | 2.9938 | -4.1977 | 3.3875 | -119.4946 | 3.0304 | -119.1605 | -119.3985 | -118.5471 | -0.20142 | -0.032044 | -0.45319 | 114.5599 | 122.4792 | 122.3648 | 122.6807 | 122.5662 | -0.009155 | 0.045776 | -0.31128 | 0.32501 | 0.93842 | 0.086975 | 0.94757 | 0.09613 | 114.7614 | 122.5754 | 0.33417 | 122.525 | 122.9965 | 122.8821 | 122.7951 | 122.8729 | -123.0286 | -122.8363 | 122.374 | 122.5159 | 122.4472 | 115.2878
1041.4844 | 122.818 | -119.5221 | 3.2639 | -0.66803 | 0.72069 | 0.12573 | 0.0017389 | 0.0019077 | 0.57835 | 0.0026789 | -0.047638 | 0.0013907 | 0.069626 | 0.061141 | -3.4196e-05 | -0.0012348 | -0.0016129 | 2.9846 | 3.2867 | -119.6915 | 2.8427 | -4.6417 | 2.8061 | 2.9343 | -4.2755 | 3.36 | -119.545 | 3.0624 | -119.252 | -119.4626 | -118.5471 | -0.16937 | 0.022888 | -0.42114 | 114.8804 | 122.4564 | 122.3282 | 122.6257 | 122.4976 | -0.022888 | 0.09613 | -0.20142 | 0.27008 | 0.97504 | 0.05951 | 0.99792 | 0.082398 | 115.0497 | 122.5342 | 0.29297 | 122.6074 | 122.9782 | 122.905 | 122.8088 | 122.8821 | -122.9553 | -122.8088 | 122.3648 | 122.5845 | 122.5067 | 115.2466
1042.5469 | 122.8638 | -119.5038 | 3.2639 | -0.71381 | 0.71812 | 0.12488 | 0.00067072 | -0.00022866 | 0.57792 | -0.0037299 | 0.034759 | 0.0016043 | 0.068344 | 0.056655 | -0.0028112 | -0.00080758 | -0.0011855 | 2.948 | 3.2547 | -119.7327 | 2.8885 | -4.4861 | 2.8656 | 2.9938 | -4.216 | 3.3188 | -119.5404 | 3.0579 | -119.1742 | -119.4168 | -118.5196 | -0.22888 | -0.009155 | -0.37537 | 115.0177 | 122.4976 | 122.3694 | 122.7264 | 122.5983 | -0.036621 | 0.054932 | -0.20599 | 0.32959 | 0.98419 | 0.086975 | 1.0208 | 0.1236 | 115.2466 | 122.6212 | 0.36621 | 122.5983 | 122.9874 | 122.8592 | 122.7585 | 122.8226 | -122.9965 | -122.8043 | 122.3923 | 122.5616 | 122.4518 | 115.2878
1043.4844 | 122.7997 | -119.5404 | 3.2639 | -0.72144 | 0.7209 | 0.12573 | 0.0028069 | 0.0034029 | 0.57749 | 0.0011835 | -0.035431 | 0.0033133 | 0.069626 | 0.070968 | -0.0036658 | 0.0015424 | -0.0016129 | 2.8931 | 3.2684 | -119.7739 | 2.8152 | -4.9667 | 2.7512 | 2.9022 | -4.3854 | 3.3096 | -119.5816 | 3.0121 | -119.2841 | -119.5175 | -118.5928 | -0.23346 | 0.004578 | -0.44861 | 114.5737 | 122.4426 | 122.2916 | 122.6761 | 122.525 | -0.041199 | 0.045776 | -0.25177 | 0.25635 | 0.94757 | 0.022888 | 0.98877 | 0.064087 | 114.8071 | 122.5891 | 0.29755 | 122.5937 | 123.0423 | 122.8912 | 122.8088 | 122.85 | -123.0377 | -122.8455 | 122.3557 | 122.5525 | 122.4335 | 115.155
1044.5469 | 122.7951 | -119.5404 | 3.273 | -0.66803 | 0.71962 | 0.12402 | 0.0013117 | 0.00083954 | 0.57643 | -0.0015935 | 0.010345 | -0.00053192 | 0.068985 | 0.064559 | -0.0025976 | -0.0027302 | -0.00011754 | 2.8427 | 3.2822 | -119.7784 | 2.774 | -4.6875 | 2.7649 | 2.8976 | -4.3762 | 3.3417 | -119.5724 | 2.9755 | -119.2612 | -119.5129 | -118.602 | -0.23804 | 0.009156 | -0.49896 | 114.8529 | 122.438 | 122.3053 | 122.6761 | 122.5433 | -0.032044 | 0.068665 | -0.29755 | 0.27924 | 0.93842 | 0.027466 | 0.97046 | 0.05951 | 115.0909 | 122.5525 | 0.31128 | 122.5479 | 123.0606 | 122.9141 | 122.8226 | 122.8821 | -123.0515 | -122.8455 | 122.3145 | 122.5159 | 122.3831 | 115.1642
1045.4844 | 122.8592 | -119.5404 | 3.2776 | -0.67566 | 0.71876 | 0.12723 | 0.0015253 | 0.0021213 | 0.57664 | -0.00073913 | -0.047638 | 0.0011771 | 0.067276 | 0.071181 | -0.0021704 | 0.0015424 | -0.0024673 | 2.916 | 3.3005 | -119.7693 | 2.8336 | -4.6326 | 2.7924 | 2.9297 | -4.3488 | 3.3417 | -119.5587 | 3.0533 | -119.2017 | -119.458 | -118.5287 | -0.22888 | 0.022888 | -0.44403 | 114.9078 | 122.4701 | 122.3328 | 122.699 | 122.5616 | -0.018311 | 0.064087 | -0.2243 | 0.33875 | 1.0117 | 0.082397 | 1.03 | 0.10071 | 115.1367 | 122.6028 | 0.35706 | 122.612 | 123.0698 | 122.9004 | 122.8409 | 122.8821 | -123.0469 | -122.8363 | 122.374 | 122.5937 | 122.4564 | 115.1917
1046.5469 | 122.937 | -119.5038 | 3.2318 | -0.67566 | 0.71705 | 0.12488 | 0.00088432 | -0.0012967 | 0.57728 | 0.00011527 | 0.071381 | 0.00096348 | 0.065781 | 0.067763 | -0.002384 | -0.0023028 | 0.00030966 | 2.9297 | 3.2639 | -119.7235 | 2.9114 | -4.6509 | 2.8976 | 3.035 | -4.3259 | 3.3051 | -119.5312 | 3.1494 | -119.1101 | -119.3344 | -118.4555 | -0.21973 | 0.032043 | -0.32044 | 114.8529 | 122.5388 | 122.4014 | 122.7585 | 122.6212 | -0.027466 | 0.073242 | -0.082398 | 0.39368 | 1.0483 | 0.16937 | 1.0757 | 0.19684 | 115.0726 | 122.6349 | 0.42114 | 122.6807 | 122.9874 | 122.8363 | 122.7676 | 122.8088 | -122.9553 | -122.7631 | 122.4152 | 122.6532 | 122.4335 | 115.1779
1047.4844 | 122.818 | -119.5312 | 3.2455 | -0.67566 | 0.71534 | 0.12466 | 0.0030207 | -0.0027921 | 0.57835 | 0.0018243 | -0.047638 | 0.0018179 | 0.067063 | 0.068404 | -0.002384 | -0.00080758 | -0.0024673 | 2.8931 | 3.2318 | -119.783 | 2.7924 | -5.0034 | 2.774 | 2.8931 | -4.4357 | 3.3005 | -119.5862 | 3.035 | -119.2429 | -119.4672 | -118.5516 | -0.25177 | -0.013732 | -0.45319 | 114.5279 | 122.4243 | 122.3053 | 122.6761 | 122.5571 | -0.054932 | 0.054932 | -0.21057 | 0.28839 | 0.97961 | 0.064087 | 1.0345 | 0.11902 | 114.7797 | 122.5754 | 0.34332 | 122.6212 | 123.0148 | 122.8867 | 122.7631 | 122.8317 | -123.0286 | -122.8317 | 122.3236 | 122.5662 | 122.4243 | 115.0955
1048.5469 | 122.8363 | -119.5587 | 3.2547 | -0.68329 | 0.71641 | 0.12552 | 0.0019525 | -0.0015103 | 0.57429 | -0.00095273 | 0.056122 | 0.00053628 | 0.066422 | 0.064345 | -0.0021704 | -0.00080758 | -0.0020401 | 2.8976 | 3.241 | -119.7739 | 2.8244 | -4.7882 | 2.8152 | 2.9388 | -4.4449 | 3.3051 | -119.5587 | 3.0075 | -119.22 | -119.4626 | -118.5791 | -0.21515 | -0.013733 | -0.4303 | 114.7705 | 122.4976 | 122.374 | 122.7127 | 122.5891 | 0 | 0.050354 | -0.24719 | 0.33875 | 0.97961 | 0.096131 | 0.97961 | 0.096131 | 114.9857 | 122.5983 | 0.33875 | 122.5662 | 123.0148 | 122.8638 | 122.7997 | 122.8638 | -123.0286 | -122.8134 | 122.3831 | 122.5662 | 122.4564 | 115.1138
1049.4844 | 122.8271 | -119.5862 | 3.2227 | -0.69855 | 0.71428 | 0.12231 | 0.0023797 | 0.0014803 | 0.57386 | -0.0039435 | -0.029327 | 0.0024589 | 0.068131 | 0.068191 | -0.0019568 | -0.0027302 | -0.0011855 | 2.8473 | 3.1998 | -119.87 | 2.7466 | -4.866 | 2.7466 | 2.861 | -4.5044 | 3.2776 | -119.6274 | 2.9892 | -119.2566 | -119.5312 | -118.6111 | -0.28381 | -0.022888 | -0.47607 | 114.7202 | 122.4472 | 122.3328 | 122.731 | 122.6166 | -0.041198 | 0.054932 | -0.23346 | 0.32959 | 0.97504 | 0.054932 | 1.0162 | 0.09613 | 115.004 | 122.6166 | 0.37079 | 122.6166 | 123.0698 | 122.905 | 122.7859 | 122.8638 | -123.0927 | -122.85 | 122.3328 | 122.5754 | 122.4335 | 115.0818
1050.4844 | 122.8226 | -119.6686 | 3.1357 | -0.60699 | 0.71599 | 0.12552 | 0.0017389 | -1.486e-05 | 0.57643 | -0.00095273 | -0.0018616 | 0.0028861 | 0.065781 | 0.064559 | -0.0002478 | -0.0010212 | 0.0024461 | 2.7512 | 3.2089 | -119.8975 | 2.6917 | -5.1132 | 2.6642 | 2.7924 | -4.6051 | 3.2455 | -119.696 | 2.8839 | -119.3344 | -119.5862 | -118.6752 | -0.22888 | 0.073242 | -0.44403 | 114.5554 | 122.4609 | 122.3328 | 122.6898 | 122.5616 | -0.027466 | 0.10986 | -0.25177 | 0.33417 | 0.99335 | 0.082397 | 1.0208 | 0.10986 | 114.7842 | 122.5891 | 0.36163 | 122.58 | 123.1064 | 122.9416 | 122.8775 | 122.9141 | -123.0331 | -122.8317 | 122.3602 | 122.5525 | 122.4197 | 115.0635
1051.5469 | 122.8912 | -119.5862 | 3.1586 | -0.37811 | 0.71534 | 0.12936 | -0.00039728 | -0.00022866 | 0.57621 | 0.00011527 | 0.05307 | 0.00010888 | 0.067276 | 0.065627 | -3.4196e-05 | -0.001662 | -0.0024673 | 2.6825 | 3.1265 | -119.8242 | 2.7832 | -4.7882 | 2.7969 | 2.8976 | -4.4998 | 3.2272 | -119.632 | 2.98 | -119.2337 | -119.4717 | -118.5608 | -0.23804 | -0.032043 | -0.37537 | 114.798 | 122.4838 | 122.3831 | 122.7219 | 122.6212 | -0.045776 | 0.068665 | -0.17853 | 0.35248 | 1.0254 | 0.11444 | 1.0712 | 0.16022 | 115.036 | 122.6074 | 0.39825 | 122.612 | 122.9507 | 122.8592 | 122.7127 | 122.8134 | -122.9828 | -122.7905 | 122.3694 | 122.5662 | 122.2687 | 115.0864
1052.4844 | 122.8043 | -119.6594 | 3.1769 | -0.66803 | 0.71428 | 0.12594 | 0.0015253 | -0.00086946 | 0.57301 | 0.00096987 | 0.010345 | 0.0016043 | 0.069412 | 0.068831 | -0.0017432 | -0.0023028 | 0.0024461 | 2.7649 | 3.1448 | -119.8746 | 2.6779 | -4.7745 | 2.6688 | 2.7924 | -4.6555 | 3.2455 | -119.7006 | 2.8976 | -119.339 | -119.5679 | -118.6707 | -0.21515 | -0.032044 | -0.49896 | 114.8849 | 122.4518 | 122.3282 | 122.6669 | 122.5433 | -0.041199 | 0.068664 | -0.27924 | 0.32044 | 0.98877 | 0.091553 | 1.03 | 0.13275 | 115.1001 | 122.5525 | 0.36163 | 122.5983 | 123.0194 | 122.9462 | 122.8043 | 122.905 | -123.0515 | -122.8775 | 122.3373 | 122.5571 | 122.4243 | 115.004
1053.4844 | 122.8409 | -119.6411 | 3.1769 | -0.6604 | 0.7115 | 0.1253 | 0.0017389 | -0.0010831 | 0.57279 | 0.0026789 | -0.0049134 | 0.00032248 | 0.068131 | 0.067123 | -0.002384 | -0.0020892 | 0.00073706 | 2.7832 | 3.186 | -119.8654 | 2.6917 | -4.3625 | 2.6642 | 2.7878 | -4.7195 | 3.2364 | -119.6548 | 2.9205 | -119.3069 | -119.5633 | -118.6295 | -0.2243 | 0.009155 | -0.48523 | 115.2786 | 122.4289 | 122.3053 | 122.6532 | 122.5296 | -0.013733 | 0.059509 | -0.25635 | 0.33417 | 1.0117 | 0.07782 | 1.0254 | 0.091553 | 115.5029 | 122.5571 | 0.3479 | 122.5754 | 123.0515 | 122.8912 | 122.8271 | 122.8775 | -123.0423 | -122.8317 | 122.3328 | 122.5616 | 122.4243 | 114.9216
1054.5469 | 122.8043 | -119.6457 | 3.1677 | -0.70618 | 0.71428 | 0.12552 | -0.00018368 | 0.0048983 | 0.57514 | -0.00073913 | 0.028656 | 0.00074988 | 0.067063 | 0.057509 | -0.002384 | -0.0014484 | 0.0030869 | 2.7832 | 3.1769 | -119.8654 | 2.6825 | -4.3213 | 2.6733 | 2.8015 | -4.747 | 3.2455 | -119.6548 | 2.8885 | -119.3527 | -119.577 | -118.6798 | -0.21973 | 0.009155 | -0.48523 | 115.3244 | 122.4472 | 122.319 | 122.6669 | 122.5388 | -0.009155 | 0.077819 | -0.27924 | 0.29297 | 0.96588 | 0.068665 | 0.97504 | 0.07782 | 115.5441 | 122.5479 | 0.30212 | 122.5433 | 123.0423 | 122.9004 | 122.8226 | 122.8912 | -123.0331 | -122.8226 | 122.3282 | 122.5342 | 122.4289 | 114.8987
1055.4844 | 122.7859 | -119.6411 | 3.1403 | -0.73669 | 0.71449 | 0.12616 | 0.0025933 | 0.00083954 | 0.57194 | 0.0016107 | -0.062897 | -0.00053192 | 0.068772 | 0.064132 | -0.002384 | -0.00038018 | -0.00011754 | 2.7878 | 3.1723 | -119.8975 | 2.6825 | -4.541 | 2.6367 | 2.7649 | -4.8386 | 3.2181 | -119.664 | 2.8839 | -119.3893 | -119.6274 | -118.6752 | -0.25635 | 0.032043 | -0.45776 | 115.1001 | 122.406 | 122.2778 | 122.6624 | 122.5342 | -0.022888 | 0.07782 | -0.25635 | 0.25177 | 0.96588 | 0.013733 | 0.98877 | 0.036621 | 115.3564 | 122.58 | 0.27466 | 122.5479 | 123.0698 | 122.8821 | 122.8134 | 122.8592 | -123.0377 | -122.8043 | 122.3236 | 122.525 | 122.4289 | 114.8026
1056.4844 | 122.8271 | -119.6136 | 3.186 | -0.72906 | 0.71385 | 0.12488 | 0.0036615 | 0.0034029 | 0.57108 | -9.8328e-05 | -0.053741 | 0.0020315 | 0.066422 | 0.066268 | -0.0017432 | -0.001662 | 0.0013779 | 2.7649 | 3.1174 | -119.9203 | 2.6871 | -4.8843 | 2.6459 | 2.7786 | -5.0308 | 3.1815 | -119.7006 | 3.1357 | -119.2245 | -119.5358 | -118.6157 | -0.3067 | -0.068664 | -0.49896 | 114.7293 | 122.3923 | 122.2595 | 122.699 | 122.5662 | -0.086976 | -0.004577 | -0.050354 | 0.3891 | 0.99792 | 0.077819 | 1.0849 | 0.16479 | 115.036 | 122.6074 | 0.47607 | 122.8363 | 123.0377 | 122.8821 | 122.731 | 122.7951 | -123.1064 | -122.8867 | 122.3007 | 122.7493 | 122.3785 | 114.5828
1057.5469 | 122.7219 | -119.6182 | 3.1769 | -0.69092 | 0.71193 | 0.12381 | 0.0019525 | 0.00019874 | 0.57087 | -9.8328e-05 | 0.016449 | -0.00010472 | 0.066849 | 0.065627 | -0.001316 | -0.003371 | 0.0056503 | 2.7145 | 3.1403 | -119.9203 | 2.6367 | -5.1086 | 2.6321 | 2.7786 | -6.2485 | 3.2043 | -119.7052 | 2.8473 | -119.3756 | -119.2795 | -118.5287 | -0.30212 | -0.036621 | -0.54016 | 114.5096 | 122.3969 | 122.2504 | 122.699 | 122.5525 | -0.086975 | 0.027466 | -0.32959 | 0.24262 | 1.0895 | 0.33874 | 1.1765 | 0.42572 | 114.8117 | 122.5571 | 0.32959 | 122.5525 | 123.0606 | 122.9095 | 122.7585 | 122.8226 | -123.0972 | -122.8821 | 122.2549 | 122.4655 | 122.3328 | 113.3698
1058.4844 | 122.8134 | -119.6365 | 3.1769 | -0.66803 | 0.71064 | 0.1253 | 0.0025933 | -0.0032193 | 0.57237 | -9.8328e-05 | -0.029327 | 0.0035269 | 0.066635 | 0.063491 | -3.4196e-05 | 4.7018e-05 | 0.0015915 | 2.7512 | 3.186 | -119.8608 | 2.6642 | -5.072 | 2.7466 | 2.7649 | -6.427 | 3.2639 | -119.6732 | 2.8931 | -119.3344 | -119.5679 | -118.6523 | -0.2243 | 0.009155 | -0.5127 | 114.5645 | 122.4014 | 122.3831 | 122.6257 | 122.6074 | -0.036621 | 0.086975 | -0.28381 | 0.30212 | 0.98419 | 0.068665 | 1.0208 | 0.10529 | 114.7888 | 122.525 | 0.33875 | 122.5662 | 123.0469 | 122.937 | 122.8226 | 122.9004 | -123.0377 | -122.85 | 122.3007 | 122.5296 | 122.3877 | 113.2095
1059.5469 | 122.905 | -121.5912 | 1.1581 | -0.70618 | 0.71748 | 0.13 | 0.0019525 | -0.0015103 | 0.57066 | 0.00011527 | 0.059174 | 0.0011771 | 0.068131 | 0.063918 | -0.0011022 | -0.00038018 | -0.00033114 | 0.81482 | 1.1719 | -121.8246 | 0.77362 | 0.92926 | 0.76904 | 0.90637 | -6.5231 | 1.2314 | -121.6232 | 1.0254 | -121.1975 | -121.4401 | -120.5292 | -0.23346 | 0.013733 | -0.38452 | 122.5204 | 122.4976 | 122.3602 | 122.731 | 122.5937 | -0.032043 | 0.073242 | -0.13275 | 0.39368 | 1.062 | 0.15106 | 1.0941 | 0.18311 | 122.7539 | 122.5983 | 0.42572 | 122.6486 | 122.9965 | 122.8546 | 122.7631 | 122.8226 | -122.9828 | -122.7814 | 122.3648 | 122.6166 | 122.406 | 115.0681
1060.4844 | 122.8409 | -121.6232 | 1.181 | -0.67566 | 0.71577 | 0.12744 | 0.0040887 | -1.486e-05 | 0.56938 | -9.8328e-05 | -0.0049134 | -0.00031832 | 0.068558 | 0.067123 | -0.0019568 | -0.00038018 | 0.0022323 | 0.79193 | 1.1948 | -121.8979 | 0.70496 | 0.82398 | 0.69122 | 0.81482 | -6.633 | 1.2589 | -121.6415 | 0.92468 | -121.2936 | -121.5454 | -120.6162 | -0.27466 | 0.013733 | -0.47607 | 122.4472 | 122.438 | 122.3145 | 122.7127 | 122.5891 | -0.018311 | 0.07782 | -0.25635 | 0.32959 | 1.0071 | 0.07782 | 1.0254 | 0.096131 | 122.7219 | 122.6028 | 0.3479 | 122.5662 | 123.0927 | 122.9004 | 122.818 | 122.8821 | -123.0789 | -122.8226 | 122.3282 | 122.5479 | 122.4152 | 114.9902
1061.5469 | 122.8088 | -121.8658 | 0.95673 | -0.62225 | 0.71577 | 0.12744 | 0.00045712 | -0.00065586 | 0.57279 | 0.0035333 | -0.011017 | 0.00032248 | 0.06749 | 0.065841 | -0.001316 | -0.0012348 | -0.00075834 | 0.55847 | 0.9613 | -122.0947 | 0.45319 | 0.62714 | 0.45319 | 0.58594 | -6.6833 | 1.0345 | -121.8613 | 0.6546 | -121.55 | -121.788 | -120.8633 | -0.22888 | 0.004578 | -0.50354 | 122.493 | 122.4518 | 122.319 | 122.6807 | 122.5479 | 0.004578 | 0.07782 | -0.30212 | 0.31586 | 1.0025 | 0.07782 | 0.99792 | 0.073242 | 122.7219 | 122.5479 | 0.31128 | 122.5159 | 123.056 | 122.8958 | 122.8271 | 122.9004 | -123.0515 | -122.818 | 122.319 | 122.5204 | 122.4243 | 115.1825
1062.5 | 122.8088 | -121.843 | 0.96588 | -0.75958 | 0.71299 | 0.12872 | 0.0017389 | 0.0010531 | 0.57151 | 0.0050287 | -0.10562 | 0.0018179 | 0.067917 | 0.0652 | -0.0017432 | 0.00047422 | -0.0016129 | 0.55847 | 0.98419 | -122.0901 | 0.4303 | 0.48523 | 0.7782 | 0.61798 | -6.8481 | 1.0529 | -121.843 | 0.71411 | -121.5546 | -121.8246 | -120.8588 | -0.24719 | 0.018311 | -0.53558 | 122.3282 | 122.4609 | 122.6212 | 122.7081 | 122.8683 | 0 | 0.086975 | -0.25177 | 0.28839 | 0.98419 | 0.018311 | 0.98419 | 0.018311 | 122.5754 | 122.5204 | 0.28839 | 122.5571 | 123.0743 | 122.8958 | 122.8271 | 122.8958 | -123.056 | -122.8088 | 122.2733 | 122.5571 | 122.4014 | 114.9948
1063.4844 | 122.7997 | -121.8109 | 1.0117 | -0.72144 | 0.71449 | 0.12851 | 0.0019525 | 0.0023349 | 0.57173 | 0.00075627 | -0.053741 | 0.0016043 | 0.068344 | 0.063491 | -0.002384 | 4.7018e-05 | -0.00075834 | 0.62256 | 1.0117 | -122.0398 | 0.52185 | 0.67291 | 0.48523 | 0.60883 | -6.8985 | 1.062 | -121.8384 | 0.73242 | -121.5271 | -121.7926 | -120.8313 | -0.22888 | 0 | -0.48981 | 122.4838 | 122.4197 | 122.2961 | 122.6486 | 122.525 | -0.027466 | 0.050354 | -0.27924 | 0.28381 | 0.97961 | 0.01831 | 1.0071 | 0.045776 | 122.7127 | 122.5616 | 0.31128 | 122.5708 | 123.0515 | 122.9004 | 122.8226 | 122.8729 | -123.0515 | -122.85 | 122.3328 | 122.5433 | 122.4335 | 114.9124
1064.5469 | 122.7676 | -121.5088 | 1.3229 | -0.64514 | 0.71534 | 0.12723 | 0.0013117 | -0.0021513 | 0.57066 | -9.8328e-05 | -0.0049134 | 0.0024589 | 0.06749 | 0.063277 | -0.0021704 | -0.00059378 | -0.00033114 | 0.79651 | 1.2222 | -121.8109 | 0.6958 | 0.8606 | 0.70953 | 0.85144 | -6.8756 | 1.2909 | -121.6049 | 0.95673 | -121.1792 | -121.463 | -120.5246 | -0.30212 | -0.10071 | -0.62714 | 122.3694 | 122.3602 | 122.2183 | 122.6624 | 122.5204 | -0.09613 | -0.032043 | -0.36621 | 0.32959 | 0.98419 | 0.045776 | 1.0803 | 0.14191 | 122.6715 | 122.5067 | 0.42572 | 122.5616 | 123.0331 | 122.8958 | 122.731 | 122.7997 | -123.1338 | -122.9279 | 122.2046 | 122.4655 | 122.3053 | 114.6332
1065.4844 | 122.9233 | -121.5363 | 1.2726 | -0.6604 | 0.71406 | 0.12872 | 0.0025933 | 0.00083954 | 0.56895 | -0.00031193 | -0.05069 | 0.00074988 | 0.069626 | 0.063918 | -0.0015296 | 0.00047422 | 0.00052346 | 0.92468 | 1.2817 | -121.7926 | 0.81024 | 0.97961 | 0.78278 | 0.9201 | -6.9168 | 1.3458 | -121.55 | 1.0391 | -121.2112 | -121.4447 | -120.5154 | -0.25635 | 0.009155 | -0.46234 | 122.5159 | 122.4564 | 122.319 | 122.7127 | 122.5754 | -0.013733 | 0.073242 | -0.23346 | 0.32501 | 1.0208 | 0.091553 | 1.0345 | 0.10529 | 122.7722 | 122.6028 | 0.33875 | 122.5891 | 123.0743 | 122.8958 | 122.818 | 122.8821 | -123.0652 | -122.8226 | 122.3465 | 122.5754 | 122.4609 | 114.6194
1066.4844 | 122.7173 | -4.715 | 118.0618 | -0.019531 | 0.0031253 | -0.00052126 | 0.0013117 | 0.0031893 | -0.00035682 | -0.0011663 | -0.0079652 | 0.0033133 | 0.082657 | 0.065627 | 0.000393 | -0.00059378 | -0.00033114 | -4.4449 | -4.1382 | -4.7012 | -4.6051 | -3.5019 | -4.5227 | -0.29297 | 0.29755 | 118.4463 | -4.6188 | 117.8696 | -4.6326 | -4.7424 | -4.6417 | 0.013733 | -122.2 | -122.6669 | 1.2131 | 4.422 | 0.19226 | 4.4083 | 0.17853 | 0.096131 | 0.38452 | -0.19226 | 0.082398 | 0.073242 | -0.027466 | -0.022889 | -0.1236 | 1.1993 | 0.09613 | -0.013733 | 122.4884 | 0.56305 | 123.0652 | 0.57678 | 123.1613 | -122.7631 | -122.6807 | 0.10986 | 122.5845 | 0.27008 | 5.0125
1067.5 | 122.9553 | -4.1885 | 118.4235 | -0.057678 | 0.0041935 | -0.00094846 | 0.0028069 | 0.0036165 | 7.0582e-05 | 0.00011527 | -0.035431 | 0.0026725 | 0.081589 | 0.069472 | -0.0008886 | -0.00080758 | -0.0024673 | -4.1107 | -3.8818 | -4.4312 | -4.1611 | -3.1723 | -4.1473 | -4.0512 | 0.14648 | 118.6935 | -4.3076 | 118.7805 | -3.9505 | -4.0375 | -3.9642 | -0.24261 | -122.3053 | -122.5845 | 1.0162 | 0.13733 | 0.041199 | 0.37994 | 0.28381 | -0.11902 | 0.27008 | 0.35706 | 0.23804 | 0.22431 | 0.15106 | 0.34332 | 0.27008 | 1.2588 | 0.27008 | 0.35706 | 123.0881 | 0.54932 | 123.0011 | 0.3067 | 122.8821 | -122.8546 | -122.731 | 0.027466 | 122.9691 | 0.07782 | 4.335
1068.4844 | 122.8134 | -3.2318 | 119.6411 | 0.056763 | 0.0031253 | -0.0056483 | 0.0030207 | -0.00065586 | 0.0011386 | -0.00073913 | -0.044586 | 0.0045951 | 0.081803 | 0.06285 | -0.001316 | -0.0023028 | 9.6064e-05 | -3.1448 | -2.7603 | -3.4607 | -3.2959 | -3.1311 | -3.2089 | -2.8381 | 0.041199 | 119.7281 | -3.3691 | 119.5679 | -3.0441 | -3.1998 | -3.0853 | -0.22888 | -122.4014 | -122.937 | 0.10071 | 0.39368 | 0.022889 | 0.62256 | 0.25177 | -0.13733 | 0.086975 | -0.073242 | 0.18768 | 0.14649 | 0.032044 | 0.28381 | 0.16937 | 0.32959 | 0.16479 | 0.32501 | 122.937 | 0.70038 | 123.0972 | 0.4715 | 122.9599 | -123.1018 | -123.0103 | -0.064086 | 122.7997 | 0.086976 | 3.273
1069.4844 | 122.85 | -3.4882 | 119.4351 | -0.050049 | 0.0029117 | -0.0041529 | 0.0023797 | -0.00065586 | -0.002493 | 0.00032907 | -0.069 | 0.0018179 | 0.082444 | 0.061568 | -0.0025976 | -0.0010212 | -0.00011754 | -3.4058 | -3.0396 | -3.6575 | -3.36 | -3.1631 | -3.3234 | -3.2684 | 0.050354 | 119.4077 | -3.6346 | 119.4168 | -3.3325 | -3.3737 | -3.2318 | -0.16937 | -122.4747 | -122.7951 | 0.32501 | 0.21973 | 0.16479 | 0.3891 | 0.33417 | -0.14649 | -0.027466 | -0.018311 | 0.15564 | 0.25635 | 0.11444 | 0.40283 | 0.26093 | 0.49438 | 0.29755 | 0.30212 | 123.0515 | 0.61798 | 123.0423 | 0.44861 | 122.8958 | -123.0927 | -123.0698 | 0.12817 | 122.905 | 0.082397 | 3.5385
1070.5469 | 122.9691 | -3.1311 | 119.7693 | -0.050049 | 0.0039799 | -0.0032983 | -0.0021063 | 0.00041234 | 0.00049778 | -0.0015935 | 0.037811 | 0.0020315 | 0.080521 | 0.065414 | -0.0011022 | -0.0012348 | -0.0016129 | -2.8656 | -2.6688 | -3.1906 | -2.9755 | -2.7649 | -2.8885 | -2.8244 | 0.47607 | 119.8883 | -3.1723 | 119.8196 | -2.7924 | -2.9434 | -2.8839 | -0.059509 | -122.438 | -122.7448 | 0.36621 | 0.3067 | 0.24262 | 0.36621 | 0.30212 | -0.041198 | 0.11902 | 0.050354 | 0.33875 | 0.24719 | 0.18768 | 0.28839 | 0.22888 | 0.42572 | 0.21515 | 0.37994 | 122.9919 | 0.52185 | 123.0606 | 0.46234 | 123.0194 | -122.9599 | -122.9416 | 0.15564 | 122.9507 | 0.2655 | 3.6072
1071.4844 | 122.9004 | -4.9942 | 117.8146 | -0.011902 | 0.0031253 | -0.0041529 | 0.0025933 | 0.0027621 | 0.00071138 | -0.0015935 | -0.075104 | 0.0024589 | 0.080521 | 0.067123 | -0.0036658 | -0.00059378 | -0.00097194 | -4.9347 | -4.6097 | -5.3009 | -4.9942 | -4.8523 | -5.0079 | -4.9118 | 0.11444 | 118.0069 | -5.127 | 117.8604 | -4.8523 | -5.0217 | -4.8843 | -0.3067 | -122.4243 | -122.8088 | 0.14191 | 0.082398 | -0.013733 | 0.3891 | 0.29297 | -0.13275 | 0.19226 | 0.045777 | 0.14191 | 0.10986 | -0.027465 | 0.24262 | 0.10529 | 0.44861 | 0.3067 | 0.27466 | 122.9874 | 0.69122 | 123.1338 | 0.38452 | 123.0011 | -123.1155 | -122.9416 | 0 | 122.8546 | 0.05951 | 5.1086
1072.5625 | 122.8958 | -3.7079 | 119.1925 | -0.080566 | 0.0029117 | -0.0032983 | 0.0028069 | -0.00086946 | 0.00092498 | -0.0022345 | -0.072052 | 0.0013907 | 0.082871 | 0.063064 | -0.0028112 | 4.7018e-05 | 0.00052346 | -3.6758 | -3.1815 | -3.804 | -3.6758 | -3.5934 | -3.6942 | -3.5797 | -0.032043 | 119.3024 | -3.8315 | 119.1834 | -3.5614 | -3.6987 | -3.5614 | -0.09613 | -122.374 | -122.8683 | 0.11444 | 0.12817 | 0.013733 | 0.2243 | 0.10986 | -0.1236 | 0.10986 | -0.009155 | 0.14648 | 0.14648 | 0.009156 | 0.27008 | 0.13275 | 0.21057 | 0.12817 | 0.27008 | 123.0148 | 0.62256 | 123.1338 | 0.52643 | 123.0103 | -122.9965 | -123.024 | 0.032044 | 122.8912 | 0.032044 | 3.6758
1073.4844 | 122.937 | -4.0558 | 118.8309 | -0.027161 | 0.0039799 | -0.0050073 | 0.0021661 | 0.0046847 | 0.0017794 | 0.00075627 | -0.053741 | 0.0028861 | 0.081162 | 0.068191 | -0.0002478 | -0.0023028 | -0.00097194 | -3.9871 | -3.6804 | -4.3259 | -4.1153 | -3.9871 | -4.129 | -4.0649 | 0.068665 | 118.84 | -4.3076 | 118.8629 | -3.7674 | -4.0009 | -3.9093 | -0.27008 | -122.5113 | -122.9462 | 0.068664 | -0.009155 | -0.073242 | 0.26093 | 0.19684 | -0.25177 | 0.009155 | 0.032043 | 0.28839 | 0.14648 | 0.054932 | 0.39825 | 0.3067 | 0.33874 | 0.21057 | 0.54016 | 123.1705 | 0.64545 | 123.1476 | 0.37537 | 122.8958 | -123.1567 | -123.1384 | -0.059509 | 122.9187 | 0.068664 | 4.1245
1074.5469 | 122.9507 | -5.0629 | 117.8192 | -0.065308 | 0.0041935 | -0.0043665 | 0.00045712 | 0.0036165 | 0.0017794 | -0.0041571 | 0.034759 | 0.0018179 | 0.080948 | 0.061355 | -0.0019568 | -0.00016658 | 9.6064e-05 | -4.9164 | -4.5639 | -5.2094 | -5.0034 | -4.8431 | -4.953 | -4.8614 | -0.11902 | 117.9016 | -5.1773 | 117.8421 | -4.8843 | -4.9942 | -4.8798 | -0.14649 | -122.3831 | -122.8226 | 0.21973 | 0.20142 | 0.10986 | 0.3479 | 0.25635 | -0.11444 | 0.082397 | 0.022888 | 0.17853 | 0.1831 | 0.068664 | 0.29755 | 0.18311 | 0.36621 | 0.20599 | 0.29297 | 123.0194 | 0.64545 | 123.0789 | 0.49896 | 122.9645 | -123.0286 | -122.9965 | 0.059509 | 122.905 | 0.14648 | 4.9438
1075.4844 | 122.9233 | -5.8273 | 117.0685 | -0.050049 | 0.0035525 | -0.0058619 | 0.0025933 | 0.00019874 | 0.0039158 | 0.00096987 | -0.05069 | -0.00053192 | 0.082444 | 0.066268 | -0.0028112 | 0.00047422 | -0.0018265 | -5.6763 | -5.2963 | -6.0242 | -5.8182 | -5.6122 | -5.7266 | -5.6763 | -0.09613 | 117.215 | -5.9418 | 117.0547 | -5.6854 | -5.8273 | -5.6534 | -0.19684 | -122.3648 | -122.8867 | 0.21515 | 0.15106 | 0.10071 | 0.3479 | 0.29755 | -0.11444 | 0.14648 | -0.013732 | 0.14191 | 0.17395 | 0 | 0.28839 | 0.11444 | 0.41199 | 0.20599 | 0.25635 | 122.9965 | 0.72784 | 123.1567 | 0.53101 | 123.0423 | -123.0927 | -123.0103 | 0.009156 | 122.8821 | 0.15106 | 5.7312
1076.5469 | 122.9233 | -5.8594 | 117.0639 | -0.027161 | 0.0056889 | -0.0022303 | -0.0010383 | -0.00086946 | 0.0011386 | -0.0011663 | 0.043915 | 0.00096348 | 0.083725 | 0.061355 | 0.0006066 | -0.00016658 | -0.0011855 | -5.8594 | -5.5206 | -6.2485 | -6.0471 | -5.8868 | -6.0104 | -5.9326 | -0.050354 | 116.9128 | -6.2119 | 117.0273 | -5.69 | -5.8273 | -5.7312 | -0.3891 | -122.5845 | -123.111 | -0.027466 | -0.073242 | -0.15106 | 0.31586 | 0.23804 | -0.35248 | -0.15106 | -0.036621 | 0.16937 | 0.12817 | 0.032043 | 0.48065 | 0.38452 | 0.36163 | 0.20142 | 0.52185 | 123.2391 | 0.72784 | 123.1247 | 0.33875 | 122.7722 | -123.3124 | -123.2758 | -0.18768 | 122.8867 | 0 | 5.809
1077.5 | 122.9874 | -5.2048 | 117.6544 | -0.057678 | 0.0039799 | -0.0020167 | 2.9918e-05 | 0.0034029 | 0.0024204 | -0.0013799 | 0.013397 | 0.00032248 | 0.083298 | 0.066268 | -0.002384 | -0.0023028 | 0.00095066 | -5.0674 | -4.7699 | -5.4016 | -5.1727 | -4.985 | -5.1361 | -5.0537 | -0.064087 | 117.7505 | -5.3329 | 117.7231 | -5.0217 | -5.1315 | -5.0217 | -0.19684 | -122.4243 | -122.8271 | 0.21973 | 0.15106 | 0.068665 | 0.3479 | 0.2655 | -0.12817 | 0.09613 | 0.068664 | 0.18311 | 0.18311 | 0.073242 | 0.31128 | 0.20142 | 0.41657 | 0.22888 | 0.31128 | 123.056 | 0.63171 | 123.0835 | 0.43488 | 122.9553 | -123.056 | -122.9874 | 0.032044 | 122.9279 | 0.13733 | 5.1407
1078.5469 | 123.0423 | -5.3467 | 117.5308 | -0.042419 | 0.0050479 | -0.0041529 | -0.0021063 | 0.00083954 | 0.00071138 | -0.0030889 | 0.022552 | 0.00032248 | 0.081803 | 0.061141 | -0.001316 | -0.0014484 | -0.0031081 | -5.1315 | -4.8111 | -5.4428 | -5.2139 | -5.0491 | -5.191 | -4.9255 | -0.10071 | 117.6361 | -5.4749 | 117.6178 | -5.0858 | -5.2551 | -5.1682 | -0.09613 | -122.3419 | -122.7448 | 0.29755 | 0.42114 | 0.15564 | 0.51727 | 0.25177 | -0.12817 | 0.10528 | 0.086975 | 0.26093 | 0.17853 | 0.091553 | 0.3067 | 0.21973 | 0.39368 | 0.22888 | 0.3891 | 123.0927 | 0.63171 | 123.111 | 0.53558 | 122.9828 | -122.9736 | -123.0057 | 0.13275 | 122.9645 | 0.21515 | 5.246
1079.4844 | 122.9462 | -5.3146 | 117.5995 | 0.049133 | 0.0048343 | -0.0043665 | 0.0023797 | 0.0021213 | 7.0582e-05 | 0.0016107 | -0.065949 | 0.00053628 | 0.08223 | 0.067336 | 0.0001794 | 0.00026062 | -0.00075834 | -5.1498 | -4.8157 | -5.4886 | -5.3101 | -5.1727 | -5.2597 | -5.2185 | -0.068665 | 117.7322 | -5.452 | 117.6224 | -5.1636 | -5.3101 | -5.1727 | -0.17395 | -122.4152 | -122.9095 | 0.14191 | 0.09613 | 0.054931 | 0.27008 | 0.22888 | -0.13733 | 0.13275 | 0.022888 | 0.15106 | 0.14191 | 0.004577 | 0.27924 | 0.14191 | 0.31586 | 0.17853 | 0.28839 | 123.0743 | 0.67291 | 123.1842 | 0.49896 | 123.0469 | -123.0881 | -123.0515 | 0.004577 | 122.937 | 0.16479 | 5.246
1080.5469 | 122.9919 | -5.4199 | 117.4805 | -0.03479 | 0.0052615 | -0.0041529 | 0.00045712 | -0.00044226 | 0.0017794 | -0.0024481 | 0.025604 | 0.00053628 | 0.083084 | 0.064345 | -0.002384 | -0.0046528 | 0.00073706 | -5.2963 | -4.9942 | -5.6351 | -5.3879 | -5.2277 | -5.3558 | -5.2963 | -0.054932 | 117.5217 | -5.5939 | 117.5079 | -5.2368 | -5.3558 | -5.2414 | -0.21515 | -122.4747 | -122.8683 | 0.19226 | 0.1236 | 0.064087 | 0.33875 | 0.27924 | -0.17395 | 0.041198 | 0.027466 | 0.18311 | 0.17853 | 0.064087 | 0.35248 | 0.23804 | 0.40741 | 0.24719 | 0.35706 | 123.1018 | 0.64087 | 123.1155 | 0.42572 | 122.9416 | -123.1155 | -123.0743 | 0.032044 | 122.9279 | 0.1236 | 5.365
1081.4844 | 122.9599 | -5.928 | 117.0319 | -0.057678 | 0.0041935 | -0.0039393 | 0.0028069 | 0.0040439 | 0.0017794 | -0.0030889 | -0.075104 | 0.0013907 | 0.079026 | 0.070327 | -0.0017432 | -0.00059378 | 0.0033005 | -5.7907 | -5.397 | -6.102 | -5.983 | -5.8411 | -5.9692 | -5.896 | -0.16479 | 117.0639 | -6.1478 | 116.9952 | -5.6213 | -5.8823 | -5.7816 | -0.17395 | -122.4289 | -123.0148 | 0.086976 | 0.032044 | -0.041198 | 0.20599 | 0.13275 | -0.21973 | 0.032044 | -0.036621 | 0.3067 | 0.14649 | 0.045777 | 0.36621 | 0.2655 | 0.26093 | 0.11902 | 0.52643 | 123.143 | 0.70496 | 123.2117 | 0.53101 | 122.9919 | -123.1338 | -123.1796 | -0.054931 | 122.9233 | 0.13733 | 5.7632
1082.5625 | 122.9599 | -5.2643 | 117.6727 | -0.03479 | 0.0037661 | -0.0052209 | 0.0025933 | -0.00022866 | 0.00028418 | 0.00075627 | -0.075104 | 0.0013907 | 0.08458 | 0.06755 | 0.0014612 | -0.0035846 | 9.6064e-05 | -5.0903 | -4.715 | -5.4245 | -5.2551 | -5.0858 | -5.2414 | -5.1865 | -0.14191 | 117.7826 | -5.4291 | 117.6819 | -5.1682 | -5.246 | -5.127 | -0.16022 | -122.3877 | -122.9279 | 0.17853 | 0.07782 | 0.022888 | 0.23804 | 0.18311 | -0.1648 | 0.10986 | 0.009156 | 0.09613 | 0.13733 | 0.01831 | 0.30212 | 0.18311 | 0.33875 | 0.16937 | 0.26093 | 123.111 | 0.70953 | 123.2117 | 0.54932 | 123.0469 | -123.0972 | -123.1018 | 0.009155 | 122.9462 | 0.17395 | 5.1224
1083.4844 | 122.9553 | -6.2485 | 116.6794 | 0.0033567 | 0.0024845 | -0.0047937 | 0.0028069 | 0.00083954 | 0.0032748 | -0.0035163 | -0.05069 | 0.0035269 | 0.081803 | 0.065627 | 0.0001794 | -0.0010212 | -0.0020401 | -5.8548 | -5.5435 | -6.2531 | -6.2073 | -5.9738 | -6.1478 | -6.1523 | -0.32044 | 116.7572 | -6.395 | 116.7343 | -6.0837 | -6.2393 | -6.0608 | -0.004578 | -122.2229 | -122.8867 | 0.27466 | 0.09613 | 0.10071 | 0.10071 | 0.10529 | -0.14648 | 0.07782 | 0.054932 | 0.16479 | 0.18768 | 0.009155 | 0.33417 | 0.15564 | 0.27924 | 0.045777 | 0.31128 | 123.1293 | 0.70953 | 123.1522 | 0.70496 | 123.0057 | -122.9324 | -123.0743 | 0.041199 | 122.9828 | 0.39368 | 5.928
1084.4844 | 122.9599 | -6.0791 | 116.8808 | 0.0033567 | 0.0031253 | -0.0052209 | 0.0036615 | -0.0023649 | 0.0032748 | -0.0015935 | -0.032379 | 0.0016043 | 0.081589 | 0.067336 | -0.0011022 | -0.0012348 | 0.0018051 | -5.8777 | -5.4886 | -6.2393 | -6.134 | -5.9921 | -6.0379 | -5.9052 | -0.36163 | 117.0639 | -6.1249 | 116.8854 | -5.896 | -6.0791 | -5.8731 | -0.16022 | -122.3694 | -123.0148 | 0.086976 | 0.17395 | 0.041199 | 0.33417 | 0.20142 | -0.045776 | 0.18311 | 0.004578 | 0.18311 | 0.20599 | 0 | 0.25177 | 0.045776 | 0.24719 | 0.10529 | 0.22888 | 123.0103 | 0.75073 | 123.1888 | 0.59052 | 123.143 | -123.1201 | -123.0057 | -0.054931 | 122.9645 | 0.20142 | 5.7175
1085.5469 | 123.0515 | -6.4819 | 116.4185 | -0.11108 | 0.0044071 | -0.0024439 | 0.00024352 | -0.0025785 | 0.0045566 | -0.0024481 | 0.034759 | -0.00010472 | 0.082871 | 0.065627 | -0.000675 | -0.0027302 | 0.0013779 | -6.3446 | -5.9738 | -6.7245 | -6.5689 | -6.4087 | -6.4911 | -6.3995 | -0.30212 | 116.4047 | -6.7245 | 116.4917 | -6.2531 | -6.3675 | -6.2714 | -0.24261 | -122.3923 | -122.9874 | 0.073243 | 0.082398 | -0.009155 | 0.32501 | 0.23346 | -0.24261 | -0.013733 | 0.073242 | 0.22888 | 0.21057 | 0.11444 | 0.45319 | 0.35706 | 0.31586 | 0.15564 | 0.4715 | 123.2162 | 0.75073 | 123.1293 | 0.50812 | 122.8867 | -123.143 | -123.143 | -0.086975 | 122.9736 | 0.13733 | 6.1798
1086.4844 | 122.9416 | -6.1523 | 116.8396 | -0.019531 | 0.0020573 | -0.0056483 | 0.0017389 | -0.00086946 | 0.00092498 | -0.00052553 | -0.011017 | 0.0016043 | 0.08223 | 0.063277 | -0.0008886 | -0.003371 | 0.0022323 | -6.0471 | -5.5115 | -6.2805 | -6.2439 | -6.0928 | -6.2027 | -6.1203 | -0.21973 | 116.8991 | -6.3492 | 116.7114 | -6.0608 | -6.1981 | -6.0333 | -0.12817 | -122.3511 | -123.0835 | 0.05951 | 0.032044 | -0.050354 | 0.16022 | 0.07782 | -0.19684 | 0.059509 | -0.12817 | 0.091553 | 0.11902 | -0.045776 | 0.31586 | 0.15106 | 0.18768 | 0.036622 | 0.28839 | 123.0606 | 0.76904 | 123.2483 | 0.64087 | 123.0515 | -123.1201 | -123.1888 | -0.091552 | 122.8638 | 0.10529 | 5.9326
1087.5469 | 123.0652 | -6.4682 | 116.4551 | -0.0042723 | 0.0039799 | -0.0039393 | 0.0013117 | -0.0023649 | 0.00028418 | -0.00031193 | 0.037811 | -0.00010472 | 0.07988 | 0.062423 | -0.0017432 | -0.0014484 | 0.0015915 | -6.34 | -5.8777 | -6.5643 | -6.3766 | -6.2759 | -6.2942 | -6.2897 | -0.18768 | 116.5329 | -6.6193 | 116.5421 | -6.2485 | -6.4087 | -6.3171 | -0.09613 | -122.3328 | -122.8317 | 0.19226 | 0.17853 | 0.17395 | 0.27466 | 0.27008 | -0.15106 | 0.07782 | 0.086975 | 0.21973 | 0.15106 | 0.05951 | 0.30212 | 0.21057 | 0.28839 | 0.18768 | 0.37079 | 123.1613 | 0.68665 | 123.1522 | 0.59051 | 123.0011 | -123.0194 | -123.0743 | 0.091553 | 123.0103 | 0.12817 | 6.2805
1088.4844 | 122.9599 | -6.5323 | 116.4413 | 0.026245 | 0.0041935 | -0.0052209 | 0.0040887 | -1.486e-05 | 0.00049778 | 0.0013971 | -0.01712 | 0.0037405 | 0.082657 | 0.069259 | -0.000675 | -0.00038018 | 0.0011643 | -6.2805 | -5.809 | -6.6376 | -6.4407 | -6.3034 | -6.4087 | -6.0837 | -0.48523 | 116.6336 | -6.5918 | 116.391 | -6.3904 | -6.5369 | -6.4087 | -0.10528 | -122.2504 | -122.8821 | 0.22888 | 0.44861 | 0.1236 | 0.55389 | 0.22888 | -0.059509 | 0.19226 | -0.050354 | 0.14191 | 0.1236 | -0.004577 | 0.18311 | 0.054932 | 0.33417 | 0.19684 | 0.20142 | 122.9828 | 0.82855 | 123.2254 | 0.72327 | 123.1659 | -123.0789 | -123.0331 | 0.091553 | 122.9233 | 0.25177 | 6.0471
1089.4844 | 122.9919 | -6.3309 | 116.6428 | -0.03479 | 0.0061161 | -0.0030847 | 0.0028069 | 0.0010531 | 0.0024204 | 0.0013971 | -0.05069 | 0.0011771 | 0.082444 | 0.065414 | -0.0021704 | 4.7018e-05 | -0.00075834 | -6.0928 | -5.722 | -6.4682 | -6.2347 | -6.0425 | -6.1935 | -6.1523 | -0.28839 | 116.7389 | -6.4682 | 116.6245 | -6.221 | -6.3583 | -6.2073 | -0.13733 | -122.3648 | -122.8775 | 0.28839 | 0.17853 | 0.13733 | 0.31586 | 0.27466 | -0.13733 | 0.096131 | -0.01831 | 0.10986 | 0.1236 | -0.027465 | 0.26093 | 0.10986 | 0.42572 | 0.23346 | 0.24719 | 123.0927 | 0.74615 | 123.2071 | 0.60883 | 123.0698 | -123.111 | -123.111 | 0.096131 | 122.9553 | 0.23804 | 6.0425
1090.5469 | 123.0972 | -6.4499 | 116.4459 | -0.095825 | 0.0024845 | -0.0047937 | 0.00045712 | -0.0017239 | 0.0030612 | -0.0015935 | 0.068329 | 0.00074988 | 0.079026 | 0.066054 | -0.000675 | -0.0023028 | 0.0018051 | -6.2439 | -5.9006 | -6.5826 | -6.3446 | -6.1844 | -6.3217 | -6.2439 | -0.16937 | 116.5649 | -6.5826 | 116.5512 | -6.221 | -6.3354 | -6.2393 | -0.13275 | -122.3465 | -122.7905 | 0.2655 | 0.20599 | 0.12817 | 0.33875 | 0.26093 | -0.13275 | 0.11902 | 0.10529 | 0.22888 | 0.21057 | 0.11444 | 0.34332 | 0.24719 | 0.39825 | 0.23804 | 0.36163 | 123.1338 | 0.68207 | 123.1476 | 0.54932 | 123.0148 | -123.0286 | -123.0286 | 0.10529 | 123.0011 | 0.20599 | 6.2805
1091.4844 | 123.0057 | -7.2739 | 115.6311 | -0.027161 | 0.0044071 | -0.0037257 | 0.0034479 | 0.0014803 | 0.0015658 | 0.0011835 | -0.072052 | 0.0016043 | 0.081589 | 0.070968 | -0.0038794 | -0.00059378 | 0.00095066 | -7.0724 | -6.72 | -7.5211 | -7.1686 | -7.0358 | -7.164 | -7.1045 | -0.34332 | 115.8234 | -7.3883 | 115.6906 | -7.1732 | -7.3471 | -7.2189 | -0.24719 | -122.3511 | -122.7997 | 0.23804 | 0.16937 | 0.10986 | 0.41657 | 0.35706 | -0.11444 | 0.19226 | 0.059509 | 0.10071 | 0.054932 | -0.073242 | 0.16937 | 0.041199 | 0.48523 | 0.35248 | 0.21515 | 123.0789 | 0.80109 | 123.2117 | 0.55389 | 123.0972 | -123.1522 | -123.0194 | 0.10529 | 122.9645 | 0.20142 | 6.9305
1092.5469 | 123.0469 | -6.7612 | 116.153 | -0.019531 | 0.0046207 | -0.0045801 | 0.00067072 | 0.00041234 | 7.0582e-05 | -0.0035163 | 0.013397 | 0.00010888 | 0.081803 | 0.065627 | -0.000675 | -0.0020892 | -0.0020401 | -6.6055 | -6.1111 | -6.926 | -6.7154 | -6.5598 | -6.6925 | -6.5552 | -0.32959 | 116.3086 | -6.8848 | 116.1758 | -6.6101 | -6.7841 | -6.6422 | -0.16479 | -122.2641 | -122.8683 | 0.20142 | 0.20599 | 0.068664 | 0.37079 | 0.23346 | -0.1236 | 0.15564 | 0.022888 | 0.15106 | 0.11902 | -0.022889 | 0.24261 | 0.10071 | 0.36621 | 0.21057 | 0.27466 | 123.0606 | 0.81482 | 123.1934 | 0.65002 | 123.0698 | -123.0789 | -123.0377 | 0.045776 | 122.937 | 0.15564 | 6.4316
1093.4844 | 123.0057 | -6.4224 | 116.5466 | 0.018616 | 0.0039799 | -0.0030847 | 0.0038751 | 0.0048983 | 0.0011386 | -0.0011663 | -0.056793 | 0.0018179 | 0.081375 | 0.062636 | -0.0036658 | -0.00059378 | -0.0011855 | -6.2897 | -5.8502 | -6.633 | -6.4087 | -6.2805 | -6.3721 | -6.3126 | -0.2655 | 116.6336 | -6.5918 | 116.5466 | -6.2897 | -6.4178 | -6.2897 | -0.21057 | -122.3969 | -122.9553 | 0.14191 | 0.10986 | 0.050354 | 0.32044 | 0.26093 | -0.16937 | 0.086975 | 0 | 0.13275 | 0.13275 | 0.004577 | 0.30212 | 0.17395 | 0.35248 | 0.22431 | 0.30212 | 123.1384 | 0.78278 | 123.2254 | 0.5722 | 123.056 | -123.1796 | -123.1384 | 0.013733 | 122.9691 | 0.13275 | 6.1569
1094.4844 | 123.0377 | -6.3354 | 116.6748 | 0.010986 | 0.0046207 | -0.0050073 | 0.0010981 | 0.0066073 | 0.0011386 | -0.00073913 | -0.032379 | 0.0033133 | 0.083298 | 0.063064 | -0.0025976 | -0.0014484 | -0.0054581 | -6.1157 | -5.6442 | -6.3995 | -6.2164 | -6.0928 | -6.1707 | -6.1157 | -0.3067 | 116.8213 | -6.4041 | 116.6336 | -6.1981 | -6.3309 | -6.1752 | -0.064087 | -122.319 | -122.8912 | 0.24261 | 0.21973 | 0.16479 | 0.28381 | 0.22888 | -0.068665 | 0.14648 | -0.041199 | 0.13733 | 0.16022 | 0.004577 | 0.22888 | 0.073242 | 0.3067 | 0.18311 | 0.20599 | 123.0377 | 0.75531 | 123.2254 | 0.69122 | 123.1567 | -123.0743 | -123.0789 | 0.11902 | 122.9691 | 0.21973 | 6.0287
1095.5469 | 123.0606 | -6.1249 | 116.835 | -0.011902 | 0.0039799 | -0.0032983 | 0.0015253 | 0.0023349 | 0.002634 | -0.0013799 | -0.029327 | 0.0011771 | 0.083084 | 0.062423 | -0.0021704 | -0.0018756 | 0.0052231 | -5.9418 | -5.5527 | -6.2851 | -6.015 | -5.8731 | -6.0791 | -6.0379 | -0.28381 | 116.8991 | -6.3034 | 116.8808 | -5.9143 | -6.0745 | -5.9738 | -0.16022 | -122.3877 | -122.85 | 0.25177 | 0.086975 | 0.045776 | 0.24719 | 0.20599 | -0.17853 | 0.064087 | 0.045776 | 0.21057 | 0.15106 | 0.050354 | 0.32959 | 0.22888 | 0.41199 | 0.27008 | 0.3891 | 123.1842 | 0.73242 | 123.2025 | 0.5722 | 123.024 | -123.1201 | -123.1384 | 0.10986 | 123.0057 | 0.18311 | 5.8411
1096.4844 | 122.9828 | -6.2531 | 116.7664 | 0.064392 | 0.0050479 | -0.0045801 | 0.0025933 | -0.0019377 | 0.0017794 | -0.00031193 | -0.038483 | 0.0028861 | 0.082444 | 0.069259 | -0.0034522 | -0.003371 | -0.0026809 | -5.9921 | -5.5481 | -6.3583 | -6.1752 | -5.7632 | -5.9189 | -6.1615 | -0.35248 | 116.9128 | -6.308 | 116.7023 | -6.134 | -6.2759 | -6.1249 | -0.10528 | -122.3145 | -122.9416 | 0.48981 | 0.091553 | 0.33417 | 0.19684 | 0.43945 | -0.054931 | 0.14648 | -0.064086 | 0.11902 | 0.12817 | -0.022888 | 0.18311 | 0.032043 | 0.59509 | 0.1831 | 0.17395 | 123.0103 | 0.81024 | 123.2208 | 0.70496 | 123.1659 | -123.1247 | -123.0743 | 0.07782 | 122.9553 | 0.26093 | 5.9006
1097.4844 | 123.0377 | -6.2439 | 116.7343 | -0.0042723 | 0.0037661 | -0.0043665 | -0.00039728 | 0.0021213 | 0.0015658 | -0.0015935 | -0.056793 | 0.00053628 | 0.081803 | 0.063491 | -0.0015296 | -0.00038018 | -0.00075834 | -6.0654 | -5.6854 | -6.4728 | -6.1935 | -6.0425 | -6.1844 | -6.1111 | -0.2655 | 116.8213 | -6.4178 | 116.7343 | -6.0928 | -6.2393 | -6.0974 | -0.22888 | -122.4197 | -122.9279 | 0.20142 | 0.13275 | 0.059509 | 0.36163 | 0.28839 | -0.17395 | 0.086975 | 0 | 0.15106 | 0.14648 | 0.004577 | 0.32043 | 0.17853 | 0.4303 | 0.27924 | 0.32501 | 123.1522 | 0.78735 | 123.2391 | 0.55847 | 123.0652 | -123.2071 | -123.1522 | 0.050354 | 122.9782 | 0.17853 | 5.9784
1098.5469 | 122.9691 | -6.5277 | 116.4825 | 0.026245 | 0.0031253 | -0.0028711 | 0.0017389 | 0.00041234 | 0.0013522 | 0.00011527 | 0.0011902 | 0.0016043 | 0.082444 | 0.064132 | -0.0021704 | 0.0015424 | 0.00095066 | -6.3309 | -5.9235 | -6.72 | -6.4362 | -6.2759 | -6.3766 | -6.3217 | -0.35248 | 116.5878 | -6.665 | 116.4185 | -6.3995 | -6.546 | -6.4499 | -0.19226 | -122.406 | -122.9187 | 0.25177 | 0.20599 | 0.15106 | 0.39825 | 0.34332 | -0.13733 | 0.10529 | -0.064087 | 0.12817 | 0.07782 | -0.018311 | 0.21515 | 0.11902 | 0.44403 | 0.28381 | 0.2655 | 123.0835 | 0.79651 | 123.2529 | 0.60425 | 123.1155 | -123.2025 | -123.1476 | 0.091553 | 122.9462 | 0.19684 | 6.1752
1099.4844 | 122.9782 | -6.9031 | 116.1118 | -0.019531 | 0.0037661 | -0.0045801 | 0.0049433 | 0.00019874 | 0.0030612 | -0.0018073 | -0.078156 | 0.0018179 | 0.082016 | 0.060927 | -0.001316 | -0.0018756 | -0.0052445 | -6.4133 | -5.9692 | -6.7978 | -6.6193 | -6.5964 | -6.8115 | -6.7429 | -0.59967 | 116.2582 | -7.0175 | 116.0751 | -6.8207 | -7.0084 | -6.8527 | 0.10529 | -122.081 | -122.731 | 0.3067 | 0.16022 | 0.091553 | 0.054932 | -0.013732 | -0.11444 | 0.14648 | -0.036621 | 0.082397 | 0.050354 | -0.10529 | 0.16479 | 0.009155 | 0.20142 | 0.17853 | 0.19684 | 123.0927 | 0.82855 | 123.2758 | 0.93384 | 123.1613 | -122.9095 | -123.1293 | 0.28381 | 122.9782 | 0.48981 | 6.3034
1100.4844 | 122.9782 | -6.4087 | 116.6107 | 0.010986 | 0.0031253 | -0.0039393 | 0.0017389 | 0.00019874 | 0.0019932 | -0.0030889 | -0.0018616 | 0.00032248 | 0.081803 | 0.068618 | -0.001316 | -0.0025164 | -0.0026809 | -6.1066 | -5.6442 | -6.4728 | -6.3309 | -6.1935 | -6.2805 | -6.1981 | -0.40741 | 116.748 | -6.5323 | 116.5787 | -6.2805 | -6.3538 | -6.2393 | -0.064087 | -122.2549 | -122.9416 | 0.21515 | 0.21057 | 0.12817 | 0.27466 | 0.19226 | -0.1236 | 0.13733 | -0.032044 | 0.12817 | 0.16937 | 0.054931 | 0.29297 | 0.17853 | 0.27924 | 0.14191 | 0.25177 | 123.111 | 0.82855 | 123.2803 | 0.76447 | 123.1567 | -123.0835 | -123.143 | 0.077819 | 122.9874 | 0.30212 | 6.0013
1101.5469 | 123.1018 | -6.6971 | 116.2491 | -0.080566 | 0.0046207 | -0.0045801 | -0.00039728 | 0.0046847 | 7.0582e-05 | -0.0026617 | 0.065277 | 0.00074988 | 0.081589 | 0.060927 | -0.0011022 | -0.0014484 | -0.00097194 | -6.5186 | -6.1203 | -6.9031 | -6.6193 | -6.459 | -6.5781 | -6.4728 | -0.33417 | 116.3315 | -6.8665 | 116.3177 | -6.4865 | -6.633 | -6.5186 | -0.20599 | -122.3694 | -122.8683 | 0.23804 | 0.22431 | 0.11902 | 0.4303 | 0.32501 | -0.16937 | 0.082398 | 0.068665 | 0.21057 | 0.17853 | 0.064087 | 0.3479 | 0.23346 | 0.44403 | 0.28381 | 0.37994 | 123.1842 | 0.78278 | 123.1979 | 0.57678 | 123.0286 | -123.1522 | -123.1155 | 0.07782 | 123.0148 | 0.17853 | 6.3629
1102.4844 | 123.024 | -6.6833 | 116.3086 | -0.0042723 | 0.0041935 | -0.0054347 | 0.0017389 | -0.0027921 | 0.0017794 | -0.00073913 | -0.01712 | 0.00053628 | 0.081589 | 0.065414 | -0.0025976 | -0.00080758 | -0.00033114 | -6.4819 | -6.015 | -6.8985 | -6.6467 | -6.5186 | -6.601 | -6.5323 | -0.40283 | 116.4368 | -6.8344 | 116.2903 | -6.5598 | -6.6925 | -6.5598 | -0.21515 | -122.3236 | -122.9553 | 0.16479 | 0.15106 | 0.082398 | 0.36621 | 0.29755 | -0.15106 | 0.12817 | -0.018311 | 0.1236 | 0.1236 | -0.009155 | 0.27466 | 0.14191 | 0.37994 | 0.25177 | 0.27466 | 123.1247 | 0.88348 | 123.2712 | 0.66833 | 123.1201 | -123.2071 | -123.143 | 0.036621 | 122.9736 | 0.20142 | 6.2805
1103.4844 | 122.9645 | -6.8115 | 116.2079 | -0.011902 | 0.0026981 | -0.0030847 | 0.0032343 | -0.0010831 | 0.0019932 | 0.0011835 | -0.062897 | 0.0020315 | 0.08223 | 0.064559 | -0.005802 | -0.00038018 | -0.00033114 | -6.6101 | -6.1981 | -7.0038 | -6.7795 | -6.6742 | -6.7841 | -6.7062 | -0.48981 | 116.3132 | -6.9626 | 116.1438 | -6.7062 | -6.8665 | -6.6925 | -0.19226 | -122.406 | -122.9874 | 0.13733 | 0.10529 | 0.027465 | 0.29755 | 0.21973 | -0.15106 | 0.10528 | -0.064087 | 0.10529 | 0.11902 | -0.054932 | 0.27008 | 0.09613 | 0.32959 | 0.2243 | 0.25635 | 123.1064 | 0.80566 | 123.2758 | 0.6134 | 123.1247 | -123.2117 | -123.1705 | 0.032043 | 122.9553 | 0.20142 | 6.3217
1104.5469 | 123.1155 | -6.9717 | 115.9698 | -0.050049 | 0.0046207 | -0.0039393 | -0.00039728 | -1.486e-05 | 0.0030612 | -0.0024481 | 0.046967 | 0.0026725 | 0.081375 | 0.069686 | -0.0047338 | -0.0023028 | -0.0022537 | -6.6742 | -6.3217 | -7.077 | -6.8207 | -6.6696 | -6.7932 | -6.7017 | -0.29755 | 116.0706 | -7.1136 | 116.0614 | -6.7474 | -6.8939 | -6.7978 | -0.10529 | -122.2916 | -122.7905 | 0.30212 | 0.27008 | 0.17853 | 0.37537 | 0.28381 | -0.14191 | 0.10071 | 0.091552 | 0.2243 | 0.17395 | 0.07782 | 0.31586 | 0.21973 | 0.40741 | 0.25635 | 0.36621 | 123.175 | 0.75531 | 123.1842 | 0.65002 | 123.0423 | -123.0469 | -123.0835 | 0.15106 | 123.0331 | 0.29755 | 6.6742
1105.4844 | 122.9691 | -6.8436 | 116.1987 | -0.088196 | 0.0031253 | -0.00052126 | 0.0017389 | 0.0023349 | 0.00028418 | -0.00095273 | -0.075104 | 0.0028861 | 0.082444 | 0.068831 | -0.0025976 | -0.00080758 | 0.00095066 | -6.7245 | -6.2073 | -7.0724 | -6.839 | -6.72 | -6.8573 | -6.752 | -0.40741 | 116.3086 | -7.0038 | 116.1072 | -6.7703 | -6.8939 | -6.7291 | -0.22888 | -122.406 | -123.0377 | 0.1236 | 0.091553 | -0.013733 | 0.32043 | 0.21515 | -0.16022 | 0.10986 | -0.091552 | 0.073242 | 0.11444 | -0.050354 | 0.27466 | 0.10986 | 0.35248 | 0.23346 | 0.23346 | 123.111 | 0.86517 | 123.3124 | 0.63629 | 123.1522 | -123.2712 | -123.2025 | 0.004578 | 122.9507 | 0.11902 | 6.4362
1106.5469 | 122.9782 | -7.0679 | 115.9653 | -0.019531 | 0.0044071 | -0.0013757 | 0.00088432 | 0.0025485 | 0.0051974 | -0.0024481 | -0.014069 | 0.0013907 | 0.081375 | 0.064773 | -0.001316 | -0.0020892 | -0.00075834 | -6.7795 | -6.3583 | -7.2784 | -6.871 | -6.7337 | -6.926 | -6.8024 | -0.068665 | 116.1346 | -7.1915 | 115.8875 | -6.9305 | -7.1136 | -6.9809 | -0.21057 | -122.3236 | -122.8363 | 0.33417 | 0.2655 | 0.14191 | 0.47607 | 0.35248 | -0.1236 | 0.16937 | -0.07782 | 0.13733 | 0.086975 | -0.045776 | 0.21057 | 0.07782 | 0.54474 | 0.40741 | 0.26093 | 123.0789 | 0.92011 | 123.3261 | 0.70953 | 123.2025 | -123.2437 | -123.1567 | 0.19684 | 122.9553 | 0.28839 | 6.9992
1107.4844 | 123.0652 | -6.9122 | 116.1438 | -0.057678 | 0.0048343 | -0.0024439 | 0.0032343 | -0.00065586 | 0.00028418 | 0.0020379 | -0.075104 | 0.0018179 | 0.083084 | 0.064773 | -0.001316 | -0.00080758 | 0.0011643 | -6.6879 | -6.3034 | -7.0999 | -6.8207 | -6.6605 | -6.7795 | -6.7383 | -0.23804 | 116.2537 | -7.0221 | 116.1346 | -6.7566 | -6.9305 | -6.7474 | -0.18768 | -122.4472 | -122.9645 | 0.25177 | 0.17395 | 0.13275 | 0.36163 | 0.32043 | -0.10986 | 0.10986 | -0.009155 | 0.15564 | 0.16479 | -0.018311 | 0.27466 | 0.091553 | 0.43945 | 0.27924 | 0.2655 | 123.1567 | 0.79651 | 123.2758 | 0.60883 | 123.1659 | -123.2437 | -123.1659 | 0.091552 | 123.0469 | 0.2243 | 6.6742
1108.4844 | 123.024 | -7.132 | 115.9149 | -0.011902 | 0.0029117 | -0.0045801 | 0.0013117 | -0.00065586 | 0.002634 | -0.00031193 | -0.026276 | 0.0026725 | 0.082016 | 0.062209 | -0.0034522 | -0.00016658 | -0.00097194 | -7.0175 | -6.5094 | -7.4158 | -7.1136 | -6.9305 | -7.0999 | -7.0633 | -0.4303 | 115.8966 | -7.3608 | 115.8371 | -7.077 | -7.1091 | -6.9168 | -0.28381 | -122.4243 | -123.0286 | 0.20142 | 0.068665 | 0.032043 | 0.35248 | 0.31586 | -0.22888 | -0.018311 | -0.07782 | 0.054932 | 0.21515 | 0.022888 | 0.44403 | 0.25177 | 0.48523 | 0.30212 | 0.28381 | 123.1979 | 0.90637 | 123.2574 | 0.62256 | 123.0286 | -123.3307 | -123.2758 | 0.018311 | 122.9691 | 0.11444 | 6.7017
1109.4844 | 123.0194 | -6.4774 | 116.5604 | -0.057678 | 0.0035525 | -0.0032983 | 0.0013117 | 0.0048983 | 0.0015658 | 0.00011527 | -0.075104 | 0.00074988 | 0.083725 | 0.066268 | -0.0015296 | -0.00080758 | 0.0024461 | -6.2714 | -5.8502 | -6.6513 | -6.4224 | -6.2897 | -6.4407 | -6.34 | -0.23346 | 116.6473 | -6.6101 | 116.5237 | -6.3583 | -6.5002 | -6.3446 | -0.17395 | -122.4106 | -122.9828 | 0.18768 | 0.13733 | 0.036621 | 0.31128 | 0.21057 | -0.13275 | 0.086975 | -0.036621 | 0.11902 | 0.13275 | -0.022888 | 0.2655 | 0.10986 | 0.36163 | 0.22888 | 0.25177 | 123.1338 | 0.80109 | 123.2574 | 0.62714 | 123.1247 | -123.2117 | -123.1705 | 0.054932 | 123.0011 | 0.20599 | 6.2439
1110.4844 | 123.0606 | -7.0038 | 115.9836 | 0.010986 | 0.0048343 | -0.0030847 | 0.00088432 | 0.0036165 | 0.0028476 | -0.00073913 | -0.038483 | 0.0018179 | 0.080948 | 0.061782 | -0.0043066 | -0.00059378 | -0.0024673 | -6.7337 | -6.2805 | -7.1686 | -6.8527 | -6.6879 | -6.871 | -6.7841 | 0.004578 | 116.1713 | -7.1091 | 116.0156 | -6.8207 | -6.9855 | -6.8619 | -0.1648 | -122.2641 | -122.8363 | 0.31586 | 0.21973 | 0.13275 | 0.38452 | 0.29755 | -0.10529 | 0.18768 | 0.032043 | 0.1831 | 0.14191 | 0.01831 | 0.24719 | 0.1236 | 0.48065 | 0.31586 | 0.28839 | 123.1247 | 0.88806 | 123.2803 | 0.72327 | 123.175 | -123.1522 | -123.0927 | 0.15106 | 123.0194 | 0.27008 | 7.0084
1111.5469 | 123.0789 | -6.9763 | 116.0522 | -0.0042723 | 0.0037661 | -0.0050073 | -0.00039728 | -0.0012967 | 0.0028476 | -0.0018073 | 0.028656 | 0.00074988 | 0.081803 | 0.068404 | -0.0008886 | -0.0040118 | 0.0035141 | -6.6742 | -6.3034 | -7.1228 | -6.7795 | -6.6147 | -6.7062 | -6.6284 | -0.018311 | 116.1392 | -7.0816 | 116.0431 | -6.7703 | -6.8939 | -6.7841 | -0.14649 | -122.3557 | -122.8317 | 0.36163 | 0.3479 | 0.27008 | 0.49439 | 0.41657 | -0.10529 | 0.086975 | -0.009155 | 0.20599 | 0.19226 | 0.082397 | 0.29755 | 0.18768 | 0.50812 | 0.34332 | 0.31128 | 123.1247 | 0.8194 | 123.2208 | 0.67291 | 123.1155 | -123.175 | -123.1338 | 0.19684 | 123.0194 | 0.30212 | 6.958
1112.4844 | 123.0652 | -7.2739 | 115.7181 | -0.011902 | 0.0026981 | -0.0039393 | 0.0043023 | 0.0019077 | 0.0024204 | -0.0018073 | -0.059845 | 0.0041679 | 0.080521 | 0.066054 | -0.0034522 | 0.00026062 | 0.00030966 | -7.0084 | -6.5735 | -7.5027 | -7.1503 | -7.0221 | -7.1548 | -7.0908 | -0.15106 | 115.8188 | -7.4295 | 115.7547 | -7.132 | -7.3059 | -7.1686 | -0.22888 | -122.2916 | -122.8683 | 0.25177 | 0.18311 | 0.11902 | 0.41199 | 0.3479 | -0.15564 | 0.10071 | 0.036621 | 0.14191 | 0.10529 | -0.032043 | 0.26092 | 0.1236 | 0.48065 | 0.35248 | 0.29755 | 123.1842 | 0.92926 | 123.2483 | 0.70038 | 123.0927 | -123.2208 | -123.1476 | 0.1236 | 123.0286 | 0.2655 | 7.1228
1113.4844 | 122.9507 | -6.7795 | 116.2582 | -0.042419 | 0.0035525 | -0.0037257 | 0.0030207 | -0.0010831 | -0.00035682 | -0.0013799 | -0.047638 | -0.00010472 | 0.081162 | 0.068404 | -0.0034522 | -0.0012348 | 0.0028733 | -6.546 | -6.102 | -6.9809 | -6.7017 | -6.5918 | -6.7245 | -6.6513 | -0.24261 | 116.3544 | -6.9351 | 116.1804 | -6.6971 | -6.839 | -6.6742 | -0.20142 | -122.3602 | -122.9599 | 0.18768 | 0.12817 | 0.054932 | 0.32959 | 0.25635 | -0.15564 | 0.09613 | -0.07782 | 0.082397 | 0.10529 | -0.059509 | 0.26093 | 0.096131 | 0.3891 | 0.27924 | 0.23804 | 123.1155 | 0.87891 | 123.2895 | 0.67749 | 123.1339 | -123.2391 | -123.1934 | 0.07782 | 122.9599 | 0.23346 | 6.5369
1114.5469 | 123.0469 | -7.3196 | 115.7318 | 0.056763 | 0.0035525 | -0.0037257 | 0.0021661 | -0.00044226 | 0.0051974 | -0.00031193 | -0.0079652 | 0.00053628 | 0.08223 | 0.065841 | -0.0015296 | -0.0010212 | 0.0022323 | -7.0862 | -6.5414 | -7.5119 | -7.2418 | -7.1136 | -7.1823 | -7.1228 | -0.18768 | 115.8234 | -7.4661 | 115.686 | -7.1869 | -7.3288 | -7.2006 | -0.19226 | -122.2733 | -122.9736 | 0.20599 | 0.19684 | 0.13733 | 0.3891 | 0.32959 | -0.14648 | 0.091552 | -0.045777 | 0.13275 | 0.11902 | -0.009155 | 0.2655 | 0.13733 | 0.39825 | 0.27008 | 0.27923 | 123.1522 | 0.97046 | 123.2895 | 0.7782 | 123.143 | -123.2437 | -123.1979 | 0.07782 | 123.0057 | 0.23346 | 7.132
1115.4844 | 122.9965 | -7.4249 | 115.5899 | 0.018616 | 0.0046207 | -0.0032983 | 0.0036615 | 0.0019077 | 0.005411 | -0.0015935 | -0.047638 | 0.0033133 | 0.080735 | 0.065627 | -0.002384 | -0.00038018 | 0.0011643 | -7.1548 | -6.6376 | -7.608 | -7.3151 | -7.1915 | -7.3471 | -7.2372 | -0.25635 | 115.7501 | -7.5531 | 115.5441 | -7.3654 | -7.5348 | -7.3654 | -0.1831 | -122.2275 | -122.905 | 0.23346 | 0.18768 | 0.07782 | 0.37079 | 0.26092 | -0.12817 | 0.16022 | -0.045777 | 0.05951 | 0.05951 | -0.10986 | 0.18768 | 0.018311 | 0.41656 | 0.29297 | 0.18768 | 123.0972 | 0.97046 | 123.3032 | 0.78735 | 123.175 | -123.1979 | -123.143 | 0.10986 | 122.9691 | 0.27008 | 7.1686
1116.5469 | 123.0881 | -6.2393 | 116.7389 | -0.072937 | 0.0052615 | -0.0020167 | -0.0010383 | -0.00086946 | 0.002634 | -0.0028753 | 0.077484 | 0.00010888 | 0.082016 | 0.064773 | -0.0025976 | -0.0035846 | 0.0015915 | -6.0059 | -5.6351 | -6.4865 | -6.0974 | -5.9143 | -6.0608 | -6.0059 | 0.14648 | 116.7847 | -6.4224 | 116.7892 | -6.0425 | -6.1707 | -6.0699 | -0.24719 | -122.374 | -122.8363 | 0.32501 | 0.23346 | 0.17853 | 0.48065 | 0.42572 | -0.18311 | 0.045776 | 0.050354 | 0.19684 | 0.16937 | 0.068665 | 0.35248 | 0.25177 | 0.5722 | 0.3891 | 0.37994 | 123.2117 | 0.85144 | 123.2071 | 0.60425 | 123.024 | -123.2254 | -123.1613 | 0.14191 | 123.0286 | 0.23346 | 6.3858
1117.4844 | 123.0789 | -6.4178 | 116.5649 | -0.065308 | 0.0054751 | -0.0030847 | 0.0038751 | -0.00044226 | 0.0022068 | -0.00095273 | -0.059845 | 0.0020315 | 0.082657 | 0.068191 | -0.0025976 | -0.00059378 | -0.0011855 | -6.2164 | -5.7587 | -6.5826 | -6.3583 | -6.2119 | -6.3446 | -6.2393 | 0.054932 | 116.7023 | -6.5689 | 116.5924 | -6.3263 | -6.4636 | -6.2988 | -0.16479 | -122.3236 | -122.9233 | 0.20599 | 0.17853 | 0.073243 | 0.34332 | 0.23804 | -0.15106 | 0.13733 | 0.027466 | 0.091553 | 0.11902 | -0.045776 | 0.27008 | 0.10529 | 0.37079 | 0.22431 | 0.24261 | 123.1613 | 0.82397 | 123.2712 | 0.65918 | 123.1201 | -123.1476 | -123.1339 | 0.05951 | 123.0103 | 0.20142 | 6.4728
1118.5469 | 123.024 | -6.3675 | 116.6931 | 0.0033567 | 0.0029117 | -0.0032983 | -0.0010383 | -0.0040739 | 0.00092498 | 0.00054267 | 0.028656 | 0.0022453 | 0.081375 | 0.064559 | -0.0019568 | -0.0014484 | -0.0018265 | -6.0562 | -5.6946 | -6.5002 | -6.102 | -5.9418 | -6.0471 | -5.9921 | 0.10529 | 116.8304 | -6.4453 | 116.6565 | -6.2073 | -6.3538 | -6.2347 | -0.13275 | -122.3877 | -122.7951 | 0.42572 | 0.37537 | 0.32043 | 0.50812 | 0.45319 | -0.077819 | 0.13733 | -0.036621 | 0.16022 | 0.13275 | 0.013733 | 0.21057 | 0.091552 | 0.55847 | 0.39825 | 0.23804 | 123.1018 | 0.80566 | 123.2758 | 0.67291 | 123.1979 | -123.1934 | -123.1384 | 0.2655 | 123.024 | 0.31128 | 6.4728
1119.4844 | 122.9874 | -6.4224 | 116.6748 | 0.010986 | 0.0044071 | -0.0013757 | 0.0023797 | 0.0010531 | 0.0013522 | 0.0022517 | -0.041534 | 0.0037405 | 0.083725 | 0.066909 | -0.0034522 | 0.00047422 | 0.0028733 | -6.0928 | -5.6305 | -6.5781 | -6.221 | -6.0837 | -6.4362 | -6.1111 | -0.11902 | 116.7435 | -6.5643 | 116.5741 | -6.34 | -6.6238 | -6.4041 | -0.15564 | -122.3053 | -122.8958 | 0.33875 | 0.31128 | -0.013733 | 0.46692 | 0.14191 | -0.14191 | 0.068664 | -0.10071 | 0.082397 | 0.01831 | -0.20142 | 0.16022 | -0.059509 | 0.49439 | 0.35706 | 0.2243 | 123.1384 | 0.94757 | 123.3078 | 0.79193 | 123.1659 | -123.2529 | -123.2391 | 0.20142 | 122.9965 | 0.32959 | 6.3034
1120.4844 | 123.056 | -6.6055 | 116.4322 | 0.010986 | 0.0033389 | -0.0018031 | 0.0034479 | 0.0010531 | 0.00028418 | 0.0026789 | -0.029327 | 0.0016043 | 0.080735 | 0.061141 | -0.0019568 | 0.001115 | 0.0026597 | -5.4337 | -5.0766 | -6.7932 | -5.5756 | -5.4062 | -6.7017 | -5.4886 | 0.004578 | 116.5329 | -6.7429 | 116.4322 | -6.4362 | -6.601 | -6.4545 | -0.18768 | -121.5088 | -122.0078 | 1.1993 | 1.1169 | -0.09613 | 1.3046 | 0.091553 | -0.13733 | 0.10071 | 0 | 0.16937 | 0.15106 | 0.004578 | 0.28839 | 0.14191 | 1.387 | 1.2177 | 0.3067 | 123.175 | 1.7166 | 123.2758 | 1.5289 | 123.1384 | -123.2254 | -123.175 | 1.03 | 123.0377 | 1.1719 | 6.6101
1121.4844 | 123.0057 | -6.4819 | 116.5695 | 0.010986 | 0.0039799 | -0.0013757 | 0.0010981 | 0.0023349 | 0.0013522 | -0.00095273 | -0.035431 | 0.0033133 | 0.081803 | 0.06755 | -0.002384 | 0.00026062 | -0.00075834 | -5.1819 | -4.7836 | -6.6101 | -5.3513 | -5.2002 | -6.5964 | -5.2689 | -0.13275 | 116.6977 | -6.601 | 116.5192 | -6.3721 | -6.514 | -6.3538 | -0.12817 | -121.3531 | -121.9208 | 1.2817 | 1.2131 | -0.11444 | 1.3412 | 0.013732 | -0.11902 | 0.12817 | -0.050354 | 0.10986 | 0.12817 | -0.032043 | 0.24719 | 0.086975 | 1.4099 | 1.2588 | 0.22888 | 123.1201 | 1.8265 | 123.2986 | 1.6983 | 123.1796 | -123.1796 | -123.1705 | 1.1307 | 123.0011 | 1.3 | 6.3492
1122.5469 | 123.0331 | -6.6833 | 116.3818 | -0.03479 | 0.0035525 | -0.0039393 | 0.00088432 | -0.0012967 | -0.00014322 | -0.0024481 | 0.0011902 | 0.0013907 | 0.081589 | 0.066482 | -0.0019568 | -0.001662 | -0.00033114 | -5.4611 | -5.0537 | -6.8344 | -5.6488 | -5.4794 | -6.752 | -5.4886 | -0.10071 | 116.5054 | -6.7932 | 116.2811 | -6.5781 | -6.72 | -6.601 | -0.15106 | -121.4355 | -122.0306 | 1.2039 | 1.1948 | -0.068664 | 1.3458 | 0.082398 | -0.10986 | 0.1236 | -0.10071 | 0.10529 | 0.082398 | -0.036621 | 0.19226 | 0.073242 | 1.355 | 1.1856 | 0.21515 | 123.0743 | 1.7807 | 123.2986 | 1.6296 | 123.1888 | -123.2162 | -123.175 | 1.0345 | 122.9645 | 1.2222 | 6.5826
1123.4844 | 123.0606 | -6.7108 | 116.3773 | -0.027161 | 0.0022709 | -0.00094846 | 0.0034479 | 0.0044711 | 7.0582e-05 | -0.0013799 | -0.038483 | 0.0020315 | 0.081589 | 0.063064 | -0.0034522 | -0.0014484 | 0.00052346 | -5.0903 | -4.6967 | -6.6925 | -5.2368 | -5.1315 | -6.7245 | -5.2505 | -0.2655 | 116.5192 | -6.7795 | 116.304 | -6.601 | -6.7612 | -6.5872 | 0.01831 | -121.0739 | -121.6141 | 1.5793 | 1.4603 | -0.013733 | 1.442 | -0.032043 | -0.068665 | 0.14191 | -0.073242 | 0.10986 | 0.1236 | -0.050354 | 0.19226 | 0.018311 | 1.561 | 1.4557 | 0.17853 | 123.0835 | 1.9958 | 123.2986 | 2.0142 | 123.23 | -123.0698 | -123.1567 | 1.474 | 123.0148 | 1.6205 | 6.4453
1124.4844 | 123.0377 | -6.1203 | 116.9403 | -0.011902 | 0.0029117 | -0.00030766 | 0.0034479 | -0.0012967 | -0.00014322 | -0.00031193 | -0.038483 | 0.0016043 | 0.080948 | 0.075454 | -0.0019568 | 0.00026062 | -0.00054474 | -4.6143 | -4.2252 | -6.3126 | -4.7424 | -4.6326 | -6.2851 | -4.6692 | -0.11444 | 117.0639 | -6.2759 | 116.8716 | -6.015 | -6.1661 | -5.9967 | -0.19226 | -121.1655 | -121.6827 | 1.4877 | 1.4511 | -0.16479 | 1.6434 | 0.027466 | -0.15564 | 0.1236 | -0.068665 | 0.10529 | 0.1236 | -0.045777 | 0.27924 | 0.10986 | 1.68 | 1.5701 | 0.26093 | 123.1476 | 2.0874 | 123.3398 | 1.8951 | 123.1842 | -123.2529 | -123.2162 | 1.3779 | 122.9919 | 1.506 | 6.0059
1125.5469 | 123.0652 | -6.4041 | 116.6153 | -0.057678 | 0.0022709 | -0.0011621 | 0.0021661 | 0.00019874 | 0.0022068 | 0.0024653 | -0.014069 | 0.0016043 | 0.082016 | 0.065841 | -0.003025 | -0.00016658 | -0.00097194 | -4.8981 | -4.5456 | -6.5689 | -4.985 | -4.834 | -6.4911 | -4.9255 | 0.14191 | 116.7755 | -6.5277 | 116.6519 | -6.2897 | -6.459 | -6.3217 | -0.16479 | -121.1609 | -121.6003 | 1.5701 | 1.4786 | -0.086975 | 1.6434 | 0.07782 | -0.1236 | 0.16022 | 0.036622 | 0.11444 | 0.082398 | -0.054931 | 0.20599 | 0.068665 | 1.7349 | 1.5839 | 0.23804 | 123.1796 | 2.0233 | 123.3032 | 1.8585 | 123.1796 | -123.1842 | -123.143 | 1.4191 | 123.056 | 1.506 | 6.546
1126.4844 | 123.0377 | -6.3034 | 116.7618 | -0.03479 | 0.0056889 | -0.0024439 | 0.0010981 | 0.0012667 | -0.00099762 | 0.0013971 | -0.044586 | 0.0035269 | 0.079239 | 0.071609 | -0.0021704 | -0.00016658 | -0.0020401 | -4.7699 | -4.39 | -6.3995 | -4.9622 | -4.8111 | -6.4087 | -4.8889 | 0.5127 | 116.8533 | -6.4682 | 116.7297 | -6.189 | -6.34 | -6.2073 | -0.09613 | -121.1517 | -121.7239 | 1.4923 | 1.4145 | -0.10529 | 1.5106 | -0.009155 | -0.16479 | 0.091553 | -0.032044 | 0.11444 | 0.096131 | -0.036621 | 0.26093 | 0.12817 | 1.5884 | 1.4374 | 0.27924 | 123.1979 | 2.0096 | 123.3215 | 1.9135 | 123.1567 | -123.1613 | -123.23 | 1.3412 | 123.0331 | 1.5335 | 6.8161
1127.5469 | 123.056 | -6.0608 | 116.9632 | -0.065308 | 0.0037661 | -0.0015893 | 0.00088432 | -0.0034329 | 0.0024204 | -0.0013799 | -0.056793 | -0.00031832 | 0.079026 | 0.068618 | -0.0017432 | -0.0018756 | 0.0013779 | -4.66 | -4.3121 | -6.2576 | -4.7607 | -4.5776 | -6.134 | -4.6921 | 0.75073 | 117.1646 | -6.1752 | 116.9495 | -5.9418 | -6.134 | -5.9647 | -0.19684 | -121.2753 | -121.7239 | 1.4832 | 1.3687 | -0.073242 | 1.5656 | 0.1236 | -0.11444 | 0.20142 | -0.013733 | 0.11902 | 0.09613 | -0.073242 | 0.21057 | 0.041199 | 1.68 | 1.4969 | 0.23346 | 123.1247 | 1.9455 | 123.3398 | 1.7487 | 123.2254 | -123.2208 | -123.1384 | 1.3 | 123.0103 | 1.4008 | 6.8115
1128.4844 | 123.0652 | -5.8228 | 117.2333 | 0.026245 | 0.0037661 | -0.0032983 | 0.0021661 | 0.0010531 | 0.0037022 | -0.0011663 | -0.038483 | 0.0037405 | 0.082657 | 0.070113 | -0.0011022 | -0.00080758 | -0.0031081 | -5.5618 | -5.1956 | -6.0059 | -5.69 | -5.5069 | -5.6351 | -5.5984 | 0.70038 | 117.3431 | -5.9601 | 117.2058 | -5.658 | -5.809 | -5.658 | -0.18311 | -122.4289 | -122.9233 | 0.31586 | 0.2243 | 0.18768 | 0.40741 | 0.37079 | -0.13733 | 0.10986 | -0.027465 | 0.16479 | 0.16479 | 0.013733 | 0.30212 | 0.15106 | 0.49896 | 0.31586 | 0.30212 | 123.1659 | 0.81024 | 123.3032 | 0.62714 | 123.1659 | -123.2391 | -123.1934 | 0.13275 | 123.0286 | 0.26092 | 6.5231
1129.4844 | 123.1064 | -6.3721 | 116.7068 | -0.0042723 | 0.0041935 | -0.0039393 | 0.0032343 | 0.0057529 | 0.0037022 | -0.00095273 | -0.032379 | 0.0020315 | 0.078812 | 0.067336 | -0.0021704 | -0.0014484 | 0.0020187 | -5.9784 | -5.603 | -6.4865 | -6.1661 | -6.0654 | -6.1798 | -6.0699 | 0.43488 | 116.835 | -6.5094 | 116.6885 | -6.2714 | -6.427 | -6.2622 | -0.11444 | -122.3099 | -122.8729 | 0.3067 | 0.30212 | 0.19226 | 0.41657 | 0.3067 | -0.13733 | 0.12817 | -0.01831 | 0.10071 | 0.10986 | -0.054932 | 0.24719 | 0.082397 | 0.42114 | 0.32043 | 0.23804 | 123.1979 | 0.88348 | 123.3444 | 0.76904 | 123.2071 | -123.1934 | -123.2162 | 0.20599 | 123.0606 | 0.39368 | 6.8069
1130.4844 | 123.0927 | -5.9967 | 117.0868 | -0.027161 | 0.0033389 | -0.0054347 | 0.00088432 | 0.00041234 | -0.001852 | -0.00052553 | -0.023224 | 0.0030997 | 0.080307 | 0.067977 | -0.004093 | -0.00059378 | -0.0022537 | -5.6488 | -5.2322 | -6.1752 | -5.7358 | -5.6259 | -5.7404 | -5.6808 | 0.49896 | 117.1875 | -6.1478 | 117.0456 | -5.8502 | -6.0059 | -5.8548 | -0.17853 | -122.319 | -122.8226 | 0.37079 | 0.31586 | 0.25635 | 0.49439 | 0.43488 | -0.15106 | 0.10071 | -0.041199 | 0.14648 | 0.14191 | -0.009155 | 0.29297 | 0.14191 | 0.54932 | 0.43945 | 0.29755 | 123.1934 | 0.94299 | 123.3353 | 0.76447 | 123.1842 | -123.262 | -123.2346 | 0.26093 | 123.0423 | 0.3479 | 6.4957
1131.4844 | 123.0423 | -6.4499 | 116.6382 | -0.057678 | 0.0048343 | -0.0041529 | 0.0028069 | 0.0014803 | 0.0032748 | -0.0018073 | -0.044586 | 0.0013907 | 0.08223 | 0.065841 | -3.4196e-05 | -0.00038018 | -0.0043899 | -6.1111 | -5.7312 | -6.6376 | -6.3171 | -6.2027 | -6.3171 | -6.2439 | -0.31128 | 116.7526 | -6.5689 | 116.5924 | -6.3217 | -6.4728 | -6.2942 | -0.18768 | -122.3694 | -122.9553 | 0.24719 | 0.20599 | 0.13275 | 0.39368 | 0.32043 | -0.11902 | 0.11444 | -0.045777 | 0.12817 | 0.15564 | -0.022888 | 0.27466 | 0.096131 | 0.43487 | 0.32043 | 0.24719 | 123.1613 | 0.90637 | 123.3215 | 0.71869 | 123.2025 | -123.2758 | -123.2071 | 0.13275 | 123.0423 | 0.33875 | 6.1386
1132.5469 | 123.0515 | -6.2622 | 116.8762 | -0.011902 | 0.0012027 | -0.0024439 | 0.00045712 | -0.0015103 | 0.002634 | -0.00095273 | 0.050018 | 0.00010888 | 0.081803 | 0.061996 | -0.0021704 | -0.001662 | -0.00054474 | -6.0104 | -5.6122 | -6.395 | -6.1249 | -5.9509 | -6.134 | -6.0242 | -0.19684 | 116.9769 | -6.3812 | 116.7618 | -6.1111 | -6.2393 | -6.1203 | -0.13275 | -122.4884 | -123.0011 | 0.31128 | 0.23804 | 0.12817 | 0.37079 | 0.26093 | -0.11902 | 0.10071 | -0.11444 | 0.15106 | 0.14191 | 0.022888 | 0.26093 | 0.14191 | 0.44403 | 0.27008 | 0.27008 | 123.143 | 0.78277 | 123.3582 | 0.65002 | 123.2391 | -123.2712 | -123.2574 | 0.13733 | 123.024 | 0.25177 | 6.0654
1133.4844 | 123.0423 | -6.0837 | 116.9678 | 0.010986 | 0.0029117 | -0.0020167 | 0.0023797 | -0.00065586 | 0.0015658 | -0.0011663 | -0.047638 | 0.00010888 | 0.082016 | 0.066482 | -0.000675 | 0.001115 | 0.0020187 | -5.7449 | -5.3101 | -6.2759 | -5.8868 | -5.7632 | -5.9006 | -5.7999 | -0.24261 | 117.128 | -6.221 | 116.9037 | -5.9006 | -6.1935 | -6.0471 | -0.19226 | -122.2778 | -122.8546 | 0.32043 | 0.28381 | 0.18311 | 0.47607 | 0.37537 | -0.13733 | 0.16022 | -0.064086 | 0.18311 | 0.036621 | -0.10986 | 0.17395 | 0.027466 | 0.51269 | 0.3891 | 0.32043 | 123.1247 | 0.96588 | 123.349 | 0.77362 | 123.2117 | -123.2437 | -123.1888 | 0.19684 | 122.9874 | 0.33875 | 5.8411
1134.4844 | 123.0743 | -5.8502 | 117.1875 | -0.011902 | 0.0037661 | -0.0024439 | 0.0023797 | -0.0019377 | 0.00049778 | -9.8328e-05 | -0.029327 | 0.0018179 | 0.080521 | 0.06285 | -0.0028112 | -0.0012348 | -0.0020401 | -5.5573 | -5.2002 | -6.015 | -5.7083 | -5.5298 | -5.6717 | -5.5984 | -0.064087 | 117.3203 | -5.9921 | 117.1967 | -5.7175 | -5.8411 | -5.7083 | -0.16479 | -122.3877 | -122.8958 | 0.32043 | 0.25177 | 0.17853 | 0.41657 | 0.34332 | -0.14191 | 0.13275 | 0.009155 | 0.13275 | 0.14191 | 0.009156 | 0.28381 | 0.15106 | 0.48523 | 0.3067 | 0.27466 | 123.1888 | 0.81482 | 123.3124 | 0.65003 | 123.1705 | -123.2025 | -123.1796 | 0.14191 | 123.0469 | 0.29297 | 5.7861
1135.5469 | 123.0286 | -5.603 | 117.4667 | 0.033875 | 0.0054751 | -0.0045801 | 0.0010981 | -0.0021513 | 0.0015658 | -0.0013799 | 0.031708 | 0.0026725 | 0.081589 | 0.068404 | -0.0011022 | -0.0020892 | -0.0020401 | -5.3146 | -4.9164 | -5.7541 | -5.4428 | -5.2826 | -5.397 | -5.3192 | -0.073242 | 117.572 | -5.7541 | 117.3981 | -5.4703 | -5.6076 | -5.5115 | -0.15106 | -122.3831 | -122.9095 | 0.32043 | 0.28381 | 0.20599 | 0.43487 | 0.35705 | -0.15106 | 0.10529 | -0.068665 | 0.13275 | 0.091552 | -0.004578 | 0.24261 | 0.14648 | 0.4715 | 0.31128 | 0.28381 | 123.1522 | 0.83771 | 123.3261 | 0.68665 | 123.175 | -123.2208 | -123.2208 | 0.16022 | 123.0011 | 0.28839 | 5.5298
1136.4844 | 123.0835 | -5.7175 | 117.3431 | -0.042419 | 0.0039799 | -0.0026575 | 0.0030207 | -0.0010831 | 0.0013522 | 0.00075627 | -0.035431 | 0.00032248 | 0.084793 | 0.066268 | -0.004093 | -0.0020892 | -0.0035355 | -5.246 | -4.8843 | -5.8731 | -5.3925 | -5.2368 | -5.397 | -5.3009 | 0.11902 | 117.5491 | -5.8044 | 117.3523 | -5.5756 | -5.722 | -5.5801 | -0.15564 | -122.2275 | -122.7356 | 0.48065 | 0.41657 | 0.32043 | 0.57221 | 0.47607 | -0.086975 | 0.20599 | 0.009155 | 0.14191 | 0.13733 | -0.004578 | 0.2243 | 0.082397 | 0.63629 | 0.48065 | 0.22888 | 123.1567 | 0.98877 | 123.3536 | 0.83313 | 123.2666 | -123.2162 | -123.1476 | 0.32501 | 123.0698 | 0.4715 | 5.8365
1137.5469 | 123.0835 | -5.9601 | 117.1234 | -0.027161 | 0.0059025 | -0.0032983 | 0.0025933 | 0.0019077 | -0.0016384 | 0.0013971 | -0.020172 | 0.00032248 | 0.080521 | 0.069472 | -0.0034522 | 4.7018e-05 | -0.0011855 | -4.2801 | -3.9368 | -6.1295 | -4.4037 | -4.248 | -6.015 | -4.3121 | -0.013733 | 117.215 | -6.0974 | 117.0868 | -5.809 | -5.9509 | -5.8228 | -0.16937 | -121.0602 | -121.5271 | 1.712 | 1.6479 | -0.054932 | 1.8173 | 0.11444 | -0.13733 | 0.091553 | -0.036621 | 0.15106 | 0.13733 | 0.009155 | 0.27466 | 0.14648 | 1.8814 | 1.7258 | 0.28839 | 123.1842 | 2.1927 | 123.3124 | 2.0233 | 123.175 | -123.2529 | -123.2208 | 1.5564 | 123.0469 | 1.68 | 5.9463
1138.4844 | 123.0789 | -6.0059 | 117.0593 | -0.03479 | 0.0037661 | 0.0011877 | 0.0023797 | -0.00044226 | 0.0017794 | -0.0028753 | -0.035431 | 0.00010888 | 0.080307 | 0.0652 | -0.0045202 | -0.00038018 | -0.0018265 | -4.0237 | -3.9139 | -6.1432 | -4.3625 | -4.2023 | -6.134 | -4.2801 | -0.013733 | 117.1646 | -6.1707 | 117.0364 | -5.9143 | -6.0516 | -5.896 | -0.13733 | -120.9732 | -121.4218 | 1.8036 | 1.7258 | -0.12817 | 1.8631 | 0.009155 | -0.16479 | 0.10529 | -0.022888 | 0.091552 | 0.10986 | -0.045777 | 0.27466 | 0.11902 | 1.9409 | 1.7807 | 0.25635 | 123.2071 | 2.2293 | 123.3353 | 2.092 | 123.1705 | -123.2025 | -123.23 | 1.6434 | 123.0423 | 1.9821 | 5.9921
1139.5469 | 123.1613 | -5.8777 | 117.1692 | -0.057678 | 0.0048343 | -0.00030766 | 0.0010981 | 0.0021213 | 0.0017794 | -0.0035163 | 0.12936 | 0.00074988 | 0.080521 | 0.066054 | -0.002384 | -0.0020892 | -0.00011754 | -4.0558 | -3.804 | -6.0333 | -4.1519 | -3.9642 | -5.8502 | -4.0329 | 0.21057 | 117.2241 | -6.0013 | 117.2379 | -5.6946 | -5.777 | -5.69 | -0.15564 | -120.9732 | -121.3211 | 1.9135 | 1.8448 | 0.027466 | 2.0004 | 0.1831 | -0.1236 | 0.054932 | 0.068665 | 0.18311 | 0.18768 | 0.10071 | 0.31128 | 0.2243 | 2.0691 | 1.8814 | 0.3067 | 123.2391 | 2.2293 | 123.2254 | 2.0737 | 123.1018 | -123.2025 | -123.1705 | 1.7258 | 123.1155 | 1.8219 | 6.0883
1140.4844 | 123.1064 | -5.7083 | 117.3477 | 0.033875 | 0.0026981 | -0.0020167 | 0.0038751 | 0.0012667 | -0.00014322 | -0.0018073 | -0.023224 | 0.0016043 | 0.082016 | 0.062636 | -0.0021704 | -0.0010212 | -0.00011754 | -3.9459 | -3.6346 | -5.8868 | -4.0924 | -3.9276 | -5.7816 | -3.9871 | 0.073242 | 117.4713 | -5.8228 | 117.3157 | -5.5939 | -5.7175 | -5.5984 | -0.17853 | -120.9824 | -121.4401 | 1.7807 | 1.7212 | -0.073242 | 1.8997 | 0.10529 | -0.11444 | 0.1236 | -0.032043 | 0.11444 | 0.10986 | -0.009155 | 0.2243 | 0.10529 | 1.9592 | 1.7944 | 0.22888 | 123.1384 | 2.2522 | 123.2941 | 2.0737 | 123.1796 | -123.2346 | -123.1705 | 1.6159 | 123.024 | 1.7624 | 5.7816
1141.4844 | 123.0927 | -6.1844 | 116.8945 | -0.072937 | 0.0044071 | 0.00011954 | 0.00045712 | -0.00022866 | 0.0024204 | 0.00032907 | -0.035431 | 0.00074988 | 0.083725 | 0.064132 | -0.0017432 | -0.00059378 | 0.0020187 | -4.3671 | -3.9963 | -6.2714 | -4.5227 | -4.3625 | -6.2119 | -4.422 | 0.022888 | 117.0456 | -6.3034 | 116.8671 | -6.0699 | -6.2302 | -6.0516 | -0.086975 | -120.8908 | -121.4172 | 1.8219 | 1.7624 | -0.027466 | 1.8494 | 0.059509 | -0.11902 | 0.15106 | -0.027466 | 0.11444 | 0.13275 | -0.045777 | 0.25177 | 0.073242 | 1.9089 | 1.7487 | 0.23346 | 123.1705 | 2.2751 | 123.349 | 2.1881 | 123.23 | -123.1659 | -123.1979 | 1.6617 | 123.0515 | 1.8173 | 6.2073
1142.4844 | 123.1384 | -6.0608 | 117.0364 | -0.0042723 | 0.0020573 | 0.00054694 | 0.0043023 | 0.0031893 | 0.00071138 | 0.0013971 | -0.0079652 | 0.0024589 | 0.083939 | 0.066909 | -0.0019568 | -0.00080758 | 0.00073706 | -4.1656 | -3.8086 | -6.221 | -4.3167 | -4.1702 | -6.0928 | -4.1977 | 0.059509 | 117.1646 | -6.1707 | 117.0181 | -5.8731 | -6.0425 | -5.9143 | -0.16022 | -120.845 | -121.3531 | 1.8906 | 1.8631 | -0.032043 | 2.0233 | 0.12817 | -0.10986 | 0.12817 | -0.018311 | 0.18768 | 0.14648 | 0.018311 | 0.25635 | 0.12817 | 2.0508 | 1.9043 | 0.29755 | 123.1888 | 2.4124 | 123.3353 | 2.2522 | 123.2254 | -123.2574 | -123.2071 | 1.7441 | 123.0789 | 1.8951 | 6.1203
1143.4844 | 123.056 | -4.7012 | 118.428 | -0.03479 | 0.0039799 | -0.0043665 | 0.0023797 | 0.0029757 | 0.0013522 | -0.00095273 | -0.029327 | 0.00096348 | 0.081162 | 0.067123 | -0.0036658 | -0.0018756 | 0.00052346 | -3.3325 | -2.9938 | -4.834 | -3.4653 | -3.3096 | -4.747 | -3.3829 | 0.20599 | 118.5333 | -4.7882 | 118.3594 | -4.5319 | -4.7058 | -4.5593 | -0.13275 | -121.4218 | -121.8933 | 1.3916 | 1.3184 | -0.045776 | 1.4511 | 0.086975 | -0.086975 | 0.10529 | -0.068665 | 0.16937 | 0.14191 | -0.004578 | 0.22888 | 0.082397 | 1.5244 | 1.3687 | 0.25635 | 123.1476 | 1.8402 | 123.3215 | 1.7075 | 123.2346 | -123.262 | -123.2162 | 1.236 | 123.0606 | 1.3687 | 4.9072
1144.5469 | 123.1018 | -4.6326 | 118.4372 | -0.042419 | 0.0052615 | -0.0022303 | 2.9918e-05 | -0.0042875 | 0.002634 | -0.00052553 | 0.065277 | 0.0013907 | 0.080307 | 0.059646 | -0.0017432 | -0.0010212 | -0.00097194 | -3.2135 | -3.0396 | -4.8111 | -3.3279 | -3.1265 | -4.5914 | -3.1998 | 0.41199 | 118.5333 | -4.7379 | 118.4463 | -4.2068 | -4.3671 | -4.3762 | -0.17853 | -121.4767 | -121.7651 | 1.506 | 1.4328 | 0.041198 | 1.6113 | 0.21973 | -0.10529 | 0.09613 | 0.009155 | 0.42572 | 0.25635 | 0.2655 | 0.36163 | 0.37079 | 1.6846 | 1.4832 | 0.53101 | 123.1842 | 1.7715 | 123.2712 | 1.593 | 123.1659 | -123.2483 | -123.175 | 1.3046 | 123.0789 | 1.4191 | 5.0446
1145.4844 | 123.0743 | -4.953 | 118.1808 | -0.057678 | 0.0046207 | -0.00094846 | 0.0040887 | 0.0040439 | 0.0015658 | -0.0033025 | -0.020172 | 0.0018179 | 0.081162 | 0.066054 | -0.0021704 | -0.0027302 | -0.0013991 | -3.4332 | -3.0533 | -5.0308 | -3.5889 | -3.447 | -5.0446 | -3.4927 | 0.20142 | 118.2632 | -5.0995 | 118.1122 | -4.8386 | -4.9484 | -4.8019 | -0.07782 | -121.2341 | -121.7697 | 1.506 | 1.4603 | -0.091553 | 1.5381 | -0.013733 | -0.14648 | 0.082398 | -0.068664 | 0.11444 | 0.15106 | 0.004578 | 0.29755 | 0.15106 | 1.5839 | 1.442 | 0.26093 | 123.2117 | 1.9775 | 123.3627 | 1.8997 | 123.2162 | -123.2117 | -123.2803 | 1.3641 | 123.0652 | 1.5198 | 5.1544
1146.5469 | 123.0652 | -5.0446 | 118.0664 | -0.019531 | 0.0037661 | -0.0022303 | 0.0036615 | 0.00041234 | 0.0019932 | -0.0026617 | 0.016449 | 0.0018179 | 0.080948 | 0.06285 | -3.4196e-05 | -0.0027302 | -0.0033219 | -3.4882 | -3.1403 | -5.0583 | -3.6804 | -3.5202 | -5.0629 | -3.5889 | 0.13733 | 118.2037 | -5.1636 | 118.0206 | -4.8706 | -5.0308 | -4.9072 | -0.013733 | -121.2067 | -121.7468 | 1.5244 | 1.4557 | -0.01831 | 1.4694 | -0.004577 | -0.11902 | 0.13733 | -0.045776 | 0.17395 | 0.13733 | 0.013733 | 0.25635 | 0.13275 | 1.5381 | 1.3779 | 0.29297 | 123.1842 | 1.918 | 123.3673 | 1.9043 | 123.2483 | -123.1247 | -123.23 | 1.3641 | 123.0652 | 1.5564 | 5.1819
1147.4844 | 123.0743 | -4.6783 | 118.4372 | -0.057678 | 0.0050479 | -0.0030847 | 0.0028069 | 0.0023349 | -0.00078402 | -0.0015935 | -0.084259 | 0.0035269 | 0.082444 | 0.065841 | -0.0032386 | 0.0015424 | 0.0015915 | -3.1769 | -2.8427 | -4.7516 | -3.3325 | -3.1723 | -4.6738 | -3.2364 | 0.16022 | 118.5791 | -4.747 | 118.4052 | -4.541 | -4.7058 | -4.5639 | -0.073242 | -121.2799 | -121.7697 | 1.506 | 1.442 | 0.004578 | 1.5152 | 0.07782 | -0.068664 | 0.14191 | -0.032044 | 0.13733 | 0.11444 | -0.027466 | 0.18311 | 0.041198 | 1.5793 | 1.4191 | 0.20599 | 123.1522 | 1.9089 | 123.3261 | 1.8356 | 123.2574 | -123.1888 | -123.1842 | 1.3458 | 123.0835 | 1.5015 | 4.8386
1148.5469 | 123.1842 | -4.8294 | 118.2175 | -0.050049 | 0.0035525 | -0.0013757 | -0.0014655 | -1.486e-05 | 0.0011386 | -0.0020209 | 0.080536 | 0.00053628 | 0.081589 | 0.061355 | -0.0019568 | -0.0029438 | -0.00075834 | -3.4607 | -3.1677 | -5.0308 | -3.5156 | -3.3325 | -4.834 | -3.3783 | 0.38452 | 118.2724 | -4.9805 | 118.309 | -4.5731 | -4.715 | -4.6097 | -0.20142 | -121.3852 | -121.7331 | 1.4969 | 1.4511 | -0.004577 | 1.6525 | 0.19684 | -0.15106 | 0.054932 | 0.091553 | 0.25635 | 0.21973 | 0.11444 | 0.37079 | 0.2655 | 1.6983 | 1.5152 | 0.40741 | 123.2895 | 1.8631 | 123.2529 | 1.6617 | 123.1018 | -123.2483 | -123.1979 | 1.3138 | 123.1384 | 1.3687 | 5.2139
1149.4844 | 123.1201 | -4.5914 | 118.515 | -0.011902 | 0.0048343 | -0.0050073 | 0.0045159 | 0.0019077 | 0.00028418 | -0.0018073 | -0.069 | 0.0020315 | 0.082016 | 0.064559 | -0.0017432 | -0.0012348 | -0.00011754 | -3.3051 | -3.0121 | -4.8111 | -3.4195 | -3.2593 | -4.6875 | -3.3463 | 0.064087 | 118.5791 | -4.7836 | 118.515 | -4.3579 | -4.5502 | -4.422 | -0.21973 | -121.5271 | -121.9345 | 1.3321 | 1.2451 | -0.09613 | 1.4648 | 0.1236 | -0.19226 | 0.064087 | 0 | 0.23346 | 0.16937 | 0.041199 | 0.36163 | 0.23346 | 1.5518 | 1.3916 | 0.42572 | 123.2986 | 1.799 | 123.3627 | 1.5793 | 123.1705 | -123.3261 | -123.2986 | 1.1719 | 123.1064 | 1.2863 | 4.6555
1150.4844 | 123.111 | -4.9026 | 118.1625 | 0.0033567 | 0.0024845 | -0.0020167 | 0.0017389 | 0.0038303 | -0.0012112 | -0.0018073 | -0.047638 | 0.0039541 | 0.081162 | 0.068191 | -0.001316 | -0.00059378 | -0.0011855 | -3.4149 | -3.0808 | -5.1041 | -3.5294 | -3.3783 | -4.9713 | -3.4241 | 0.086975 | 118.2816 | -5.0674 | 118.1808 | -4.7104 | -4.8706 | -4.7653 | -0.20142 | -121.2433 | -121.6919 | 1.5244 | 1.4786 | -0.068664 | 1.68 | 0.13275 | -0.16479 | 0.11902 | 0.01831 | 0.19226 | 0.13733 | 0.032044 | 0.30212 | 0.19684 | 1.7258 | 1.5747 | 0.35706 | 123.2483 | 2.0233 | 123.349 | 1.8219 | 123.1842 | -123.2666 | -123.23 | 1.3733 | 123.0835 | 1.4877 | 4.9896
1151.5469 | 123.0972 | -4.7333 | 118.3731 | -0.019531 | 0.0041935 | -0.00030766 | 0.0015253 | -1.486e-05 | 0.0015658 | -0.0020209 | 0.028656 | -0.00010472 | 0.082016 | 0.064986 | -0.0021704 | -0.0040118 | 0.0011643 | -3.4012 | -3.1174 | -4.8294 | -3.4973 | -3.3234 | -4.6692 | -3.3737 | 0.17853 | 118.5013 | -4.8111 | 118.3594 | -4.5319 | -4.6875 | -4.5776 | -0.096131 | -121.4905 | -121.8704 | 1.4099 | 1.3596 | 0.064087 | 1.4557 | 0.16022 | -0.07782 | 0.12817 | -0.013733 | 0.20142 | 0.15564 | 0.045776 | 0.23346 | 0.1236 | 1.506 | 1.3321 | 0.27924 | 123.1705 | 1.712 | 123.3124 | 1.6159 | 123.2346 | -123.2025 | -123.1842 | 1.236 | 123.0927 | 1.3321 | 4.9118
1152.4844 | 123.0927 | -5.1682 | 117.9337 | 0.0033567 | 0.0031253 | -0.0030847 | 0.0023797 | -0.0017239 | -0.00099762 | -0.0030889 | -0.029327 | 0.0022453 | 0.080735 | 0.066054 | 0.000393 | -0.00080758 | 0.0020187 | -3.7582 | -3.392 | -5.2872 | -3.923 | -3.7765 | -5.2368 | -3.7949 | -0.041199 | 118.0984 | -5.2872 | 117.9153 | -4.9942 | -5.1361 | -5.0171 | -0.11902 | -121.3257 | -121.8567 | 1.3916 | 1.3733 | -0.068664 | 1.4923 | 0.050354 | -0.11902 | 0.16479 | -0.018311 | 0.17395 | 0.15106 | 0.032044 | 0.27008 | 0.15106 | 1.5106 | 1.3641 | 0.29297 | 123.2025 | 1.8951 | 123.3856 | 1.7761 | 123.2666 | -123.2208 | -123.2208 | 1.2451 | 123.0835 | 1.4099 | 5.127
1153.5625 | 123.1979 | -5.3787 | 117.6865 | -0.027161 | 0.0033389 | -0.0026575 | 0.0030207 | 0.0010531 | 0.0019932 | -0.00095273 | -0.038483 | 0.0030997 | 0.080735 | 0.070968 | -0.002384 | -0.00059378 | -0.0011855 | -3.9871 | -3.6346 | -5.4977 | -4.0649 | -3.9276 | -5.4199 | -3.9917 | -0.082397 | 117.8375 | -5.4749 | 117.7048 | -5.1956 | -5.3329 | -5.1727 | -0.11902 | -121.3211 | -121.7514 | 1.4511 | 1.387 | -0.041199 | 1.506 | 0.07782 | -0.096131 | 0.15106 | 0.018311 | 0.18311 | 0.20599 | 0.045776 | 0.30212 | 0.14191 | 1.5701 | 1.4328 | 0.27924 | 123.1796 | 1.8631 | 123.3124 | 1.7441 | 123.2162 | -123.1842 | -123.1613 | 1.3138 | 123.0835 | 1.3916 | 5.2963
1154.4844 | 123.1018 | -4.6875 | 118.4189 | 0.018616 | 0.0041935 | -0.0018031 | 0.0038751 | 0.0040439 | -0.0012112 | -0.0022345 | -0.029327 | 0.0028861 | 0.082657 | 0.067763 | -3.4196e-05 | 0.00026062 | 0.0015915 | -3.1952 | -2.8519 | -4.8752 | -3.3051 | -3.1357 | -4.7333 | -3.1906 | 0.059509 | 118.515 | -4.8294 | 118.4235 | -4.4998 | -4.6509 | -4.5227 | -0.18768 | -121.2708 | -121.7239 | 1.5518 | 1.4969 | -0.045776 | 1.6846 | 0.14191 | -0.14191 | 0.096131 | 0.004578 | 0.18768 | 0.16479 | 0.036621 | 0.3067 | 0.17853 | 1.7395 | 1.5701 | 0.32959 | 123.2529 | 2.0233 | 123.3444 | 1.8356 | 123.2025 | -123.2941 | -123.2483 | 1.3824 | 123.111 | 1.4923 | 4.747
1155.5469 | 123.1293 | -2.8244 | 120.369 | 0.010986 | 0.0022709 | -0.0039393 | 0.0013117 | 0.0023349 | -0.0012112 | -0.00031193 | 0.022552 | 0.00074988 | 0.082657 | 0.06755 | 0.0008204 | -0.0035846 | 9.6064e-05 | -2.092 | -1.7441 | -3.0716 | -2.2522 | -2.0828 | -3.0304 | -2.1149 | 0.35248 | 120.3186 | -3.0945 | 120.2454 | -2.6505 | -2.7695 | -2.5909 | -0.24719 | -122.113 | -122.6212 | 0.74158 | 0.70953 | -0.20599 | 0.95673 | 0.041198 | -0.27008 | -0.050354 | -0.1236 | 0.17395 | 0.23346 | 0.054932 | 0.50354 | 0.32501 | 0.98877 | 0.8194 | 0.44403 | 123.3398 | 1.3275 | 123.4131 | 1.0803 | 123.143 | -123.4406 | -123.4634 | 0.57221 | 123.0698 | 0.73242 | 3.1769
1156.4844 | 123.1201 | -2.9572 | 120.1813 | 0.026245 | 0.0033389 | -0.0022303 | 0.0019525 | -0.00044226 | 7.0582e-05 | -0.00095273 | -0.029327 | 0.00096348 | 0.082657 | 0.063491 | -0.000675 | 0.00026062 | 0.00030966 | -2.2339 | -1.8906 | -3.2318 | -2.3117 | -2.1561 | -3.0396 | -2.1927 | 0.041199 | 120.2545 | -3.1448 | 120.1309 | -2.6917 | -2.8015 | -2.7557 | -0.27466 | -122.0718 | -122.493 | 0.80109 | 0.76446 | -0.082398 | 1.0391 | 0.19226 | -0.18768 | 0.073243 | -0.050354 | 0.2655 | 0.20142 | 0.15564 | 0.3891 | 0.34332 | 1.0757 | 0.9201 | 0.45319 | 123.2758 | 1.3412 | 123.3994 | 1.0666 | 123.2117 | -123.4131 | -123.3261 | 0.64545 | 123.0881 | 0.72327 | 2.9984
1157.4844 | 123.1155 | -2.623 | 120.4971 | -0.050049 | 0.0039799 | -0.0035119 | 0.00045712 | 0.0014803 | 7.0582e-05 | -0.0013799 | -0.099518 | 0.0011771 | 0.082657 | 0.061782 | -0.001316 | -0.00038018 | 0.00095066 | -1.9547 | -1.6617 | -2.8015 | -2.0645 | -1.9043 | -2.6642 | -1.8677 | 0.15106 | 120.6757 | -2.7145 | 120.4926 | -2.4536 | -2.5772 | -2.4536 | -0.17853 | -122.1588 | -122.5616 | 0.71869 | 0.75531 | -0.041199 | 0.93384 | 0.13733 | -0.091553 | 0.17853 | -0.004577 | 0.16937 | 0.16937 | 0.045777 | 0.26093 | 0.13733 | 0.89722 | 0.737 | 0.26093 | 123.2071 | 1.1398 | 123.3902 | 0.9613 | 123.2986 | -123.2986 | -123.2117 | 0.55847 | 123.1155 | 0.66834 | 2.774
1158.5625 | 123.0469 | -3.4149 | 119.7601 | -0.095825 | 0.0054751 | -0.0030847 | 0.0025933 | 0.0012667 | 0.0022068 | 0.0022517 | -0.059845 | 0.00053628 | 0.082016 | 0.068831 | -0.0019568 | 4.7018e-05 | -0.00033114 | -2.4216 | -2.1332 | -3.5339 | -2.6001 | -2.449 | -3.4882 | -2.5131 | 0.050354 | 119.838 | -3.5522 | 119.6503 | -3.2593 | -3.4561 | -3.2822 | -0.11902 | -121.8933 | -122.3602 | 0.96588 | 0.90179 | -0.073242 | 1.0208 | 0.045777 | -0.13733 | 0.07782 | -0.10986 | 0.15564 | 0.13275 | -0.041199 | 0.27008 | 0.09613 | 1.0849 | 0.93384 | 0.29297 | 123.2025 | 1.4008 | 123.3902 | 1.2817 | 123.2529 | -123.2941 | -123.3124 | 0.81482 | 123.0652 | 0.99335 | 3.4653
1159.4844 | 123.1201 | -3.0487 | 120.163 | -0.057678 | 0.0037661 | -0.0013757 | 0.0019525 | 0.0012667 | 0.00092498 | -0.0011663 | -0.029327 | 0.0026725 | 0.081162 | 0.066482 | -0.0034522 | -0.0010212 | 0.0033005 | -2.2064 | -1.9089 | -3.1906 | -2.3163 | -2.1378 | -3.0396 | -2.2797 | 0.10529 | 120.1767 | -3.1769 | 120.108 | -2.8336 | -2.9572 | -2.8381 | -0.14191 | -122.0718 | -122.4792 | 0.91095 | 0.76904 | 0.009155 | 0.91095 | 0.15106 | -0.12817 | 0.013733 | -0.054932 | 0.21515 | 0.21057 | 0.091553 | 0.33875 | 0.21973 | 1.0529 | 0.87433 | 0.34332 | 123.2849 | 1.2817 | 123.3536 | 1.1398 | 123.2254 | -123.3536 | -123.3398 | 0.73242 | 123.1567 | 0.84228 | 3.154
1160.4844 | 123.1201 | -2.6871 | 120.4422 | -0.019531 | 0.0037661 | -0.0024439 | 0.0019525 | 0.0027621 | 0.00028418 | 0.00075627 | 0.010345 | -0.00031832 | 0.083084 | 0.066482 | -0.0036658 | -0.0042254 | 0.00030966 | -1.9775 | -1.6388 | -2.8473 | -2.1057 | -1.9501 | -2.7374 | -1.9867 | 0.050354 | 120.5566 | -2.8427 | 120.4147 | -2.4902 | -2.6413 | -2.5223 | -0.16022 | -122.081 | -122.5479 | 0.737 | 0.70038 | -0.050354 | 0.8606 | 0.10986 | -0.15564 | 0.11444 | -0.027466 | 0.19684 | 0.16479 | 0.045777 | 0.32043 | 0.20142 | 0.89722 | 0.74158 | 0.35248 | 123.2574 | 1.2085 | 123.3994 | 1.0483 | 123.2437 | -123.2895 | -123.2849 | 0.58136 | 123.1018 | 0.70953 | 2.7374
1161.5469 | 123.1201 | -2.7237 | 120.4285 | -0.0042723 | 0.00098907 | -0.0026575 | -0.00061088 | 0.00019874 | 0.00071138 | -0.0026617 | 0.05307 | 0.00032248 | 0.085861 | 0.061568 | -0.002384 | -0.001662 | 0.0020187 | -1.9867 | -1.7349 | -2.8702 | -2.0782 | -1.9043 | -2.7054 | -1.9684 | 0.23346 | 120.4788 | -2.8748 | 120.3918 | -2.4994 | -2.6047 | -2.5269 | -0.14648 | -122.1634 | -122.5067 | 0.8194 | 0.75531 | 0.018311 | 0.90179 | 0.1648 | -0.15106 | 0.050354 | -0.036621 | 0.2243 | 0.19684 | 0.11902 | 0.3479 | 0.27008 | 0.96588 | 0.79193 | 0.37537 | 123.2666 | 1.1353 | 123.3536 | 0.98877 | 123.2025 | -123.2986 | -123.3032 | 0.64545 | 123.1155 | 0.737 | 2.9572
1162.4844 | 123.0927 | -2.742 | 120.4102 | 0.08728 | 0.00077547 | -0.0030847 | 0.00024352 | 0.0012667 | 0.00092498 | -0.0013799 | 0.004242 | -0.00031832 | 0.082657 | 0.06755 | -0.0019568 | -0.0018756 | 9.6064e-05 | -2.0508 | -1.6708 | -2.9068 | -2.1744 | -1.9958 | -2.7878 | -2.0187 | 0.013733 | 120.5429 | -2.8885 | 120.4834 | -2.6138 | -2.8519 | -2.6962 | -0.16479 | -122.081 | -122.5845 | 0.74615 | 0.72327 | -0.045777 | 0.88806 | 0.11902 | -0.14648 | 0.13275 | 0.073242 | 0.12817 | 0.045776 | -0.10986 | 0.19226 | 0.036621 | 0.91095 | 0.73242 | 0.27466 | 123.3719 | 1.236 | 123.4314 | 1.0712 | 123.2849 | -123.317 | -123.2986 | 0.56763 | 123.2254 | 0.69122 | 2.7557
1163.5 | 123.1934 | -2.5681 | 120.4971 | -0.011902 | 0.0048343 | -0.0022303 | 0.0019525 | 0.00019874 | 0.00049778 | 0.0013971 | -0.014069 | 0.00053628 | 0.083939 | 0.065627 | -0.0043066 | -0.00080758 | -0.0013991 | -1.918 | -1.7303 | -2.8885 | -1.9775 | -1.8265 | -2.623 | -1.886 | 0.21515 | 120.5566 | -2.7374 | 120.5521 | -2.3666 | -2.5085 | -2.3758 | -0.32043 | -122.2275 | -122.4747 | 0.74158 | 0.68207 | -0.054932 | 1.0025 | 0.2655 | -0.16937 | 0.05951 | 0.054932 | 0.20142 | 0.19226 | 0.059509 | 0.36163 | 0.22888 | 1.062 | 0.91095 | 0.37079 | 123.2895 | 1.1581 | 123.2941 | 0.83771 | 123.1247 | -123.3856 | -123.2346 | 0.59052 | 123.1201 | 0.65002 | 2.7832
1164.5469 | 123.0927 | -2.71 | 120.4468 | 0.079651 | 0.0033389 | -0.0052209 | 0.0015253 | -0.0030057 | -0.00078402 | -0.0039435 | 0.0011902 | 0.0026725 | 0.084793 | 0.066054 | -0.0017432 | -0.0018756 | 0.0026597 | -1.9958 | -1.6296 | -2.8931 | -2.1103 | -1.9363 | -2.7786 | -1.9684 | 0.059509 | 120.5475 | -2.8702 | 120.4468 | -2.298 | -2.7832 | -2.7145 | -0.18311 | -122.0764 | -122.5571 | 0.77362 | 0.74158 | -0.068664 | 0.92468 | 0.11444 | -0.16022 | 0.10071 | 0 | 0.41199 | -0.004578 | -0.073242 | 0.15564 | 0.086975 | 0.95673 | 0.78277 | 0.5722 | 123.317 | 1.2634 | 123.4177 | 1.0803 | 123.2574 | -123.3398 | -123.317 | 0.59967 | 123.1567 | 0.71411 | 2.7695
1165.4844 | 123.1247 | -2.6276 | 120.5109 | -0.11871 | 0.0052615 | -0.0047937 | 0.0013117 | -1.486e-05 | -0.00035682 | 0.00075627 | -0.041534 | 0.00074988 | 0.083084 | 0.070327 | -0.0032386 | -0.00038018 | 0.00073706 | -1.8631 | -1.5244 | -2.71 | -1.9638 | -1.8219 | -2.6459 | -1.886 | 0.082397 | 120.6299 | -2.7832 | 120.4971 | -2.4719 | -2.6047 | -2.4811 | -0.082398 | -122.0352 | -122.4747 | 0.80566 | 0.74158 | -0.018311 | 0.82397 | 0.064087 | -0.15564 | 0.11902 | -0.013733 | 0.15564 | 0.14648 | 0.022888 | 0.30212 | 0.17853 | 0.88806 | 0.74615 | 0.31128 | 123.2803 | 1.1856 | 123.4131 | 1.1032 | 123.2574 | -123.2208 | -123.2941 | 0.66376 | 123.1247 | 0.76446 | 2.71
1166.5469 | 123.2529 | -2.5543 | 120.5383 | -0.050049 | 0.0044071 | -0.0024439 | 0.00067072 | -0.0010831 | 0.00092498 | 0.00054267 | 0.031708 | -0.00053192 | 0.08223 | 0.05815 | -0.001316 | -0.0025164 | -0.0020401 | -1.7853 | -1.5518 | -2.6917 | -1.8494 | -1.6525 | -2.4948 | -1.7212 | 0.24261 | 120.6345 | -2.6825 | 120.6436 | -2.2888 | -2.417 | -2.3346 | -0.13733 | -122.0901 | -122.3877 | 0.90179 | 0.83313 | 0.059509 | 0.97046 | 0.19684 | -0.12817 | 0.09613 | 0.10529 | 0.2655 | 0.21973 | 0.13733 | 0.3479 | 0.2655 | 1.0391 | 0.84229 | 0.39368 | 123.3261 | 1.1398 | 123.317 | 1.0025 | 123.1888 | -123.23 | -123.2208 | 0.70496 | 123.1979 | 0.76904 | 2.7969
1167.4844 | 123.1293 | -2.6093 | 120.5383 | -0.027161 | 0.0026981 | -0.0032983 | 0.00024352 | 0.0023349 | 0.0017794 | -0.0035163 | -0.072052 | 0.0035269 | 0.083512 | 0.068618 | -0.0028112 | -0.0010212 | -0.0031081 | -1.8768 | -1.5518 | -2.7786 | -1.8448 | -1.6983 | -2.5818 | -1.8448 | 0.1236 | 120.6528 | -2.7237 | 120.52 | -2.449 | -2.5818 | -2.449 | -0.16937 | -122.0901 | -122.3831 | 0.91095 | 0.76446 | 0.027466 | 0.93384 | 0.19684 | -0.11444 | 0.11444 | -0.01831 | 0.16022 | 0.16022 | 0.027466 | 0.27466 | 0.14191 | 1.0803 | 0.93384 | 0.27466 | 123.2437 | 1.2268 | 123.3765 | 1.0574 | 123.262 | -123.317 | -123.262 | 0.76446 | 123.1293 | 0.73242 | 2.7328
1168.4844 | 123.175 | -2.4536 | 120.639 | -0.042419 | 0.0033389 | -0.0035119 | -0.00061088 | 0.0016939 | 0.0037022 | -0.0015935 | 0.016449 | 0.0022453 | 0.08223 | 0.063491 | -0.001316 | -0.0029438 | 0.0015915 | -1.7807 | -1.474 | -2.5818 | -1.8494 | -1.6571 | -2.4811 | -1.7166 | 0.35248 | 120.7443 | -2.6184 | 120.6619 | -2.2705 | -2.3895 | -2.2934 | -0.12817 | -122.113 | -122.4884 | 0.79651 | 0.737 | -0.027466 | 0.86517 | 0.10071 | -0.1648 | 0.10529 | 0.022888 | 0.1831 | 0.16022 | 0.064087 | 0.32501 | 0.22888 | 0.92468 | 0.73242 | 0.3479 | 123.2803 | 1.1078 | 123.3627 | 0.97961 | 123.1979 | -123.2208 | -123.2574 | 0.60425 | 123.1155 | 0.67291 | 2.8061
1169.5469 | 123.1201 | -2.71 | 120.488 | -0.03479 | 0.0035525 | -0.0041529 | 0.0028069 | -0.00086946 | 0.00028418 | -0.00073913 | -0.011017 | 0.0013907 | 0.084366 | 0.074172 | -0.0025976 | -0.00016658 | -0.0018265 | -1.9455 | -1.5289 | -2.8336 | -2.0462 | -1.8951 | -2.6871 | -1.9501 | 0.091553 | 120.5658 | -2.8473 | 120.3827 | -2.5452 | -2.6917 | -2.5818 | -0.1236 | -122.0169 | -122.5342 | 0.81482 | 0.75989 | 0.022888 | 0.88348 | 0.14648 | -0.13733 | 0.07782 | -0.10529 | 0.16479 | 0.12817 | 0.018311 | 0.2655 | 0.15564 | 0.93841 | 0.78735 | 0.30212 | 123.23 | 1.3046 | 123.4131 | 1.181 | 123.2758 | -123.3215 | -123.3353 | 0.66376 | 123.0927 | 0.76446 | 2.8015
1170.4844 | 123.1384 | -2.6596 | 120.5017 | -0.027161 | 0.0018435 | -0.0058619 | 0.0023797 | -0.0047147 | 0.0034884 | -0.0035163 | -0.023224 | 0.0030997 | 0.082444 | 0.068831 | -0.000675 | -0.0018756 | -0.00033114 | -1.9043 | -1.5244 | -2.7695 | -2.0142 | -1.886 | -2.7054 | -1.9135 | 0.082397 | 120.6345 | -2.7924 | 120.433 | -2.4948 | -2.6459 | -2.5223 | -0.10986 | -122.0261 | -122.5159 | 0.77362 | 0.74615 | -0.045776 | 0.85602 | 0.064087 | -0.13275 | 0.13275 | -0.068665 | 0.16479 | 0.13733 | 0.013733 | 0.27008 | 0.14648 | 0.88348 | 0.75531 | 0.29755 | 123.2254 | 1.2451 | 123.4268 | 1.1353 | 123.2941 | -123.2712 | -123.2941 | 0.64545 | 123.0927 | 0.75531 | 2.742
1171.4844 | 123.111 | -2.8839 | 120.3506 | 0.0033567 | 0.0056889 | -0.0024439 | 0.0015253 | -1.486e-05 | 0.0024204 | -9.8328e-05 | -0.053741 | 0.0011771 | 0.083939 | 0.062636 | -0.0032386 | -0.0023028 | 0.0015915 | -2.0004 | -1.7075 | -3.0258 | -2.0416 | -1.8951 | -2.8198 | -1.9684 | 0.1831 | 120.4285 | -2.9617 | 120.2316 | -2.7649 | -2.8656 | -2.71 | -0.14191 | -122.0581 | -122.3923 | 0.98877 | 0.91553 | 0.064087 | 1.0574 | 0.20599 | -0.07782 | 0.07782 | -0.11902 | 0.11902 | 0.17395 | 0.01831 | 0.25177 | 0.09613 | 1.1307 | 0.98419 | 0.19684 | 123.1934 | 1.3184 | 123.3902 | 1.1765 | 123.3124 | -123.3765 | -123.3124 | 0.84228 | 123.1155 | 0.88348 | 3.067
1172.5469 | 123.1796 | -2.6825 | 120.4376 | -0.011902 | 0.0031253 | -0.00030766 | 0.00045712 | 0.0036165 | 0.00092498 | -0.00073913 | 0.028656 | -0.00010472 | 0.084793 | 0.05815 | -0.0019568 | -0.00080758 | 0.0030869 | -1.8997 | -1.6663 | -2.8244 | -1.9363 | -1.7578 | -2.6596 | -1.8402 | 0.3479 | 120.5109 | -2.8107 | 120.4926 | -2.4445 | -2.5497 | -2.4536 | -0.14191 | -122.1039 | -122.374 | 0.92468 | 0.84228 | 0.022888 | 0.98419 | 0.1648 | -0.12817 | 0.073242 | 0.054932 | 0.23804 | 0.22888 | 0.13275 | 0.35706 | 0.26092 | 1.0666 | 0.88806 | 0.36621 | 123.3032 | 1.1581 | 123.3215 | 1.0162 | 123.1934 | -123.262 | -123.2483 | 0.74615 | 123.175 | 0.78278 | 3.0304
1173.4844 | 123.1018 | -4.1702 | 118.959 | -0.057678 | 0.0046207 | -0.0026575 | 0.0017389 | -0.00065586 | 0.0013522 | -0.0011663 | -0.032379 | 0.0011771 | 0.080094 | 0.065627 | -0.0036658 | 0.00026062 | -0.00011754 | -2.8381 | -2.5223 | -4.3304 | -2.9068 | -2.774 | -4.184 | -2.8152 | 0.11444 | 119.1147 | -4.2755 | 118.9453 | -3.9871 | -4.1565 | -3.9963 | -0.16022 | -121.4813 | -121.8658 | 1.3962 | 1.355 | -0.013733 | 1.5152 | 0.14648 | -0.10529 | 0.15564 | -0.013733 | 0.1831 | 0.17395 | 0.013733 | 0.27924 | 0.11902 | 1.5564 | 1.4236 | 0.28839 | 123.2208 | 1.8082 | 123.3902 | 1.6479 | 123.2849 | -123.2895 | -123.2346 | 1.2634 | 123.1155 | 1.3321 | 4.2847
1174.5469 | 123.2208 | -4.7379 | 118.3548 | 0.041504 | 0.0044071 | -0.0013757 | 0.00088432 | -1.486e-05 | 0.0032748 | -0.00052553 | 0.065277 | 0.0033133 | 0.083939 | 0.062636 | -0.002384 | -0.00038018 | -0.00033114 | -3.2822 | -3.0029 | -5.0446 | -3.3417 | -3.1448 | -4.866 | -3.0991 | -0.018311 | 118.2861 | -5.0537 | 118.4143 | -4.4861 | -4.6097 | -4.541 | -0.3067 | -121.3577 | -121.6965 | 1.593 | 1.6388 | -0.12817 | 1.9455 | 0.17853 | -0.31586 | -0.068664 | 0.05951 | 0.25177 | 0.19684 | 0.12817 | 0.51269 | 0.44403 | 1.8997 | 1.7029 | 0.56763 | 123.468 | 2.0416 | 123.3398 | 1.7349 | 123.024 | -123.3994 | -123.4085 | 1.3962 | 123.1522 | 1.4557 | 4.7195
1175.4844 | 123.1522 | -5.246 | 117.8696 | 0.0033567 | 0.0022709 | -0.0018031 | 0.0040887 | 0.0053255 | 0.00049778 | 0.00096987 | -0.026276 | 0.00010888 | 0.081803 | 0.073104 | -0.0019568 | -0.0023028 | 0.0013779 | -3.6255 | -3.447 | -5.4474 | -3.7582 | -3.5751 | -5.3101 | -3.4653 | 0.036621 | 118.0298 | -5.3375 | 117.8696 | -5.0995 | -5.2414 | -5.0903 | -0.20142 | -121.3165 | -121.6278 | 1.6708 | 1.7807 | -0.064087 | 1.9821 | 0.13733 | -0.091552 | 0.16022 | 0 | 0.14649 | 0.15564 | 0.004578 | 0.24719 | 0.09613 | 1.8723 | 1.6891 | 0.23804 | 123.2071 | 2.0004 | 123.3673 | 1.799 | 123.2758 | -123.317 | -123.2071 | 1.4877 | 123.1155 | 1.6205 | 5.2826
1176.4844 | 123.1064 | -5.1498 | 117.9703 | 0.033875 | 0.0035525 | -0.0032983 | 0.0010981 | 0.0027621 | -0.00035682 | -0.00031193 | -0.0018616 | -0.00074552 | 0.083725 | 0.066909 | 0.000393 | -0.0044392 | -0.00011754 | -4.3579 | -3.8864 | -5.3238 | -4.4861 | -4.3167 | -5.3421 | -4.3808 | -0.022888 | 118.0298 | -5.4016 | 118.0481 | -5.2002 | -5.2368 | -5.0446 | -0.17395 | -121.8567 | -122.4564 | 0.83313 | 0.76904 | -0.19226 | 0.94299 | -0.01831 | -0.25177 | 0.059509 | 0.07782 | -0.050354 | 0.10529 | -0.086975 | 0.35705 | 0.16479 | 1.0071 | 0.83771 | 0.20142 | 123.4497 | 1.4374 | 123.4314 | 1.2634 | 123.1796 | -123.2941 | -123.3719 | 0.66376 | 123.1979 | 0.79193 | 5.127
1177.4844 | 123.1338 | -4.5227 | 118.6111 | -0.027161 | 0.0024845 | -0.0011621 | 0.0010981 | 0.0029757 | 0.0013522 | 0.00032907 | -0.069 | -0.0011727 | 0.082657 | 0.067763 | -0.0034522 | -0.0023028 | -0.00011754 | -3.0853 | -2.7832 | -4.7653 | -3.1082 | -2.9526 | -4.6509 | -3.0212 | 0.13733 | 118.8126 | -4.6188 | 118.6066 | -4.3671 | -4.5227 | -4.3945 | -0.24261 | -121.3943 | -121.7194 | 1.5701 | 1.5015 | -0.12817 | 1.7441 | 0.11444 | -0.09613 | 0.20142 | -0.004578 | 0.15564 | 0.12817 | 0 | 0.2243 | 0.09613 | 1.8127 | 1.6571 | 0.25177 | 123.2254 | 1.9821 | 123.4314 | 1.7395 | 123.3353 | -123.3765 | -123.23 | 1.4145 | 123.1293 | 1.4374 | 4.66
1178.5469 | 123.1705 | -5.1041 | 117.9932 | -0.080566 | 0.0048343 | -0.0020167 | 0.0010981 | 0.0029757 | 0.0013522 | 0.00075627 | 0.0072936 | 0.00053628 | 0.082444 | 0.063491 | -0.0015296 | 4.7018e-05 | -0.0018265 | -3.4332 | -3.1494 | -5.2551 | -3.5065 | -3.3691 | -5.2094 | -3.4515 | 0.073242 | 118.0481 | -5.3192 | 118.0023 | -4.9301 | -5.0995 | -4.9393 | -0.15106 | -121.1426 | -121.4996 | 1.7349 | 1.6525 | -0.10529 | 1.8036 | 0.045776 | -0.21515 | 0.054932 | 0.009155 | 0.17395 | 0.1648 | 0.004578 | 0.37994 | 0.21973 | 1.886 | 1.7487 | 0.3891 | 123.3215 | 2.1057 | 123.3673 | 1.9547 | 123.1522 | -123.2483 | -123.3124 | 1.5976 | 123.1064 | 1.6708 | 5.1773
1179.4844 | 123.111 | -2.829 | 120.3598 | -0.042419 | 0.0041935 | -0.0024439 | 0.0025933 | 0.0036165 | -0.00099762 | -0.0020209 | -0.087311 | 0.0018179 | 0.083939 | 0.063705 | -0.0019568 | -0.00038018 | 0.0015915 | -1.9043 | -1.5701 | -2.9526 | -2.037 | -1.8906 | -2.861 | -1.9455 | 0.009155 | 120.5017 | -2.9343 | 120.3049 | -2.655 | -2.7832 | -2.6596 | -0.1236 | -121.9299 | -122.3969 | 0.93841 | 0.88348 | -0.032044 | 1.0071 | 0.091553 | -0.10529 | 0.14191 | -0.054931 | 0.17395 | 0.16937 | 0.045776 | 0.27466 | 0.15106 | 1.062 | 0.91553 | 0.27924 | 123.2391 | 1.3824 | 123.436 | 1.2588 | 123.3307 | -123.3124 | -123.2941 | 0.79193 | 123.1339 | 0.92468 | 2.8381
1180.5469 | 123.1705 | -2.8656 | 120.2774 | 0.0033567 | 0.0052615 | -0.0045801 | 0.00024352 | 0.0016939 | 0.00028418 | -0.0015935 | 0.031708 | -0.00053192 | 0.084366 | 0.059432 | -0.0028112 | -0.00059378 | 9.6064e-05 | -1.9409 | -1.7029 | -2.9984 | -2.0279 | -1.8402 | -2.829 | -1.9089 | 0.10529 | 120.3735 | -2.9938 | 120.282 | -2.6093 | -2.7512 | -2.6642 | -0.13275 | -121.9803 | -122.3053 | 1.0254 | 0.95673 | 0.036622 | 1.0895 | 0.16937 | -0.12817 | 0.09613 | 0.004577 | 0.25635 | 0.20142 | 0.11444 | 0.32959 | 0.24261 | 1.1581 | 0.97046 | 0.38452 | 123.2758 | 1.2955 | 123.3673 | 1.1627 | 123.2391 | -123.2758 | -123.2712 | 0.83771 | 123.1476 | 0.92468 | 2.9709
1181.4844 | 123.1201 | -4.4174 | 118.7256 | -0.0042723 | 0.0052615 | -0.00073486 | 0.0036615 | 0.0014803 | 0.0017794 | -0.00052553 | -0.044586 | 0.00032248 | 0.078598 | 0.069472 | -0.001316 | 0.00047422 | -0.0020401 | -2.9205 | -2.5955 | -4.5502 | -3.067 | -2.9205 | -4.509 | -2.9984 | 0.004578 | 118.8629 | -4.5731 | 118.6707 | -4.2984 | -4.4403 | -4.3121 | -0.13275 | -121.3211 | -121.7926 | 1.4969 | 1.4191 | -0.091553 | 1.5518 | 0.041199 | -0.15564 | 0.13733 | -0.054932 | 0.11902 | 0.10528 | -0.022889 | 0.26092 | 0.13275 | 1.6296 | 1.4832 | 0.27466 | 123.2437 | 1.9547 | 123.436 | 1.8219 | 123.2803 | -123.2758 | -123.2986 | 1.3504 | 123.0881 | 1.4969 | 4.422
1182.4844 | 123.143 | -4.6051 | 118.5471 | -0.011902 | 0.0037661 | -0.0037257 | 0.0025933 | -0.0012967 | -0.0014248 | -9.8328e-05 | -0.026276 | 0.00096348 | 0.084366 | 0.069259 | -0.0028112 | -0.0023028 | -0.00033114 | -3.0396 | -2.6276 | -4.7333 | -3.1815 | -3.0487 | -4.6555 | -2.417 | 0.036621 | 119.0918 | -4.2435 | 118.4784 | -4.4449 | -4.5319 | -4.3808 | -0.12817 | -121.1746 | -121.7285 | 1.5564 | 2.1881 | -0.050354 | 2.3163 | 0.077819 | 0.36163 | 0.54474 | -0.068664 | 0.16022 | 0.2243 | 0.073243 | -0.13733 | -0.28839 | 1.6846 | 1.5518 | -0.20142 | 122.7219 | 2.1057 | 123.3353 | 1.9775 | 123.6969 | -123.2803 | -122.7905 | 1.4236 | 123.0835 | 1.5656 | 4.6417
1183.5469 | 123.1338 | -2.7557 | 120.4514 | 0.010986 | 0.0018435 | -0.0043665 | 0.0017389 | 0.0051119 | 0.0022068 | 0.00032907 | -0.044586 | 0.0022453 | 0.083512 | 0.065414 | -0.0034522 | -0.0014484 | -0.00054474 | -1.8356 | -1.5564 | -2.9068 | -1.9501 | -1.7899 | -2.774 | -1.8539 | 0.82855 | 120.5475 | -2.8885 | 120.4102 | -2.5589 | -2.6688 | -2.5635 | -0.15106 | -122.0078 | -122.4014 | 0.96588 | 0.90179 | -0.018311 | 1.0529 | 0.13275 | -0.13275 | 0.09613 | -0.041199 | 0.19684 | 0.19226 | 0.086975 | 0.32501 | 0.21973 | 1.1169 | 0.95673 | 0.32959 | 123.2986 | 1.3504 | 123.436 | 1.1993 | 123.3032 | -123.3582 | -123.3398 | 0.80566 | 123.1659 | 0.9201 | 3.5843
1184.4844 | 123.143 | -4.3716 | 118.7256 | -0.0042723 | 0.0041935 | -0.0037257 | 0.0019525 | 0.00041234 | 0.0015658 | -0.0013799 | -0.026276 | 0.0020315 | 0.082657 | 0.066054 | -0.0045202 | -0.00080758 | 0.0011643 | -2.8564 | -2.5406 | -4.5776 | -2.9755 | -2.8198 | -4.4678 | -2.8839 | 0.52185 | 118.8858 | -4.5319 | 118.7393 | -4.216 | -4.3945 | -4.2618 | -0.20599 | -121.2662 | -121.7011 | 1.5518 | 1.4877 | -0.09613 | 1.6937 | 0.10986 | -0.16022 | 0.16022 | 0.013733 | 0.15564 | 0.10986 | -0.022888 | 0.27008 | 0.13733 | 1.7578 | 1.6022 | 0.31586 | 123.2712 | 2.037 | 123.4177 | 1.8311 | 123.2574 | -123.3032 | -123.2574 | 1.3962 | 123.111 | 1.5152 | 4.8935
1185.4844 | 123.1155 | -4.1107 | 119.0826 | -0.011902 | 0.0046207 | -0.0022303 | 0.0030207 | 0.0059665 | 0.0017794 | -0.0015935 | -0.032379 | 0.0022453 | 0.082016 | 0.063918 | -0.004093 | -0.0012348 | -0.0016129 | -2.7786 | -2.4399 | -4.216 | -3.067 | -3.241 | -4.422 | -3.3463 | 0.53101 | 119.0918 | -4.2938 | 119.0323 | -3.9322 | -4.0924 | -3.9597 | -0.10528 | -121.5225 | -122.1497 | 0.86975 | 0.76447 | -0.31128 | 0.86975 | -0.20599 | -0.1831 | 0.009155 | -0.050354 | 0.17853 | 0.15106 | 0.018311 | 0.33417 | 0.20142 | 0.97504 | 1.149 | 0.36163 | 123.3261 | 1.7761 | 123.3856 | 1.6708 | 123.2025 | -123.2986 | -123.3765 | 1.0437 | 123.143 | 1.3321 | 4.6417
1186.5469 | 123.2025 | -2.8656 | 120.2637 | 0.018616 | 0.0037661 | -0.0041529 | -0.00018368 | 0.0019077 | 0.00071138 | -0.0043707 | 0.071381 | 0.00010888 | 0.08223 | 0.0652 | -0.0043066 | -0.0059344 | -0.0011855 | -1.7944 | -1.5472 | -2.9343 | -1.8494 | -1.6479 | -2.7283 | -1.7166 | 0.92468 | 120.4285 | -2.9114 | 120.3918 | -2.774 | -2.6962 | -2.5726 | -0.068664 | -121.8109 | -122.113 | 1.2177 | 1.149 | 0.13733 | 1.2177 | 0.20599 | -0.045776 | 0.16479 | 0.12817 | 0.091553 | 0.29297 | 0.16937 | 0.33874 | 0.21515 | 1.2863 | 1.0849 | 0.13733 | 123.3032 | 1.387 | 123.3398 | 1.3184 | 123.2941 | -123.1979 | -123.175 | 1.0162 | 123.2574 | 1.0712 | 3.7903
1187.4844 | 123.1338 | -4.0787 | 119.0643 | -0.11108 | 0.0048343 | -9.4056e-05 | 0.0028069 | 0.0025485 | 0.0039158 | -0.0011663 | -0.05069 | 0.00053628 | 0.081375 | 0.058578 | -0.002384 | -0.00059378 | 0.0022323 | -2.6688 | -2.3209 | -4.2709 | -2.7328 | -2.7924 | -4.2984 | -2.4445 | 0.57678 | 119.1925 | -4.2114 | 119.0186 | -3.9368 | -4.0833 | -3.9642 | -0.19226 | -121.3852 | -121.7972 | 1.2863 | 1.6342 | -0.21973 | 1.8265 | -0.027466 | -0.13275 | 0.12817 | -0.045776 | 0.14191 | 0.11444 | -0.004578 | 0.24719 | 0.12817 | 1.4786 | 1.5381 | 0.27466 | 123.23 | 1.9501 | 123.4039 | 1.7578 | 123.2712 | -123.3353 | -123.2758 | 1.3458 | 123.0972 | 1.4099 | 4.6555
1188.5469 | 123.1842 | -4.0741 | 119.0506 | -0.042419 | 0.0050479 | -0.0013757 | 0.00088432 | 0.0012667 | 0.0019932 | -0.0028753 | 0.05307 | 0.00074988 | 0.081375 | 0.066695 | -0.0028112 | -0.00080758 | -0.0026809 | -2.5314 | -2.2522 | -4.2297 | -2.5681 | -2.3849 | -4.0054 | -2.4582 | 0.70953 | 119.2017 | -4.1702 | 119.0598 | -3.8727 | -4.0009 | -3.923 | -0.15564 | -121.3028 | -121.6187 | 1.6891 | 1.6159 | 0.068665 | 1.7715 | 0.2243 | -0.09613 | 0.15106 | 0.009155 | 0.20142 | 0.15106 | 0.073243 | 0.24719 | 0.16937 | 1.8448 | 1.6617 | 0.29755 | 123.23 | 1.9775 | 123.3719 | 1.8219 | 123.2758 | -123.2803 | -123.2208 | 1.506 | 123.1338 | 1.5427 | 4.7836
1189.4844 | 123.1247 | -4.0054 | 119.1422 | -0.0042723 | 0.0035525 | -9.4056e-05 | 0.0038751 | -0.0019377 | -0.00035682 | 0.00075627 | -0.075104 | 0.0013907 | 0.08223 | 0.073745 | -0.0015296 | -0.0010212 | -0.0028945 | -2.5085 | -2.1698 | -4.1702 | -2.6413 | -2.4994 | -4.0833 | -2.5497 | 0.51727 | 119.2841 | -4.1473 | 119.1101 | -3.8727 | -4.0283 | -3.8864 | -0.16479 | -121.312 | -121.7834 | 1.506 | 1.4557 | -0.07782 | 1.6205 | 0.086975 | -0.14191 | 0.14191 | -0.032044 | 0.13275 | 0.11902 | -0.022888 | 0.26092 | 0.11902 | 1.6708 | 1.5289 | 0.27466 | 123.2574 | 2.0004 | 123.4314 | 1.8356 | 123.2895 | -123.3124 | -123.2895 | 1.3641 | 123.1155 | 1.4969 | 4.5227
1190.4844 | 123.143 | -4.3991 | 118.7531 | 0.0033567 | 0.0039799 | -0.0030847 | 0.0023797 | -0.0012967 | 0.002634 | -0.0026617 | -0.038483 | 0.00053628 | 0.081589 | 0.068831 | -0.002384 | 4.7018e-05 | 0.0020187 | -2.9343 | -2.6596 | -4.5639 | -3.0579 | -2.8931 | -4.4266 | -2.9205 | 0.65918 | 118.8858 | -4.5181 | 118.7393 | -4.2664 | -4.3945 | -4.2297 | -0.16479 | -121.4127 | -121.8109 | 1.506 | 1.4786 | -0.027466 | 1.6434 | 0.13733 | -0.11902 | 0.13275 | -0.013733 | 0.13275 | 0.16937 | 0.004578 | 0.28839 | 0.1236 | 1.6708 | 1.506 | 0.25177 | 123.2574 | 1.9043 | 123.4039 | 1.7395 | 123.2849 | -123.317 | -123.2712 | 1.3412 | 123.1384 | 1.4648 | 5.0583
1191.4844 | 123.0927 | -2.6047 | 120.6024 | -0.072937 | 0.0039799 | -0.00030766 | 0.0019525 | 0.0012667 | 0.0011386 | -0.00052553 | -0.047638 | 0.0011771 | 0.086716 | 0.070113 | -0.000675 | -0.00038018 | -0.00097194 | -1.7029 | -1.3184 | -2.7466 | -1.8402 | -1.6891 | -2.7191 | -1.7212 | 0.9201 | 120.7489 | -2.742 | 120.5063 | -2.4399 | -2.5818 | -2.4307 | -0.14191 | -121.9208 | -122.4426 | 0.91553 | 0.88348 | -0.11444 | 1.0254 | 0.027466 | -0.13733 | 0.14648 | -0.09613 | 0.16479 | 0.17395 | 0.022888 | 0.31128 | 0.16022 | 1.0574 | 0.90637 | 0.30212 | 123.2483 | 1.4282 | 123.4909 | 1.2863 | 123.3536 | -123.349 | -123.3444 | 0.76446 | 123.111 | 0.90179 | 3.5248
1192.5469 | 123.1064 | -2.9434 | 120.2957 | -0.03479 | 0.0024845 | -0.0020167 | 0.00067072 | -0.0023649 | 0.0013522 | -0.00031193 | 0.031708 | 0.00032248 | 0.083725 | 0.064345 | -0.0021704 | -0.0014484 | 0.00052346 | -1.8951 | -1.5564 | -3.067 | -1.9958 | -1.8219 | -2.9846 | -1.8906 | 0.31586 | 120.3918 | -3.0533 | 120.1675 | -2.7466 | -2.8793 | -2.8015 | -0.1236 | -121.8521 | -122.2916 | 1.1215 | 1.0529 | -0.041199 | 1.1765 | 0.082398 | -0.10986 | 0.096131 | -0.12817 | 0.19684 | 0.14191 | 0.064087 | 0.25177 | 0.17395 | 1.2451 | 1.0712 | 0.3067 | 123.2208 | 1.5106 | 123.4451 | 1.387 | 123.3353 | -123.3627 | -123.349 | 0.94757 | 123.111 | 1.0483 | 3.2593
1193.4844 | 123.1476 | -2.6871 | 120.4697 | -0.050049 | 0.0037661 | -0.0026575 | 0.0034479 | -0.00044226 | 0.00049778 | 0.00075627 | -0.05069 | 0.0033133 | 0.08458 | 0.0652 | -0.0008886 | -0.0010212 | 0.00030966 | -1.9089 | -1.5427 | -3.067 | -1.8723 | -1.8356 | -2.7832 | -1.4969 | 0.28381 | 120.6802 | -2.7557 | 120.4422 | -2.5269 | -2.6642 | -2.5452 | -0.37994 | -122.0123 | -122.3419 | 0.85144 | 1.1902 | -0.09613 | 1.5701 | 0.28381 | -0.068664 | 0.21057 | -0.027466 | 0.16022 | 0.14191 | 0.022888 | 0.21057 | 0.091552 | 1.2314 | 1.1948 | 0.22888 | 123.1979 | 1.5244 | 123.436 | 1.1444 | 123.3673 | -123.5367 | -123.2254 | 0.81482 | 123.1293 | 0.7782 | 2.9709
1194.5469 | 123.1613 | -2.7008 | 120.4926 | 0.026245 | 0.0018435 | -0.0030847 | 0.0043023 | -0.0021513 | 0.0017794 | -0.00073913 | 0.028656 | 0.0020315 | 0.082871 | 0.064773 | -0.003025 | -0.0023028 | -0.0013991 | -1.7715 | -1.3916 | -2.8381 | -1.8951 | -1.7578 | -2.7557 | -1.7761 | 0.07782 | 120.5978 | -2.8519 | 120.4376 | -2.4994 | -2.6413 | -2.5452 | -0.13733 | -121.8842 | -122.3877 | 0.94299 | 0.92468 | -0.054931 | 1.062 | 0.082398 | -0.15106 | 0.10528 | -0.054932 | 0.20142 | 0.15564 | 0.05951 | 0.3067 | 0.21057 | 1.0803 | 0.94299 | 0.35248 | 123.2895 | 1.4465 | 123.4497 | 1.3092 | 123.2986 | -123.3307 | -123.3444 | 0.80566 | 123.1384 | 0.92926 | 2.7786
1195.4844 | 123.1155 | -2.6825 | 120.52 | -0.065308 | 0.0018435 | -0.0026575 | 0.0043023 | 0.0044711 | 0.002634 | -0.00031193 | -0.16971 | 0.00010888 | 0.079666 | 0.063491 | -0.001316 | -0.001662 | 0.00030966 | -1.7853 | -1.4328 | -2.8519 | -1.9089 | -1.7853 | -2.8061 | -1.8173 | 0.48981 | 120.6482 | -2.8198 | 120.4605 | -2.504 | -2.6917 | -2.5909 | -0.16937 | -121.9528 | -122.4289 | 0.89722 | 0.86517 | -0.1236 | 1.0345 | 0.045777 | -0.13733 | 0.12817 | -0.05951 | 0.17853 | 0.091553 | -0.009155 | 0.22888 | 0.12817 | 1.0666 | 0.94299 | 0.31586 | 123.2803 | 1.4191 | 123.468 | 1.2497 | 123.3307 | -123.3719 | -123.3398 | 0.77362 | 123.143 | 0.89722 | 3.1723
1196.5469 | 123.1613 | -2.5772 | 120.5978 | 0.033875 | 0.0037661 | -0.0037257 | 0.0021661 | 0.00062594 | 0.0032748 | -0.0024481 | -0.0079652 | 0.0011771 | 0.083512 | 0.066268 | -0.0017432 | -0.003371 | -0.0058853 | -1.7258 | -1.3687 | -2.7603 | -1.8402 | -1.7029 | -2.6367 | -1.7212 | 0.1236 | 120.7123 | -2.7328 | 120.5887 | -2.3529 | -2.504 | -2.417 | -0.18311 | -121.9666 | -122.438 | 0.87433 | 0.85602 | -0.05951 | 1.0391 | 0.1236 | -0.15564 | 0.11444 | -0.009155 | 0.2243 | 0.16022 | 0.073242 | 0.31586 | 0.22888 | 1.0574 | 0.9201 | 0.37994 | 123.3215 | 1.3916 | 123.4451 | 1.2085 | 123.2895 | -123.3582 | -123.3307 | 0.737 | 123.1659 | 0.85144 | 2.7008
1197.4844 | 123.1155 | -2.5635 | 120.6436 | -0.057678 | 0.0029117 | -0.0039393 | 0.0025933 | 0.00019874 | -0.00035682 | 0.0026789 | -0.05069 | 0.0020315 | 0.082657 | 0.07054 | -0.002384 | 0.001756 | -0.0013991 | -1.7532 | -1.4053 | -2.7649 | -1.8768 | -1.7395 | -2.6871 | -1.767 | 0.18768 | 120.7397 | -2.7191 | 120.5429 | -2.4445 | -2.5864 | -2.449 | -0.20142 | -122.0489 | -122.5204 | 0.82397 | 0.79651 | -0.1236 | 0.99792 | 0.07782 | -0.15564 | 0.09613 | -0.10071 | 0.11902 | 0.11444 | -0.022888 | 0.27008 | 0.13275 | 1.0254 | 0.88806 | 0.27466 | 123.262 | 1.3596 | 123.4589 | 1.1581 | 123.3032 | -123.4085 | -123.3627 | 0.68665 | 123.1064 | 0.81024 | 2.7512
1198.4844 | 123.1659 | -2.5818 | 120.6162 | -0.057678 | 0.0046207 | -0.0035119 | 0.0043023 | 0.0019077 | 0.0013522 | -0.0015935 | -0.026276 | 0.0024589 | 0.082657 | 0.069045 | -0.0015296 | -0.0020892 | -0.00097194 | -1.6479 | -1.3367 | -2.6367 | -1.7853 | -1.6342 | -2.6047 | -1.6937 | 0.64087 | 120.7443 | -2.7237 | 120.5658 | -2.4124 | -2.5543 | -2.4261 | -0.054932 | -121.9528 | -122.4014 | 0.94757 | 0.88806 | -0.022888 | 0.94299 | 0.032044 | -0.14191 | 0.12817 | -0.050354 | 0.16937 | 0.15564 | 0.027466 | 0.29755 | 0.16937 | 1.0025 | 0.85144 | 0.31128 | 123.2895 | 1.3 | 123.468 | 1.2451 | 123.3261 | -123.2529 | -123.3398 | 0.79651 | 123.1476 | 0.93384 | 3.2227
1199.4844 | 123.1476 | -2.8107 | 120.3827 | 0.049133 | 0.0059025 | -0.0026575 | 0.0021661 | 0.0036165 | 0.0019932 | 0.00011527 | -0.044586 | 0.0011771 | 0.083298 | 0.064986 | -0.0008886 | -0.0027302 | -0.00033114 | -1.8631 | -1.5152 | -2.9663 | -2.005 | -1.8585 | -2.9205 | -1.8723 | 0.7782 | 120.5154 | -2.9434 | 120.3369 | -2.6505 | -2.7924 | -2.655 | -0.15564 | -121.8979 | -122.3877 | 0.95215 | 0.93842 | -0.10986 | 1.0941 | 0.045777 | -0.13275 | 0.13275 | -0.045776 | 0.16022 | 0.15564 | 0.018311 | 0.28839 | 0.15106 | 1.1078 | 0.9613 | 0.29297 | 123.2803 | 1.4511 | 123.4589 | 1.2955 | 123.3261 | -123.349 | -123.3261 | 0.80566 | 123.1476 | 0.94757 | 3.5889
1200.4844 | 123.1201 | -2.4673 | 120.7352 | -0.057678 | 0.0067569 | -0.0037257 | 0.0034479 | 0.0025485 | 0.00071138 | -0.0013799 | -0.014069 | 0.00096348 | 0.081803 | 0.072036 | -0.002384 | -0.00038018 | -0.00054474 | -1.6617 | -1.2909 | -2.5955 | -1.7899 | -1.6571 | -2.5818 | -1.6891 | 1.3641 | 120.8633 | -2.6138 | 120.639 | -2.3071 | -2.4628 | -2.3346 | -0.12817 | -122.0261 | -122.525 | 0.81024 | 0.7782 | -0.11444 | 0.90637 | 0.013733 | -0.14648 | 0.12817 | -0.09613 | 0.16022 | 0.13275 | 0.004577 | 0.27924 | 0.15106 | 0.93842 | 0.80566 | 0.3067 | 123.2529 | 1.3046 | 123.4772 | 1.1765 | 123.3307 | -123.3307 | -123.349 | 0.67749 | 123.1064 | 0.80566 | 3.8315
1201.4844 | 123.1201 | -2.7191 | 120.4559 | -0.011902 | 0.0035525 | -0.0035119 | 0.0017389 | -0.00065586 | -0.00057042 | -0.0011663 | 0.11716 | 0.00096348 | 0.085221 | 0.066482 | -0.000675 | -0.0018756 | -0.00097194 | -1.8127 | -1.4465 | -2.8519 | -1.9089 | -1.7395 | -3.035 | -1.8036 | 0.97504 | 120.6116 | -2.8198 | 120.433 | -2.5635 | -2.6688 | -2.5543 | -0.13275 | -121.9025 | -122.3648 | 0.97961 | 0.91553 | -0.31586 | 1.0483 | -0.1831 | -0.10071 | 0.15564 | -0.022889 | 0.15564 | 0.1648 | 0.050354 | 0.2655 | 0.15106 | 1.1124 | 0.94299 | 0.25635 | 123.2529 | 1.4053 | 123.4314 | 1.2726 | 123.3307 | -123.3078 | -123.2758 | 0.81024 | 123.1522 | 0.90637 | 3.6942
1202.5469 | 123.1613 | -2.7466 | 120.4697 | -0.065308 | -7.913e-05 | -0.0039393 | -0.00061088 | -0.0030057 | 0.0019932 | -0.0020209 | 0.010345 | 0.0020315 | 0.082016 | 0.0652 | -0.0017432 | -0.0012348 | -0.00011754 | -1.8768 | -1.4877 | -2.9388 | -1.9913 | -1.8082 | -2.8427 | -1.8219 | 0.97961 | 120.5154 | -2.9297 | 120.4651 | -2.3895 | -2.8381 | -2.7374 | -0.19226 | -121.9574 | -122.4609 | 0.93841 | 0.92468 | -0.09613 | 1.1169 | 0.096131 | -0.1831 | 0.045776 | -0.004578 | 0.35706 | 0.009155 | -0.091553 | 0.19226 | 0.091552 | 1.1307 | 0.94757 | 0.54016 | 123.3948 | 1.4511 | 123.4451 | 1.2589 | 123.262 | -123.4085 | -123.3994 | 0.75531 | 123.2117 | 0.86975 | 3.7262
1203.4844 | 123.1293 | -2.3895 | 120.813 | -0.088196 | 0.0044071 | -0.0039393 | 0.0010981 | -0.00044226 | -0.00014322 | -9.8328e-05 | -0.041534 | 0.0026725 | 0.083298 | 0.067977 | -0.0034522 | -0.0010212 | -0.00097194 | -1.6159 | -1.2589 | -2.536 | -1.6937 | -1.5427 | -2.4078 | -1.5793 | 1.3 | 120.9778 | -2.4719 | 120.7764 | -2.2568 | -2.3895 | -2.2476 | -0.14648 | -122.0718 | -122.5067 | 0.84686 | 0.81024 | -0.018311 | 0.95673 | 0.12817 | -0.082398 | 0.16479 | -0.036621 | 0.13275 | 0.14191 | 0 | 0.2243 | 0.082398 | 0.99335 | 0.84228 | 0.21515 | 123.2483 | 1.2772 | 123.4497 | 1.1307 | 123.3673 | -123.349 | -123.2849 | 0.6958 | 123.1659 | 0.77362 | 3.6896
1204.4844 | 123.1384 | -2.5177 | 120.6528 | -0.050049 | 0.0022709 | -0.0026575 | 0.0038751 | 0.0023349 | 0.0011386 | 0.0028925 | -0.032379 | 0.0035269 | 0.081589 | 0.072249 | -0.0025976 | -0.001662 | -0.0013991 | -1.6296 | -1.3229 | -2.623 | -1.7624 | -1.6067 | -2.5497 | -1.6754 | 2.0187 | 120.845 | -2.6093 | 120.6253 | -2.3575 | -2.5131 | -2.3712 | -0.10529 | -121.9757 | -122.4152 | 0.91095 | 0.84228 | -0.032044 | 0.94757 | 0.073242 | -0.091553 | 0.19226 | -0.027466 | 0.16022 | 0.14648 | 0.004577 | 0.23804 | 0.09613 | 1.0162 | 0.8606 | 0.25177 | 123.2346 | 1.3 | 123.4543 | 1.1948 | 123.3627 | -123.2758 | -123.262 | 0.75531 | 123.143 | 0.88806 | 4.5364
1205.4844 | 123.0972 | -2.3712 | 120.8771 | -0.050049 | 0.0039799 | -0.0037257 | 0.0036615 | -0.0010831 | 0.0015658 | 0.00054267 | -0.038483 | 0.00074988 | 0.083939 | 0.071609 | -0.0028112 | 0.0015424 | 0.0030869 | -1.5884 | -1.2497 | -2.5223 | -1.7029 | -1.5884 | -2.4857 | -1.6022 | 0.74158 | 120.9595 | -2.4948 | 120.7672 | -2.2247 | -2.3666 | -2.2202 | -0.15106 | -122.1268 | -122.58 | 0.78278 | 0.76904 | -0.11444 | 0.9201 | 0.036621 | -0.1236 | 0.082398 | -0.10986 | 0.14649 | 0.15106 | 0.004578 | 0.27466 | 0.12817 | 0.93384 | 0.8194 | 0.27008 | 123.262 | 1.2726 | 123.4543 | 1.1215 | 123.3307 | -123.3994 | -123.3719 | 0.66833 | 123.1384 | 0.78278 | 3.1128
1206.5469 | 123.2483 | -2.4811 | 120.6711 | -0.050049 | 0.0029117 | -0.0039393 | 0.0013117 | -0.00044226 | 0.0028476 | -0.0028753 | 0.089691 | 0.00010888 | 0.083084 | 0.066695 | -0.0032386 | -0.00080758 | -0.0026809 | -1.6296 | -1.355 | -2.623 | -1.712 | -1.5427 | -2.4811 | -1.561 | 0.80566 | 120.7443 | -2.623 | 120.726 | -2.2064 | -2.3529 | -2.2614 | -0.14191 | -122.0261 | -122.3831 | 0.93841 | 0.9201 | 0 | 1.062 | 0.14191 | -0.14191 | 0.073242 | 0.054931 | 0.27466 | 0.21973 | 0.12817 | 0.36163 | 0.27008 | 1.0803 | 0.91095 | 0.41656 | 123.349 | 1.268 | 123.3673 | 1.1261 | 123.2254 | -123.2941 | -123.2941 | 0.76904 | 123.2071 | 0.85144 | 3.2867
1207.4844 | 123.0057 | -2.2797 | 120.9412 | -0.027161 | 0.0052615 | -0.0020167 | 0.0030207 | 0.00083954 | -0.00014322 | -0.00095273 | -0.059845 | 0.0026725 | 0.083512 | 0.062423 | -0.0011022 | -0.00038018 | 0.0041551 | -1.5564 | -1.1993 | -2.4673 | -1.6846 | -1.5472 | -2.4216 | -1.5884 | 0.032043 | 121.0373 | -2.4261 | 120.8588 | -2.1515 | -2.3117 | -2.0782 | -0.18768 | -122.1405 | -122.6257 | 0.73242 | 0.69122 | -0.14191 | 0.87891 | 0.045776 | -0.14648 | 0.09613 | -0.082397 | 0.12817 | 0.20142 | -0.032044 | 0.3479 | 0.11444 | 0.9201 | 0.78278 | 0.27466 | 123.2849 | 1.268 | 123.4634 | 1.0803 | 123.317 | -123.4085 | -123.3673 | 0.59509 | 123.1384 | 0.72327 | 2.3117
1208.4844 | 123.1522 | -2.3117 | 120.8633 | -0.019531 | 0.0056889 | -0.0024439 | 0.0040887 | 0.00062594 | -0.0014248 | -0.0013799 | -0.078156 | 0.0020315 | 0.083512 | 0.074172 | -0.0017432 | -0.0012348 | 0.0018051 | -1.5289 | -1.2085 | -2.4582 | -1.6159 | -1.3504 | -2.3026 | -1.4145 | 0.091553 | 121.0327 | -2.4078 | 120.8771 | -2.0966 | -2.2385 | -2.1332 | -0.14648 | -122.0718 | -122.4792 | 0.9613 | 0.89722 | 0.009156 | 1.0437 | 0.15564 | -0.09613 | 0.16937 | 0.013733 | 0.21515 | 0.17853 | 0.073243 | 0.27466 | 0.16937 | 1.1078 | 0.84228 | 0.31128 | 123.2849 | 1.2497 | 123.4406 | 1.1032 | 123.3444 | -123.3215 | -123.2712 | 0.6958 | 123.1888 | 0.78278 | 2.4033
1209.5469 | 123.2208 | -2.3117 | 120.8542 | -0.042419 | 0.0046207 | -0.00073486 | 0.0019525 | -0.0012967 | -0.00099762 | -0.00031193 | 0.050018 | -0.0011727 | 0.084152 | 0.066268 | -0.0011022 | -0.001662 | 0.0030869 | -1.5244 | -1.2817 | -2.4857 | -1.5976 | -1.4282 | -2.2934 | -1.474 | 0.76904 | 120.9366 | -2.4673 | 120.845 | -2.0645 | -2.2064 | -2.1332 | -0.17395 | -122.1359 | -122.4518 | 0.88348 | 0.83771 | 0.018311 | 1.0117 | 0.19226 | -0.15564 | 0.082397 | -0.009155 | 0.24719 | 0.17853 | 0.10529 | 0.33417 | 0.26092 | 1.0574 | 0.88806 | 0.40283 | 123.3124 | 1.2039 | 123.4039 | 1.03 | 123.2483 | -123.3398 | -123.3215 | 0.71411 | 123.1567 | 0.78735 | 3.0808
1210.4844 | 123.1888 | -2.6596 | 120.5658 | 0.033875 | 0.0037661 | -0.0060755 | 0.0047295 | 0.0023349 | 0.002634 | -0.00073913 | -0.011017 | -0.00031832 | 0.083725 | 0.061782 | -0.0015296 | -0.0023028 | -0.0018265 | -1.7303 | -1.4465 | -2.7649 | -1.8585 | -1.6983 | -2.6047 | -1.7487 | 0.022888 | 120.7031 | -2.7557 | 120.4926 | -2.4353 | -2.5726 | -2.449 | -0.10529 | -122.0123 | -122.4243 | 0.9613 | 0.91095 | 0.054932 | 1.0162 | 0.16022 | -0.09613 | 0.13733 | -0.073242 | 0.2243 | 0.21057 | 0.086975 | 0.3067 | 0.1831 | 1.0666 | 0.90637 | 0.32043 | 123.2483 | 1.3184 | 123.4589 | 1.2131 | 123.3627 | -123.3307 | -123.3215 | 0.80109 | 123.1522 | 0.92926 | 2.6825
1211.4844 | 123.1613 | -2.5314 | 120.6573 | -0.050049 | 0.0033389 | -0.0011621 | 0.0038751 | 0.0010531 | 0.00049778 | -0.00052553 | -0.032379 | 0.0011771 | 0.082871 | 0.068404 | -0.0025976 | 0.0015424 | -0.0050307 | -1.4648 | -1.2772 | -2.6001 | -1.7075 | -1.5427 | -2.5314 | -1.6159 | 0.050354 | 120.8176 | -2.6505 | 120.6711 | -2.3758 | -2.4994 | -2.3621 | -0.068665 | -121.9345 | -122.3648 | 0.98877 | 0.91553 | 0 | 0.98419 | 0.068665 | -0.11902 | 0.16022 | 0.013733 | 0.15564 | 0.16937 | 0.032043 | 0.28839 | 0.15106 | 1.0574 | 0.89264 | 0.27466 | 123.3215 | 1.3229 | 123.468 | 1.2543 | 123.349 | -123.2574 | -123.3078 | 0.82397 | 123.2025 | 1.0666 | 2.5818
1212.5469 | 123.2025 | -2.3895 | 120.7993 | 0.0033567 | 0.0016299 | -0.0037257 | 0.00045712 | -0.0021513 | 0.00092498 | -0.00073913 | 0.056122 | -0.00074552 | 0.083298 | 0.061782 | -0.002384 | -0.0018756 | 0.00095066 | -1.5244 | -1.2543 | -2.5726 | -1.5656 | -1.3824 | -2.3575 | -1.442 | 0.10071 | 120.9137 | -2.504 | 120.7993 | -2.1469 | -2.298 | -2.179 | -0.18311 | -122.0535 | -122.3648 | 1.0071 | 0.94757 | 0.032043 | 1.1307 | 0.21515 | -0.11444 | 0.11444 | 0 | 0.24261 | 0.21057 | 0.091552 | 0.32501 | 0.20599 | 1.1902 | 1.0071 | 0.35705 | 123.3032 | 1.3184 | 123.4177 | 1.1353 | 123.3032 | -123.3719 | -123.3032 | 0.82397 | 123.1888 | 0.86517 | 2.4902
1213.4844 | 123.1155 | -2.4948 | 120.7581 | -0.019531 | 0.0037661 | -0.0020167 | 0.0017389 | 0.0021213 | 7.0582e-05 | -0.00052553 | -0.069 | -0.00010472 | 0.08458 | 0.063705 | -0.0038794 | 0.00026062 | -0.00011754 | -1.6251 | -1.3229 | -2.6779 | -1.7349 | -1.6342 | -2.5864 | -1.6617 | -0.054932 | 120.845 | -2.6367 | 120.6436 | -2.3392 | -2.4902 | -2.3575 | -0.1831 | -122.081 | -122.493 | 0.8606 | 0.83313 | -0.091553 | 1.0162 | 0.091552 | -0.14191 | 0.086975 | -0.11444 | 0.15564 | 0.13733 | 0.004578 | 0.27924 | 0.14648 | 1.0437 | 0.94299 | 0.29755 | 123.2803 | 1.355 | 123.4818 | 1.1719 | 123.3398 | -123.436 | -123.3948 | 0.75989 | 123.1384 | 0.86975 | 2.4399
1214.4844 | 123.1705 | -2.2934 | 120.9091 | 0.026245 | 0.0037661 | -0.0037257 | 0.0036615 | -0.0023649 | 7.0582e-05 | 0.00011527 | -0.020172 | 0.0020315 | 0.083939 | 0.064559 | -0.0032386 | -0.00016658 | 0.0028733 | -1.4557 | -1.1627 | -2.4261 | -1.5976 | -1.4191 | -2.3117 | -1.474 | 0.059509 | 121.0785 | -2.417 | 120.8679 | -2.1011 | -2.2339 | -2.124 | -0.13275 | -122.0718 | -122.5067 | 0.87433 | 0.8194 | -0.018311 | 0.95215 | 0.11444 | -0.1236 | 0.16937 | -0.041199 | 0.19226 | 0.16937 | 0.059509 | 0.29297 | 0.1831 | 1.0071 | 0.82855 | 0.31586 | 123.2849 | 1.2634 | 123.4955 | 1.1307 | 123.3719 | -123.3353 | -123.3261 | 0.6958 | 123.1613 | 0.83771 | 2.3529
1215.5469 | 123.1796 | -2.4124 | 120.8267 | 0.041504 | 0.0026981 | -0.0050073 | 0.0013117 | 0.0021213 | 0.00092498 | -0.0024481 | -0.023224 | 0.0011771 | 0.083084 | 0.066268 | -0.003025 | 4.7018e-05 | -0.00054474 | -1.5701 | -1.2634 | -2.6001 | -1.7166 | -1.5472 | -2.4628 | -1.561 | 0.022888 | 120.9091 | -2.5497 | 120.7855 | -2.1652 | -2.33 | -2.2293 | -0.18768 | -122.0901 | -122.5433 | 0.86517 | 0.85144 | -0.050354 | 1.0391 | 0.13733 | -0.13733 | 0.082398 | -0.041199 | 0.24719 | 0.18311 | 0.082398 | 0.32043 | 0.21973 | 1.0529 | 0.88348 | 0.38452 | 123.3353 | 1.3367 | 123.4589 | 1.149 | 123.3215 | -123.4268 | -123.3765 | 0.6958 | 123.1979 | 0.84229 | 2.4353
1216.4844 | 123.1705 | -2.1149 | 121.0876 | 0.026245 | 0.00034827 | -0.0020167 | 0.0025933 | -0.0010831 | 7.0582e-05 | -0.0015935 | -0.011017 | 0.0030997 | 0.083084 | 0.061568 | -0.0011022 | -0.0010212 | 0.0030869 | -1.3824 | -1.03 | -2.2522 | -1.5152 | -1.3504 | -2.1561 | -1.3916 | -0.009155 | 121.2296 | -2.2705 | 121.0464 | -1.9135 | -2.0554 | -1.9638 | -0.13733 | -122.1176 | -122.6028 | 0.76446 | 0.72327 | -0.041199 | 0.86059 | 0.09613 | -0.15564 | 0.14191 | -0.041198 | 0.20142 | 0.15106 | 0.059509 | 0.3067 | 0.21515 | 0.90179 | 0.737 | 0.35706 | 123.317 | 1.2222 | 123.5001 | 1.0849 | 123.3444 | -123.3398 | -123.3582 | 0.59967 | 123.1613 | 0.73242 | 2.1057
1217.5469 | 123.2666 | -2.3941 | 120.7581 | -0.3476 | 0.0041935 | -0.00073486 | 0.00088432 | -0.0017239 | 0.0011386 | -0.00095273 | 0.05307 | -0.00031832 | 0.083939 | 0.063491 | -0.001316 | -0.003371 | -0.0018265 | -1.6388 | -1.1856 | -2.504 | -1.68 | -1.5015 | -2.4307 | -1.5244 | 0.068665 | 120.845 | -2.6093 | 120.7764 | -2.1561 | -2.298 | -2.211 | -0.10986 | -121.9437 | -122.438 | 0.89264 | 0.86975 | -0.036621 | 0.97961 | 0.073242 | -0.21515 | 0.086975 | 0.01831 | 0.23804 | 0.1831 | 0.09613 | 0.39825 | 0.31128 | 1.0025 | 0.82397 | 0.45319 | 123.3856 | 1.3184 | 123.4543 | 1.2085 | 123.2391 | -123.262 | -123.3673 | 0.71411 | 123.1705 | 0.75531 | 2.4628
1218.4844 | 123.1842 | -2.7603 | 120.488 | 0.064392 | 0.0050479 | -0.0032983 | 0.0030207 | 0.0021213 | -0.00035682 | 0.00011527 | -0.011017 | 0.0020315 | 0.082657 | 0.069686 | -0.0034522 | -0.0010212 | -0.0013991 | -1.799 | -1.4465 | -2.9526 | -1.8677 | -1.7258 | -2.7832 | -1.7441 | 0.022888 | 120.5658 | -2.8976 | 120.4285 | -2.536 | -2.7054 | -2.5635 | -0.19226 | -121.9345 | -122.3557 | 1.0345 | 1.0162 | -0.022888 | 1.2085 | 0.16937 | -0.13733 | 0.07782 | -0.059509 | 0.2243 | 0.19684 | 0.054932 | 0.33417 | 0.19226 | 1.2268 | 1.0849 | 0.36163 | 123.3261 | 1.506 | 123.4634 | 1.3138 | 123.3261 | -123.4406 | -123.3856 | 0.89264 | 123.1888 | 0.9613 | 2.7832
1219.5469 | 123.1705 | -2.623 | 120.5658 | 0.041504 | 0.0014163 | -0.0032983 | 0.00067072 | -0.0032193 | 0.00092498 | -0.0015935 | -0.014069 | 0.0022453 | 0.082444 | 0.064773 | -0.0028112 | -0.0012348 | 0.0037277 | -1.6525 | -1.3138 | -2.7283 | -1.8173 | -1.6571 | -2.6321 | -1.6937 | -0.022888 | 120.7306 | -2.7374 | 120.5429 | -2.417 | -2.5589 | -2.4719 | -0.10528 | -121.8796 | -122.3831 | 0.96588 | 0.92926 | -0.009155 | 1.0345 | 0.09613 | -0.11444 | 0.16479 | -0.022888 | 0.20599 | 0.15106 | 0.064087 | 0.2655 | 0.17853 | 1.0712 | 0.91095 | 0.32043 | 123.2803 | 1.4145 | 123.468 | 1.3092 | 123.3536 | -123.2941 | -123.3032 | 0.80566 | 123.1659 | 0.97046 | 2.6001
1220.4844 | 123.175 | -2.4948 | 120.7352 | 0.026245 | 0.0033389 | -0.0026575 | 0.0013117 | 0.0016939 | 0.0030612 | -0.0015935 | -0.020172 | 0.00096348 | 0.084793 | 0.066909 | 0.0006066 | -0.0027302 | 0.00052346 | -1.6113 | -1.2314 | -2.6093 | -1.712 | -1.5747 | -2.5085 | -1.593 | 0.004578 | 120.8908 | -2.5909 | 120.7077 | -2.2476 | -2.4216 | -2.33 | -0.11444 | -121.9666 | -122.4472 | 0.9201 | 0.90179 | -0.013733 | 1.0162 | 0.10071 | -0.09613 | 0.15564 | -0.027465 | 0.24719 | 0.1648 | 0.073242 | 0.26093 | 0.16937 | 1.0345 | 0.89722 | 0.34332 | 123.2986 | 1.3779 | 123.4818 | 1.2634 | 123.3856 | -123.3444 | -123.3261 | 0.78278 | 123.2025 | 0.88348 | 2.4994
1221.5469 | 123.1384 | -2.33 | 120.9091 | 0.0033567 | 0.0012027 | -0.0050073 | 0.0010981 | 0.0034029 | -0.0033474 | 0.00011527 | -0.0079652 | 0.0020315 | 0.082444 | 0.059859 | -0.0019568 | 0.002824 | 0.0024461 | -1.6022 | -1.181 | -2.5269 | -1.6434 | -1.4923 | -2.3529 | -1.5152 | 0.009155 | 121.0236 | -2.4994 | 120.7672 | -2.0782 | -2.3071 | -2.1973 | -0.19684 | -122.0901 | -122.5525 | 0.83771 | 0.81482 | -0.022888 | 1.0117 | 0.17395 | -0.16937 | 0.11444 | -0.14191 | 0.25177 | 0.13275 | 0.022888 | 0.30212 | 0.19226 | 1.0345 | 0.88348 | 0.42114 | 123.2666 | 1.3458 | 123.523 | 1.149 | 123.3536 | -123.436 | -123.4085 | 0.68664 | 123.0972 | 0.72784 | 2.3392
1222.4844 | 123.2071 | -2.5177 | 120.694 | -0.057678 | 0.0044071 | -0.0028711 | 0.0030207 | 0.00083954 | 0.0013522 | -0.0011663 | -0.01712 | 0.00074988 | 0.083298 | 0.066482 | -0.002384 | -0.0014484 | 0.00095066 | -1.6754 | -1.2863 | -2.6184 | -1.7532 | -1.5976 | -2.504 | -1.6342 | 0.054932 | 120.813 | -2.6642 | 120.6802 | -2.2797 | -2.4445 | -2.3438 | -0.10071 | -121.9803 | -122.4472 | 0.9201 | 0.88348 | 0.013733 | 0.98419 | 0.11444 | -0.14648 | 0.11902 | -0.013733 | 0.23804 | 0.17395 | 0.073242 | 0.32043 | 0.21973 | 1.0208 | 0.86517 | 0.38452 | 123.3444 | 1.3321 | 123.4772 | 1.2314 | 123.3307 | -123.3124 | -123.3582 | 0.76446 | 123.1979 | 0.84228 | 2.5726
1223.5469 | 123.2803 | -2.1561 | 121.0327 | -0.011902 | 0.0046207 | 0.00033334 | 0.0013117 | 0.0012667 | 7.0582e-05 | -0.0039435 | 0.050018 | 0.0011771 | 0.082016 | 0.06285 | -0.0036658 | -0.0014484 | -0.0063125 | -1.3687 | -1.1124 | -2.2888 | -1.4328 | -1.236 | -2.0874 | -1.2863 | 0.22888 | 121.1151 | -2.2751 | 121.1105 | -1.8265 | -1.9821 | -1.9226 | -0.13275 | -122.1451 | -122.4655 | 0.92011 | 0.86975 | 0.068665 | 1.0025 | 0.20142 | -0.11902 | 0.082397 | 0.07782 | 0.32959 | 0.23346 | 0.17395 | 0.35248 | 0.29297 | 1.0529 | 0.85602 | 0.44861 | 123.3856 | 1.1765 | 123.3902 | 1.0437 | 123.2712 | -123.3215 | -123.3078 | 0.72327 | 123.2666 | 0.78735 | 2.3849
1224.4844 | 123.1842 | -2.7145 | 120.4926 | 0.049133 | 0.0037661 | -0.0035119 | 0.0030207 | 0.0016939 | 0.00028418 | -0.00073913 | -0.029327 | 0.0016043 | 0.083939 | 0.067123 | -0.0021704 | 4.7018e-05 | 0.00073706 | -1.7853 | -1.442 | -2.8107 | -1.9226 | -1.7853 | -2.7466 | -1.8311 | 0.022888 | 120.639 | -2.8381 | 120.4605 | -2.504 | -2.6733 | -2.5543 | -0.09613 | -121.9345 | -122.4152 | 0.92926 | 0.88348 | -0.032043 | 0.97961 | 0.064087 | -0.1236 | 0.14648 | -0.032044 | 0.21057 | 0.16022 | 0.041199 | 0.28381 | 0.16479 | 1.0254 | 0.88806 | 0.33417 | 123.2986 | 1.3687 | 123.4772 | 1.2726 | 123.3536 | -123.3032 | -123.3307 | 0.79193 | 123.175 | 0.92926 | 2.7374
1225.5469 | 123.2025 | -2.4857 | 120.7443 | 0.026245 | 0.0041935 | -0.0028711 | 0.0038751 | 0.0027621 | 0.0022068 | 0.0011835 | -0.026276 | 0.0011771 | 0.082871 | 0.066695 | -0.0015296 | -0.001662 | -0.00097194 | -1.6571 | -1.3184 | -2.6779 | -1.767 | -1.6342 | -2.536 | -1.6388 | 0 | 120.8954 | -2.6184 | 120.6757 | -2.3117 | -2.449 | -2.3346 | -0.19226 | -122.0627 | -122.5113 | 0.85144 | 0.84686 | -0.050354 | 1.0391 | 0.14191 | -0.13275 | 0.15106 | -0.068665 | 0.17395 | 0.15106 | 0.036621 | 0.28381 | 0.16937 | 1.0437 | 0.91095 | 0.3067 | 123.2941 | 1.3596 | 123.5138 | 1.1673 | 123.381 | -123.4222 | -123.3627 | 0.71869 | 123.1613 | 0.82855 | 2.4857
1226.4844 | 123.1705 | -2.5681 | 120.6711 | 0.018616 | 0.0046207 | -0.0039393 | 0.0034479 | 0.00083954 | 0.0013522 | 0.00011527 | -0.011017 | 0.0011771 | 0.081803 | 0.067763 | 0.000393 | -0.0010212 | -0.0031081 | -1.7029 | -1.3458 | -2.7145 | -1.799 | -1.6891 | -2.5864 | -1.6891 | 0 | 120.8267 | -2.6825 | 120.5933 | -2.3758 | -2.5131 | -2.4353 | -0.14648 | -122.0169 | -122.4701 | 0.87891 | 0.87891 | -0.018311 | 1.0254 | 0.12817 | -0.11444 | 0.15564 | -0.07782 | 0.19226 | 0.13275 | 0.054931 | 0.24719 | 0.16937 | 1.0254 | 0.91553 | 0.3067 | 123.2758 | 1.3687 | 123.5092 | 1.2222 | 123.3948 | -123.3856 | -123.3536 | 0.76904 | 123.1613 | 0.86517 | 2.5681
1227.4844 | 123.1888 | -2.6688 | 120.6024 | -0.019531 | 0.0044071 | -0.0018031 | 0.0021661 | -1.486e-05 | 0.0015658 | 0.0024653 | -0.062897 | 0.0022453 | 0.084152 | 0.068831 | -0.0019568 | -0.00059378 | 0.00030966 | -1.7029 | -1.4511 | -2.8152 | -1.8311 | -1.6754 | -2.7145 | -1.7441 | 0.10529 | 120.6573 | -2.7969 | 120.5292 | -2.4673 | -2.6001 | -2.4399 | -0.14648 | -122.0535 | -122.4335 | 0.99335 | 0.92468 | -0.045777 | 1.0712 | 0.10071 | -0.12817 | 0.054932 | -0.073242 | 0.20142 | 0.22888 | 0.068664 | 0.35706 | 0.19684 | 1.1398 | 0.98419 | 0.32959 | 123.3261 | 1.3641 | 123.4543 | 1.2177 | 123.3261 | -123.4177 | -123.3994 | 0.83771 | 123.1979 | 0.96588 | 2.774
1228.5469 | 123.1979 | -2.5223 | 120.6711 | -0.042419 | 0.0033389 | -0.0018031 | 0.00088432 | -0.0023649 | 0.0028476 | -0.0015935 | 0.056122 | 0.0039541 | 0.083512 | 0.060287 | -0.0015296 | -0.0025164 | -0.0013991 | -1.6159 | -1.3 | -2.5909 | -1.68 | -1.506 | -2.4582 | -1.5793 | 0.12817 | 120.7809 | -2.6596 | 120.6711 | -2.2934 | -2.4307 | -2.3483 | -0.068664 | -121.9711 | -122.3511 | 1.0162 | 0.94299 | 0.064087 | 1.0117 | 0.13275 | -0.13733 | 0.10986 | 0 | 0.22888 | 0.17395 | 0.091553 | 0.31128 | 0.22888 | 1.0849 | 0.91095 | 0.36621 | 123.3307 | 1.2909 | 123.4406 | 1.2222 | 123.3032 | -123.262 | -123.3307 | 0.84228 | 123.1934 | 0.90637 | 2.6505
1229.4844 | 123.2117 | -2.2934 | 120.8908 | 0.0033567 | 0.0031253 | -0.0018031 | 0.0036615 | 0.00083954 | -0.00057042 | -0.0022345 | -0.059845 | 0.00010888 | 0.083939 | 0.068618 | -0.0049476 | 0.0026104 | -0.0018265 | -1.4832 | -1.1993 | -2.449 | -1.6159 | -1.4511 | -2.3804 | -1.5106 | 0.11444 | 120.9961 | -2.4765 | 120.8542 | -2.0462 | -2.2614 | -2.1423 | -0.15564 | -122.0901 | -122.5067 | 0.84228 | 0.78278 | -0.086975 | 0.93842 | 0.068665 | -0.1831 | 0.10529 | -0.036621 | 0.24719 | 0.15106 | 0.032043 | 0.33417 | 0.21515 | 0.99792 | 0.83313 | 0.4303 | 123.3307 | 1.2497 | 123.4726 | 1.0941 | 123.2895 | -123.3398 | -123.3673 | 0.67749 | 123.1476 | 0.81024 | 2.4078
1230.4844 | 123.1567 | -2.33 | 120.9274 | -0.03479 | 0.0044071 | -0.0028711 | 0.0013117 | -0.0021513 | 0.0015658 | -0.0011663 | 0.010345 | 0.0041679 | 0.083084 | 0.0652 | -0.0021704 | -0.0023028 | -0.0024673 | -1.5518 | -1.1902 | -2.4216 | -1.6754 | -1.506 | -2.3666 | -1.5198 | 0.036621 | 121.0556 | -2.4628 | 120.813 | -2.1332 | -2.2842 | -2.2018 | -0.091553 | -122.1176 | -122.6028 | 0.82397 | 0.81024 | -0.036621 | 0.90179 | 0.054932 | -0.13275 | 0.12817 | -0.11444 | 0.19684 | 0.12817 | 0.045776 | 0.26093 | 0.17853 | 0.91553 | 0.74615 | 0.32959 | 123.2758 | 1.2314 | 123.5184 | 1.1398 | 123.3856 | -123.349 | -123.3902 | 0.6546 | 123.143 | 0.7782 | 2.3666
1231.5469 | 123.143 | -2.2476 | 121.0052 | -0.0042723 | 0.0059025 | -0.0043665 | 0.00045712 | 0.0014803 | 0.0011386 | -0.0018073 | 0.013397 | 0.00053628 | 0.080735 | 0.065414 | -0.000675 | -0.0025164 | -0.00054474 | -1.4923 | -1.1398 | -2.3758 | -1.6022 | -1.4191 | -2.2797 | -1.4511 | 0 | 121.1243 | -2.3666 | 120.932 | -2.0462 | -2.1927 | -2.1057 | -0.12817 | -122.1451 | -122.6074 | 0.82855 | 0.79651 | -0.032043 | 0.92468 | 0.09613 | -0.11902 | 0.11902 | -0.073242 | 0.20142 | 0.14191 | 0.054932 | 0.26092 | 0.17395 | 0.95673 | 0.77362 | 0.32043 | 123.2986 | 1.236 | 123.4909 | 1.1078 | 123.3719 | -123.381 | -123.3719 | 0.64545 | 123.1796 | 0.75531 | 2.2476
1232.4844 | 123.1613 | -2.1423 | 121.0922 | 0.08728 | 0.0029117 | -0.0039393 | 0.0028069 | -0.00065586 | -0.00078402 | -0.0011663 | 0.0072936 | 0.0013907 | 0.083725 | 0.066054 | -0.0017432 | -0.0027302 | 0.00030966 | -1.4603 | -1.0803 | -2.33 | -1.561 | -1.4053 | -2.2156 | -1.4236 | 0.013733 | 121.2158 | -2.2934 | 121.0373 | -1.9958 | -2.1011 | -1.9638 | -0.18768 | -122.1725 | -122.6532 | 0.737 | 0.71869 | -0.073242 | 0.90637 | 0.11444 | -0.15106 | 0.1236 | -0.054932 | 0.14648 | 0.17853 | 0.041199 | 0.32959 | 0.19226 | 0.92468 | 0.76904 | 0.29755 | 123.3307 | 1.2497 | 123.5092 | 1.062 | 123.3582 | -123.4222 | -123.3856 | 0.58136 | 123.1796 | 0.68207 | 2.1561
1233.4844 | 123.1979 | -2.4902 | 120.7031 | -0.042419 | 0.0035525 | -0.0032983 | 0.0021661 | 0.0019077 | 0.00028418 | 0.0011835 | -0.035431 | 0.0022453 | 0.081589 | 0.073104 | -0.003025 | -0.00059378 | -0.0018265 | -1.5884 | -1.3 | -2.6505 | -1.6525 | -1.4832 | -2.449 | -1.6022 | 0.11444 | 120.8542 | -2.6367 | 120.7031 | -2.2705 | -2.4307 | -2.3438 | -0.16022 | -122.0032 | -122.3557 | 1.0071 | 0.88806 | 0.041198 | 1.0483 | 0.20142 | -0.14648 | 0.15106 | 0 | 0.21973 | 0.14648 | 0.059509 | 0.29297 | 0.20599 | 1.1673 | 0.99792 | 0.36621 | 123.3398 | 1.3504 | 123.4909 | 1.1902 | 123.3444 | -123.3536 | -123.3398 | 0.83771 | 123.1934 | 0.90179 | 2.6047
1234.4844 | 123.1842 | -2.2888 | 120.9549 | -0.065308 | 0.0078251 | -0.0039393 | 0.0040887 | 0.0021213 | -0.00099762 | -0.0015935 | -0.020172 | 0.0020315 | 0.083298 | 0.070113 | -0.002384 | -0.0018756 | 0.0024461 | -1.4282 | -1.1169 | -2.3758 | -1.5884 | -1.4465 | -2.33 | -1.4694 | -0.036621 | 121.0922 | -2.4078 | 120.9 | -2.092 | -2.2614 | -2.1286 | -0.086975 | -122.0718 | -122.5433 | 0.84228 | 0.8194 | -0.041199 | 0.90637 | 0.045776 | -0.11902 | 0.13733 | -0.054932 | 0.19684 | 0.16022 | 0.027465 | 0.27924 | 0.14648 | 0.92926 | 0.78735 | 0.31586 | 123.3078 | 1.2588 | 123.5001 | 1.1719 | 123.381 | -123.3307 | -123.3627 | 0.70038 | 123.1888 | 0.86059 | 2.2522
1235.5469 | 123.2025 | -2.2064 | 121.0236 | 0.010986 | 0.0018435 | -0.0039393 | 0.0010981 | 0.0016939 | -0.0027066 | -0.0026617 | 0.0072936 | 0.00074988 | 0.082657 | 0.0652 | -0.0008886 | -0.00016658 | -0.00011754 | -1.5015 | -1.1261 | -2.3895 | -1.5976 | -1.4282 | -2.2751 | -1.474 | -0.082397 | 121.1472 | -2.3621 | 120.9229 | -2.0279 | -2.243 | -1.9272 | -0.1831 | -122.1497 | -122.6212 | 0.7782 | 0.73242 | -0.068664 | 0.91553 | 0.11444 | -0.15564 | 0.1236 | -0.10071 | 0.17853 | 0.27924 | -0.036621 | 0.43488 | 0.11902 | 0.9613 | 0.79193 | 0.33417 | 123.2849 | 1.2634 | 123.5092 | 1.0803 | 123.3536 | -123.4131 | -123.3856 | 0.60883 | 123.1293 | 0.70496 | 2.124
1236.4844 | 123.1613 | -2.1378 | 121.106 | 0.018616 | 0.0039799 | -0.0037257 | 0.0010981 | 0.0031893 | 0.00092498 | -0.0054389 | -0.0018616 | 0.0028861 | 0.084366 | 0.063918 | -0.0017432 | -0.0027302 | 0.00095066 | -1.4282 | -1.0666 | -2.3163 | -1.3092 | -1.2955 | -2.4307 | -1.355 | 2.3621 | 121.2296 | -2.2568 | 121.0236 | -1.918 | -2.2385 | -1.9363 | -0.17853 | -122.1725 | -122.4152 | 0.84228 | 0.78278 | -0.29297 | 0.9613 | -0.11444 | -0.11902 | 0.1236 | -0.082397 | 0.21973 | 0.20142 | -0.10071 | 0.32044 | 0.018311 | 1.0208 | 1.0071 | 0.33875 | 123.2803 | 1.2497 | 123.4863 | 1.0712 | 123.3673 | -123.4222 | -123.3627 | 0.82855 | 123.1613 | 0.70953 | 4.4998
1237.4844 | 123.2071 | -2.4536 | 120.7855 | 0.026245 | 0.0029117 | -0.0013757 | 0.0038751 | 0.0042575 | -0.00099762 | -0.00052553 | -0.056793 | 0.0018179 | 0.084793 | 0.062209 | -0.0015296 | -0.0018756 | -0.0031081 | -1.5518 | -1.2772 | -2.6001 | -1.6754 | -1.5198 | -2.4719 | -1.5976 | 0.009155 | 120.9229 | -2.5681 | 120.7672 | -2.2247 | -2.298 | -2.3026 | -0.14649 | -122.0627 | -122.4609 | 0.93384 | 0.85602 | -0.018311 | 1.0025 | 0.12817 | -0.11444 | 0.13733 | -0.01831 | 0.22888 | 0.15106 | 0.15564 | 0.2655 | 0.27008 | 1.0803 | 0.92468 | 0.34332 | 123.3353 | 1.3229 | 123.4909 | 1.1765 | 123.3765 | -123.3856 | -123.3536 | 0.7782 | 123.2208 | 0.90179 | 2.4628
1238.5469 | 123.2071 | -2.2659 | 120.9961 | 0.010986 | 0.0037661 | -0.0030847 | 0.0010981 | -0.00086946 | 0.0015658 | -0.0022345 | 0.05307 | 0.00053628 | 0.083512 | 0.069259 | -0.000675 | -0.0018756 | 0.0013779 | -1.3962 | -1.149 | -2.3438 | -1.4786 | -1.3046 | -2.1515 | -1.3641 | 3.0853 | 121.0648 | -2.3483 | 120.9412 | -2.005 | -2.1606 | -2.0828 | -0.07782 | -122.1451 | -122.4747 | 0.9613 | 0.90179 | 0.11444 | 0.97961 | 0.19226 | -0.082398 | 0.068664 | -0.054932 | 0.26092 | 0.1831 | 0.10528 | 0.2655 | 0.18768 | 1.0391 | 0.86517 | 0.34332 | 123.2895 | 1.1948 | 123.4131 | 1.1169 | 123.3307 | -123.3398 | -123.3444 | 0.78735 | 123.2071 | 0.86975 | 5.3513
1239.4844 | 123.2025 | -2.1286 | 121.1151 | -0.019531 | 0.0052615 | -0.0037257 | 0.00088432 | -0.0040739 | -0.00057042 | -0.0013799 | -0.029327 | 0.0020315 | 0.082016 | 0.067763 | -0.0049476 | -0.0014484 | -0.0013991 | -1.3962 | -1.1032 | -2.3483 | -1.5198 | -1.3596 | -2.2018 | -1.4191 | 3.0167 | 121.1929 | -2.3071 | 121.0556 | -1.9135 | -2.0828 | -1.9821 | -0.21973 | -122.2183 | -122.6349 | 0.76904 | 0.70953 | -0.073242 | 0.92926 | 0.14648 | -0.17853 | 0.07782 | -0.059509 | 0.21515 | 0.14648 | 0.045776 | 0.32501 | 0.2243 | 0.98877 | 0.82855 | 0.39368 | 123.3627 | 1.2451 | 123.5001 | 1.0254 | 123.3215 | -123.4634 | -123.4222 | 0.60883 | 123.1842 | 0.73242 | 5.1453
1240.4844 | 123.1934 | -2.2339 | 121.0876 | -0.011902 | 0.0033389 | -0.0045801 | 0.0025933 | -0.00044226 | 0.00049778 | -0.0018073 | -0.01712 | 0.0016043 | 0.084366 | 0.06755 | -0.0008886 | -0.0025164 | -0.00011754 | -1.4511 | -1.0986 | -2.3804 | -1.5656 | -1.4053 | -2.2797 | -1.4236 | -0.07782 | 121.1288 | -2.3712 | 120.9274 | -2.0416 | -2.1835 | -1.8997 | -0.14648 | -122.1863 | -122.6532 | 0.82855 | 0.81024 | -0.045776 | 0.95673 | 0.10071 | -0.13733 | 0.041199 | -0.16022 | 0.19226 | 0.33417 | 0.050354 | 0.4715 | 0.18768 | 0.97504 | 0.81482 | 0.32959 | 123.2986 | 1.2817 | 123.5001 | 1.1353 | 123.3627 | -123.468 | -123.4589 | 0.66834 | 123.1613 | 0.78278 | 2.1561
1241.4844 | 123.2254 | -2.4902 | 120.7306 | -0.050049 | 0.0018435 | -0.0024439 | 0.0021661 | 0.00062594 | 0.00071138 | -0.0026617 | -0.056793 | 0.0022453 | 0.084793 | 0.064986 | -0.003025 | -0.00038018 | 0.00073706 | -1.6159 | -1.2863 | -2.655 | -1.7029 | -1.5656 | -2.5314 | -1.6388 | -0.027466 | 120.8588 | -2.6459 | 120.7352 | -2.2705 | -2.4261 | -2.3209 | -0.16479 | -122.0169 | -122.4335 | 0.92468 | 0.85144 | -0.041199 | 1.0162 | 0.1236 | -0.15564 | 0.12817 | 0.004577 | 0.21973 | 0.16937 | 0.064087 | 0.32501 | 0.21973 | 1.0895 | 0.95215 | 0.37537 | 123.381 | 1.3687 | 123.5046 | 1.2039 | 123.349 | -123.3856 | -123.3765 | 0.78735 | 123.2254 | 0.87433 | 2.4628
1242.5469 | 123.2391 | -2.2751 | 120.8908 | -0.10345 | 0.0063297 | -0.0022303 | 0.0017389 | 0.00019874 | -0.0012112 | 0.00011527 | 0.031708 | 0.0018179 | 0.083512 | 0.0652 | -0.0008886 | -0.0010212 | 0.0011643 | -1.474 | -1.181 | -2.3987 | -1.5656 | -1.4099 | -2.3071 | -1.442 | 0.009155 | 121.019 | -2.4078 | 120.9229 | -2.037 | -2.2064 | -2.092 | -0.1236 | -122.0718 | -122.4564 | 0.86517 | 0.83313 | -0.032044 | 0.95673 | 0.091553 | -0.13275 | 0.12817 | 0.032044 | 0.23804 | 0.1831 | 0.068664 | 0.31586 | 0.20142 | 0.98877 | 0.83313 | 0.37079 | 123.3307 | 1.2177 | 123.4268 | 1.0941 | 123.2941 | -123.2895 | -123.2986 | 0.70953 | 123.1979 | 0.80109 | 2.2842
1243.4844 | 123.0286 | -2.4582 | 120.8176 | -0.080566 | 0.0033389 | -0.0032983 | 0.0019525 | -0.00065586 | 0.0019932 | -0.0013799 | -0.035431 | 0.00053628 | 0.08223 | 0.069045 | -0.001316 | -0.0029438 | -0.0020401 | -1.6891 | -1.4282 | -2.5955 | -1.8219 | -1.6525 | -2.4719 | -1.712 | 0.013733 | 120.9091 | -2.5772 | 120.7306 | -2.2476 | -2.4033 | -2.2934 | -0.13733 | -122.2458 | -122.6395 | 0.80566 | 0.74615 | -0.013733 | 0.88348 | 0.1236 | -0.11902 | 0.091553 | -0.086975 | 0.21057 | 0.16479 | 0.054932 | 0.28381 | 0.17395 | 0.94299 | 0.77362 | 0.32959 | 123.3078 | 1.1673 | 123.4863 | 1.03 | 123.3673 | -123.4131 | -123.3948 | 0.63629 | 123.1888 | 0.76904 | 2.4719
1244.5 | 123.2254 | -2.3026 | 120.8862 | -0.065308 | 0.0056889 | -0.0011621 | 0.0036615 | 0.0012667 | 0.00071138 | -9.8328e-05 | -0.0049134 | -0.00010472 | 0.080948 | 0.062636 | 0.001034 | -0.0012348 | -0.0052445 | -1.5884 | -1.3504 | -2.4445 | -1.6296 | -1.4603 | -2.3254 | -1.5381 | 0.073242 | 120.9778 | -2.4353 | 120.932 | -2.0554 | -2.2018 | -2.092 | -0.14191 | -122.2366 | -122.5159 | 0.84228 | 0.76446 | -0.022888 | 0.90637 | 0.11902 | -0.13275 | 0.091553 | 0.045777 | 0.24719 | 0.21057 | 0.10071 | 0.34332 | 0.23346 | 0.98419 | 0.81482 | 0.37994 | 123.3673 | 1.0941 | 123.4131 | 0.95215 | 123.2803 | -123.3307 | -123.3215 | 0.67291 | 123.2346 | 0.71411 | 2.3758
1245.5469 | 123.1659 | -2.449 | 120.7626 | -0.042419 | 0.0056889 | -0.0037257 | 0.00067072 | -0.0025785 | 0.0028476 | -0.0018073 | 0.031708 | 0.0020315 | 0.081803 | 0.062636 | -0.0017432 | 0.00068782 | -0.0016129 | -1.5976 | -1.3596 | -2.5818 | -1.6983 | -1.5244 | -2.4261 | -1.6159 | 0.004578 | 120.8267 | -2.6138 | 120.7306 | -2.2293 | -2.3758 | -2.2934 | -0.13275 | -122.1222 | -122.4609 | 0.92468 | 0.83313 | 0.022889 | 0.96588 | 0.15564 | -0.16479 | 0.064087 | -0.032043 | 0.21973 | 0.15564 | 0.073243 | 0.32043 | 0.23804 | 1.0574 | 0.88348 | 0.38452 | 123.3444 | 1.2222 | 123.4406 | 1.0895 | 123.2758 | -123.3444 | -123.3765 | 0.75073 | 123.1796 | 0.85144 | 2.4536
1246.4844 | 123.1979 | -2.4811 | 120.7123 | 0.010986 | 0.0037661 | -0.0035119 | 0.0028069 | -0.00022866 | 0.0017794 | -0.00031193 | -0.084259 | 0.0011771 | 0.081589 | 0.064986 | -0.0049476 | 0.00090142 | -0.0022537 | -1.6525 | -1.3504 | -2.6413 | -1.7715 | -1.6022 | -2.5177 | -1.6617 | 0.009155 | 120.8542 | -2.6276 | 120.7169 | -2.2888 | -2.4399 | -2.3392 | -0.16022 | -122.0627 | -122.4838 | 0.87891 | 0.8194 | -0.036621 | 0.97961 | 0.1236 | -0.14648 | 0.14191 | 0.004578 | 0.19226 | 0.14191 | 0.041199 | 0.28839 | 0.18768 | 1.0391 | 0.86975 | 0.33874 | 123.3444 | 1.2909 | 123.4817 | 1.1307 | 123.3353 | -123.3536 | -123.3398 | 0.70953 | 123.1979 | 0.82855 | 2.4902
1247.5469 | 123.2758 | -2.2705 | 120.9229 | -0.03479 | 0.0029117 | -0.0062891 | 0.0032343 | -0.0053555 | -0.00078402 | -0.00052553 | 0.016449 | -0.00010472 | 0.084152 | 0.061355 | 0.000393 | -0.0010212 | 0.00095066 | -1.5198 | -1.2817 | -2.4216 | -1.5564 | -1.4099 | -2.0325 | -1.6846 | 0.073242 | 121.0236 | -2.4033 | 120.9641 | -1.9775 | -2.1515 | -2.0691 | -0.15106 | -122.2046 | -122.4792 | 0.8606 | 0.58594 | 0.23804 | 0.737 | 0.3891 | -0.13275 | 0.10071 | 0.041198 | 0.29297 | 0.20142 | 0.11902 | 0.33417 | 0.25177 | 1.0117 | 0.86517 | 0.42572 | 123.3673 | 1.1398 | 123.4268 | 0.98877 | 123.2941 | -123.3444 | -123.3261 | 0.71411 | 123.2346 | 0.75073 | 2.3438
1248.4844 | 123.2117 | -2.4536 | 120.7764 | 0.0033567 | 0.0026981 | -0.0015893 | 0.0036615 | 0.0040439 | 0.0028476 | -0.0011663 | -0.011017 | -0.00095912 | 0.08223 | 0.06755 | -0.003025 | -0.0029438 | -0.0011855 | -1.6388 | -1.2955 | -2.5955 | -1.7807 | -1.6342 | -2.4994 | -1.6571 | -0.064087 | 120.8954 | -2.5955 | 120.7443 | -2.2293 | -2.4078 | -2.2842 | -0.14191 | -122.0718 | -122.5571 | 0.8194 | 0.79651 | -0.045777 | 0.93842 | 0.09613 | -0.14191 | 0.11902 | -0.032043 | 0.2243 | 0.16937 | 0.045776 | 0.31128 | 0.18768 | 0.9613 | 0.81482 | 0.36621 | 123.3398 | 1.3 | 123.4909 | 1.1581 | 123.349 | -123.3719 | -123.3719 | 0.67291 | 123.1979 | 0.81482 | 2.3895
1249.5625 | 123.1796 | -2.6505 | 120.6253 | -0.0042723 | 0.0056889 | -0.0032983 | 0.0045159 | -0.0027921 | 0.0024204 | 0.0011835 | -0.062897 | 0.00053628 | 0.083725 | 0.071181 | -0.0011022 | -0.0010212 | 0.0011643 | -1.7075 | -1.3687 | -2.71 | -1.8173 | -1.68 | -2.6779 | -1.7532 | 0.068665 | 120.694 | -2.7832 | 120.5292 | -2.4628 | -2.6184 | -2.4902 | -0.059509 | -121.994 | -122.4426 | 0.97046 | 0.89722 | -0.027465 | 0.95673 | 0.032044 | -0.13275 | 0.068665 | -0.09613 | 0.18768 | 0.16022 | 0.032044 | 0.29297 | 0.16479 | 1.03 | 0.89264 | 0.32043 | 123.3124 | 1.3412 | 123.4772 | 1.2817 | 123.3444 | -123.3353 | -123.4085 | 0.83313 | 123.1796 | 0.94299 | 2.7191
1250.4844 | 123.1979 | -2.4857 | 120.7214 | -0.019531 | 0.0054751 | -0.0013757 | 0.0015253 | -0.00086946 | 0.0013522 | 0.00011527 | -0.0049134 | 0.00010888 | 0.082871 | 0.066695 | -0.002384 | -0.00080758 | -0.0028945 | -1.6571 | -1.2909 | -2.6321 | -1.7624 | -1.6342 | -2.5177 | -1.6434 | -0.018311 | 120.9 | -2.5955 | 120.7077 | -2.2797 | -2.449 | -2.3254 | -0.14648 | -122.0123 | -122.4838 | 0.85144 | 0.84228 | -0.032043 | 0.98877 | 0.11444 | -0.10986 | 0.17853 | -0.013733 | 0.20599 | 0.16022 | 0.036621 | 0.27008 | 0.14648 | 0.99792 | 0.86975 | 0.31586 | 123.3032 | 1.3412 | 123.4955 | 1.1948 | 123.3856 | -123.3536 | -123.317 | 0.72327 | 123.1934 | 0.82855 | 2.4673
1251.5469 | 123.2025 | -2.2888 | 120.9778 | 0.041504 | 0.0041935 | -0.0052209 | 2.9918e-05 | -0.00022866 | 0.00092498 | 0.0022517 | -0.032379 | 0.00053628 | 0.085007 | 0.065414 | -0.0015296 | -0.0020892 | -0.0037491 | -1.5656 | -1.1948 | -2.4628 | -1.7075 | -1.2589 | -2.1515 | -1.6479 | -0.022888 | 121.1151 | -2.3758 | 120.8954 | -2.0828 | -2.243 | -2.1149 | -0.17395 | -122.1725 | -122.6852 | 1.03 | 0.64087 | 0.13733 | 0.81482 | 0.31128 | -0.086975 | 0.13733 | -0.082397 | 0.20599 | 0.17395 | 0.045776 | 0.26092 | 0.13275 | 1.2039 | 0.75531 | 0.29297 | 123.2712 | 1.268 | 123.4909 | 1.0941 | 123.4039 | -123.4406 | -123.3536 | 0.58136 | 123.1842 | 0.72327 | 2.2659
1252.4844 | 123.2117 | -2.124 | 121.138 | -0.050049 | 0.0022709 | -0.0032983 | 0.0025933 | 0.0016939 | -0.00099762 | -0.0018073 | -0.011017 | 0.0024589 | 0.08458 | 0.064559 | -0.0008886 | -0.0018756 | 0.0013779 | -1.4374 | -1.0803 | -2.2522 | -1.561 | -1.4191 | -2.1423 | -1.4511 | -0.018311 | 121.2616 | -2.2614 | 121.0739 | -1.9135 | -2.092 | -1.973 | -0.12817 | -122.2183 | -122.699 | 0.70496 | 0.67291 | -0.018311 | 0.80109 | 0.10986 | -0.13733 | 0.1236 | -0.064086 | 0.21057 | 0.15106 | 0.032043 | 0.28839 | 0.16937 | 0.83313 | 0.69122 | 0.3479 | 123.3353 | 1.1719 | 123.5229 | 1.0437 | 123.3856 | -123.3902 | -123.3994 | 0.56305 | 123.1979 | 0.68665 | 2.1057
1253.4844 | 123.1979 | -2.3712 | 120.8359 | -0.042419 | 0.0029117 | -0.0028711 | 0.0015253 | 0.0023349 | 0.0011386 | -0.0020209 | -0.059845 | 0.0016043 | 0.082871 | 0.069472 | -0.0015296 | 4.7018e-05 | -0.0041763 | -1.593 | -1.3138 | -2.5681 | -1.7029 | -1.5335 | -2.417 | -1.5976 | 0.24261 | 121.0922 | -2.4445 | 120.8221 | -2.1973 | -2.3849 | -2.2018 | -0.19684 | -122.1497 | -122.5388 | 0.83771 | 0.77362 | -0.045776 | 0.97046 | 0.15106 | -0.073242 | 0.25635 | -0.013732 | 0.17395 | 0.16937 | -0.013733 | 0.24261 | 0.059509 | 1.0345 | 0.86517 | 0.24719 | 123.2666 | 1.2543 | 123.5367 | 1.0574 | 123.4634 | -123.4039 | -123.2803 | 0.66833 | 123.1934 | 0.7782 | 2.6138
1254.5625 | 123.1567 | -2.2064 | 121.0464 | -0.065308 | 0.0039799 | 0.00054694 | 0.0017389 | 0.00062594 | -0.00014322 | -0.00073913 | -0.05069 | 0.0030997 | 0.081162 | 0.06755 | -0.0034522 | 4.7018e-05 | 0.0022323 | -1.4969 | -1.181 | -2.3712 | -1.6296 | -1.4694 | -2.3026 | -1.5472 | 0.009155 | 121.17 | -2.3392 | 121.0007 | -2.0187 | -2.1698 | -2.0828 | -0.16479 | -122.2275 | -122.6761 | 0.737 | 0.65918 | -0.09613 | 0.82397 | 0.068665 | -0.13275 | 0.1236 | -0.045777 | 0.18768 | 0.1236 | 0.036621 | 0.25635 | 0.16937 | 0.90179 | 0.74158 | 0.32043 | 123.3398 | 1.1902 | 123.5092 | 1.0254 | 123.3765 | -123.4177 | -123.3856 | 0.57678 | 123.2071 | 0.70953 | 2.2156
1255.4844 | 123.175 | -2.1606 | 121.0922 | 0.018616 | 0.0029117 | 0.00076054 | 0.0017389 | 0.0025485 | -0.00014322 | 0.00011527 | -0.026276 | 0.00096348 | 0.083512 | 0.069472 | -0.0025976 | -0.0010212 | 0.00030966 | -1.4374 | -1.1124 | -2.2751 | -1.5518 | -1.4008 | -2.1973 | -1.474 | 0.054932 | 121.2204 | -2.2751 | 121.0464 | -1.9501 | -2.1194 | -1.9821 | -0.11444 | -122.2046 | -122.644 | 0.75989 | 0.68665 | -0.036621 | 0.80109 | 0.077819 | -0.11444 | 0.12817 | -0.045776 | 0.21057 | 0.17853 | 0.041199 | 0.29297 | 0.15564 | 0.87433 | 0.72327 | 0.32501 | 123.3215 | 1.1627 | 123.4955 | 1.0483 | 123.381 | -123.3673 | -123.3673 | 0.60883 | 123.2071 | 0.72327 | 2.2156
1256.5469 | 123.2849 | -2.0462 | 121.0922 | -0.042419 | 0.0046207 | -0.0032983 | 0.00067072 | -0.0021513 | 0.0019932 | 0.0013971 | 0.046967 | 0.00032248 | 0.081803 | 0.06285 | -0.0019568 | -0.0023028 | -0.00075834 | -1.3596 | -1.0941 | -2.2202 | -1.4145 | -1.2405 | -2.0325 | -1.2726 | 0.21057 | 121.2433 | -2.1835 | 121.1884 | -1.7487 | -1.9089 | -1.8494 | -0.17395 | -122.1863 | -122.5067 | 0.80566 | 0.77362 | 0.013733 | 0.94757 | 0.18768 | -0.13733 | 0.15106 | 0.09613 | 0.29755 | 0.19684 | 0.13733 | 0.33417 | 0.27466 | 0.97961 | 0.80566 | 0.43488 | 123.3719 | 1.1261 | 123.4268 | 0.95215 | 123.2895 | -123.3124 | -123.2758 | 0.63171 | 123.2346 | 0.68665 | 2.2568
1257.4844 | 123.2071 | -1.973 | 121.2753 | -0.042419 | 0.0067569 | -0.0032983 | 0.0028069 | 0.00083954 | 0.0028476 | -0.00031193 | -0.044586 | 0.0018179 | 0.082871 | 0.066909 | -0.0032386 | -0.0029438 | 0.0015915 | -1.3138 | -0.99792 | -2.1149 | -1.4282 | -1.2726 | -2.0416 | -1.3458 | 0.082397 | 121.3852 | -2.1057 | 121.225 | -1.7899 | -1.9547 | -1.8448 | -0.14191 | -122.2733 | -122.7036 | 0.70038 | 0.62714 | -0.068665 | 0.76904 | 0.073242 | -0.13275 | 0.10986 | -0.050354 | 0.18311 | 0.12817 | 0.01831 | 0.26093 | 0.15106 | 0.84228 | 0.68664 | 0.31586 | 123.3307 | 1.1169 | 123.4909 | 0.97504 | 123.3582 | -123.3902 | -123.381 | 0.54474 | 123.1979 | 0.65918 | 2.0554
1258.5469 | 123.1567 | -2.0462 | 121.2341 | 0.049133 | 0.0059025 | -0.0060755 | -0.00039728 | -0.0025785 | 0.0011386 | -0.0026617 | 0.028656 | 0.0039541 | 0.083298 | 0.068831 | -0.0015296 | -0.0040118 | -0.00033114 | -1.3229 | -1.0254 | -2.1652 | -1.442 | -1.268 | -2.0508 | -1.3275 | 0.045776 | 121.3715 | -2.1515 | 121.1472 | -1.8219 | -1.9821 | -1.918 | -0.11902 | -122.2595 | -122.6761 | 0.7782 | 0.71869 | -0.004577 | 0.83771 | 0.11444 | -0.10529 | 0.13733 | -0.086975 | 0.2243 | 0.12817 | 0.064087 | 0.23346 | 0.16937 | 0.89722 | 0.72327 | 0.32959 | 123.2986 | 1.1398 | 123.5229 | 1.0208 | 123.4177 | -123.3994 | -123.3856 | 0.60425 | 123.1934 | 0.72327 | 2.092
1259.4844 | 123.175 | -2.1835 | 121.0602 | -0.050049 | 0.0016299 | -0.0041529 | 0.0036615 | 0.0016939 | -0.00078402 | -0.0015935 | -0.078156 | 0.0016043 | 0.085221 | 0.06755 | -0.0045202 | -0.0014484 | -0.0026809 | -1.3916 | -1.0895 | -2.2842 | -1.5152 | -1.3596 | -2.211 | -1.4282 | 0.032043 | 121.1975 | -2.2934 | 121.0327 | -1.9638 | -2.1423 | -2.0233 | -0.10071 | -122.1497 | -122.5754 | 0.82398 | 0.75531 | -0.027466 | 0.85602 | 0.073242 | -0.10986 | 0.13733 | -0.027466 | 0.21973 | 0.16022 | 0.041199 | 0.27008 | 0.15106 | 0.92468 | 0.76904 | 0.32959 | 123.3261 | 1.1948 | 123.4909 | 1.0941 | 123.381 | -123.3444 | -123.3536 | 0.66834 | 123.2162 | 0.79193 | 2.2156
1260.5469 | 123.2574 | -2.0325 | 121.1884 | 0.026245 | 0.0067569 | -0.0037257 | -0.00039728 | -0.0030057 | 0.0034884 | 0.00054267 | 0.034759 | 0.00096348 | 0.08458 | 0.059859 | -0.0032386 | -0.001662 | 0.00073706 | -1.3275 | -1.0941 | -2.1744 | -1.3962 | -1.2131 | -1.973 | -1.268 | 0.13275 | 121.3028 | -2.1561 | 121.2021 | -1.7532 | -1.9089 | -1.8723 | -0.14191 | -122.2824 | -122.5845 | 0.8194 | 0.76447 | 0.05951 | 0.90637 | 0.20142 | -0.1236 | 0.11444 | 0.013733 | 0.27924 | 0.16022 | 0.1236 | 0.28381 | 0.24719 | 0.9613 | 0.7782 | 0.40283 | 123.3582 | 1.0803 | 123.4589 | 0.93842 | 123.3353 | -123.3627 | -123.3444 | 0.63629 | 123.2346 | 0.70496 | 2.1652
1261.4844 | 123.1567 | -2.0554 | 121.2067 | -0.065308 | 0.0048343 | -0.0020167 | 0.0030207 | 0.0031893 | 0.0032748 | -0.0028753 | -0.053741 | 0.0020315 | 0.083512 | 0.061568 | -0.0032386 | -0.00016658 | 0.00073706 | -1.387 | -1.0391 | -2.211 | -1.4694 | -1.3733 | -2.1606 | -1.3916 | -0.004578 | 121.3257 | -2.1881 | 121.1197 | -1.886 | -2.092 | -1.9409 | -0.15564 | -122.2458 | -122.6761 | 0.68207 | 0.66376 | -0.10529 | 0.8194 | 0.050354 | -0.13275 | 0.11902 | -0.086975 | 0.16937 | 0.11444 | -0.036621 | 0.24719 | 0.09613 | 0.83771 | 0.74158 | 0.30212 | 123.3078 | 1.1719 | 123.5138 | 1.0162 | 123.381 | -123.4177 | -123.3948 | 0.58594 | 123.175 | 0.66834 | 2.0508
1262.4844 | 123.2346 | -2.037 | 121.1838 | -0.011902 | 0.0031253 | -0.0026575 | 0.00045712 | 0.0016939 | 0.0024204 | 0.0016107 | -0.047638 | 0.0024589 | 0.082016 | 0.068618 | -0.0004614 | -0.0029438 | -0.0035355 | -1.3916 | -1.0895 | -2.2522 | -1.4969 | -1.3321 | -2.124 | -1.387 | 0.09613 | 121.3074 | -2.2156 | 121.1472 | -1.8311 | -2.0096 | -1.9043 | -0.21515 | -122.2733 | -122.6807 | 0.70496 | 0.65002 | -0.086975 | 0.86517 | 0.12817 | -0.17853 | 0.1236 | -0.036621 | 0.20599 | 0.13275 | 0.027465 | 0.31128 | 0.20599 | 0.9201 | 0.75531 | 0.38452 | 123.3627 | 1.1627 | 123.5229 | 0.94757 | 123.3444 | -123.436 | -123.3994 | 0.54016 | 123.1842 | 0.64545 | 2.1332
1263.5469 | 123.2346 | -2.1835 | 121.0281 | -0.095825 | 0.0033389 | -0.0032983 | 0.0019525 | 0.00083954 | 0.0015658 | -0.0022345 | -0.01712 | 0.0016043 | 0.086289 | 0.063491 | -0.0021704 | -0.00038018 | 0.0024461 | -1.4969 | -1.2177 | -2.4261 | -1.5884 | -1.4191 | -2.243 | -1.4694 | 0.07782 | 121.1563 | -2.3575 | 121.0419 | -1.9592 | -2.1149 | -2.0142 | -0.24261 | -122.2458 | -122.6166 | 0.76447 | 0.71411 | -0.059509 | 0.95673 | 0.1831 | -0.17395 | 0.12817 | 0.013733 | 0.2243 | 0.16937 | 0.068665 | 0.34332 | 0.24262 | 1.0071 | 0.83771 | 0.39825 | 123.3994 | 1.2085 | 123.5138 | 0.96588 | 123.3398 | -123.4543 | -123.3856 | 0.59509 | 123.2254 | 0.68665 | 2.2614
1264.4844 | 123.2162 | -2.4719 | 120.7626 | 0.0033567 | 0.0024845 | -0.0037257 | 0.0015253 | 0.0012667 | 0.0017794 | 0.00096987 | -0.020172 | 0.0013907 | 0.083084 | 0.066482 | -0.0034522 | -0.001662 | 0.00073706 | -1.6159 | -1.2909 | -2.6321 | -1.7303 | -1.5701 | -2.5269 | -1.6159 | 0.086975 | 120.9 | -2.5955 | 120.7581 | -2.2247 | -2.3987 | -2.2842 | -0.16022 | -122.0535 | -122.493 | 0.90179 | 0.85602 | -0.054931 | 1.0162 | 0.10529 | -0.1236 | 0.13733 | -0.004577 | 0.24719 | 0.18768 | 0.073242 | 0.31128 | 0.19684 | 1.062 | 0.90179 | 0.37079 | 123.3536 | 1.3412 | 123.4955 | 1.181 | 123.3719 | -123.3948 | -123.3582 | 0.74158 | 123.23 | 0.85602 | 2.5589
1265.4844 | 123.1888 | -2.2659 | 121.0052 | -0.027161 | 0.0046207 | -0.0018031 | 0.0032343 | 0.0019077 | 0.0017794 | 0.0011835 | -0.053741 | 0.0018179 | 0.083725 | 0.066054 | -0.001316 | -0.0010212 | 0.0013779 | -1.4511 | -1.1398 | -2.4078 | -1.5793 | -1.4145 | -2.3026 | -1.4786 | 0.050354 | 121.138 | -2.3712 | 120.9549 | -2.0599 | -2.2339 | -2.1103 | -0.14191 | -122.1451 | -122.5845 | 0.85144 | 0.78735 | -0.036621 | 0.92926 | 0.10529 | -0.10529 | 0.13275 | -0.050354 | 0.20599 | 0.15564 | 0.032043 | 0.26092 | 0.13733 | 0.99335 | 0.82855 | 0.31128 | 123.3261 | 1.268 | 123.5092 | 1.1261 | 123.4039 | -123.4131 | -123.3765 | 0.68664 | 123.2208 | 0.81482 | 2.3163
1266.5469 | 123.2529 | -2.0828 | 121.1517 | -0.042419 | 0.0024845 | -0.0026575 | 0.0013117 | 0.0021213 | -0.001852 | -0.0024481 | 0.0011902 | 0.0018179 | 0.082444 | 0.066695 | -0.0021704 | 0.00026062 | 9.6064e-05 | -1.4008 | -1.062 | -2.2705 | -1.5152 | -1.3412 | -2.124 | -1.3916 | 0.032043 | 121.2845 | -2.2247 | 121.1105 | -1.8448 | -2.0279 | -1.9272 | -0.18768 | -122.2137 | -122.6669 | 0.74158 | 0.69122 | -0.041198 | 0.87891 | 0.14648 | -0.14191 | 0.13275 | -0.041198 | 0.23804 | 0.15564 | 0.054932 | 0.29755 | 0.19684 | 0.92926 | 0.75531 | 0.37994 | 123.3353 | 1.2085 | 123.5092 | 1.0208 | 123.3673 | -123.4222 | -123.3765 | 0.56763 | 123.1934 | 0.68207 | 2.1149
1267.4844 | 123.2803 | -2.4216 | 120.7672 | -0.019531 | 0.0037661 | -0.0041529 | 0.0015253 | 0.0031893 | 0.00049778 | -0.00052553 | -0.011017 | 0.00074988 | 0.083512 | 0.059859 | -0.002384 | -0.0018756 | 0.00095066 | -1.6388 | -1.3184 | -2.5955 | -1.7349 | -1.5701 | -2.536 | -1.6296 | 0.082397 | 120.9091 | -2.5681 | 120.8084 | -2.179 | -2.3666 | -2.243 | -0.17395 | -122.0856 | -122.5021 | 0.85144 | 0.79193 | -0.11444 | 0.96588 | 0.059509 | -0.14648 | 0.14191 | 0.041199 | 0.24261 | 0.17853 | 0.054932 | 0.32501 | 0.20142 | 1.0254 | 0.8606 | 0.3891 | 123.3765 | 1.2772 | 123.4772 | 1.1032 | 123.3307 | -123.3627 | -123.3353 | 0.68665 | 123.23 | 0.78278 | 2.504
1268.4844 | 123.2025 | -2.2751 | 120.9412 | -0.027161 | 0.0052615 | -0.0020167 | 0.0043023 | 0.0025485 | 7.0582e-05 | -0.0022345 | -0.020172 | 0.0024589 | 0.082657 | 0.067763 | -0.0028112 | 0.00026062 | -0.0033219 | -1.5289 | -1.2314 | -2.4628 | -1.6296 | -1.4648 | -2.3575 | -1.5335 | 0.082397 | 121.0556 | -2.4445 | 120.9366 | -2.0599 | -2.2522 | -2.1515 | -0.18768 | -122.1725 | -122.5708 | 0.81024 | 0.74158 | -0.082398 | 0.92926 | 0.10529 | -0.16937 | 0.11444 | -0.004578 | 0.21515 | 0.1236 | 0.022888 | 0.29297 | 0.19226 | 0.99793 | 0.83313 | 0.38452 | 123.381 | 1.2314 | 123.5001 | 1.0437 | 123.3307 | -123.4039 | -123.3856 | 0.64545 | 123.2117 | 0.74615 | 2.3575
1269.4844 | 123.1888 | -2.3209 | 120.9 | -0.095825 | 0.0059025 | -0.0043665 | 0.0010981 | 0.00062594 | 0.005411 | 0.00011527 | 0.098846 | 0.0018179 | 0.08458 | 0.064986 | -0.0015296 | -0.00038018 | -0.0022537 | -1.8402 | -1.387 | -2.7924 | -1.9638 | -1.7578 | -3.0853 | -1.6983 | -0.059509 | 120.9641 | -2.6276 | 120.8542 | -2.1515 | -2.3163 | -2.1744 | -0.4715 | -122.287 | -122.8638 | 0.56305 | 0.62256 | -0.76446 | 1.0941 | -0.29297 | -0.3067 | 0.064087 | -0.045776 | 0.16937 | 0.14649 | 0.004578 | 0.45319 | 0.31128 | 1.0345 | 0.82855 | 0.47607 | 123.4817 | 1.4053 | 123.5916 | 0.93384 | 123.2849 | -123.6923 | -123.5275 | 0.35706 | 123.175 | 0.48065 | 2.2614
1270.4844 | 123.2071 | -2.3529 | 120.9091 | -0.057678 | 0.0046207 | -0.0026575 | 0.0032343 | 0.00062594 | 0.0011386 | 0.0011835 | -0.047638 | 0.0016043 | 0.08458 | 0.071395 | -0.0019568 | -0.00080758 | -0.00075834 | -1.5839 | -1.2543 | -2.4536 | -1.6891 | -1.5335 | -2.3712 | -1.593 | 0.041199 | 121.0831 | -2.4353 | 120.8679 | -2.1286 | -2.3163 | -2.1881 | -0.10071 | -122.1634 | -122.5983 | 0.8194 | 0.75989 | -0.018311 | 0.86059 | 0.082397 | -0.082398 | 0.17395 | -0.041199 | 0.2243 | 0.16479 | 0.036621 | 0.24719 | 0.11902 | 0.9201 | 0.76446 | 0.3067 | 123.3032 | 1.1993 | 123.5184 | 1.0986 | 123.436 | -123.3627 | -123.3444 | 0.66376 | 123.2208 | 0.76904 | 2.3941
1271.5469 | 123.2162 | -2.1149 | 121.1334 | -0.011902 | 0.0026981 | -0.0035119 | 0.0015253 | 0.0014803 | 0.0022068 | -0.00031193 | -0.0018616 | 0.0016043 | 0.083298 | 0.061782 | -0.004093 | 4.7018e-05 | -0.0016129 | -1.4374 | -1.1581 | -2.2476 | -1.5427 | -1.3733 | -2.1515 | -1.442 | 0.1236 | 121.2479 | -2.243 | 121.1151 | -1.8723 | -2.0599 | -1.9363 | -0.13275 | -122.2916 | -122.6761 | 0.74158 | 0.67291 | -0.036621 | 0.80566 | 0.096131 | -0.12817 | 0.11444 | -0.018311 | 0.24262 | 0.17853 | 0.054931 | 0.3067 | 0.1831 | 0.87433 | 0.70496 | 0.37079 | 123.3582 | 1.0895 | 123.4909 | 0.95673 | 123.3627 | -123.381 | -123.3765 | 0.5722 | 123.23 | 0.67749 | 2.2385
1272.4844 | 123.2391 | -2.0142 | 121.225 | -0.019531 | 0.0037661 | -0.0039393 | 0.0023797 | 0.0014803 | 0.0015658 | -0.0020209 | -0.041534 | 0.0016043 | 0.082871 | 0.064132 | -0.0032386 | -0.0023028 | 0.0030869 | -1.4053 | -1.1215 | -2.2202 | -1.5335 | -1.3367 | -2.0874 | -1.4145 | 0.10986 | 121.2982 | -2.1973 | 121.2387 | -1.7487 | -1.9775 | -1.8448 | -0.20599 | -122.3465 | -122.7585 | 0.67749 | 0.59967 | -0.073242 | 0.80566 | 0.13275 | -0.18311 | 0.073242 | 0.013732 | 0.2655 | 0.16937 | 0.036621 | 0.35248 | 0.21973 | 0.88348 | 0.68665 | 0.44861 | 123.436 | 1.0986 | 123.4955 | 0.89264 | 123.3124 | -123.4451 | -123.4222 | 0.48065 | 123.2529 | 0.60883 | 2.124
1273.5469 | 123.1934 | -2.2797 | 121.0236 | -0.0042723 | 0.0054751 | -0.0030847 | 0.00067072 | -0.0021513 | 7.0582e-05 | -0.0022345 | 0.05307 | 0.00010888 | 0.082871 | 0.066054 | -0.003025 | -0.0014484 | -0.00011754 | -1.5152 | -1.2131 | -2.3895 | -1.6251 | -1.4648 | -2.2842 | -1.4923 | 0.064087 | 121.1334 | -2.4078 | 120.9045 | -2.037 | -2.211 | -2.1378 | -0.10986 | -122.2366 | -122.6486 | 0.81482 | 0.78735 | -0.004578 | 0.89722 | 0.10528 | -0.12817 | 0.10986 | -0.11902 | 0.24262 | 0.14191 | 0.068664 | 0.27008 | 0.19684 | 0.92468 | 0.76446 | 0.37079 | 123.3124 | 1.1765 | 123.5413 | 1.0666 | 123.4131 | -123.4131 | -123.4314 | 0.6546 | 123.1842 | 0.76447 | 2.3438
1274.5312 | 123.1842 | -2.2247 | 121.0007 | -0.0042723 | 0.0039799 | -0.0013757 | 0.0051569 | 0.0025485 | 0.0022068 | -0.0043707 | -0.05069 | 0.0024589 | 0.083725 | 0.066482 | -0.0049476 | -0.00059378 | -0.00011754 | -1.5472 | -1.2177 | -2.4033 | -1.6708 | -1.5518 | -2.3529 | -1.5564 | 0.022888 | 121.1426 | -2.3941 | 120.8954 | -1.9913 | -2.2568 | -2.1561 | -0.17853 | -122.2183 | -122.6715 | 0.67291 | 0.66833 | -0.12817 | 0.84686 | 0.050354 | -0.16937 | 0.14191 | -0.10528 | 0.23346 | 0.068664 | -0.032044 | 0.23804 | 0.13733 | 0.85144 | 0.73242 | 0.40283 | 123.2895 | 1.1856 | 123.5367 | 1.0071 | 123.3673 | -123.4039 | -123.3948 | 0.55389 | 123.1201 | 0.67749 | 2.2476
1275.6562 | 123.1796 | -2.2797 | 120.9641 | -0.0042723 | 0.0018435 | -0.0024439 | 0.0023797 | -0.00065586 | 0.0062656 | -0.00052553 | -0.014069 | 0.0024589 | 0.082871 | 0.066054 | -0.003025 | -0.00038018 | -0.0031081 | -1.5793 | -1.2268 | -2.4628 | -1.7624 | -1.5518 | -2.1149 | -1.6205 | 0.022888 | 121.0785 | -2.4445 | 120.9229 | -2.0966 | -2.2751 | -2.1561 | -0.18311 | -122.1909 | -122.7264 | 0.72784 | 0.65918 | 0.1648 | 0.84229 | 0.3479 | -0.16479 | 0.11444 | -0.041198 | 0.18311 | 0.1236 | 0.004578 | 0.28839 | 0.16937 | 0.91095 | 0.70038 | 0.3479 | 123.3673 | 1.236 | 123.5229 | 1.0529 | 123.3582 | -123.4268 | -123.4085 | 0.51727 | 123.2025 | 0.70038 | 2.3026
1277.125 | 123.2208 | -2.2705 | 120.9457 | -0.057678 | 0.0056889 | -0.0028711 | 0.0034479 | 0.0021213 | 0.0069064 | -0.0045843 | -0.044586 | 0.0018179 | 0.08458 | 0.066054 | -0.0019568 | -0.00080758 | -0.0011855 | -1.5244 | -1.2314 | -2.449 | -1.5656 | -1.3229 | -2.243 | -1.4786 | 0.1236 | 121.1517 | -2.3438 | 120.9549 | -2.0462 | -2.2614 | -2.124 | -0.17853 | -122.1771 | -122.5113 | 0.94757 | 0.79193 | 0.027466 | 0.97046 | 0.20599 | -0.073242 | 0.20599 | 0.009155 | 0.2243 | 0.14648 | 0.009155 | 0.21973 | 0.082397 | 1.1261 | 0.88348 | 0.29755 | 123.2986 | 1.2177 | 123.4955 | 1.0391 | 123.4222 | -123.3948 | -123.2895 | 0.70496 | 123.2254 | 0.74615 | 2.3941
1278.5156 | 123.1934 | -2.243 | 121.0327 | -0.019531 | 0.0022709 | -0.0043665 | 0.00067072 | 0.00019874 | -0.00035682 | -0.00095273 | 0.0011902 | 0.0028861 | 0.083512 | 0.068831 | -0.0004614 | -0.0031574 | 0.00030966 | -1.5472 | -1.181 | -2.4033 | -1.6708 | -1.4877 | -2.3071 | -1.4969 | -0.018311 | 121.1655 | -2.3804 | 120.9595 | -2.0462 | -2.1835 | -2.0691 | -0.16022 | -122.2137 | -122.7036 | 0.75531 | 0.74615 | -0.064087 | 0.90637 | 0.09613 | -0.13733 | 0.13275 | -0.073242 | 0.19684 | 0.17395 | 0.059509 | 0.31128 | 0.19684 | 0.91553 | 0.73242 | 0.33417 | 123.3398 | 1.2222 | 123.5458 | 1.062 | 123.4085 | -123.436 | -123.4131 | 0.57221 | 123.2025 | 0.6958 | 2.2247
1279.1562 | 123.1979 | -2.1881 | 121.0785 | -0.080566 | 0.0035525 | -0.00094846 | 0.0025933 | 0.0036165 | 0.0039158 | 0.0013971 | -0.035431 | 0.0018179 | 0.085434 | 0.07289 | -0.0034522 | -0.0014484 | 0.00030966 | -1.4603 | -1.1353 | -2.3163 | -1.5701 | -1.4191 | -2.2385 | -1.4923 | 0.07782 | 121.2021 | -2.298 | 121.0327 | -1.973 | -2.1606 | -2.0554 | -0.12817 | -122.2137 | -122.6486 | 0.76904 | 0.6958 | -0.050354 | 0.82397 | 0.07782 | -0.10986 | 0.1236 | -0.045776 | 0.21515 | 0.13275 | 0.027465 | 0.24261 | 0.13733 | 0.89722 | 0.74615 | 0.32501 | 123.3307 | 1.181 | 123.5001 | 1.0529 | 123.3902 | -123.3948 | -123.3765 | 0.61798 | 123.2208 | 0.72784 | 2.2659
1281.2344 | 123.2574 | -2.0233 | 121.2021 | -0.03479 | 0.0029117 | -0.0026575 | 0.0023797 | 0.00019874 | -0.0012112 | -0.00052553 | 0.046967 | -0.00031832 | 0.081803 | 0.0652 | -0.0019568 | -0.001662 | -0.0013991 | -1.355 | -1.0483 | -2.1561 | -1.4191 | -1.2772 | -2.0416 | -1.3092 | 0.091553 | 121.3303 | -2.1606 | 121.2021 | -1.7624 | -1.9318 | -1.8082 | -0.13275 | -122.2504 | -122.6212 | 0.74615 | 0.71411 | -0.018311 | 0.84686 | 0.11444 | -0.13733 | 0.12817 | 0 | 0.26093 | 0.21515 | 0.091552 | 0.35248 | 0.22888 | 0.87891 | 0.737 | 0.39826 | 123.3627 | 1.1078 | 123.4909 | 0.97504 | 123.3536 | -123.3582 | -123.3627 | 0.60425 | 123.2254 | 0.66834 | 2.1149
1282.2812 | 123.1888 | -2.0874 | 121.17 | -0.057678 | 0.0037661 | -0.0039393 | 0.0023797 | -0.00086946 | 0.0017794 | 0.00096987 | -0.056793 | 0.0030997 | 0.084793 | 0.064773 | -0.0034522 | -0.0012348 | 0.0018051 | -1.4236 | -1.0803 | -2.2522 | -1.5564 | -1.4328 | -2.211 | -1.4374 | 0.004578 | 121.3486 | -2.2339 | 121.1197 | -1.9043 | -2.0966 | -1.9501 | -0.16479 | -122.2504 | -122.7264 | 0.6546 | 0.65002 | -0.1236 | 0.81482 | 0.041198 | -0.14649 | 0.17853 | -0.050354 | 0.18311 | 0.13733 | -0.009156 | 0.28381 | 0.13733 | 0.8194 | 0.6958 | 0.32959 | 123.3536 | 1.1719 | 123.5825 | 1.0071 | 123.436 | -123.4222 | -123.4039 | 0.53101 | 123.2071 | 0.66376 | 2.092
1283.0312 | 123.2574 | -2.1378 | 121.0556 | -0.080566 | 0.0018435 | -0.00030766 | 0.00088432 | -0.0032193 | 0.0019932 | 0.00075627 | 0.037811 | -0.0011727 | 0.083298 | 0.064559 | -0.0028112 | -0.0031574 | -0.0035355 | -1.4191 | -1.149 | -2.3026 | -1.474 | -1.3046 | -2.1515 | -1.3687 | 0.15106 | 121.2341 | -2.2522 | 121.1105 | -1.8814 | -2.0508 | -1.9409 | -0.16479 | -122.2046 | -122.5296 | 0.83313 | 0.76904 | -0.013733 | 0.93384 | 0.15106 | -0.11444 | 0.17853 | 0.054932 | 0.25635 | 0.19684 | 0.086975 | 0.31128 | 0.20142 | 0.99792 | 0.82855 | 0.37079 | 123.3627 | 1.1536 | 123.4863 | 0.98877 | 123.3719 | -123.3582 | -123.3078 | 0.66376 | 123.2483 | 0.71869 | 2.2888
1287.6562 | 123.2071 | -2.3254 | 120.813 | -0.080566 | 0.0026981 | -0.0024439 | 0.0017389 | 0.0036165 | 0.0019932 | 0.0020379 | 0.004242 | -0.00074552 | 0.080948 | 0.065841 | -0.0038794 | -0.0025164 | -0.00054474 | -1.5106 | -1.2909 | -2.4536 | -1.5701 | -1.4191 | -2.3163 | -1.5152 | 2.1515 | 121.0052 | -2.449 | 120.9778 | -2.0187 | -2.2156 | -2.1927 | -0.12817 | -122.1039 | -122.3831 | 0.90637 | 0.81024 | 0.009155 | 0.93841 | 0.13733 | -0.1236 | 0.19226 | 0.16479 | 0.3067 | 0.13275 | 0.10986 | 0.25635 | 0.23346 | 1.0345 | 0.88348 | 0.4303 | 123.4268 | 1.1627 | 123.4543 | 1.0345 | 123.3307 | -123.2666 | -123.262 | 0.75531 | 123.3032 | 0.81482 | 4.4769
1288.2188 | 123.2162 | -2.0966 | 121.138 | -0.042419 | 0.0020573 | -0.0026575 | 0.0015253 | 0.00041234 | 7.0582e-05 | 0.00075627 | 0.025604 | -0.00010472 | 0.081375 | 0.061568 | -0.0034522 | -0.0035846 | -0.0018265 | -1.3641 | -1.1261 | -2.2522 | -1.4694 | -1.3092 | -2.0737 | -1.3367 | 1.5656 | 121.2936 | -2.2293 | 121.1105 | -1.8539 | -2.0325 | -1.9547 | -0.15564 | -122.2641 | -122.6074 | 0.78735 | 0.75989 | 0.022889 | 0.91553 | 0.17853 | -0.13275 | 0.15564 | -0.027465 | 0.24262 | 0.14191 | 0.064087 | 0.27466 | 0.19684 | 0.94299 | 0.78278 | 0.37537 | 123.3398 | 1.1261 | 123.5229 | 0.97046 | 123.3902 | -123.3902 | -123.3673 | 0.62714 | 123.2071 | 0.73242 | 3.6621
1288.7656 | 123.2117 | -2.0737 | 121.1838 | -0.042419 | 0.0033389 | -0.0015893 | 0.0040887 | 0.0027621 | 0.00049778 | -0.0024481 | -0.065949 | 0.0035269 | 0.085434 | 0.066695 | -0.0038794 | -0.0031574 | 0.0030869 | -1.3733 | -1.0941 | -2.2293 | -1.4832 | -1.3275 | -2.1057 | -1.3824 | 1.5198 | 121.3165 | -2.2018 | 121.1792 | -1.8082 | -2.0187 | -1.9043 | -0.15564 | -122.2778 | -122.6669 | 0.74615 | 0.69122 | -0.032044 | 0.84686 | 0.1236 | -0.12817 | 0.13275 | -0.004578 | 0.2655 | 0.16937 | 0.054931 | 0.29755 | 0.18311 | 0.90179 | 0.74616 | 0.39368 | 123.381 | 1.1353 | 123.5184 | 0.97961 | 123.3902 | -123.4131 | -123.3856 | 0.59052 | 123.2529 | 0.70038 | 3.5934
1289.4844 | 123.3032 | -2.1515 | 121.0602 | -0.065308 | 0.0035525 | -0.0043665 | 0.0025933 | -0.00022866 | 0.0015658 | -0.0011663 | 0.016449 | 0.00010888 | 0.08223 | 0.061568 | -0.0021704 | -0.0010212 | -0.0022537 | -1.4191 | -1.1902 | -2.33 | -1.6891 | -1.4008 | -1.973 | -1.4191 | 0.29297 | 121.138 | -2.3346 | 121.1334 | -1.8768 | -2.0325 | -1.9501 | -0.17853 | -122.2504 | -122.7493 | 0.75073 | 0.73242 | 0.17853 | 0.91095 | 0.35706 | -0.18311 | 0.077819 | 0.073242 | 0.27466 | 0.20142 | 0.11902 | 0.38452 | 0.30212 | 0.92926 | 0.64087 | 0.45776 | 123.468 | 1.1398 | 123.4726 | 0.9613 | 123.2895 | -123.3902 | -123.3948 | 0.46234 | 123.2849 | 0.73242 | 2.4445
1290.5625 | 123.2712 | -2.3209 | 120.8542 | -0.13397 | 0.0048343 | -0.0024439 | -0.00082468 | -0.0030057 | 0.0013522 | -0.0015935 | 0.0072936 | 0.00096348 | 0.080521 | 0.059432 | -0.0036658 | -0.001662 | 0.0018051 | -1.5976 | -1.3275 | -2.504 | -1.6663 | -1.4969 | -2.4033 | -1.5381 | 0.21973 | 120.9778 | -2.4811 | 120.9 | -2.0737 | -2.2339 | -2.1469 | -0.1831 | -122.1817 | -122.5204 | 0.82397 | 0.78278 | -0.082397 | 0.96588 | 0.10071 | -0.16022 | 0.1236 | 0.045776 | 0.24719 | 0.17395 | 0.086975 | 0.33417 | 0.24719 | 1.0071 | 0.83771 | 0.40741 | 123.381 | 1.1765 | 123.4589 | 0.99335 | 123.2986 | -123.3582 | -123.3353 | 0.6546 | 123.2208 | 0.72327 | 2.5406
1291.4844 | 123.2986 | -2.8839 | 120.0851 | -0.042419 | 0.0052615 | -0.0026575 | 0.0023797 | -0.00022866 | 0.0028476 | 0.0022517 | -0.020172 | 0.00074988 | 0.081589 | 0.064986 | -0.0038794 | -0.00080758 | 0.0011643 | -1.9409 | -1.6525 | -3.0258 | -1.9867 | -1.8356 | -2.9617 | -1.8906 | 0.27008 | 120.4193 | -3.0258 | 120.4468 | -2.5497 | -2.742 | -2.6596 | -0.14191 | -121.7377 | -122.0718 | 1.0483 | 0.99335 | -0.07782 | 1.1353 | 0.064087 | -0.14191 | 0.33417 | 0.36163 | 0.33417 | 0.2243 | 0.14191 | 0.36621 | 0.28381 | 1.1902 | 1.0391 | 0.47607 | 123.4726 | 1.3733 | 123.4451 | 1.2314 | 123.3032 | -123.111 | -123.111 | 0.89722 | 123.3307 | 0.94299 | 3.154
1292.4844 | 123.2208 | -2.211 | 121.0327 | 0.056763 | 0.0033389 | -0.0045801 | 0.0013117 | -0.00065586 | 0.0015658 | -0.00073913 | -0.069 | 0.00053628 | 0.084793 | 0.067763 | -0.003025 | -0.0014484 | 0.00095066 | -1.5289 | -1.1719 | -2.3117 | -1.6296 | -1.4786 | -2.2614 | -1.5472 | 0.2243 | 121.2021 | -2.3621 | 121.0327 | -2.0004 | -2.211 | -2.0874 | -0.10071 | -122.2046 | -122.6624 | 0.73242 | 0.66376 | -0.050354 | 0.76447 | 0.050354 | -0.15106 | 0.16937 | 0 | 0.21057 | 0.1236 | 0 | 0.27466 | 0.15106 | 0.83313 | 0.68207 | 0.36163 | 123.3948 | 1.1398 | 123.5641 | 1.0391 | 123.4131 | -123.3444 | -123.3948 | 0.58136 | 123.2437 | 0.68207 | 2.4353
1293.4844 | 123.3215 | -2.0096 | 121.1792 | -0.057678 | 0.0031253 | -0.0024439 | 0.0021661 | 0.0010531 | 0.0030612 | -0.0011663 | -0.023224 | 0.0026725 | 0.083939 | 0.066054 | -0.0021704 | -0.001662 | -0.00097194 | -1.4374 | -1.149 | -2.1881 | -1.4923 | -1.3504 | -2.0599 | -1.3824 | 1.4877 | 121.2936 | -2.179 | 121.2753 | -1.7441 | -2.0142 | -1.7944 | -0.17853 | -122.3282 | -122.6715 | 0.65918 | 0.62714 | -0.050354 | 0.80566 | 0.12817 | -0.16937 | 0.11444 | 0.096131 | 0.2655 | 0.21515 | -0.004577 | 0.38452 | 0.1648 | 0.83771 | 0.6958 | 0.43488 | 123.4543 | 1.0391 | 123.4726 | 0.8606 | 123.3032 | -123.3673 | -123.3582 | 0.51727 | 123.2849 | 0.57221 | 3.4973
1294.4844 | 123.1842 | -2.1194 | 121.1288 | -0.050049 | 0.0037661 | -0.0035119 | 0.0055841 | 0.0016939 | 0.00028418 | 0.0016107 | -0.084259 | 0.0022453 | 0.084793 | 0.063918 | -0.0021704 | -0.00080758 | -0.0028945 | -1.4969 | -1.1673 | -2.3026 | -1.6113 | -1.4694 | -2.2156 | -1.5289 | 1.2268 | 121.2936 | -2.2568 | 121.1014 | -1.918 | -2.1378 | -1.9867 | -0.1831 | -122.2961 | -122.7402 | 0.65002 | 0.59051 | -0.09613 | 0.77362 | 0.086975 | -0.13733 | 0.16479 | -0.027466 | 0.20142 | 0.13275 | -0.01831 | 0.27008 | 0.11902 | 0.83313 | 0.69122 | 0.33875 | 123.3582 | 1.1353 | 123.5504 | 0.95215 | 123.4131 | -123.4314 | -123.3856 | 0.50812 | 123.2208 | 0.62256 | 3.3463
1295.4844 | 123.2758 | -2.1423 | 121.0648 | -0.11871 | 0.0044071 | -0.0013757 | 0.0017389 | -0.0027921 | 0.0019932 | 0.00011527 | 0.019501 | -0.00010472 | 0.083725 | 0.066268 | -0.002384 | -0.0023028 | -0.0035355 | -1.4694 | -1.2314 | -2.2842 | -1.5244 | -1.3412 | -2.1606 | -1.4099 | 1.2131 | 121.1746 | -2.2797 | 121.1197 | -1.8494 | -2.0187 | -1.9272 | -0.14191 | -122.2961 | -122.5891 | 0.80109 | 0.73242 | -0.018311 | 0.87433 | 0.1236 | -0.13733 | 0.10986 | 0.054932 | 0.29297 | 0.21515 | 0.1236 | 0.35248 | 0.26093 | 0.94299 | 0.75989 | 0.4303 | 123.3994 | 1.0529 | 123.4543 | 0.91095 | 123.317 | -123.349 | -123.3444 | 0.61798 | 123.262 | 0.67291 | 3.3554
1296.4844 | 123.2025 | -2.2797 | 120.9732 | -0.03479 | 0.0037661 | -0.0022303 | 0.0023797 | -0.00065586 | 0.0017794 | -0.00073913 | -0.069 | 0.00096348 | 0.083298 | 0.067763 | -0.0008886 | -0.0010212 | 0.0028733 | -1.6022 | -1.2589 | -2.4353 | -1.712 | -1.6022 | -2.3895 | -1.6205 | 0.48523 | 121.17 | -2.4307 | 120.9457 | -2.0874 | -2.2751 | -2.1515 | -0.15564 | -122.2321 | -122.6852 | 0.67749 | 0.65918 | -0.10986 | 0.81482 | 0.045777 | -0.15106 | 0.19684 | -0.027466 | 0.19226 | 0.12817 | 0.004578 | 0.27924 | 0.15564 | 0.83313 | 0.72327 | 0.34332 | 123.3765 | 1.1765 | 123.6008 | 1.0208 | 123.4497 | -123.4085 | -123.4039 | 0.56763 | 123.2254 | 0.67749 | 2.7649
1297.5625 | 123.3261 | -2.1881 | 120.9778 | -0.057678 | 0.0024845 | -0.0018031 | 0.0017389 | -0.00022866 | -0.00078402 | 0.0018243 | -0.023224 | 0.0013907 | 0.083084 | 0.066054 | -0.0032386 | -0.0027302 | 0.0052231 | -1.4969 | -1.268 | -2.3438 | -1.5564 | -1.3824 | -2.211 | -1.4694 | 0.82855 | 121.0785 | -2.3529 | 121.1105 | -1.9272 | -2.092 | -1.9775 | -0.15564 | -122.2458 | -122.5342 | 0.80566 | 0.71869 | -0.022889 | 0.87433 | 0.13275 | -0.16479 | 0.10071 | 0.13275 | 0.26093 | 0.21057 | 0.09613 | 0.37537 | 0.26092 | 0.9613 | 0.78735 | 0.42572 | 123.4634 | 1.0757 | 123.4314 | 0.9201 | 123.2666 | -123.3215 | -123.3307 | 0.63171 | 123.2986 | 0.69122 | 3.0167
1298.4844 | 123.1705 | -2.092 | 121.1609 | -0.042419 | 0.0035525 | -0.0024439 | 0.0047295 | 0.0025485 | 7.0582e-05 | -0.0015935 | -0.069 | 0.0016043 | 0.084366 | 0.066054 | -0.0021704 | -0.0014484 | 0.00052346 | -1.474 | -1.1353 | -2.2339 | -1.5839 | -1.4465 | -2.1927 | -1.4877 | 0.91095 | 121.3303 | -2.2156 | 121.1151 | -1.9043 | -2.092 | -1.9684 | -0.14191 | -122.2961 | -122.7448 | 0.64545 | 0.60425 | -0.10071 | 0.74616 | 0.041199 | -0.1236 | 0.16937 | -0.045777 | 0.18768 | 0.1236 | 0 | 0.24719 | 0.1236 | 0.78735 | 0.65003 | 0.31128 | 123.3307 | 1.0986 | 123.5458 | 0.95673 | 123.4222 | -123.3948 | -123.3765 | 0.50812 | 123.2071 | 0.61798 | 3.0029
1299.4844 | 123.2254 | -2.0782 | 121.1426 | -0.011902 | 0.0026981 | 0.00054694 | 0.0036615 | 0.0012667 | 0.0015658 | 0.00011527 | -0.069 | 0.0033133 | 0.084366 | 0.063491 | -0.0034522 | 0.00068782 | -0.0035355 | -1.5793 | -1.1169 | -2.2339 | -1.5839 | -1.4694 | -2.179 | -1.4832 | 0.79651 | 121.2891 | -2.2293 | 121.1517 | -1.8814 | -2.0599 | -1.9318 | -0.15564 | -122.2595 | -122.7264 | 0.60883 | 0.59509 | -0.10071 | 0.75073 | 0.054932 | -0.15106 | 0.14648 | 0.009155 | 0.19684 | 0.14648 | 0.01831 | 0.29755 | 0.16937 | 0.76447 | 0.65003 | 0.3479 | 123.381 | 1.1169 | 123.5184 | 0.9613 | 123.3673 | -123.3765 | -123.3719 | 0.49439 | 123.23 | 0.49896 | 2.8748
1300.5469 | 123.1842 | -2.0782 | 121.2158 | -0.03479 | 0.0046207 | -0.00073486 | 0.00045712 | -0.00044226 | 0.00028418 | 0.00075627 | -0.069 | 0.0020315 | 0.082444 | 0.063491 | -0.0011022 | -0.0018756 | -0.00097194 | -1.4877 | -1.1581 | -2.2339 | -1.5884 | -1.4557 | -2.1744 | -1.5106 | 0.98877 | 121.3394 | -2.2064 | 121.1517 | -1.886 | -2.0691 | -1.9409 | -0.15564 | -122.374 | -122.8043 | 0.62256 | 0.56763 | -0.09613 | 0.72327 | 0.05951 | -0.12817 | 0.1236 | -0.064087 | 0.19226 | 0.13733 | 0.009155 | 0.2655 | 0.13733 | 0.7782 | 0.64545 | 0.32044 | 123.3582 | 1.0757 | 123.5458 | 0.92011 | 123.4177 | -123.4497 | -123.4222 | 0.48981 | 123.23 | 0.59052 | 3.067
1301.4844 | 123.317 | -2.2018 | 121.0236 | -0.057678 | 0.0044071 | -0.0030847 | 0.0013117 | 0.0012667 | 0.0028476 | 0.00075627 | -0.029327 | 0.0018179 | 0.086716 | 0.068618 | -0.0011022 | -0.001662 | -0.0013991 | -1.5564 | -1.2314 | -2.3712 | -1.6251 | -1.4694 | -2.2522 | -1.5106 | 1.2772 | 121.1563 | -2.3392 | 121.0831 | -1.9043 | -2.0737 | -1.9592 | -0.16937 | -122.2549 | -122.6486 | 0.73242 | 0.69122 | -0.050354 | 0.8606 | 0.11902 | -0.13733 | 0.13275 | 0.059509 | 0.29755 | 0.24261 | 0.12817 | 0.37994 | 0.2655 | 0.90179 | 0.74615 | 0.43488 | 123.4222 | 1.1398 | 123.4955 | 0.97046 | 123.3582 | -123.3948 | -123.3627 | 0.57678 | 123.2849 | 0.64545 | 3.479
1302.4844 | 123.1934 | -2.2293 | 121.0419 | -0.0042723 | 0.0039799 | -0.0035119 | 0.0021661 | -0.0030057 | 0.0024204 | -0.00095273 | -0.059845 | 0.0020315 | 0.083939 | 0.061568 | -0.0038794 | 0.00047422 | 0.0022323 | -1.5839 | -1.2222 | -2.3804 | -1.6937 | -1.5427 | -2.3438 | -1.5747 | 0.26093 | 121.1884 | -2.3804 | 121.0281 | -2.0187 | -2.2018 | -2.0828 | -0.15106 | -122.2641 | -122.7356 | 0.68665 | 0.6546 | -0.11444 | 0.80566 | 0.036621 | -0.15106 | 0.14648 | -0.013733 | 0.21057 | 0.14648 | 0.027466 | 0.29755 | 0.17853 | 0.83771 | 0.68664 | 0.36163 | 123.4085 | 1.1581 | 123.5687 | 1.0071 | 123.4177 | -123.4222 | -123.4222 | 0.53558 | 123.2574 | 0.64545 | 2.4902
1303.4844 | 123.3307 | -2.7054 | 120.5154 | -0.16449 | 0.0061161 | 0.0011877 | 2.9918e-05 | -0.00065586 | 0.004343 | -0.00052553 | 0.0011902 | -0.00095912 | 0.081803 | 0.060927 | -0.0015296 | -0.00059378 | 0.00052346 | -1.8173 | -1.5747 | -2.8793 | -1.8585 | -1.6891 | -2.7145 | -1.7715 | 1.2039 | 120.6482 | -2.8015 | 120.5704 | -2.298 | -2.6001 | -2.4765 | -0.17395 | -122.0901 | -122.374 | 1.0162 | 0.93384 | -0.009156 | 1.1078 | 0.16479 | -0.096131 | 0.13275 | 0.054932 | 0.40741 | 0.22888 | 0.10528 | 0.32501 | 0.20142 | 1.1902 | 1.0208 | 0.50354 | 123.3719 | 1.3046 | 123.4497 | 1.1307 | 123.3536 | -123.3948 | -123.317 | 0.84686 | 123.2758 | 0.88806 | 3.9093
1304.4844 | 123.2346 | -1.9547 | 121.3165 | -0.10345 | 0.0033389 | -0.0030847 | 0.0019525 | -0.00065586 | 0.00071138 | 0.0020379 | -0.065949 | -0.00010472 | 0.08223 | 0.061568 | -0.002384 | -0.0014484 | -0.0013991 | -1.4053 | -1.0574 | -2.2064 | -1.5289 | -1.3687 | -2.1469 | -1.4008 | 0.4715 | 121.4172 | -2.1469 | 121.3165 | -1.7166 | -1.8906 | -1.7761 | -0.25177 | -122.374 | -122.8455 | 0.58594 | 0.55389 | -0.19226 | 0.80566 | 0.059509 | -0.19226 | 0.10071 | 0 | 0.23804 | 0.17853 | 0.064087 | 0.37079 | 0.25635 | 0.83771 | 0.67749 | 0.4303 | 123.4634 | 1.149 | 123.5641 | 0.89722 | 123.3719 | -123.5229 | -123.4634 | 0.42572 | 123.2712 | 0.54932 | 2.4261
1305.4844 | 123.2849 | -2.0325 | 121.1792 | -0.03479 | 0.0052615 | -0.0022303 | 0.0025933 | 0.0034029 | 0.00049778 | -0.0018073 | 0.013397 | 0.0033133 | 0.082657 | 0.061355 | -0.0034522 | 0.00026062 | 0.0013779 | -1.268 | -1.0117 | -2.0737 | -1.3504 | -1.1719 | -1.9867 | -1.2497 | 0.3479 | 121.2753 | -2.1469 | 121.2753 | -1.7349 | -1.8814 | -1.7807 | -0.041198 | -122.1909 | -122.5296 | 0.8606 | 0.78278 | 0.045777 | 0.82397 | 0.086975 | -0.11444 | 0.096131 | 0.096131 | 0.29755 | 0.25177 | 0.15106 | 0.36621 | 0.2655 | 0.90179 | 0.72327 | 0.41199 | 123.4222 | 1.062 | 123.4222 | 1.0208 | 123.3078 | -123.2529 | -123.3261 | 0.68207 | 123.3078 | 0.76447 | 2.3804
1306.5469 | 123.1888 | -2.0691 | 121.2616 | -0.011902 | 0.0039799 | -0.0026575 | 0.0038751 | -0.0012967 | 0.0017794 | -0.00031193 | -0.072052 | 0.0016043 | 0.083939 | 0.066268 | -0.0021704 | -0.00038018 | -0.0033219 | -1.3962 | -1.0529 | -2.243 | -1.5152 | -1.3916 | -2.1698 | -1.4236 | 0.16479 | 121.3669 | -2.1835 | 121.1197 | -1.8631 | -2.0737 | -1.9043 | -0.17395 | -122.3145 | -122.7768 | 0.67749 | 0.64545 | -0.10071 | 0.8194 | 0.073242 | -0.11444 | 0.10529 | -0.14191 | 0.20599 | 0.1648 | -0.004577 | 0.27924 | 0.10986 | 0.85144 | 0.72784 | 0.32044 | 123.3032 | 1.1902 | 123.5504 | 1.0162 | 123.436 | -123.5046 | -123.4451 | 0.55389 | 123.1888 | 0.67291 | 2.2339
1307.4844 | 123.317 | -1.9867 | 121.2067 | -0.027161 | 0.0024845 | -0.0039393 | 0.0036615 | 0.0031893 | 0.0034884 | 0.0013971 | -0.032379 | -0.00095912 | 0.083939 | 0.064773 | -0.0028112 | -0.0027302 | 0.0015915 | -1.2817 | -1.0483 | -2.1011 | -1.5976 | -1.3 | -1.7807 | -1.2817 | 0.27466 | 121.344 | -2.1744 | 121.312 | -1.7075 | -1.886 | -1.7807 | -0.11444 | -122.2549 | -122.8043 | 0.68664 | 0.70496 | 0.20599 | 0.8194 | 0.32043 | -0.18768 | 0.13733 | 0.10529 | 0.27924 | 0.20599 | 0.10071 | 0.39368 | 0.28839 | 0.80109 | 0.50354 | 0.46692 | 123.4863 | 1.0529 | 123.5184 | 0.93841 | 123.3307 | -123.3078 | -123.381 | 0.3891 | 123.2986 | 0.70496 | 2.2614
1308.4844 | 123.2895 | -2.1423 | 121.0922 | -0.057678 | 0.0026981 | -0.0045801 | 0.0049433 | -0.00086946 | 0.0024204 | 0.0011835 | -0.053741 | 0.0028861 | 0.08223 | 0.064345 | -0.0045202 | -0.001662 | 0.0011643 | -1.442 | -1.1124 | -2.2888 | -1.5152 | -1.387 | -2.2156 | -1.4008 | 0.16479 | 121.2708 | -2.2659 | 121.17 | -1.8723 | -2.0599 | -1.9363 | -0.14648 | -122.2046 | -122.6074 | 0.75531 | 0.74158 | -0.073242 | 0.88806 | 0.073242 | -0.1236 | 0.17853 | 0.07782 | 0.27008 | 0.20599 | 0.082397 | 0.32959 | 0.20599 | 0.90179 | 0.77362 | 0.39368 | 123.436 | 1.1765 | 123.5367 | 1.03 | 123.4131 | -123.381 | -123.3582 | 0.62714 | 123.3124 | 0.70038 | 2.3071
1309.5469 | 123.3124 | -2.005 | 121.1929 | -0.080566 | 0.0048343 | -0.0030847 | 0.0010981 | -0.0010831 | 0.0024204 | -0.0013799 | -0.029327 | 0.00010888 | 0.084152 | 0.073318 | -0.004093 | 0.0013288 | -0.0028945 | -1.2863 | -1.0483 | -2.1057 | -1.3596 | -1.181 | -1.9913 | -1.236 | 0.40283 | 121.3898 | -2.1057 | 121.2524 | -1.506 | -1.8265 | -1.7761 | -0.10071 | -122.2412 | -122.5525 | 0.82398 | 0.76904 | 0.013733 | 0.86975 | 0.11444 | -0.10071 | 0.19684 | 0.059509 | 0.49896 | 0.22888 | 0.17853 | 0.32959 | 0.27924 | 0.92468 | 0.74616 | 0.59967 | 123.3582 | 1.0574 | 123.4955 | 0.95673 | 123.3948 | -123.2986 | -123.2986 | 0.64545 | 123.2574 | 0.71869 | 2.4078
1310.4844 | 123.3856 | -1.8219 | 121.3165 | -0.03479 | 0.0048343 | -0.0043665 | 0.0023797 | 0.0016939 | 0.0034884 | 0.0018243 | -0.0079652 | 0.00032248 | 0.084793 | 0.069045 | -0.002384 | -0.00059378 | 0.0030869 | -1.1856 | -0.95215 | -1.9547 | -1.2314 | -1.0849 | -1.8311 | -1.1353 | 0.78278 | 121.5408 | -1.9547 | 121.4951 | -1.5152 | -1.712 | -1.5747 | -0.13275 | -122.2687 | -122.5479 | 0.737 | 0.68664 | -0.009156 | 0.8194 | 0.1236 | -0.13275 | 0.22431 | 0.17853 | 0.3067 | 0.24719 | 0.10986 | 0.37994 | 0.24262 | 0.86975 | 0.72327 | 0.43945 | 123.4497 | 1.0025 | 123.4955 | 0.86975 | 123.3627 | -123.2712 | -123.2712 | 0.59051 | 123.317 | 0.63629 | 2.6047
1311.4844 | 123.2071 | -1.8906 | 121.431 | -0.072937 | 0.0031253 | -0.0026575 | 0.0034479 | -0.0034329 | 0.0013522 | -0.0026617 | 0.004242 | 0.0016043 | 0.08458 | 0.067336 | -0.0017432 | -0.0035846 | 0.00095066 | -1.2543 | -0.90179 | -1.9867 | -1.3504 | -1.1856 | -1.8997 | -1.236 | 0.37537 | 121.5866 | -2.0004 | 121.3531 | -1.6342 | -1.8219 | -1.7258 | -0.09613 | -122.3328 | -122.7814 | 0.70496 | 0.6546 | -0.009155 | 0.75073 | 0.086975 | -0.10986 | 0.15564 | -0.07782 | 0.25635 | 0.16479 | 0.068665 | 0.27466 | 0.17853 | 0.80109 | 0.63629 | 0.36621 | 123.3536 | 1.0849 | 123.587 | 0.98877 | 123.4772 | -123.4177 | -123.4314 | 0.54016 | 123.2437 | 0.63629 | 2.2659
1312.5469 | 123.2849 | -1.7258 | 121.5042 | -0.03479 | 0.0020573 | -0.0054347 | 0.0021661 | 0.00062594 | 0.00071138 | -0.0018073 | -0.062897 | 0.0024589 | 0.083084 | 0.068618 | -0.0036658 | 0.00047422 | 0.0018051 | -1.1993 | -0.85144 | -1.8906 | -1.2726 | -1.1307 | -1.8082 | -1.1673 | 1.0666 | 121.6644 | -1.8677 | 121.5408 | -1.4648 | -1.6525 | -1.5289 | -0.16479 | -122.3557 | -122.7768 | 0.59509 | 0.55847 | -0.082398 | 0.72327 | 0.082397 | -0.14191 | 0.16022 | 0.036622 | 0.26093 | 0.19684 | 0.073242 | 0.33874 | 0.21515 | 0.75989 | 0.61798 | 0.40283 | 123.4085 | 1.0391 | 123.5321 | 0.87433 | 123.3902 | -123.3948 | -123.3719 | 0.45319 | 123.2666 | 0.52643 | 2.7924
1313.4844 | 123.2895 | -2.0279 | 121.1929 | -0.050049 | 0.0018435 | -0.0054347 | 0.00024352 | 0.0019077 | 0.00071138 | -0.00095273 | 0.034759 | -0.00053192 | 0.08223 | 0.063277 | -0.0034522 | -0.0027302 | 9.6064e-05 | -1.3412 | -1.1169 | -2.1973 | -1.3824 | -1.2131 | -2.0462 | -1.2817 | 1.1673 | 121.3074 | -2.1744 | 121.2433 | -1.7624 | -1.9135 | -1.8402 | -0.16937 | -122.3099 | -122.5754 | 0.81482 | 0.74616 | -0.018311 | 0.91553 | 0.15106 | -0.14648 | 0.11444 | 0.050354 | 0.2655 | 0.18768 | 0.11444 | 0.33417 | 0.26092 | 0.98419 | 0.81482 | 0.41199 | 123.4177 | 1.0803 | 123.4818 | 0.91095 | 123.3353 | -123.3902 | -123.3673 | 0.64545 | 123.2712 | 0.68665 | 3.1952
1314.4844 | 123.3124 | -1.6891 | 121.5225 | -0.10345 | 0.0026981 | -0.0018031 | -0.0012519 | -0.0074919 | 0.0013522 | -0.0013799 | -0.014069 | 0.00010888 | 0.081589 | 0.065414 | -0.0025976 | -0.0025164 | 0.00052346 | -1.1078 | -0.87891 | -1.8677 | -1.2268 | -1.0025 | -1.68 | -1.0941 | 1.355 | 121.6644 | -1.8585 | 121.5958 | -1.4191 | -1.5884 | -1.4832 | -0.17853 | -122.4014 | -122.7493 | 0.68665 | 0.59509 | 0.009155 | 0.77362 | 0.18768 | -0.16937 | 0.14191 | 0.073242 | 0.27008 | 0.20599 | 0.10071 | 0.37537 | 0.27008 | 0.86517 | 0.64087 | 0.43945 | 123.4543 | 0.98877 | 123.5229 | 0.81024 | 123.3536 | -123.3902 | -123.381 | 0.46234 | 123.2849 | 0.58136 | 3.0441
1315.4844 | 123.3444 | -1.8631 | 121.3165 | -0.065308 | 0.0054751 | -0.0041529 | 0.0023797 | -0.0012967 | -0.00078402 | -9.8328e-05 | 0.013397 | 0.00096348 | 0.082657 | 0.066482 | -0.0034522 | -0.0027302 | 0.0011643 | -1.2131 | -0.94757 | -1.9638 | -1.2909 | -1.1444 | -1.8723 | -1.1719 | 1.1673 | 121.55 | -1.9867 | 121.4447 | -1.5335 | -1.6846 | -1.799 | -0.10071 | -122.2641 | -122.6074 | 0.71869 | 0.69122 | -0.009155 | 0.79193 | 0.091553 | -0.1236 | 0.23346 | 0.12817 | 0.32959 | 0.064087 | 0.17853 | 0.18768 | 0.30212 | 0.8194 | 0.67291 | 0.45319 | 123.4314 | 1.0162 | 123.5367 | 0.91553 | 123.4131 | -123.2803 | -123.3032 | 0.5722 | 123.3078 | 0.65002 | 3.0304
1316.5469 | 123.349 | -1.9638 | 121.2341 | -0.027161 | 0.0046207 | -0.0050073 | 0.0023797 | -0.0012967 | -0.00057042 | -0.0052251 | 0.043915 | 0.0011771 | 0.080521 | 0.068831 | -0.004093 | -0.0035846 | -0.0011855 | -1.2405 | -0.99792 | -2.0966 | -1.2543 | -1.0941 | -1.9409 | -1.1307 | 0.40741 | 121.3806 | -2.0874 | 121.3623 | -1.6251 | -1.7899 | -1.7212 | -0.13275 | -122.2321 | -122.4884 | 0.86975 | 0.83313 | 0.022888 | 0.96588 | 0.15564 | -0.1236 | 0.14648 | 0.12817 | 0.33874 | 0.24262 | 0.17395 | 0.36621 | 0.29755 | 1.0025 | 0.84229 | 0.46234 | 123.4497 | 1.0986 | 123.468 | 0.96588 | 123.3444 | -123.3307 | -123.3215 | 0.70953 | 123.3261 | 0.72327 | 2.3712
1317.4844 | 123.317 | -1.8173 | 121.3989 | -0.050049 | 0.0044071 | -0.0020167 | 0.0010981 | 0.0012667 | -0.00035682 | 0.0013971 | 0.013397 | 0.00010888 | 0.082444 | 0.067123 | -0.002384 | -0.0020892 | 0.00030966 | -1.0849 | -0.82855 | -1.9272 | -1.1581 | -0.99335 | -1.799 | -0.99792 | 0.35248 | 121.5683 | -1.9363 | 121.4859 | -1.5244 | -1.6708 | -1.5839 | -0.10986 | -122.2275 | -122.5571 | 0.82398 | 0.8194 | 0.018311 | 0.92926 | 0.12817 | -0.11902 | 0.16937 | 0.086975 | 0.29297 | 0.23346 | 0.14649 | 0.35248 | 0.2655 | 0.93384 | 0.76904 | 0.41199 | 123.4222 | 1.0986 | 123.5046 | 0.98877 | 123.3856 | -123.3261 | -123.3353 | 0.65918 | 123.3032 | 0.73242 | 2.1698
1318.5469 | 123.3353 | -1.8631 | 121.3531 | -0.027161 | 0.0026981 | -0.0041529 | 0.0025933 | 0.0023349 | -0.00078402 | 0.0011835 | -0.047638 | 0.00074988 | 0.081589 | 0.070754 | -0.0032386 | -0.00038018 | -0.00033114 | -1.2039 | -0.92926 | -2.037 | -1.2405 | -1.0757 | -1.9592 | -1.1627 | 0.40741 | 121.5134 | -1.9913 | 121.4172 | -1.6113 | -1.7624 | -1.6388 | -0.17395 | -122.2824 | -122.5937 | 0.78735 | 0.70038 | -0.096131 | 0.87433 | 0.077819 | -0.12817 | 0.16022 | 0.064087 | 0.25177 | 0.2243 | 0.10071 | 0.35248 | 0.22888 | 0.9613 | 0.79651 | 0.37994 | 123.4085 | 1.1078 | 123.5046 | 0.93384 | 123.3765 | -123.3902 | -123.3444 | 0.62256 | 123.2803 | 0.65918 | 2.2705
1319.4844 | 123.3673 | -2.0462 | 121.1609 | -0.057678 | 0.0046207 | -0.0035119 | -0.00061088 | -0.0038603 | 0.0049838 | -0.00052553 | 0.0011902 | 0.0024589 | 0.08223 | 0.059859 | -0.002384 | -0.001662 | -0.0033219 | -1.268 | -1.0345 | -2.1835 | -1.3092 | -1.1398 | -1.9913 | -1.2085 | 0.41657 | 121.2936 | -2.1927 | 121.2891 | -1.712 | -1.9043 | -1.8265 | -0.13733 | -122.1954 | -122.4701 | 0.90637 | 0.83771 | 0.054932 | 0.97504 | 0.19226 | -0.14648 | 0.13275 | 0.12817 | 0.33417 | 0.21973 | 0.14191 | 0.36621 | 0.28839 | 1.0437 | 0.87433 | 0.48065 | 123.4818 | 1.149 | 123.4863 | 1.0117 | 123.3398 | -123.3444 | -123.3536 | 0.737 | 123.3353 | 0.7782 | 2.4628
1320.5469 | 123.2849 | -1.8082 | 121.4218 | -0.042419 | 0.0022709 | -0.0045801 | 0.0038751 | 0.0016939 | 0.0013522 | 0.00075627 | 0.0011902 | 0.0013907 | 0.083939 | 0.070327 | -0.002384 | -0.00059378 | -0.00054474 | -1.1765 | -0.89264 | -1.9501 | -1.2543 | -1.0941 | -1.8494 | -1.1261 | 0.35706 | 121.5729 | -1.9547 | 121.4676 | -1.5335 | -1.7029 | -1.6022 | -0.14191 | -122.3145 | -122.6761 | 0.71411 | 0.68207 | -0.041198 | 0.82397 | 0.10071 | -0.14648 | 0.15106 | 0.045776 | 0.27466 | 0.20599 | 0.10529 | 0.35248 | 0.25177 | 0.85602 | 0.6958 | 0.42114 | 123.4222 | 1.0574 | 123.5275 | 0.91553 | 123.381 | -123.3719 | -123.3765 | 0.5539 | 123.2758 | 0.63171 | 2.1652
1321.5 | 123.2254 | -2.1561 | 121.1105 | 0.0033567 | 0.0044071 | -0.00094846 | 0.0040887 | 0.0025485 | 0.00092498 | 0.0022517 | -0.12088 | 0.0028861 | 0.082871 | 0.073531 | -0.0025976 | -0.0014484 | -0.0026809 | -1.5152 | -1.181 | -2.3895 | -1.6113 | -1.4694 | -2.2614 | -1.5335 | 0.27466 | 121.1975 | -2.3712 | 121.106 | -1.9409 | -2.1286 | -2.0096 | -0.23346 | -122.2916 | -122.7219 | 0.68665 | 0.62256 | -0.10529 | 0.85602 | 0.12817 | -0.21515 | 0.086975 | -0.004578 | 0.21515 | 0.14648 | 0.027466 | 0.36163 | 0.24261 | 0.9201 | 0.7782 | 0.4303 | 123.4772 | 1.2085 | 123.5687 | 0.97504 | 123.3536 | -123.5001 | -123.4818 | 0.54474 | 123.262 | 0.64087 | 2.4307
1322.5469 | 123.3398 | -1.8631 | 121.3623 | -0.080566 | 0.0050479 | -0.0024439 | 0.0025933 | -0.0012967 | 0.0017794 | 0.00075627 | -0.01712 | 0.00053628 | 0.083298 | 0.066268 | -0.0021704 | -0.0018756 | -0.0018265 | -1.149 | -0.90637 | -2.0096 | -1.2131 | -1.0849 | -1.8265 | -1.1261 | 0.36163 | 121.4767 | -2.0004 | 121.4493 | -1.5656 | -1.7578 | -1.6434 | -0.14649 | -122.2687 | -122.5754 | 0.7782 | 0.737 | 0.036621 | 0.88348 | 0.18311 | -0.13733 | 0.11444 | 0.086975 | 0.29755 | 0.21973 | 0.10529 | 0.35706 | 0.24262 | 0.92468 | 0.79651 | 0.43488 | 123.4497 | 1.1032 | 123.4772 | 0.95673 | 123.3398 | -123.3719 | -123.3627 | 0.65002 | 123.3124 | 0.71411 | 2.2247
1323.4844 | 123.3398 | -1.9455 | 121.2753 | 0.033875 | 0.0046207 | -0.0041529 | 0.0017389 | 0.0012667 | 0.0019932 | -0.0022345 | 0.013397 | 0.00032248 | 0.083298 | 0.069472 | -0.002384 | -0.001662 | 0.00095066 | -1.2131 | -0.97046 | -2.0325 | -1.2543 | -1.0803 | -1.8402 | -1.1765 | 0.33417 | 121.4081 | -2.0691 | 121.3623 | -1.6113 | -1.7944 | -1.7303 | -0.086975 | -122.2458 | -122.5296 | 0.86517 | 0.76904 | 0.10529 | 0.85602 | 0.19226 | -0.1236 | 0.13275 | 0.086975 | 0.33417 | 0.21515 | 0.15106 | 0.33874 | 0.27466 | 0.95215 | 0.7782 | 0.45776 | 123.4314 | 1.062 | 123.4772 | 0.97504 | 123.3536 | -123.3078 | -123.3444 | 0.69122 | 123.3078 | 0.73242 | 2.2797
1324.4844 | 123.2803 | -1.9409 | 121.2936 | -0.057678 | 0.0018435 | -0.0043665 | 0.0017389 | 0.0042575 | 7.0582e-05 | -0.0020209 | -0.026276 | 0.00053628 | 0.083084 | 0.063277 | -0.0008886 | -0.0023028 | -0.0037491 | -1.3275 | -1.062 | -2.124 | -1.4328 | -1.3596 | -2.0142 | -1.2634 | 0.2243 | 121.4172 | -2.1332 | 121.3531 | -1.6479 | -1.8173 | -1.7303 | -0.18311 | -122.3557 | -122.7264 | 0.58136 | 0.67749 | -0.073242 | 0.8606 | 0.10986 | -0.19226 | 0.1236 | 0.059509 | 0.29297 | 0.21057 | 0.1236 | 0.40283 | 0.31586 | 0.76447 | 0.69122 | 0.48523 | 123.4863 | 1.062 | 123.5504 | 0.87891 | 123.3582 | -123.4177 | -123.4268 | 0.50812 | 123.2941 | 0.6134 | 2.1652
1325.4844 | 123.3124 | -2.0187 | 121.2112 | 0.010986 | 0.0039799 | -0.0039393 | 0.0013117 | -0.0032193 | 0.0032748 | -0.0011663 | 0.013397 | 0.00074988 | 0.083725 | 0.063064 | -0.0017432 | -0.0018756 | -0.00075834 | -1.3412 | -1.0757 | -2.1606 | -1.3596 | -1.1719 | -1.9592 | -1.2451 | 0.32501 | 121.3531 | -2.1698 | 121.3257 | -1.6891 | -1.8539 | -1.7944 | -0.14191 | -122.287 | -122.5708 | 0.84686 | 0.77362 | 0.059509 | 0.91553 | 0.20142 | -0.15106 | 0.14191 | 0.11444 | 0.32959 | 0.2243 | 0.1648 | 0.37537 | 0.31586 | 0.98877 | 0.80109 | 0.48065 | 123.4955 | 1.0849 | 123.5229 | 0.94299 | 123.3719 | -123.3719 | -123.381 | 0.65918 | 123.3444 | 0.67749 | 2.3438
1326.5625 | 123.2712 | -1.8219 | 121.4172 | -0.050049 | 0.0052615 | -0.0018031 | 0.0028069 | -0.00086946 | 0.00049778 | -0.0028753 | -0.011017 | -0.00053192 | 0.08223 | 0.063277 | -0.0032386 | -0.0010212 | 9.6064e-05 | -0.99335 | -0.77362 | -1.9592 | -1.0666 | -0.86975 | -1.7441 | -0.95215 | 0.31128 | 121.55 | -1.9272 | 121.3348 | -1.2772 | -1.7075 | -1.7075 | -0.13733 | -122.1909 | -122.4838 | 0.95215 | 0.86975 | 0.077819 | 1.0071 | 0.21515 | -0.10529 | 0.13275 | -0.082397 | 0.54474 | 0.11444 | 0.11444 | 0.21973 | 0.21973 | 1.0895 | 0.89264 | 0.65002 | 123.262 | 1.1856 | 123.4772 | 1.0483 | 123.3719 | -123.3765 | -123.3444 | 0.75531 | 123.1567 | 0.82855 | 2.1332
1327.4844 | 123.3261 | -1.9638 | 121.3165 | -0.03479 | 0.0039799 | -0.0035119 | 0.0019525 | 0.0027621 | 0.0013522 | -0.0020209 | 0.022552 | 0.0018179 | 0.082871 | 0.063918 | -0.0036658 | -0.0018756 | 0.0018051 | -1.2955 | -1.0025 | -2.0966 | -1.3412 | -1.181 | -1.9318 | -1.2131 | 0.33875 | 121.4447 | -2.0828 | 121.3623 | -1.6205 | -1.8082 | -1.6983 | -0.13275 | -122.319 | -122.6578 | 0.78278 | 0.75073 | 0.032043 | 0.88348 | 0.1648 | -0.11902 | 0.12817 | 0.045777 | 0.34332 | 0.2655 | 0.15564 | 0.38452 | 0.27466 | 0.91553 | 0.75531 | 0.46234 | 123.4451 | 1.0941 | 123.5275 | 0.9613 | 123.4085 | -123.4131 | -123.3994 | 0.62256 | 123.3261 | 0.66833 | 2.3026
1328.5469 | 123.3444 | -1.8173 | 121.3486 | -0.080566 | 0.0024845 | -0.0035119 | -0.00018368 | 0.0036165 | 0.002634 | -0.0011663 | -0.072052 | 0.00032248 | 0.082444 | 0.070113 | -0.004093 | -0.0027302 | -0.00054474 | -1.2497 | -0.99335 | -2.0142 | -1.2909 | -1.1353 | -1.8723 | -1.2131 | 0.30212 | 121.5179 | -1.9913 | 121.4767 | -1.5701 | -1.7441 | -1.6159 | -0.19684 | -122.3419 | -122.6395 | 0.68207 | 0.60425 | -0.054931 | 0.80109 | 0.14191 | -0.17395 | 0.16937 | 0.12817 | 0.24719 | 0.20142 | 0.073242 | 0.37537 | 0.24719 | 0.87891 | 0.72327 | 0.42114 | 123.468 | 1.0208 | 123.5092 | 0.82398 | 123.3353 | -123.3627 | -123.3398 | 0.52643 | 123.2941 | 0.56763 | 2.1194
1329.4844 | 123.23 | -2.2842 | 121.0098 | 0.010986 | 0.0016299 | -0.0028711 | 0.0010981 | -0.00086946 | -0.001852 | -9.8328e-05 | -0.038483 | 0.0013907 | 0.080521 | 0.064345 | -0.0034522 | -0.0023028 | 0.0024461 | -1.4923 | -1.2543 | -2.4307 | -1.5701 | -1.4053 | -2.243 | -1.4603 | 0.50354 | 121.1655 | -2.3849 | 120.9869 | -1.9958 | -2.2064 | -2.1057 | -0.14648 | -122.2641 | -122.58 | 0.87891 | 0.82398 | 0.041199 | 0.97046 | 0.18768 | -0.10071 | 0.15564 | -0.022889 | 0.28839 | 0.17853 | 0.07782 | 0.27924 | 0.17853 | 1.0254 | 0.8606 | 0.3891 | 123.3719 | 1.1765 | 123.5504 | 1.03 | 123.4497 | -123.4406 | -123.3948 | 0.71411 | 123.2712 | 0.79193 | 2.7878
1330.5469 | 123.2071 | -1.9409 | 121.3531 | -0.072937 | 0.0044071 | -0.00094846 | 0.0049433 | 0.0010531 | 0.00092498 | 0.00032907 | -0.13614 | 0.0033133 | 0.082871 | 0.069259 | -0.0017432 | -0.0025164 | -0.0013991 | -1.355 | -1.03 | -2.1103 | -1.4694 | -1.355 | -2.0554 | -1.3779 | 0.15564 | 121.4996 | -2.0554 | 121.3806 | -1.8311 | -1.8539 | -1.7715 | -0.16937 | -122.3831 | -122.8226 | 0.58594 | 0.56305 | -0.11444 | 0.73242 | 0.054932 | -0.11444 | 0.14648 | 0.027466 | 0.10986 | 0.16937 | 0.086975 | 0.28381 | 0.20142 | 0.75531 | 0.64087 | 0.2243 | 123.436 | 1.0803 | 123.555 | 0.91095 | 123.4406 | -123.4634 | -123.4085 | 0.4715 | 123.3215 | 0.58594 | 2.0966
1331.4844 | 123.2666 | -2.2476 | 121.0098 | -0.011902 | 0.0037661 | -0.0015893 | 0.00088432 | -0.00044226 | 0.0024204 | -0.00031193 | -0.0018616 | 0.00053628 | 0.08223 | 0.060714 | -0.0019568 | -0.0010212 | -0.00011754 | -1.3412 | -1.0986 | -2.5131 | -1.3596 | -1.2131 | -2.2842 | -1.2451 | 0.23804 | 121.1105 | -2.4124 | 121.0281 | -1.9684 | -2.179 | -2.0691 | -0.2655 | -122.1085 | -122.3694 | 1.0345 | 1.0025 | -0.036621 | 1.268 | 0.22888 | -0.1648 | 0.10071 | 0.01831 | 0.27924 | 0.17853 | 0.068665 | 0.34332 | 0.23346 | 1.3 | 1.1536 | 0.44403 | 123.4406 | 1.4145 | 123.5229 | 1.149 | 123.3582 | -123.523 | -123.4222 | 0.88806 | 123.2758 | 0.90637 | 2.4857
1332.4844 | 123.3582 | -2.2018 | 121.0556 | -0.019531 | 0.0026981 | -0.0047937 | 0.0015253 | -0.00044226 | 0.0017794 | -0.0035163 | 0.028656 | 0.00074988 | 0.082016 | 0.060927 | -0.0017432 | -0.0023028 | -0.0022537 | -1.4648 | -1.2131 | -2.417 | -1.5198 | -1.3412 | -2.2156 | -1.3779 | 0.30212 | 121.1105 | -2.3941 | 121.1472 | -1.8448 | -1.9821 | -1.918 | -0.21515 | -122.2687 | -122.5754 | 0.8606 | 0.82397 | -0.013733 | 1.0391 | 0.20142 | -0.19226 | 0.054932 | 0.091553 | 0.35706 | 0.28381 | 0.21973 | 0.47607 | 0.41199 | 1.0757 | 0.89722 | 0.54932 | 123.5413 | 1.2039 | 123.5046 | 0.98877 | 123.3124 | -123.4726 | -123.4497 | 0.68207 | 123.349 | 0.737 | 2.504
1333.5469 | 123.3215 | -1.8539 | 121.3806 | 0.0033567 | 0.0052615 | -0.0011621 | 0.0028069 | 0.0019077 | 0.0017794 | 0.00054267 | -0.081207 | 0.0026725 | 0.080735 | 0.069686 | -0.0021704 | -0.001662 | -0.00075834 | -1.1078 | -0.82855 | -2.0508 | -1.1627 | -1.03 | -1.9272 | -1.0666 | 0.24719 | 121.5134 | -2.0142 | 121.4859 | -1.5793 | -1.7395 | -1.6296 | -0.19684 | -122.2092 | -122.5433 | 0.82397 | 0.78735 | -0.073242 | 0.98419 | 0.1236 | -0.16022 | 0.13275 | 0.10529 | 0.27466 | 0.2243 | 0.11444 | 0.38452 | 0.27466 | 1.0208 | 0.88806 | 0.43487 | 123.5001 | 1.2222 | 123.5275 | 1.0254 | 123.3673 | -123.4314 | -123.3948 | 0.69122 | 123.3398 | 0.74615 | 2.1011
1334.4844 | 123.3536 | -1.9409 | 121.2479 | 0.010986 | 0.0033389 | -0.0037257 | 0.00088432 | -0.0025785 | 0.0028476 | -9.8328e-05 | 0.004242 | 0.0016043 | 0.082657 | 0.06755 | -0.000675 | -0.0020892 | -0.0016129 | -1.1032 | -0.82855 | -2.0416 | -1.1673 | -1.0025 | -1.9821 | -1.0437 | 0.19684 | 121.4813 | -2.0508 | 121.3852 | -1.6251 | -1.9913 | -1.8768 | -0.10071 | -122.0764 | -122.4152 | 0.93842 | 0.89722 | -0.041199 | 0.99792 | 0.059509 | -0.10986 | 0.23346 | 0.13733 | 0.31586 | 0.064087 | -0.050354 | 0.17395 | 0.059509 | 1.0391 | 0.87433 | 0.42572 | 123.436 | 1.2131 | 123.5321 | 1.1124 | 123.4222 | -123.2895 | -123.2986 | 0.77362 | 123.3261 | 0.83771 | 2.1378
1335.4844 | 123.2117 | -1.8951 | 121.4127 | -0.03479 | 0.0037661 | -0.0022303 | 0.00045712 | 0.0010531 | 0.00071138 | -0.00095273 | -0.035431 | 0.0020315 | 0.085007 | 0.061141 | -0.002384 | 0.00026062 | -0.0011855 | -1.2497 | -0.9613 | -2.0416 | -1.3504 | -1.181 | -1.9043 | -1.2268 | 1.3092 | 121.5637 | -2.0233 | 121.3715 | -1.6434 | -1.8402 | -1.7715 | -0.14648 | -122.374 | -122.7631 | 0.71411 | 0.66834 | -0.009155 | 0.81482 | 0.13733 | -0.12817 | 0.15106 | -0.041199 | 0.25177 | 0.1236 | 0.054932 | 0.25177 | 0.18311 | 0.8606 | 0.69122 | 0.37994 | 123.3948 | 1.0803 | 123.587 | 0.93384 | 123.4589 | -123.4543 | -123.436 | 0.54474 | 123.2666 | 0.64545 | 3.2043
1336.5469 | 123.2391 | -2.0599 | 121.2387 | -0.03479 | 0.0024845 | -0.0026575 | 0.0032343 | 0.0029757 | -0.0014248 | 0.0024653 | -0.081207 | 0.0018179 | 0.083512 | 0.069472 | -0.0025976 | 0.0013288 | 0.0028733 | -1.9363 | -1.5976 | -2.2202 | -2.0508 | -1.9089 | -2.1606 | -1.9547 | 1.7761 | 121.4035 | -2.1973 | 121.2479 | -1.8265 | -2.0233 | -1.8906 | -0.16022 | -122.8363 | -123.2895 | 0.15106 | 0.10529 | -0.10071 | 0.2655 | 0.059509 | -0.13733 | 0.16479 | 0.009156 | 0.23346 | 0.16937 | 0.036622 | 0.3067 | 0.17395 | 0.31128 | 0.16937 | 0.37079 | 123.4451 | 0.62256 | 123.6008 | 0.46234 | 123.4634 | -123.4589 | -123.436 | 0.009156 | 123.3078 | 0.1236 | 3.8361
1337.4844 | 123.2254 | -1.8768 | 121.4264 | -0.0042723 | 0.0026981 | -0.0039393 | 0.0015253 | -1.486e-05 | 0.00049778 | 0.00054267 | -0.035431 | 0.0024589 | 0.083298 | 0.063064 | -0.0017432 | -0.0018756 | 0.0039413 | -1.1719 | -0.91095 | -1.9867 | -1.3 | -1.1261 | -1.886 | -1.1673 | 1.2817 | 121.5775 | -2.0096 | 121.3623 | -1.6479 | -1.8402 | -1.7349 | -0.10986 | -122.3373 | -122.7264 | 0.75073 | 0.70953 | -0.009155 | 0.8194 | 0.10071 | -0.13275 | 0.15106 | -0.064087 | 0.22888 | 0.14191 | 0.036621 | 0.27466 | 0.16937 | 0.86059 | 0.68664 | 0.36163 | 123.3719 | 1.0757 | 123.587 | 0.96588 | 123.4543 | -123.4131 | -123.436 | 0.57678 | 123.2391 | 0.70496 | 3.1586
1338.5469 | 123.2895 | -1.8265 | 121.4355 | -0.065308 | 0.0020573 | -0.0035119 | 0.00088432 | -1.486e-05 | 0.0022068 | -0.0011663 | 0.0072936 | 0.00010888 | 0.082444 | 0.068618 | -0.0021704 | -0.0012348 | -0.00075834 | -1.0803 | -0.8194 | -1.9547 | -1.1627 | -0.97504 | -1.8494 | -1.0437 | 1.9638 | 121.5546 | -1.9638 | 121.463 | -1.5656 | -1.7349 | -1.6342 | -0.12817 | -122.2549 | -122.5983 | 0.85144 | 0.78278 | -0.022888 | 0.91095 | 0.10529 | -0.13733 | 0.11902 | 0.027466 | 0.26092 | 0.19226 | 0.091553 | 0.32959 | 0.22888 | 0.97961 | 0.79193 | 0.39825 | 123.4268 | 1.1353 | 123.5184 | 1.0071 | 123.381 | -123.3902 | -123.3994 | 0.66376 | 123.2895 | 0.74615 | 3.7903
1339.4844 | 123.3215 | -1.8036 | 121.4584 | -0.050049 | 0.0035525 | -0.0032983 | 0.00067072 | 0.0027621 | 0.0015658 | -0.0035163 | 0.022552 | -0.00031832 | 0.082871 | 0.064132 | -0.003025 | -0.00080758 | -0.0026809 | -1.0162 | -0.7782 | -1.9455 | -1.0849 | -0.91553 | -1.7578 | -0.97961 | 1.6663 | 121.5683 | -1.9363 | 121.5042 | -1.506 | -1.6617 | -1.5976 | -0.14191 | -122.2366 | -122.5433 | 0.88806 | 0.82398 | 0.045777 | 0.96588 | 0.18768 | -0.13275 | 0.10986 | 0.045776 | 0.29755 | 0.20599 | 0.14191 | 0.33874 | 0.27466 | 1.03 | 0.8606 | 0.4303 | 123.4406 | 1.1673 | 123.5046 | 1.0254 | 123.3719 | -123.4039 | -123.3948 | 0.71869 | 123.3078 | 0.78735 | 3.4698
1340.5469 | 123.2941 | -1.918 | 121.3028 | -0.057678 | 0.0041935 | -0.0067163 | 0.00088432 | 0.0019077 | 0.0028476 | -0.0037299 | -0.023224 | 0.00032248 | 0.083084 | 0.066054 | -0.0021704 | -0.00080758 | 0.0015915 | -1.2451 | -1.0345 | -2.0599 | -1.2955 | -1.1307 | -1.9592 | -1.2039 | 1.1215 | 121.4493 | -2.0691 | 121.3669 | -1.6571 | -1.9043 | -1.7578 | -0.14191 | -122.3373 | -122.5983 | 0.78735 | 0.71411 | -0.041199 | 0.85602 | 0.10071 | -0.15106 | 0.14648 | 0.064087 | 0.26093 | 0.16022 | 0.013733 | 0.31128 | 0.1648 | 0.92926 | 0.76447 | 0.41199 | 123.436 | 1.0254 | 123.5184 | 0.88348 | 123.3673 | -123.3627 | -123.3719 | 0.62256 | 123.2849 | 0.67291 | 3.0396
1341.4844 | 123.3673 | -1.7624 | 121.4767 | -0.027161 | 0.0039799 | -0.0047937 | 0.00067072 | -0.00086946 | 0.0015658 | -0.0013799 | 0.025604 | 0.0011771 | 0.084152 | 0.064345 | -0.0028112 | -0.0014484 | 0.00073706 | -1.1124 | -0.88348 | -1.9135 | -1.149 | -0.97504 | -1.7166 | -1.0483 | 1.3138 | 121.6187 | -1.886 | 121.5866 | -1.4465 | -1.6067 | -1.5427 | -0.15106 | -122.3602 | -122.6257 | 0.78735 | 0.71411 | 0.045776 | 0.86517 | 0.19684 | -0.1236 | 0.14191 | 0.10986 | 0.31586 | 0.21973 | 0.15564 | 0.34332 | 0.27924 | 0.93841 | 0.76446 | 0.43945 | 123.4726 | 1.03 | 123.5046 | 0.87891 | 123.381 | -123.3902 | -123.3627 | 0.6134 | 123.349 | 0.65002 | 3.0762
1342.4844 | 123.3307 | -1.8402 | 121.3943 | -0.027161 | 0.0039799 | -0.0011621 | 0.0021661 | -0.0023649 | 0.0015658 | 0.00054267 | 0.013397 | -0.00010472 | 0.083939 | 0.067977 | -0.003025 | -0.0040118 | -0.0013991 | -1.1581 | -0.87891 | -1.9501 | -1.2314 | -1.062 | -1.8265 | -1.1078 | 1.3824 | 121.5591 | -1.9775 | 121.4722 | -1.5381 | -1.6937 | -1.6388 | -0.10986 | -122.2733 | -122.6257 | 0.7782 | 0.73242 | 0.013733 | 0.84228 | 0.1236 | -0.13733 | 0.1648 | 0.07782 | 0.30212 | 0.20142 | 0.14648 | 0.33874 | 0.28381 | 0.88806 | 0.71869 | 0.43945 | 123.4497 | 1.0712 | 123.5367 | 0.9613 | 123.3994 | -123.3444 | -123.3719 | 0.60883 | 123.3124 | 0.68207 | 3.2227
1343.4844 | 123.2941 | -1.9363 | 121.3211 | -0.0042723 | 0.0050479 | -0.0032983 | 0.0019525 | -0.0015103 | 0.00092498 | -0.0043707 | -0.026276 | 0.0013907 | 0.081162 | 0.068191 | -0.0028112 | -0.0035846 | -0.0018265 | -1.181 | -0.95673 | -2.0828 | -1.2405 | -1.0895 | -1.9089 | -1.1627 | 1.4145 | 121.4539 | -2.0782 | 121.3989 | -1.6663 | -1.8219 | -1.7395 | -0.14649 | -122.2778 | -122.5616 | 0.84686 | 0.77362 | 0.027465 | 0.92011 | 0.17395 | -0.14191 | 0.13275 | 0.07782 | 0.27008 | 0.19684 | 0.11444 | 0.33875 | 0.25635 | 0.99335 | 0.84229 | 0.41199 | 123.4772 | 1.1261 | 123.5321 | 0.97961 | 123.3902 | -123.4039 | -123.3994 | 0.6958 | 123.3353 | 0.75531 | 3.3508
1344.4844 | 123.3627 | -1.8311 | 121.4035 | -0.011902 | 0.0033389 | -0.0043665 | 0.0028069 | -0.0025785 | -0.002493 | -0.0037299 | 0.034759 | -0.00031832 | 0.082657 | 0.068404 | -0.003025 | 4.7018e-05 | -0.0035355 | -1.1398 | -0.88348 | -1.9592 | -1.1673 | -1.0208 | -1.8127 | -1.0529 | 1.3687 | 121.5225 | -1.9958 | 121.5042 | -1.506 | -1.6617 | -1.6022 | -0.12817 | -122.287 | -122.5708 | 0.81024 | 0.7782 | 0.018311 | 0.90637 | 0.14649 | -0.16479 | 0.11902 | 0.10071 | 0.32501 | 0.22888 | 0.16937 | 0.39368 | 0.33417 | 0.93842 | 0.79193 | 0.48981 | 123.5001 | 1.0757 | 123.5184 | 0.94757 | 123.3536 | -123.3627 | -123.3994 | 0.66376 | 123.3353 | 0.69122 | 3.1998
1345.4844 | 123.2849 | -1.9226 | 121.3623 | -0.042419 | 0.0026981 | -0.0026575 | 0.0025933 | 0.00062594 | 0.00028418 | 0.00096987 | -0.0049134 | -0.00053192 | 0.082657 | 0.069686 | -0.0028112 | -0.0018756 | -0.00011754 | -1.1856 | -0.95215 | -2.1011 | -1.2177 | -1.0529 | -1.8631 | -1.1124 | 1.3184 | 121.4722 | -2.0645 | 121.3623 | -1.6251 | -1.799 | -1.7258 | -0.17853 | -122.3145 | -122.58 | 0.86975 | 0.81024 | 0.059509 | 0.98877 | 0.23804 | -0.14191 | 0.10986 | 0 | 0.29755 | 0.19684 | 0.1236 | 0.33874 | 0.2655 | 1.0483 | 0.88348 | 0.43945 | 123.4268 | 1.149 | 123.5367 | 0.97046 | 123.3948 | -123.4634 | -123.4268 | 0.70496 | 123.2849 | 0.737 | 3.241
1346.4844 | 123.3536 | -1.7944 | 121.4905 | -0.03479 | 0.0022709 | -0.0024439 | 0.0030207 | 0.0019077 | 0.00071138 | -0.0024481 | 0.004242 | 0.00053628 | 0.083084 | 0.068618 | -0.002384 | -0.00080758 | -0.0022537 | -1.062 | -0.8194 | -1.8768 | -1.1032 | -0.95215 | -1.7212 | -0.99792 | 1.2863 | 121.637 | -1.886 | 121.4447 | -1.5564 | -1.68 | -1.5564 | -0.082397 | -122.3099 | -122.5937 | 0.84229 | 0.79651 | 0.073243 | 0.87891 | 0.15564 | -0.091552 | 0.14648 | -0.045777 | 0.23804 | 0.23804 | 0.11444 | 0.32959 | 0.20599 | 0.92468 | 0.77362 | 0.32959 | 123.3307 | 1.0574 | 123.5229 | 0.97504 | 123.4314 | -123.3673 | -123.3765 | 0.69122 | 123.2391 | 0.73242 | 3.0808
1347.5469 | 123.3124 | -1.8127 | 121.4493 | -0.072937 | 0.0016299 | -0.0015893 | 0.0045159 | -0.0025785 | 0.0011386 | -0.0026617 | -0.0079652 | 0.00032248 | 0.082444 | 0.0652 | -0.0021704 | -0.0025164 | -0.0011855 | -1.0849 | -0.79651 | -1.9547 | -1.149 | -1.0254 | -1.8219 | -1.03 | 1.268 | 121.6095 | -1.9455 | 121.5134 | -1.4832 | -1.6846 | -1.5976 | -0.14191 | -122.2458 | -122.5983 | 0.78735 | 0.78278 | -0.009155 | 0.92468 | 0.13275 | -0.13275 | 0.16022 | 0.064087 | 0.32959 | 0.21515 | 0.12817 | 0.3479 | 0.26093 | 0.92926 | 0.80566 | 0.46234 | 123.4589 | 1.1581 | 123.555 | 1.0162 | 123.4222 | -123.4039 | -123.3948 | 0.66376 | 123.3261 | 0.72784 | 3.0807
1348.4844 | 123.381 | -1.767 | 121.4676 | -0.03479 | 0.0046207 | -0.0043665 | 0.00067072 | 0.00062594 | 0.0022068 | -0.0041571 | -0.01712 | 0.00074988 | 0.082871 | 0.066482 | -0.0066564 | -0.0012348 | 0.0018051 | -1.0117 | -0.80109 | -1.9043 | -1.0666 | -0.88806 | -1.7166 | -0.94299 | 1.4282 | 121.6049 | -1.8951 | 121.5775 | -1.4374 | -1.6251 | -1.5472 | -0.13733 | -122.2687 | -122.5342 | 0.87891 | 0.82398 | 0.050354 | 0.9613 | 0.18768 | -0.12817 | 0.13733 | 0.10986 | 0.32959 | 0.21973 | 0.14191 | 0.3479 | 0.27008 | 1.0162 | 0.83771 | 0.45776 | 123.4726 | 1.1032 | 123.5001 | 0.96588 | 123.3719 | -123.3719 | -123.3627 | 0.70038 | 123.3444 | 0.75531 | 3.1952
1349.5469 | 123.381 | -118.0161 | 5.127 | -0.10345 | 0.0039799 | 0.12573 | 0.0053705 | 0.0012667 | -0.00035682 | -0.00073913 | -0.062897 | 0.14302 | 0.0040438 | 0.0032492 | -0.0025976 | -0.001662 | 0.00095066 | -3.1906 | -2.861 | -118.2907 | -3.2089 | -3.0716 | -117.9932 | -3.0991 | 0.54016 | 5.2277 | 3.8269 | 4.9713 | 4.1016 | 4.0329 | 4.1473 | -0.27466 | -7.988 | -8.3359 | 114.9445 | 114.917 | 0.022888 | 115.1917 | 0.29755 | 121.843 | 0.10071 | -0.15564 | 122.1176 | 122.1634 | 122.049 | 0.32043 | 0.20599 | 115.2191 | 115.0818 | 0.27466 | 1.1444 | 115.4297 | 1.4008 | 115.155 | 123.2437 | -123.4177 | -1.3 | 114.8071 | 122.9874 | 114.8254 | 118.5562
1350.4844 | 123.3994 | -118.3823 | 4.7699 | -0.027161 | 0.0022709 | 0.1253 | 0.0021661 | 0.0034029 | 0.0013522 | 0.0037469 | -0.038483 | 0.14409 | 0.00041225 | 0.0047446 | -0.002384 | -0.0027302 | -0.0054581 | -3.0304 | -2.742 | -118.6478 | -3.0716 | -2.948 | -118.3456 | -2.9526 | 0.6134 | 4.8798 | 3.7949 | 4.6509 | 4.1245 | 4.0787 | 4.1336 | -0.2655 | -7.5119 | -7.8415 | 115.4343 | 115.4297 | 0.036621 | 115.6952 | 0.30212 | 122.1771 | 0.10986 | -0.11902 | 122.5067 | 122.5159 | 122.4609 | 0.33875 | 0.28381 | 115.6998 | 115.5762 | 0.32959 | 0.85602 | 115.9058 | 1.0849 | 115.6403 | 123.262 | -123.4177 | -0.97504 | 115.3107 | 123.0331 | 115.3519 | 118.9957
1351.5469 | 123.3536 | -117.659 | 5.5115 | -0.15686 | 0.0041935 | 0.12295 | 0.0040887 | -0.00022866 | 0.0015658 | 0.0013971 | -0.096466 | 0.14366 | 0.00019865 | 0.0026084 | -0.0036658 | -0.00059378 | 0.0015915 | -2.8244 | -2.5726 | -117.984 | -2.8702 | -2.7237 | -117.6086 | -2.7924 | 0.63171 | 5.5801 | 3.4149 | 5.4062 | 3.7354 | 3.6758 | 3.7537 | -0.32501 | -8.0841 | -8.3817 | 114.9353 | 114.8666 | 0.050354 | 115.1917 | 0.37537 | 121.0739 | 0.068664 | -0.10529 | 121.3943 | 121.4127 | 121.3348 | 0.33874 | 0.26092 | 115.2603 | 115.1138 | 0.32043 | 1.9913 | 115.4114 | 2.1652 | 115.0864 | 123.2391 | -123.4955 | -2.0966 | 114.7888 | 123.0652 | 114.8346 | 118.2907
1352.4844 | 123.3994 | -117.5949 | 5.5435 | -0.072937 | 0.0018435 | 0.12295 | 0.0021661 | -0.0017239 | -0.00014322 | -0.0013799 | -0.056793 | 0.14089 | 0.0027622 | 0.00089939 | -0.0021704 | -0.0042254 | 0.0026597 | -2.829 | -2.5497 | -117.8238 | -2.8793 | -2.7283 | -117.5308 | -2.742 | 0.54016 | 5.6259 | 3.5019 | 5.4794 | 3.8269 | 3.7674 | 3.8544 | -0.22888 | -8.0933 | -8.4229 | 114.8666 | 114.8529 | 0.064087 | 115.0818 | 0.29297 | 121.0968 | 0.082398 | -0.064087 | 121.4218 | 121.4493 | 121.3623 | 0.35248 | 0.2655 | 115.0955 | 114.9445 | 0.32501 | 1.9775 | 115.274 | 2.124 | 115.0452 | 123.2208 | -123.3673 | -2.0416 | 114.7156 | 123.0743 | 114.7659 | 118.1351
1353.4844 | 123.3627 | -117.5079 | 5.69 | -0.050049 | 0.0050479 | 0.12402 | 0.0032343 | -0.00086946 | -0.00078402 | -0.00073913 | -0.059845 | 0.1411 | 0.0031894 | -0.0046548 | -0.0008886 | 4.7018e-05 | -0.0013991 | -2.6093 | -2.3758 | -117.7689 | -2.6688 | -2.536 | -117.4026 | -2.5589 | 0.71411 | 5.7312 | 3.479 | 5.5527 | 3.7903 | 3.717 | 3.7903 | -0.26093 | -8.0658 | -8.3588 | 114.9719 | 114.949 | 0.10529 | 115.21 | 0.36621 | 120.9869 | 0.041199 | -0.13733 | 121.2982 | 121.2982 | 121.225 | 0.31128 | 0.23804 | 115.2328 | 115.1001 | 0.31128 | 2.0737 | 115.3931 | 2.2522 | 115.1321 | 123.2391 | -123.4589 | -2.211 | 114.8392 | 123.0606 | 114.8987 | 118.222
1354.4844 | 123.3398 | -116.8625 | 6.2942 | -0.1416 | 0.0020573 | 0.12231 | 0.0025933 | 0.0042575 | -0.00014322 | -0.0015935 | -0.041534 | 0.14003 | 0.0036166 | -0.0012368 | -0.0017432 | -0.0029438 | 0.0018051 | -2.6276 | -2.3346 | -117.2104 | -2.6825 | -2.5452 | -116.8304 | -2.5772 | 0.82855 | 6.3995 | 3.4149 | 6.1615 | 3.7262 | 3.6621 | 3.7537 | -0.3479 | -8.6288 | -8.9767 | 114.3173 | 114.2853 | 0.032044 | 114.6332 | 0.37994 | 120.2774 | 0.10529 | -0.13275 | 120.5887 | 120.6162 | 120.5246 | 0.33874 | 0.24719 | 114.6652 | 114.5279 | 0.31128 | 2.7466 | 114.8758 | 2.9846 | 114.5279 | 123.262 | -123.5046 | -2.8793 | 114.18 | 123.024 | 114.2349 | 117.691
1355.5469 | 123.3398 | -118.0481 | 5.127 | -0.050049 | 0.0044071 | 0.1221 | 0.00088432 | 0.00062594 | 0.0015658 | -0.00095273 | -0.090363 | 0.14324 | 0.0042574 | 0.0047446 | -0.0025976 | -0.00016658 | -0.00075834 | -2.6459 | -2.3987 | -118.2861 | -2.7191 | -2.5497 | -117.9749 | -2.6321 | 0.58136 | 5.191 | 3.7079 | 4.9942 | 4.01 | 3.9368 | 4.0421 | -0.23804 | -7.5256 | -7.8461 | 115.4984 | 115.416 | 0.073242 | 115.654 | 0.31128 | 121.756 | 0.064087 | -0.13275 | 122.0581 | 122.0901 | 121.9849 | 0.33417 | 0.22888 | 115.7364 | 115.567 | 0.30212 | 1.2863 | 115.8875 | 1.4832 | 115.6494 | 123.2391 | -123.4131 | -1.4191 | 115.329 | 123.0423 | 115.4022 | 118.6295
1356.4844 | 123.3856 | -117.9291 | 5.2551 | -0.0042723 | 0.0018435 | 0.12253 | 0.0032343 | 0.0025485 | -0.0016384 | 0.0011835 | -0.062897 | 0.14174 | 0.001694 | -0.0048684 | -0.0028112 | -0.0020892 | 0.0011643 | -2.5864 | -2.3575 | -118.1717 | -2.655 | -2.4582 | -117.8284 | -2.5177 | 1.3504 | 5.2826 | 3.6209 | 5.1544 | 4.0237 | 3.9276 | 3.9917 | -0.24261 | -7.6126 | -7.9102 | 115.4709 | 115.4114 | 0.10071 | 115.654 | 0.34332 | 121.55 | 0.027466 | -0.10071 | 121.9528 | 121.9208 | 121.8567 | 0.37079 | 0.3067 | 115.7135 | 115.5167 | 0.40283 | 1.5335 | 115.8142 | 1.6617 | 115.5716 | 123.2117 | -123.4268 | -1.6342 | 115.274 | 123.0835 | 115.3427 | 119.2795
1357.5469 | 123.3215 | -118.0435 | 5.1682 | -0.088196 | 0.0037661 | 0.12466 | 0.0023797 | 0.00062594 | -0.00014322 | -0.0013799 | -0.10867 | 0.14281 | 0.003403 | 0.001113 | -0.0002478 | 0.00026062 | 0.0020187 | -2.4857 | -2.1881 | -118.1992 | -2.5452 | -2.4078 | -117.9886 | -2.4399 | 1.1398 | 5.246 | 3.5706 | 5.0446 | 3.8589 | 3.7582 | 3.8589 | -0.15564 | -7.3563 | -7.7133 | 115.6357 | 115.6036 | 0.054932 | 115.7593 | 0.21057 | 121.6141 | 0.07782 | -0.1236 | 121.9025 | 121.9025 | 121.8018 | 0.28839 | 0.18768 | 115.7913 | 115.654 | 0.28839 | 1.474 | 116.011 | 1.6754 | 115.8554 | 123.2895 | -123.3673 | -1.5976 | 115.4984 | 123.0881 | 115.5579 | 119.1834
1358.4844 | 123.3902 | -117.8375 | 5.3238 | -0.057678 | 0.0033389 | 0.12338 | 0.0019525 | 0.0025485 | -0.00099762 | -0.00031193 | -0.065949 | 0.14174 | 0.0027622 | 0.0013266 | -0.001316 | -0.0018756 | 0.0041551 | -2.4765 | -2.243 | -118.1305 | -2.5223 | -2.3575 | -117.778 | -2.4124 | 0.6134 | 5.3284 | 3.4424 | 5.2277 | 3.8498 | 3.772 | 3.8269 | -0.29297 | -7.5668 | -7.8461 | 115.48 | 115.4251 | 0.059509 | 115.7181 | 0.35248 | 121.2799 | 0.004577 | -0.096131 | 121.6873 | 121.6644 | 121.6095 | 0.38452 | 0.32959 | 115.773 | 115.6082 | 0.40741 | 1.7853 | 115.8875 | 1.886 | 115.5945 | 123.1659 | -123.4543 | -1.8814 | 115.3152 | 123.0652 | 115.361 | 118.4509
1359.4844 | 123.3078 | -118.0435 | 5.1682 | -0.027161 | 0.0026981 | 0.12231 | 0.0021661 | -0.0015103 | 0.00071138 | -0.00073913 | -0.087311 | 0.14217 | 0.0029758 | -0.0018778 | -0.0017432 | -0.001662 | 0.0018051 | -2.4719 | -2.243 | -118.2907 | -2.5818 | -2.4307 | -117.746 | -2.4719 | 0.53558 | 5.2689 | 3.5706 | 4.953 | 3.804 | 3.7216 | 3.8452 | -0.24719 | -7.4112 | -7.7499 | 115.6128 | 115.5716 | 0.29755 | 115.8188 | 0.54474 | 121.6141 | 0.10071 | -0.21515 | 121.8475 | 121.8887 | 121.7651 | 0.27466 | 0.15106 | 115.86 | 115.7089 | 0.23346 | 1.3824 | 116.0477 | 1.6983 | 115.8005 | 123.3124 | -123.4589 | -1.5976 | 115.4617 | 122.9965 | 115.5716 | 118.5791
1360.5469 | 123.3032 | -118.0023 | 5.1865 | -0.050049 | 0.0035525 | 0.12274 | 0.0015253 | -0.0017239 | -0.00078402 | -0.0011663 | -0.065949 | 0.14217 | 0.0055392 | -0.00038241 | -0.0015296 | -0.0029438 | -0.00054474 | -2.5864 | -2.2568 | -118.2129 | -2.6276 | -2.4765 | -117.9657 | -2.5085 | 0.56305 | 5.2505 | 3.4287 | 5.0217 | 3.7399 | 3.6392 | 3.7537 | -0.21057 | -7.4432 | -7.814 | 115.5258 | 115.4938 | 0.036621 | 115.7043 | 0.24719 | 121.431 | 0.064087 | -0.16479 | 121.7422 | 121.756 | 121.6415 | 0.32501 | 0.21057 | 115.7364 | 115.5853 | 0.31128 | 1.593 | 115.9561 | 1.8219 | 115.7455 | 123.2529 | -123.3994 | -1.7578 | 115.3748 | 123.024 | 115.416 | 118.5654
1361.4844 | 123.3353 | -117.9291 | 5.2185 | -0.042419 | 0.0065433 | 0.12423 | 0.00067072 | -0.0019377 | 0.0019932 | -0.0035163 | -0.065949 | 0.14153 | 0.0031894 | 0.00068579 | -0.002384 | -0.0023028 | 0.0015915 | -2.3895 | -2.1378 | -118.1854 | -2.4399 | -2.2705 | -117.8513 | -2.3254 | 0.737 | 5.2963 | 3.5614 | 5.0629 | 3.9093 | 3.8406 | 3.9185 | -0.25635 | -7.3563 | -7.6584 | 115.6586 | 115.6036 | 0.07782 | 115.86 | 0.33417 | 121.4905 | 0.07782 | -0.15564 | 121.8384 | 121.8475 | 121.7697 | 0.35706 | 0.27924 | 115.9149 | 115.7455 | 0.3479 | 1.5015 | 116.0477 | 1.7349 | 115.7913 | 123.2254 | -123.4039 | -1.6571 | 115.4892 | 122.9919 | 115.5396 | 118.6661
1362.4844 | 123.3673 | -118.0389 | 5.1086 | -0.019531 | 0.0054751 | 0.12253 | 0.0051569 | 0.00083954 | 0.00028418 | -0.00052553 | -0.05069 | 0.14409 | 0.0038302 | -0.00059601 | -0.0019568 | -0.001662 | -0.00033114 | -2.3941 | -2.1606 | -118.277 | -2.4353 | -2.2522 | -117.7917 | -2.33 | 0.63171 | 5.2368 | 3.5843 | 5.0217 | 3.9276 | 3.8406 | 3.8864 | -0.23804 | -7.2693 | -7.5439 | 115.7867 | 115.7089 | 0.24719 | 115.947 | 0.48523 | 121.6232 | 0.12817 | -0.086976 | 121.9666 | 121.9254 | 121.8796 | 0.30212 | 0.25635 | 116.0248 | 115.8417 | 0.34332 | 1.4374 | 116.1163 | 1.6525 | 115.8783 | 123.2758 | -123.3856 | -1.5244 | 115.6036 | 123.0606 | 115.6448 | 118.6707
1363.5469 | 123.3536 | -118.0115 | 5.1407 | 0.018616 | 0.0022709 | 0.12317 | 0.0034479 | 0.00083954 | 0.00092498 | 0.00096987 | -0.084259 | 0.1426 | 0.0046848 | -0.00059601 | -0.0025976 | -0.0031574 | 9.6064e-05 | -2.3941 | -2.1835 | -118.2861 | -2.4673 | -2.2934 | -117.9291 | -2.3849 | 1.4465 | 5.159 | 3.3691 | 5.0491 | 3.7765 | 3.7216 | 3.7674 | -0.27466 | -7.3242 | -7.608 | 115.7181 | 115.6265 | 0.082398 | 115.9012 | 0.35706 | 121.3806 | 0.018311 | -0.091553 | 121.788 | 121.7789 | 121.7331 | 0.39825 | 0.35248 | 115.9927 | 115.8188 | 0.40741 | 1.68 | 116.1026 | 1.7899 | 115.8279 | 123.1705 | -123.4268 | -1.7715 | 115.5441 | 123.0606 | 115.6174 | 119.458
1364.4844 | 123.349 | -117.865 | 5.2963 | -0.0042723 | 0.0046207 | 0.12103 | 0.0034479 | 0.0016939 | -0.00057042 | 0.0020379 | -0.062897 | 0.14089 | 0.0046848 | 0.00089939 | -0.0036658 | -0.0014484 | 0.00073706 | -2.417 | -2.2018 | -118.1763 | -2.4811 | -2.3163 | -117.6544 | -2.3712 | 0.64087 | 5.3513 | 3.5202 | 5.1727 | 3.9368 | 3.8361 | 3.891 | -0.31128 | -7.4982 | -7.7774 | 115.5487 | 115.4938 | 0.21057 | 115.8051 | 0.52185 | 121.3852 | 0.054931 | -0.1236 | 121.8018 | 121.756 | 121.7011 | 0.37079 | 0.31586 | 115.86 | 115.6952 | 0.41656 | 1.6525 | 115.9744 | 1.8311 | 115.6631 | 123.2162 | -123.4726 | -1.7761 | 115.3839 | 123.0377 | 115.448 | 118.5059
1365.4844 | 123.2483 | -118.3731 | 4.8706 | 0.026245 | 0.0022709 | 0.12466 | 0.0034479 | 0.00019874 | 0.0013522 | -0.0011663 | -0.12088 | 0.14345 | 0.0072482 | -0.005082 | -0.0008886 | 0.00026062 | 0.00095066 | -2.5177 | -2.1835 | -118.483 | -2.6321 | -2.504 | -118.0618 | -2.5177 | 0.46234 | 5.1727 | 3.4698 | 4.6188 | 3.4882 | 3.4195 | 3.4836 | -0.10986 | -7.0541 | -7.5027 | 115.8691 | 115.8554 | 0.31128 | 115.9653 | 0.42114 | 121.843 | 0.30212 | -0.25177 | 121.8613 | 121.8567 | 121.7926 | 0.013733 | -0.050354 | 115.979 | 115.8508 | 0.01831 | 1.149 | 116.2994 | 1.7029 | 116.1896 | 123.5458 | -123.3536 | -1.4008 | 115.741 | 122.9919 | 115.8554 | 118.8354
1366.4844 | 123.3307 | -118.2678 | 4.8706 | -0.095825 | 0.0033389 | 0.12274 | 0.0023797 | 0.0038303 | 0.00092498 | -0.0015935 | -0.056793 | 0.1426 | 0.003403 | 0.0041038 | -3.4196e-05 | -0.00016658 | 0.0013779 | -2.4536 | -2.2293 | -118.5699 | -2.5269 | -2.3575 | -118.1488 | -2.4124 | 0.63171 | 4.9393 | 3.3234 | 4.7516 | 3.685 | 3.5843 | 3.6896 | -0.30212 | -7.0999 | -7.3975 | 115.9103 | 115.8554 | 0.11902 | 116.1575 | 0.42114 | 121.5912 | 0.068665 | -0.11902 | 121.9528 | 121.9574 | 121.8521 | 0.36621 | 0.26093 | 116.2125 | 116.0431 | 0.36163 | 1.4282 | 116.3406 | 1.6159 | 116.0385 | 123.2071 | -123.4406 | -1.5472 | 115.741 | 123.0194 | 115.8142 | 118.8995
1367.4844 | 123.2437 | -118.1351 | 5.0537 | -0.072937 | 0.0050479 | 0.12146 | 0.0013117 | -0.0010831 | 0.00071138 | 0.00011527 | -0.075104 | 0.1443 | 0.001694 | 0.0036764 | -0.003025 | -0.0010212 | 0.0024461 | -2.4719 | -2.2064 | -118.5242 | -2.5635 | -2.4033 | -118.1122 | -2.4399 | 0.7782 | 5.0858 | 3.2501 | 4.7287 | 3.598 | 3.5339 | 3.598 | -0.3891 | -7.2601 | -7.6172 | 115.7318 | 115.6952 | 0.022888 | 116.0843 | 0.41199 | 121.3852 | 0.032043 | -0.32501 | 121.7331 | 121.7331 | 121.669 | 0.3479 | 0.28381 | 116.1209 | 115.9607 | 0.3479 | 1.4786 | 116.3177 | 1.8356 | 115.9286 | 123.2208 | -123.5779 | -1.8036 | 115.5716 | 122.8638 | 115.6631 | 118.9133
1368.5469 | 123.2574 | -118.19 | 4.9942 | -0.057678 | 0.0033389 | 0.12231 | 0.0032343 | 0.00062594 | -0.0014248 | -0.0028753 | -0.13309 | 0.1426 | 0.005112 | 0.0021812 | -0.0028112 | 4.7018e-05 | 0.0013779 | -2.5452 | -2.1927 | -118.4784 | -2.6459 | -2.5177 | -118.2632 | -2.5406 | 1.0757 | 5.0629 | 2.9297 | 4.8431 | 3.2318 | 3.1357 | 3.2639 | -0.28839 | -7.1869 | -7.6401 | 115.6723 | 115.6494 | -0.073243 | 115.9378 | 0.21515 | 121.1197 | 0.068664 | -0.15106 | 121.4218 | 121.4539 | 121.3257 | 0.33417 | 0.20599 | 115.9607 | 115.8325 | 0.30213 | 1.9135 | 116.2857 | 2.1332 | 115.9973 | 123.2529 | -123.4726 | -2.0645 | 115.5441 | 123.0331 | 115.6448 | 119.2657
1369.4844 | 123.2346 | -118.2724 | 4.9301 | 0.064392 | 0.0016299 | 0.12188 | 0.00088432 | -1.486e-05 | 0.0011386 | 0.00054267 | -0.10257 | 0.14452 | 0.0053256 | 0.0026084 | -0.000675 | -0.0023028 | 0.0018051 | -2.3621 | -2.0325 | -118.5837 | -2.4857 | -2.3392 | -118.2358 | -2.3666 | 0.98877 | 5.0262 | 2.7283 | 4.6692 | 3.0167 | 2.9434 | 3.0579 | -0.31128 | -6.9626 | -7.4158 | 115.9332 | 115.9058 | 0.036621 | 116.217 | 0.3479 | 121.0007 | 0.09613 | -0.26093 | 121.2891 | 121.3303 | 121.2158 | 0.32959 | 0.21515 | 116.2445 | 116.098 | 0.28839 | 1.9409 | 116.5512 | 2.298 | 116.2399 | 123.2986 | -123.5138 | -2.2018 | 115.7867 | 122.9416 | 115.9103 | 119.2612
1370.5469 | 123.3353 | -118.483 | 4.7012 | -0.072937 | 0.0033389 | 0.12423 | 0.00088432 | -0.0012967 | 0.0015658 | -0.0052251 | -0.020172 | 0.14174 | 0.0036166 | 0.002822 | -0.0017432 | -0.0018756 | 0.00095066 | -2.3987 | -2.1469 | -118.6752 | -2.4353 | -2.2293 | -118.2861 | -2.298 | 1.1124 | 4.7836 | 2.7695 | 4.5639 | 3.1128 | 3.0258 | 3.0762 | -0.19226 | -6.8481 | -7.1365 | 116.2537 | 116.185 | 0.19684 | 116.3773 | 0.3891 | 121.2524 | 0.082397 | -0.13733 | 121.5958 | 121.5591 | 121.5088 | 0.3067 | 0.25635 | 116.4459 | 116.2399 | 0.34332 | 1.7944 | 116.5283 | 2.0142 | 116.3361 | 123.2666 | -123.3765 | -1.9318 | 116.0477 | 123.0469 | 116.0843 | 119.5953
1371.4844 | 123.23 | -118.2541 | 4.9713 | -0.0042723 | 0.0014163 | 0.12146 | 0.0013117 | -0.0049283 | 0.0030612 | 0.00075627 | -0.084259 | 0.14217 | 0.006821 | -0.0014504 | -0.001316 | -0.00080758 | 0.0018051 | -2.4307 | -2.092 | -118.3044 | -2.5497 | -2.4124 | -117.9886 | -2.417 | 0.97961 | 5.1453 | 3.1036 | 4.7195 | 3.2227 | 3.1082 | 3.1952 | -0.050354 | -7.0633 | -7.5211 | 115.8417 | 115.8371 | 0.2655 | 115.8875 | 0.31586 | 121.3577 | 0.17395 | -0.25177 | 121.4767 | 121.4493 | 121.3623 | 0.091552 | 0.004577 | 115.892 | 115.7547 | 0.11902 | 1.6159 | 116.2125 | 2.0416 | 116.1621 | 123.3994 | -123.2758 | -1.8677 | 115.7043 | 122.9736 | 115.8234 | 119.2337
1372.5469 | 123.3307 | -118.0435 | 5.1773 | -0.042419 | 0.0020573 | 0.12359 | 0.0038751 | -0.00022866 | 0.0045566 | -0.0033025 | -0.047638 | 0.14302 | 0.0042574 | 0.00025839 | -0.0017432 | -0.0037982 | 0.0022323 | -2.4857 | -2.1973 | -118.4326 | -2.5406 | -2.3941 | -118.1168 | -2.4078 | 1.1215 | 5.072 | 3.0167 | 5.0308 | 3.5019 | 3.4607 | 3.5431 | -0.3891 | -7.3746 | -7.7179 | 115.6494 | 115.6357 | -0.073242 | 116.0248 | 0.31586 | 121.0602 | -0.10529 | -0.14648 | 121.5454 | 121.5866 | 121.5042 | 0.52643 | 0.44403 | 116.0385 | 115.892 | 0.48523 | 2.0142 | 116.2354 | 2.0554 | 115.8463 | 123.1155 | -123.6099 | -2.1606 | 115.5029 | 123.0743 | 115.5579 | 119.165
1373.4844 | 123.262 | -118.6386 | 4.5685 | -0.0042723 | 0.0024845 | 0.12146 | 0.0025933 | -0.00022866 | -0.00078402 | -0.00031193 | -0.12393 | 0.14174 | 0.00618 | 0.0019674 | -0.0043066 | -0.00038018 | -0.0026809 | -2.4994 | -2.1652 | -118.808 | -2.6184 | -2.4948 | -118.515 | -2.5223 | 0.97961 | 4.7287 | 2.8564 | 4.3213 | 3.0396 | 2.9617 | 3.0853 | -0.16937 | -6.7337 | -7.1869 | 116.1438 | 116.1163 | 0.1236 | 116.2857 | 0.29297 | 121.4951 | 0.16022 | -0.24719 | 121.6782 | 121.7239 | 121.6003 | 0.22888 | 0.10529 | 116.3132 | 116.1896 | 0.18311 | 1.4648 | 116.6428 | 1.8723 | 116.4734 | 123.3673 | -123.3765 | -1.712 | 116.0202 | 122.9599 | 116.1392 | 119.6182
1374.4844 | 123.317 | -118.4555 | 4.6921 | -0.050049 | 0.0041935 | 0.12188 | 0.00088432 | -0.0010831 | 0.00092498 | -0.0026617 | -0.047638 | 0.14324 | 0.0055392 | -0.002305 | -0.0025976 | 0.00047422 | -0.00054474 | -2.4582 | -2.2247 | -118.3868 | -2.5269 | -2.3712 | -118.158 | -2.4399 | 1.0391 | 4.9118 | 3.0853 | 4.4815 | 3.1082 | 3.0121 | 3.0716 | 0.068664 | -6.9168 | -7.2189 | 116.0843 | 116.0156 | 0.29755 | 115.947 | 0.22888 | 121.5408 | 0.21973 | -0.21057 | 121.5637 | 121.5271 | 121.4676 | -0.013733 | -0.073242 | 116.0156 | 115.86 | 0.022888 | 1.3962 | 116.1621 | 1.8265 | 116.2308 | 123.3673 | -123.0789 | -1.6068 | 115.9287 | 122.937 | 115.9973 | 119.4946
1375.5469 | 123.2254 | -118.84 | 4.4403 | 0.033875 | 0.00098907 | 0.12295 | 0.0023797 | -0.0034329 | 0.0019932 | -0.0011663 | -0.090363 | 0.14345 | 0.006821 | 0.001113 | -0.0025976 | -0.00038018 | 0.0020187 | -2.5223 | -2.1927 | -119.1055 | -2.6276 | -2.4765 | -118.8171 | -2.5085 | 1.03 | 4.5822 | 2.8473 | 4.2526 | 3.1265 | 2.98 | 3.0167 | -0.2655 | -6.633 | -7.0679 | 116.3635 | 116.3315 | 0.022888 | 116.597 | 0.28839 | 121.6873 | 0.14191 | -0.18768 | 121.9666 | 121.8567 | 121.8201 | 0.16937 | 0.13275 | 116.629 | 116.478 | 0.27924 | 1.4053 | 116.9128 | 1.7349 | 116.6473 | 123.4222 | -123.5458 | -1.593 | 116.2125 | 123.0927 | 116.3177 | 119.87
1376.4844 | 123.3032 | -118.0115 | 5.2322 | -0.050049 | 0.0029117 | 0.12082 | 0.0030207 | -1.486e-05 | 0.00049778 | 0.00032907 | -0.047638 | 0.13982 | 0.0042574 | -0.0027322 | -0.0025976 | -0.0031574 | 0.0028733 | -26.7471 | -2.1744 | -117.897 | -2.4628 | -2.2888 | -117.4759 | -2.3483 | 1.2909 | 5.6442 | 3.3051 | 4.9347 | 3.0441 | 3.0441 | 3.0899 | 0.11444 | -7.4066 | -7.695 | 115.7227 | 115.6631 | 0.53558 | 115.5487 | 0.42114 | 121.3165 | 0.41199 | -0.29755 | 121.0556 | 121.1014 | 121.0556 | -0.21515 | -0.26093 | 115.6082 | 115.4343 | -0.26093 | 1.6296 | 115.7227 | 2.3392 | 115.8371 | 123.6557 | -123.1293 | -1.9272 | 115.5487 | 122.9462 | 91.2643 | 119.3024
1377.4844 | 123.2758 | -118.4189 | 4.8203 | -0.027161 | 0.0044071 | 0.12274 | 0.0043023 | 0.0031893 | 0.0037022 | 0.00096987 | -0.13309 | 0.1411 | 0.0036166 | 0.0068808 | -0.0021704 | -0.00080758 | -0.0011855 | -26.9302 | -2.1469 | -118.602 | -2.5452 | -2.4124 | -118.2999 | -2.4399 | 0.95215 | 5.0034 | 2.7237 | 4.6463 | 2.9388 | 2.8702 | 2.9434 | -0.18311 | -6.9672 | -7.3654 | 116.0065 | 115.979 | 0.11902 | 116.1621 | 0.30212 | 121.1426 | 0.18311 | -0.17395 | 121.3577 | 121.3623 | 121.2891 | 0.21973 | 0.14648 | 116.1896 | 116.0568 | 0.21515 | 1.9226 | 116.4551 | 2.2797 | 116.272 | 123.4222 | -123.4222 | -2.0966 | 115.8737 | 123.0652 | 91.4886 | 119.371
1378.4844 | 123.2941 | -118.1442 | 5.1041 | -0.057678 | 0.0022709 | 0.12231 | 0.0032343 | 0.0025485 | -0.00035682 | -0.00031193 | -0.053741 | 0.14195 | 0.0031894 | -0.0063638 | -0.0017432 | -0.0018756 | -0.0020401 | -26.7609 | -2.0599 | -118.4738 | -2.417 | -2.2614 | -118.0573 | -2.2934 | 0.91553 | 5.2872 | 2.948 | 4.8019 | 3.2135 | 3.1906 | 3.154 | -0.32959 | -7.164 | -7.5211 | 115.8829 | 115.8508 | 0.086975 | 116.1804 | 0.41657 | 121.0922 | 0.1831 | -0.30212 | 121.3577 | 121.2982 | 121.3348 | 0.20599 | 0.24261 | 116.2125 | 116.0568 | 0.2655 | 1.8539 | 116.4139 | 2.3392 | 116.0843 | 123.4314 | -123.5779 | -2.1561 | 115.7272 | 122.9462 | 91.3834 | 119.0598
1379.5469 | 123.3261 | -117.9245 | 5.2002 | -0.065308 | 0.0039799 | 0.1221 | -0.00039728 | -0.0025785 | 0.00092498 | -9.8328e-05 | -0.020172 | 0.14089 | 0.0038302 | -0.002305 | -0.0017432 | -0.0020892 | -0.00097194 | -27.5299 | -2.1011 | -118.3182 | -2.3849 | -2.1835 | -118.2358 | -2.2522 | 1.3 | 5.2505 | 3.0029 | 5.1773 | 3.4698 | 3.3554 | 3.5385 | -0.39368 | -7.3013 | -7.5851 | 115.741 | 115.6723 | -0.31128 | 116.066 | 0.082397 | 120.9274 | 0.050354 | -0.022888 | 121.3943 | 121.463 | 121.2799 | 0.53558 | 0.35248 | 116.1346 | 115.9332 | 0.46692 | 2.1744 | 116.217 | 2.2476 | 115.8234 | 123.175 | -123.5184 | -2.1973 | 115.5396 | 123.1018 | 90.3946 | 119.2245
1380.4844 | 123.2712 | -118.1305 | 4.9759 | -0.03479 | 0.0026981 | 0.12253 | 0.0015253 | 0.0036165 | 0.0028476 | 0.0016107 | -0.11783 | 0.14195 | 0.0038302 | 0.0047446 | -0.0043066 | -0.00059378 | 0.0028733 | -27.9282 | -2.0737 | -118.5791 | -2.4857 | -2.33 | -118.0435 | -2.3529 | 0.95673 | 5.2002 | 2.8519 | 4.6783 | 2.98 | 2.9343 | 3.2227 | -0.44861 | -7.0496 | -7.4615 | 115.8005 | 115.7776 | 0.086975 | 116.2262 | 0.53558 | 120.9824 | 0.2243 | -0.29755 | 121.1105 | 121.3531 | 121.0648 | 0.37079 | 0.082397 | 116.2491 | 116.0934 | 0.12817 | 1.8265 | 116.5054 | 2.3483 | 116.0568 | 123.3307 | -123.555 | -2.124 | 115.6448 | 122.8088 | 90.2023 | 119.0872
1381.4844 | 123.2483 | -118.959 | 4.2847 | 0.018616 | 0.0029117 | 0.12188 | 0.00067072 | -0.00044226 | 0.00028418 | -0.00031193 | -0.078156 | 0.1443 | 0.0057528 | -0.00080961 | -0.0021704 | 0.0015424 | -0.00097194 | -28.0563 | -2.124 | -119.2474 | -2.5635 | -2.4353 | -118.927 | -2.4536 | 0.95215 | 4.3121 | 2.5497 | 3.9963 | 2.8427 | 2.71 | 2.8107 | -0.28839 | -6.4087 | -6.8481 | 116.5237 | 116.5054 | 0.032043 | 116.7938 | 0.32044 | 121.5088 | 0.027466 | -0.28839 | 121.8018 | 121.7697 | 121.669 | 0.26092 | 0.16022 | 116.8121 | 116.684 | 0.29297 | 1.4465 | 117.1234 | 1.7624 | 116.835 | 123.2712 | -123.5321 | -1.7349 | 116.3956 | 122.9553 | 90.9027 | 119.9112
1382.4844 | 123.3261 | -119.2612 | 3.9459 | -0.027161 | 0.0048343 | 0.12188 | 0.0025933 | -0.00022866 | 0.00071138 | -9.8328e-05 | -0.023224 | 0.14409 | 0.0057528 | -0.004014 | -0.0047338 | -0.0010212 | 9.6064e-05 | -27.6031 | -2.1881 | -119.5312 | -2.5177 | -2.33 | -118.9728 | -2.3849 | 1.1215 | 4.0787 | 2.7969 | 3.8132 | 3.0945 | 3.035 | 3.0853 | -0.27008 | -6.134 | -6.4636 | 116.9312 | 116.8762 | 0.28839 | 117.1463 | 0.55847 | 122.0581 | 0.13275 | -0.13275 | 122.3557 | 122.3465 | 122.2961 | 0.28839 | 0.23804 | 117.2012 | 117.0135 | 0.29755 | 1.0162 | 117.3431 | 1.2817 | 117.0731 | 123.3398 | -123.4772 | -1.149 | 116.7435 | 123.0743 | 91.658 | 120.3827
1383.5469 | 123.2208 | -119.1879 | 4.0192 | -0.027161 | 0.0026981 | 0.12338 | 0.0021661 | 0.0014803 | -0.00014322 | -0.0039435 | -0.032379 | 0.14495 | 0.0036166 | -0.0029458 | -0.0025976 | 4.7018e-05 | -0.00075834 | -27.3972 | -2.211 | -119.5496 | -2.5635 | -2.3987 | -119.2337 | -2.4445 | 1.0208 | 4.0009 | 2.6917 | 3.717 | 3.035 | 2.916 | 3.0396 | -0.36163 | -6.2302 | -6.5826 | 116.7892 | 116.7435 | -0.045777 | 117.1051 | 0.31586 | 121.8796 | -0.018311 | -0.30212 | 122.2229 | 122.2275 | 122.1039 | 0.3479 | 0.2243 | 117.1509 | 116.9861 | 0.34332 | 1.0254 | 117.3386 | 1.3092 | 116.9769 | 123.1888 | -123.5687 | -1.3275 | 116.6244 | 122.905 | 91.7908 | 120.2087
1384.4844 | 123.2162 | -120.2637 | 2.9938 | 0.018616 | 0.0024845 | 0.12488 | 0.0045159 | -0.0015103 | -0.00014322 | 0.00054267 | -0.072052 | 0.14537 | 0.0074618 | -0.0038004 | -0.0028112 | 4.7018e-05 | 0.00052346 | -27.8641 | -2.211 | -120.5429 | -2.6413 | -2.4719 | -120.2728 | -2.5269 | 0.82398 | 3.0258 | 2.4353 | 2.655 | 2.7054 | 2.6138 | 2.6962 | -0.27924 | -5.2048 | -5.6351 | 117.7917 | 117.7368 | -0.009155 | 118.0161 | 0.27008 | 122.699 | 0.032044 | -0.33875 | 122.9691 | 122.9599 | 122.8775 | 0.26092 | 0.17853 | 118.071 | 117.9016 | 0.27008 | 0.21973 | 118.3319 | 0.59051 | 118.0527 | 123.2895 | -123.5367 | -0.55847 | 117.6224 | 122.9187 | 92.3996 | 121.0876
1385.4844 | 123.2666 | -120.108 | 3.1265 | 0.033875 | 0.0048343 | 0.12466 | 0.0032343 | 0.00083954 | 0.00071138 | -0.00052553 | -0.10867 | 0.14537 | 0.006821 | -0.0012368 | -0.0045202 | -0.0014484 | 0.0018051 | -27.4246 | -1.9684 | -120.488 | -2.4033 | -2.2568 | -120.1904 | -2.2842 | 0.90637 | 3.0762 | 2.4628 | 2.8885 | 2.8244 | 2.774 | 2.8656 | -0.37994 | -5.0949 | -5.5298 | 117.8513 | 117.8238 | -0.082398 | 118.2037 | 0.29755 | 122.5708 | -0.050354 | -0.23804 | 122.9324 | 122.9736 | 122.8821 | 0.40283 | 0.31128 | 118.2312 | 118.0847 | 0.36163 | 0.42572 | 118.5196 | 0.6134 | 118.1396 | 123.1842 | -123.6145 | -0.66376 | 117.7048 | 122.9965 | 92.6834 | 121.0144
1386.5469 | 123.3078 | -120.1767 | 3.0075 | -0.027161 | 0.0046207 | 0.1221 | 0.00024352 | -1.486e-05 | 0.00071138 | -0.0015935 | -0.014069 | 0.1443 | 0.005112 | -0.006791 | -0.0028112 | -0.0018756 | -0.0016129 | -27.4979 | -1.9958 | -120.4559 | -2.3392 | -2.1835 | -120.1538 | -2.2202 | 0.88806 | 2.9755 | 2.4261 | 2.8381 | 2.9022 | 2.7786 | 2.8656 | -0.27924 | -5.0034 | -5.3467 | 117.9932 | 117.9565 | 0.022888 | 118.2358 | 0.30212 | 122.6028 | -0.032043 | -0.16937 | 123.0789 | 123.0423 | 122.9553 | 0.43945 | 0.35248 | 118.2724 | 118.1168 | 0.47608 | 0.41199 | 118.4601 | 0.54932 | 118.1808 | 123.1522 | -123.4634 | -0.58136 | 117.8375 | 123.0148 | 92.6788 | 121.0648
1387.4844 | 123.2758 | -120.4193 | 2.742 | -0.0042723 | 0.0026981 | 0.12723 | 0.0021661 | -0.0017239 | 0.00028418 | -0.00073913 | -0.14529 | 0.14537 | 0.0042574 | 0.00389 | -0.004093 | 4.7018e-05 | 0.0037277 | -27.9236 | -1.973 | -120.7443 | -2.3621 | -2.2018 | -120.2316 | -2.2614 | 0.78735 | 2.8564 | 2.298 | 2.5085 | 2.5635 | 2.504 | 2.6093 | -0.32501 | -4.715 | -5.1041 | 118.2175 | 118.158 | 0.18768 | 118.483 | 0.5127 | 122.7173 | 0.11444 | -0.23346 | 122.9828 | 123.0286 | 122.9233 | 0.31128 | 0.20599 | 118.5425 | 118.3823 | 0.2655 | 0.21057 | 118.7714 | 0.55847 | 118.4464 | 123.2758 | -123.4863 | -0.44403 | 118.0573 | 122.9279 | 92.4957 | 121.2067
1388.4844 | 123.2941 | -120.3232 | 2.8793 | -0.011902 | 0.0026981 | 0.12381 | 0.0021661 | -0.0021513 | 0.002634 | -0.0052251 | -0.038483 | 0.14559 | 0.0036166 | 0.0013266 | -0.0017432 | -0.00080758 | -0.0016129 | -27.713 | -2.0142 | -120.5841 | -2.33 | -2.1515 | -120.1218 | -2.1927 | 0.94299 | 2.9709 | 2.3621 | 2.6688 | 2.6688 | 2.5589 | 2.655 | -0.26093 | -4.8935 | -5.2093 | 118.1717 | 118.1305 | 0.20142 | 118.3914 | 0.46234 | 122.6852 | 0.091553 | -0.21057 | 122.9919 | 122.9782 | 122.8821 | 0.29297 | 0.19684 | 118.4326 | 118.2541 | 0.3067 | 0.3067 | 118.5699 | 0.60882 | 118.309 | 123.2941 | -123.4634 | -0.51727 | 117.9932 | 122.9919 | 92.6102 | 121.2662
1389.5469 | 123.2391 | -120.3552 | 2.916 | -0.042419 | 0.0050479 | 0.12359 | 0.0030207 | 0.00019874 | -0.0016384 | -0.0024481 | -0.056793 | 0.14559 | 0.0066074 | 0.0015402 | -0.0032386 | -0.0010212 | -0.0016129 | -28.2806 | -1.9958 | -120.6985 | -2.4216 | -2.2659 | -120.108 | -2.2934 | 0.98419 | 3.0853 | 2.4582 | 2.6825 | 2.6733 | 2.536 | 2.5909 | -0.34332 | -4.9118 | -5.3375 | 118.0893 | 118.0618 | 0.24719 | 118.4052 | 0.59052 | 122.8134 | 0.16937 | -0.23346 | 123.0286 | 122.9462 | 122.8912 | 0.13275 | 0.07782 | 118.4326 | 118.277 | 0.21515 | 0.2243 | 118.7027 | 0.62714 | 118.3594 | 123.4406 | -123.6145 | -0.45776 | 117.9337 | 123.0377 | 92.0746 | 121.3394
1390.4844 | 123.2025 | -119.1376 | 4.0512 | -0.057678 | 0.0046207 | 0.12103 | 0.0021661 | -0.0012967 | 0.00049778 | -0.0037299 | -0.05069 | 0.14345 | 0.0066074 | -0.003373 | -0.000675 | -0.0040118 | 0.0011643 | -28.4088 | -1.9958 | -119.4489 | -2.3849 | -2.243 | -118.6661 | -2.2705 | 0.93842 | 4.3945 | 2.4353 | 3.7628 | 2.4857 | 2.4902 | 2.5589 | -0.31128 | -6.0471 | -6.4362 | 116.8945 | 116.8671 | 0.4715 | 117.1783 | 0.78278 | 121.5729 | 0.34332 | -0.28839 | 121.6232 | 121.6965 | 121.6278 | 0.1236 | 0.054931 | 117.2058 | 117.0639 | 0.050354 | 1.3275 | 117.453 | 1.9592 | 117.1417 | 123.5321 | -123.5001 | -1.6159 | 116.7526 | 122.9004 | 90.7288 | 120.076
1391.5469 | 123.2574 | -119.0598 | 4.216 | -0.0042723 | 0.0044071 | 0.12423 | 0.0032343 | -0.00044226 | -0.00057042 | -0.0026617 | -0.13614 | 0.14388 | 0.0048984 | 0.00025839 | -0.0036658 | 0.001115 | 0.0045823 | -27.6901 | -1.9775 | -119.4489 | -2.3712 | -2.2064 | -119.0826 | -2.2888 | 1.2497 | 4.1748 | 2.3987 | 4.1428 | 2.7786 | 2.5864 | 2.6505 | -0.3891 | -6.1935 | -6.5872 | 116.8533 | 116.7709 | -0.022889 | 117.16 | 0.36621 | 121.4584 | -0.041198 | -0.073242 | 121.8384 | 121.7102 | 121.6461 | 0.25177 | 0.18768 | 117.2424 | 117.0776 | 0.37994 | 1.7441 | 117.4713 | 1.7761 | 117.0822 | 123.2346 | -123.6649 | -1.8173 | 116.6885 | 123.2025 | 91.3696 | 120.3094
1392.4844 | 123.2071 | -118.5059 | 4.6783 | 0.010986 | 0.0029117 | 0.12146 | 0.0021661 | 0.0021213 | 0.002634 | -0.0020209 | -0.069 | 0.14238 | 0.0066074 | 0.002822 | -0.0021704 | -0.0020892 | -0.0041763 | -27.6581 | -1.9821 | -118.8034 | -2.4353 | -2.2705 | -118.4509 | -2.3163 | 1.1032 | 4.7424 | 2.417 | 4.4174 | 2.6962 | 2.6138 | 2.742 | -0.29755 | -6.6605 | -7.1136 | 116.2354 | 116.1896 | 0.054931 | 116.4871 | 0.35248 | 120.9229 | 0.064087 | -0.26093 | 121.2021 | 121.2479 | 121.1197 | 0.32501 | 0.19684 | 116.5329 | 116.3681 | 0.27924 | 2.0004 | 116.8213 | 2.3254 | 116.5237 | 123.2483 | -123.4818 | -2.2614 | 116.0706 | 122.9233 | 90.8478 | 119.6091
1393.4844 | 122.6898 | -44.2429 | 78.9597 | -0.042419 | 0.0054751 | 0.040281 | 0.0025933 | 0.0027621 | -0.00035682 | -0.0045843 | -0.069 | 0.0039541 | 0.0038302 | 0.041274 | -0.0038794 | -0.00016658 | 0.0011643 | -10.2859 | -0.90179 | -44.4626 | -1.2955 | -1.149 | -44.458 | -1.1765 | 6.8756 | 79.0237 | 1.0757 | 78.9322 | 1.4465 | 1.2955 | 1.3962 | -0.21973 | -79.8614 | -80.2551 | 43.0939 | 43.0664 | -0.21515 | 43.2861 | 0.004577 | 45.3186 | 0.064087 | -0.027466 | 45.6894 | 45.639 | 45.5383 | 0.32043 | 0.21973 | 43.3136 | 43.1671 | 0.37079 | 77.8564 | 43.5608 | 77.948 | 43.3411 | 123.2666 | -123.4222 | -77.8839 | 42.9474 | 123.175 | 33.9569 | 51.1185
1394.5469 | 123.3032 | -43.9911 | 79.1519 | -0.0042723 | 0.0035525 | 0.043699 | 0.0013117 | -1.486e-05 | 0.0045566 | -0.0024481 | 0.022552 | 0.0039541 | 0.005112 | 0.039992 | -0.0043066 | -0.001662 | -0.00033114 | -10.2081 | -0.85602 | -44.2062 | -1.1032 | -0.90637 | -44.1742 | -1.0162 | 7.1732 | 79.1702 | 1.1261 | 79.2068 | 1.5427 | 1.442 | 1.5015 | -0.21515 | -80.0079 | -80.2551 | 43.0847 | 42.9749 | -0.1831 | 43.19 | 0.032044 | 45.1172 | 0.01831 | 0.054931 | 45.5338 | 45.4926 | 45.433 | 0.37537 | 0.31586 | 43.2999 | 43.103 | 0.41657 | 78.0807 | 43.3502 | 78.0441 | 43.1351 | 123.1613 | -123.3582 | -78.0258 | 42.8879 | 123.1979 | 33.783 | 51.1642
1395.4844 | 123.1842 | -44.133 | 79.0558 | 0.064392 | 0.0039799 | 0.040922 | 0.0034479 | 0.00019874 | 0.00028418 | -0.0020209 | -0.023224 | 0.0050223 | 0.006821 | 0.040847 | -0.0028112 | -0.0018756 | -0.00033114 | -10.3455 | -1.03 | -44.3939 | -1.4648 | -1.3275 | -44.3939 | -1.3367 | 7.1365 | 79.1473 | 1.1078 | 78.9505 | 1.4511 | 1.3046 | 1.3962 | -0.26093 | -80.0858 | -80.5206 | 42.8055 | 42.7963 | -0.26093 | 43.0573 | 0 | 45.2408 | 0.091553 | -0.10529 | 45.5841 | 45.5292 | 45.4376 | 0.28839 | 0.19684 | 43.0664 | 42.9291 | 0.34332 | 77.8427 | 43.364 | 78.0396 | 43.103 | 123.2803 | -123.4497 | -77.948 | 42.6682 | 123.0835 | 33.7875 | 51.2695
1396.4844 | 123.1934 | -44.1101 | 79.0558 | -0.065308 | 0.0037661 | 0.042203 | 0.0023797 | -0.0023649 | 0.002634 | -0.00095273 | -0.01712 | 0.0033133 | 0.005112 | 0.041915 | -0.0021704 | -0.0027302 | -0.0016129 | -10.4279 | -0.90179 | -44.3344 | -1.3092 | -1.149 | -44.3848 | -1.1627 | 7.1182 | 79.1336 | 1.1307 | 78.9871 | 1.4374 | 1.3184 | 1.4008 | -0.22431 | -79.9576 | -80.365 | 42.9611 | 42.9474 | -0.27466 | 43.1717 | -0.050354 | 45.2408 | 0.07782 | -0.068664 | 45.5475 | 45.5109 | 45.4285 | 0.27008 | 0.18768 | 43.1854 | 43.0252 | 0.3067 | 77.8564 | 43.4326 | 78.0029 | 43.2083 | 123.2437 | -123.3902 | -77.9251 | 42.8009 | 123.0972 | 33.6823 | 51.2283
1397.5469 | 123.2162 | -43.9499 | 79.1977 | 0.0033567 | 0.0026981 | 0.041776 | 0.0040887 | 0.0051119 | 0.00049778 | -0.0020209 | -0.044586 | 0.0058767 | 0.003403 | 0.046615 | -0.0021704 | -0.0035846 | 0.0015915 | -10.318 | -0.8606 | -44.1788 | -1.2863 | -1.1627 | -44.2612 | -1.1673 | 5.4245 | 79.3167 | 1.181 | 79.1428 | 1.5244 | 1.355 | 1.4648 | -0.22888 | -80.0583 | -80.484 | 42.7872 | 42.7826 | -0.31128 | 43.0115 | -0.082397 | 45.1309 | 0.11902 | -0.054932 | 45.4742 | 45.4147 | 45.3049 | 0.28381 | 0.17395 | 43.0161 | 42.8925 | 0.34332 | 77.9617 | 43.3182 | 78.1357 | 43.0893 | 123.2666 | -123.3765 | -78.0167 | 42.6636 | 123.0927 | 33.6319 | 49.3744
1398.4844 | 123.2437 | -43.9407 | 79.2526 | -0.0042723 | 0.0020573 | 0.043912 | 0.0025933 | 0.0014803 | 7.0582e-05 | 0.00054267 | -0.053741 | 0.0037405 | 0.0053256 | 0.048751 | -0.004093 | -0.003371 | 0.0011643 | -10.5606 | -0.8606 | -44.1833 | -1.3092 | -1.1627 | -44.2245 | -1.1948 | 2.7466 | 79.3304 | 1.1902 | 79.1931 | 1.5289 | 1.4053 | 1.4923 | -0.24262 | -80.1132 | -80.5618 | 42.778 | 42.746 | -0.28381 | 42.9886 | -0.041198 | 45.1309 | 0.077819 | -0.05951 | 45.4697 | 45.433 | 45.3461 | 0.30212 | 0.21515 | 43.0206 | 42.8741 | 0.33875 | 78.0029 | 43.3228 | 78.1403 | 43.0801 | 123.2712 | -123.436 | -78.0624 | 42.6315 | 123.1338 | 33.3801 | 46.6873
1399.4844 | 123.2437 | -43.8721 | 79.2801 | -0.027161 | 0.0039799 | 0.042203 | 0.0021661 | 0.0074619 | 0.00071138 | -0.0011663 | -0.05069 | 0.0041679 | 0.0040438 | 0.047896 | -0.0036658 | -0.00016658 | -0.0011855 | -10.5148 | -0.85602 | -44.1238 | -1.2634 | -1.1078 | -44.1422 | -1.1444 | 2.8473 | 79.4083 | 1.268 | 79.2938 | 1.6388 | 1.4832 | 1.5839 | -0.25177 | -80.1361 | -80.5435 | 42.7643 | 42.7277 | -0.27008 | 42.9794 | -0.018311 | 45.1401 | 0.12817 | 0.013733 | 45.5109 | 45.4559 | 45.3552 | 0.31586 | 0.21515 | 43.0161 | 42.8604 | 0.37079 | 78.0258 | 43.2678 | 78.1403 | 43.0161 | 123.2803 | -123.4039 | -78.0121 | 42.6086 | 123.1659 | 33.3572 | 46.7194
1400.4844 | 123.2162 | -44.014 | 79.1519 | 0.0033567 | 0.0041935 | 0.042203 | 0.0023797 | 0.0016939 | -0.0022794 | -0.00052553 | -0.0049134 | 0.0048087 | 0.005112 | 0.044265 | -0.0034522 | -0.0027302 | -0.00075834 | -10.6613 | -1.0162 | -44.2703 | -1.4328 | -1.2726 | -44.3161 | -1.3275 | 3.5339 | 79.2526 | 1.062 | 79.097 | 1.3779 | 1.2451 | 1.3229 | -0.25635 | -80.1682 | -80.5847 | 42.7414 | 42.6865 | -0.30212 | 42.9428 | -0.045776 | 45.076 | 0.10071 | -0.054932 | 45.3918 | 45.3369 | 45.2591 | 0.26093 | 0.18311 | 42.9977 | 42.8375 | 0.31586 | 78.035 | 43.2541 | 78.1906 | 42.9977 | 123.2666 | -123.4222 | -78.0899 | 42.5812 | 123.111 | 33.3527 | 47.5479
1401.5469 | 123.436 | -119.6091 | 3.566 | 0.026245 | 0.0026981 | 0.12701 | 0.0019525 | -0.00022866 | 0.00049778 | -0.00095273 | 0.013397 | 0.1443 | 0.0063938 | 0.0019674 | -0.0028112 | -0.0020892 | -0.0011855 | -29.4937 | -2.0508 | -120.3323 | -2.3529 | -2.1423 | -119.6548 | -2.2156 | 1.5152 | 3.479 | 2.8748 | 3.392 | 3.4012 | 3.3142 | 3.2684 | -0.72327 | -5.6168 | -5.9189 | 117.4667 | 117.3935 | -0.045776 | 118.1168 | 0.67749 | 122.4838 | -0.086975 | -0.17395 | 123.0103 | 122.8775 | 122.9233 | 0.39368 | 0.43945 | 118.19 | 117.9794 | 0.52643 | 0.51727 | 118.2816 | 0.60425 | 117.5583 | 123.0881 | -123.8983 | -0.69122 | 117.2562 | 123.0011 | 90.1154 | 121.1243
1402.4844 | 123.2483 | -43.8675 | 79.3213 | -0.072937 | 0.0031253 | 0.041563 | -0.00018368 | -0.00044226 | 0.0028476 | 0.00011527 | 0.034759 | 0.0026725 | 0.0031894 | 0.036574 | -0.0036658 | -0.0018756 | 0.0026597 | -10.3912 | -0.6958 | -44.0094 | -0.98877 | -0.82398 | -44.0186 | -0.88348 | 5.6854 | 79.3991 | 1.062 | 79.3259 | 1.4557 | 1.3092 | 1.2863 | -0.14191 | -80.0171 | -80.3101 | 43.0435 | 42.984 | -0.15106 | 43.1259 | -0.009156 | 44.9295 | 0.07782 | 0.004578 | 45.3232 | 45.1538 | 45.1767 | 0.2243 | 0.24719 | 43.1854 | 43.0206 | 0.39368 | 78.2639 | 43.3136 | 78.3371 | 43.1717 | 123.2666 | -123.3307 | -78.2593 | 42.8787 | 123.1934 | 33.4763 | 49.5529
1403.5469 | 123.2529 | -43.8583 | 79.303 | -0.042419 | 0.0061161 | 0.04434 | 0.0025933 | -0.0010831 | 0.0015658 | 0.00032907 | 0.013397 | 0.0030997 | 0.0029758 | 0.037429 | -0.0019568 | -0.0027302 | -0.0013991 | -10.6979 | -0.74158 | -44.0689 | -1.0895 | -0.94299 | -44.0918 | -0.95673 | 6.0516 | 79.3716 | 1.1444 | 79.3304 | 1.5106 | 1.3962 | 1.5152 | -0.21057 | -80.0446 | -80.3925 | 42.9153 | 42.9016 | -0.23346 | 43.1122 | -0.022888 | 45.0027 | 0.068664 | 0.027465 | 45.369 | 45.3735 | 45.2545 | 0.37079 | 0.25177 | 43.1259 | 42.9794 | 0.36621 | 78.186 | 43.3273 | 78.2272 | 43.1168 | 123.23 | -123.3719 | -78.1586 | 42.7689 | 123.1888 | 33.1604 | 49.91
1404.4844 | 122.8546 | -44.046 | 79.1748 | -0.019531 | 0.0014163 | 0.041776 | 0.0040887 | 0.0010531 | 0.0013522 | -0.00073913 | -0.056793 | 0.0043815 | 0.0059664 | 0.042769 | -0.0038794 | -0.0010212 | -0.0056717 | -10.9131 | -0.93842 | -44.2337 | -1.3733 | -1.2497 | -44.2795 | -1.2589 | 6.0379 | 79.3076 | 1.1902 | 79.1199 | 1.5015 | 1.3687 | 1.4694 | -0.18768 | -80.1132 | -80.5481 | 42.7963 | 42.7872 | -0.23346 | 42.9749 | -0.045776 | 45.2362 | 0.13275 | -0.054932 | 45.5475 | 45.5154 | 45.4147 | 0.27924 | 0.17853 | 42.984 | 42.8604 | 0.31128 | 77.9297 | 43.2953 | 78.1174 | 43.1076 | 123.3536 | -123.4085 | -77.9846 | 42.6727 | 123.1659 | 33.1329 | 50.0839
1405.5469 | 123.1934 | -44.1238 | 79.0787 | 0.0033567 | 0.0020573 | 0.040922 | 0.0010981 | -0.0019377 | 0.0019932 | -0.0024481 | -0.023224 | 0.0039541 | 0.0031894 | 0.040847 | -0.0015296 | 0.00026062 | -0.0011855 | -10.318 | -1.0483 | -44.3115 | -1.4008 | -1.2451 | -44.3253 | -1.2909 | 5.9967 | 79.1428 | 1.2222 | 79.0054 | 1.5656 | 1.4374 | 1.5152 | -0.18768 | -80.127 | -80.4794 | 42.8787 | 42.8329 | -0.20142 | 43.0206 | -0.013733 | 45.3461 | 0.064087 | -0.073242 | 45.6894 | 45.639 | 45.5612 | 0.29297 | 0.21515 | 43.0664 | 42.9108 | 0.34332 | 77.7832 | 43.2632 | 77.9205 | 43.0756 | 123.2666 | -123.3902 | -77.8564 | 42.7231 | 123.1293 | 33.8058 | 50.1205
1406.4844 | 123.1934 | -44.0506 | 79.184 | -0.042419 | 0.0022709 | 0.042844 | 0.0017389 | -0.0027921 | 0.0013522 | 0.00054267 | -0.026276 | 0.0037405 | 0.0066074 | 0.044692 | -0.0017432 | -0.0031574 | 0.0015915 | -10.3867 | -1.03 | -44.2474 | -1.4374 | -1.2817 | -44.2566 | -1.3184 | 7.5211 | 79.2526 | 1.4374 | 79.0878 | 1.7578 | 1.6205 | 1.7075 | -0.19684 | -80.2139 | -80.6213 | 42.7689 | 42.7322 | -0.20599 | 42.9291 | -0.009155 | 45.488 | 0.068665 | -0.09613 | 45.8084 | 45.7581 | 45.6711 | 0.27008 | 0.1831 | 42.9657 | 42.8101 | 0.32043 | 77.6505 | 43.2175 | 77.8152 | 43.0206 | 123.3032 | -123.4314 | -77.7466 | 42.6132 | 123.1384 | 33.6639 | 51.5717
1407.5 | 123.2117 | -43.8721 | 79.2847 | -0.072937 | 0.0050479 | 0.040922 | 0.0049433 | 0.0016939 | 0.0013522 | -0.0030889 | -0.075104 | 0.0060905 | 0.0046848 | 0.042342 | -0.0017432 | 0.00068782 | 0.00095066 | -10.4416 | -1.0025 | -44.133 | -1.4191 | -1.3046 | -44.2245 | -1.3275 | 5.7037 | 79.4266 | 1.4786 | 79.248 | 1.6983 | 1.5518 | 1.6846 | -0.26093 | -80.2872 | -80.7037 | 42.5674 | 42.5446 | -0.35248 | 42.8055 | -0.091552 | 45.3506 | 0.14191 | -0.036621 | 45.5704 | 45.5566 | 45.4239 | 0.20599 | 0.073242 | 42.8284 | 42.7139 | 0.21973 | 77.7695 | 43.1305 | 77.948 | 42.8696 | 123.2986 | -123.4177 | -77.8061 | 42.453 | 123.1201 | 33.4305 | 49.5758
1408.4844 | 123.3032 | -43.7805 | 79.3488 | -0.0042723 | 0.0029117 | 0.040708 | 0.0013117 | 0.00041234 | 0.0041294 | 0.00032907 | 0.010345 | 0.0020315 | 0.0031894 | 0.039779 | -0.0045202 | -0.0029438 | -0.0022537 | -10.231 | -0.99335 | -44.0186 | -1.2543 | -1.0986 | -43.9911 | -1.1581 | 5.7724 | 79.4495 | 1.5198 | 79.3945 | 1.9272 | 1.8036 | 1.8723 | -0.23804 | -80.3421 | -80.603 | 42.6819 | 42.6224 | -0.21057 | 42.8604 | 0.027466 | 45.3003 | 0.10071 | 0.045776 | 45.7077 | 45.6528 | 45.5841 | 0.35248 | 0.28381 | 42.9199 | 42.7643 | 0.40741 | 77.8748 | 43.0252 | 77.9297 | 42.7872 | 123.23 | -123.3673 | -77.829 | 42.5262 | 123.175 | 33.5495 | 49.5529
1409.5469 | 123.2208 | -43.8263 | 79.3671 | -0.011902 | 0.0056889 | 0.044767 | 2.9918e-05 | -0.00065586 | 0.0011386 | -0.0013799 | -0.014069 | 0.0035269 | 0.005112 | 0.037002 | -0.0017432 | -0.0031574 | -0.0024673 | -10.6155 | -0.96588 | -44.1055 | -1.3504 | -1.1856 | -44.1193 | -1.2405 | 6.5414 | 79.3716 | 1.7166 | 79.2847 | 2.0462 | 1.8448 | 1.9821 | -0.27924 | -80.3329 | -80.7175 | 42.6407 | 42.5858 | -0.29297 | 42.865 | -0.013733 | 45.5429 | 0.004578 | -0.082397 | 45.8725 | 45.8084 | 45.6711 | 0.2655 | 0.12817 | 42.9199 | 42.7551 | 0.32959 | 77.5681 | 43.1396 | 77.655 | 42.8604 | 123.1979 | -123.4726 | -77.6505 | 42.4759 | 123.111 | 33.2108 | 50.3677
1410.4844 | 123.262 | -43.7393 | 79.4037 | -0.027161 | 0.0046207 | 0.041349 | 0.0034479 | -0.0023649 | -0.0016384 | -0.00052553 | -0.0049134 | 0.0033133 | 0.003403 | 0.03807 | -0.0025976 | -0.0012348 | 0.0011643 | -10.9131 | -0.90637 | -43.9453 | -1.2039 | -1.0574 | -43.9774 | -1.1169 | 5.1041 | 79.4907 | 1.7761 | 79.4083 | 2.124 | 2.0142 | 2.1011 | -0.20599 | -80.3101 | -80.6076 | 42.6819 | 42.6224 | -0.23804 | 42.8284 | -0.032044 | 45.5154 | 0.086975 | 0.004577 | 45.8633 | 45.8405 | 45.7535 | 0.32501 | 0.23804 | 42.8879 | 42.7414 | 0.3479 | 77.6321 | 43.0389 | 77.7145 | 42.8329 | 123.23 | -123.349 | -77.6276 | 42.5354 | 123.1476 | 32.8262 | 48.8434
1411.4844 | 123.23 | -43.7119 | 79.4907 | 0.0033567 | 0.00077547 | 0.042203 | 0.0030207 | 0.0012667 | 0.0019932 | -0.0013799 | -0.044586 | 0.0039541 | 0.004471 | 0.043838 | -0.003025 | -0.001662 | 0.0028733 | -10.73 | -0.86517 | -43.9819 | -1.3092 | -1.1765 | -43.9865 | -1.1719 | 3.9093 | 79.5731 | 1.6983 | 79.3991 | 2.005 | 1.886 | 2.0004 | -0.27008 | -80.3558 | -80.7999 | 42.5354 | 42.54 | -0.27466 | 42.8101 | -0.004577 | 45.4102 | 0.082397 | -0.091553 | 45.7169 | 45.7123 | 45.5978 | 0.30212 | 0.18768 | 42.8055 | 42.6727 | 0.3067 | 77.7008 | 43.1168 | 77.8748 | 42.8467 | 123.2849 | -123.4726 | -77.7924 | 42.4026 | 123.111 | 32.9819 | 47.6212
1412.5625 | 123.2666 | -43.6249 | 79.509 | 0.026245 | 0.0018435 | 0.043058 | 0.0043023 | 0.0025485 | -0.00078402 | 0.00032907 | -0.062897 | 0.0045951 | 0.0053256 | 0.04341 | -0.0034522 | -0.00016658 | -0.0018265 | -10.7803 | -0.8606 | -43.9362 | -1.2497 | -1.0941 | -43.9316 | -1.149 | 4.5914 | 79.6143 | 1.8402 | 79.5044 | 2.1652 | 2.0462 | 2.1652 | -0.31128 | -80.3696 | -80.7587 | 42.5308 | 42.4759 | -0.3067 | 42.7872 | 0.004577 | 45.4651 | 0.10529 | -0.004577 | 45.7901 | 45.7901 | 45.6711 | 0.32501 | 0.20599 | 42.8421 | 42.6865 | 0.32501 | 77.6642 | 43.0756 | 77.774 | 42.7643 | 123.2391 | -123.4451 | -77.6688 | 42.3752 | 123.1293 | 32.8445 | 48.2162
1413.4844 | 123.2712 | -43.6432 | 79.5639 | 0.010986 | 0.0029117 | 0.041776 | 0.0021661 | 0.0021213 | 0.00092498 | -0.0018073 | -0.041534 | 0.0039541 | 0.003403 | 0.040206 | -0.0028112 | -0.0023028 | 0.00030966 | -10.4965 | -0.85144 | -43.9087 | -1.2955 | -1.1536 | -43.8721 | -1.1765 | 5.4474 | 79.6371 | 1.9272 | 79.4952 | 2.2934 | 2.1469 | 2.2522 | -0.2655 | -80.4153 | -80.8594 | 42.4896 | 42.4667 | -0.22888 | 42.7322 | 0.036621 | 45.5704 | 0.073242 | -0.068665 | 45.9366 | 45.8954 | 45.7901 | 0.32501 | 0.21973 | 42.7551 | 42.6132 | 0.36621 | 77.5681 | 43.0573 | 77.71 | 42.7917 | 123.2803 | -123.4726 | -77.6367 | 42.3477 | 123.1384 | 33.1467 | 49.0906
1414.4844 | 123.2803 | -43.6478 | 79.4952 | -0.027161 | 0.0014163 | 0.040922 | 0.0019525 | -0.0012967 | 0.00071138 | -0.0035163 | 0.031708 | 0.0037405 | 0.0053256 | 0.037429 | -0.0008886 | -0.0029438 | -0.00033114 | -10.881 | -0.92468 | -43.8721 | -1.2451 | -1.0941 | -43.9041 | -1.1261 | 5.0171 | 79.5914 | 1.918 | 79.4815 | 2.243 | 2.1286 | 2.211 | -0.2243 | -80.4199 | -80.7404 | 42.5537 | 42.5217 | -0.25635 | 42.746 | -0.032044 | 45.5658 | 0.096131 | -0.013733 | 45.8908 | 45.8588 | 45.7764 | 0.29297 | 0.21057 | 42.778 | 42.627 | 0.32501 | 77.5635 | 42.9474 | 77.6733 | 42.7231 | 123.2391 | -123.3673 | -77.5772 | 42.4026 | 123.1293 | 32.7667 | 48.6649
1415.5469 | 123.3353 | -43.5974 | 79.5135 | -0.088196 | 0.0052615 | 0.043058 | 0.0028069 | 0.0010531 | 0.0024204 | -0.00031193 | 0.025604 | 0.0030997 | 0.003403 | 0.039352 | -0.004093 | 0.00026062 | 9.6064e-05 | -10.2402 | -0.9201 | -43.8171 | -1.1902 | -1.03 | -43.7942 | -1.0803 | 6.5002 | 79.6097 | 2.0554 | 79.5822 | 2.4628 | 2.3621 | 2.4078 | -0.21973 | -80.4337 | -80.7037 | 42.5674 | 42.5171 | -0.19684 | 42.7368 | 0.022889 | 45.6528 | 0.09613 | 0.068664 | 46.0602 | 46.0052 | 45.9595 | 0.35248 | 0.3067 | 42.7872 | 42.627 | 0.40741 | 77.5269 | 42.897 | 77.5543 | 42.6773 | 123.2071 | -123.3307 | -77.4582 | 42.4072 | 123.1796 | 33.3572 | 50.0977
1416.4844 | 123.3032 | -43.5883 | 79.5731 | -0.065308 | 0.0026981 | 0.043485 | 0.0021661 | 0.00062594 | 0.0013522 | -0.0015935 | 0.013397 | 0.0026725 | 0.0046848 | 0.038924 | -0.002384 | -0.00016658 | -0.00033114 | -11.1282 | -0.88348 | -43.8354 | -1.1993 | -1.0162 | -43.8034 | -1.0666 | 2.8336 | 79.6783 | 2.0508 | 79.5868 | 2.4399 | 2.3254 | 2.3941 | -0.24719 | -80.4565 | -80.7724 | 42.572 | 42.5217 | -0.21515 | 42.7689 | 0.032043 | 45.639 | 0.10529 | 0.013733 | 46.0281 | 45.9824 | 45.9137 | 0.34332 | 0.27466 | 42.8192 | 42.6361 | 0.3891 | 77.536 | 42.952 | 77.6276 | 42.7048 | 123.2666 | -123.4085 | -77.5223 | 42.3889 | 123.175 | 32.46 | 46.4218
1417.5 | 123.2483 | -43.6615 | 79.5502 | -0.03479 | 0.0031253 | 0.045408 | 0.0040887 | 0.0036165 | 0.0024204 | -0.00073913 | -0.10867 | 0.0037405 | 0.00618 | 0.038924 | -0.002384 | -0.00016658 | -0.0016129 | -10.3592 | -0.85144 | -43.895 | -1.2955 | -1.2268 | -43.9453 | -1.2268 | 4.7379 | 79.6417 | 2.1149 | 79.4952 | 2.3895 | 2.2568 | 2.3849 | -0.23346 | -80.4016 | -80.8456 | 42.4347 | 42.4347 | -0.28381 | 42.6682 | -0.050354 | 45.7764 | 0.091553 | -0.054932 | 46.051 | 46.0464 | 45.9183 | 0.27008 | 0.14191 | 42.6682 | 42.5995 | 0.27466 | 77.3804 | 43.0435 | 77.5269 | 42.8101 | 123.3032 | -123.4451 | -77.4353 | 42.366 | 123.1567 | 33.3023 | 48.3994
1418.5469 | 123.3856 | -43.6798 | 79.3945 | -0.057678 | 0.0022709 | 0.043912 | 0.0015253 | 0.0031893 | 0.00092498 | -0.0022345 | 0.004242 | 0.0033133 | 0.0048984 | 0.037002 | -0.0028112 | -0.0031574 | -0.0018265 | -10.3409 | -0.90637 | -43.9041 | -1.1856 | -1.0025 | -43.8217 | -1.0666 | 2.298 | 79.5914 | 2.124 | 79.5776 | 2.5406 | 2.4033 | 2.4994 | -0.2243 | -80.3009 | -80.5801 | 42.6773 | 42.6132 | -0.14191 | 42.8375 | 0.082398 | 45.8038 | 0.19684 | 0.18311 | 46.2204 | 46.1792 | 46.0831 | 0.37537 | 0.27924 | 42.9016 | 42.7185 | 0.41656 | 77.4536 | 42.9977 | 77.4673 | 42.7734 | 123.2712 | -123.2986 | -77.2705 | 42.4942 | 123.2574 | 33.3389 | 45.9778
1419.4844 | 122.7539 | -43.9682 | 79.2618 | -0.065308 | -0.00029273 | 0.041776 | 0.0025933 | 0.0012667 | -0.00099762 | -9.8328e-05 | -0.044586 | 0.0033133 | -0.0055692 | 0.046615 | -0.0038794 | -0.00080758 | -0.0018265 | -10.0845 | -1.062 | -44.1559 | -1.4969 | -1.3641 | -44.3207 | -1.3962 | 1.4923 | 77.948 | 0.22888 | 79.2297 | 2.2202 | 1.7624 | 2.6321 | -0.18768 | -80.3238 | -80.7587 | 42.6041 | 42.572 | -0.35248 | 42.7597 | -0.16479 | 44.1971 | -1.3138 | -0.032044 | 46.1884 | 46.6003 | 45.7306 | 2.4033 | 1.5335 | 42.7917 | 42.659 | 1.9913 | 79.0009 | 43.0939 | 77.7191 | 42.9062 | 121.9162 | -123.4177 | -79.0329 | 42.4713 | 123.1979 | 33.8837 | 45.4605
1420.4844 | 122.8271 | -43.3273 | 78.6438 | 0.010986 | 0.0022709 | 0.044553 | 0.00024352 | 0.0023349 | 0.0019932 | -0.00052553 | 0.034759 | 0.0060905 | 0.0063938 | 0.03337 | -0.0025976 | -0.003371 | -0.0018265 | -10.0708 | -1.0117 | -44.0186 | -1.3184 | -1.1536 | -44.1925 | -1.2589 | 2.8427 | 79.3304 | 1.8494 | 79.422 | 2.2934 | 2.3026 | 2.2934 | -0.69122 | -79.6555 | -79.9622 | 42.1738 | 42.0685 | -0.86517 | 42.7597 | -0.17395 | 45.1767 | 0.68664 | 0.7782 | 45.6207 | 45.6207 | 45.6299 | 0.44403 | 0.45319 | 42.865 | 42.7002 | 0.44403 | 77.5726 | 43.0069 | 77.4811 | 42.3157 | 122.6578 | -122.6624 | -76.7944 | 42.009 | 122.7493 | 33.2565 | 46.17
1421.5469 | 118.1122 | -43.8858 | 78.4241 | -0.27893 | 0.00013467 | 0.042631 | 2.9918e-05 | -0.0066373 | 0.00049778 | -0.0050115 | 0.062225 | 0.0024589 | 0.0029758 | 0.032943 | -0.0021704 | -0.0020892 | -0.0035355 | -10.3592 | -1.0529 | -43.7714 | -1.3412 | -1.1673 | -44.2612 | -1.181 | 3.7079 | 78.7811 | 0.87433 | 79.097 | 1.236 | 1.1124 | 1.2085 | 0.11444 | -79.4769 | -79.7653 | 42.7185 | 42.7048 | -0.37537 | 42.5903 | -0.48981 | 44.7601 | 0.35706 | 0.67291 | 45.1218 | 45.0943 | 44.9982 | 0.33417 | 0.23804 | 42.6041 | 42.4301 | 0.36163 | 78.2227 | 42.7185 | 77.9068 | 42.8329 | 122.6669 | -122.1954 | -77.5497 | 42.5446 | 122.9828 | 33.5266 | 47.5937
1422.4844 | 123.3948 | -120.3827 | 2.7328 | -0.25604 | 0.023206 | 0.12423 | -0.01001 | -0.01625 | -0.014669 | -0.017615 | -0.3223 | 0.12401 | -0.013473 | -0.011491 | -0.0077246 | -0.0072162 | -0.011226 | -15.4633 | -2.0416 | -120.3049 | 0.10986 | 0.09613 | -98.6572 | 0.10071 | 0.82398 | 2.504 | 2.4811 | 2.4673 | 2.3254 | 2.4353 | 0.59052 | 0.077819 | -4.7745 | -2.623 | 120.4788 | 120.4834 | 21.7255 | 120.4056 | 21.6476 | 122.8638 | -0.22888 | -0.2655 | 122.7081 | 120.9732 | 122.818 | -1.8906 | -0.045776 | 120.401 | 120.4147 | -0.15564 | -0.013733 | 118.2632 | 0.022888 | 118.3411 | 122.8867 | -123.0377 | -0.25177 | 120.4926 | 122.85 | 104.9194 | 121.2067
1423.5469 | 123.4589 | -120.4102 | 2.774 | -0.0042723 | 0.0014163 | 0.1221 | 0.0028069 | 0.0025485 | 0.00092498 | 0.0018243 | 0.043915 | 0.14388 | 0.0040438 | -0.0048684 | -0.001316 | -0.0029438 | -0.0069533 | -29.48 | -2.0691 | -120.6619 | -2.3804 | -2.1469 | -119.8654 | -2.2293 | 1.1993 | 2.8381 | 2.4673 | 2.6367 | 2.6733 | 2.6093 | 2.6047 | -0.25177 | -4.8431 | -5.1544 | 118.2632 | 118.1808 | 0.54474 | 118.4326 | 0.79651 | 122.8775 | 0.064087 | -0.13733 | 123.0835 | 123.0148 | 123.0194 | 0.13733 | 0.14191 | 118.515 | 118.2816 | 0.20599 | 0.16937 | 118.5928 | 0.37079 | 118.3411 | 123.2483 | -123.436 | -0.3067 | 118.0298 | 123.0469 | 90.9302 | 121.6095
1424.4844 | 123.317 | -120.5109 | 2.7237 | -0.27893 | 0.0022709 | 0.12402 | 0.0025933 | 0.0027621 | 0.0037022 | 0.0031061 | -0.026276 | 0.14772 | 0.0021212 | -0.0029458 | -0.0019568 | -0.0029438 | -0.0013991 | -29.0497 | -2.0508 | -120.694 | -2.4902 | -2.4582 | -120.1813 | -2.4811 | 0.99335 | 2.6688 | 2.2385 | 2.3849 | 2.4628 | 2.1927 | 2.124 | -0.18311 | -4.7745 | -5.2139 | 118.0527 | 118.0298 | 0.32959 | 118.2129 | 0.5127 | 122.7493 | -0.054932 | -0.33874 | 122.9736 | 122.6349 | 122.7036 | -0.11444 | -0.045776 | 118.2358 | 118.2037 | 0.22431 | 0.14649 | 118.6432 | 0.4303 | 118.4601 | 123.1796 | -123.4177 | -0.48523 | 118.0206 | 122.8958 | 91.4612 | 121.5042
1425.4844 | 123.2986 | -120.6436 | 2.5909 | -0.45441 | 0.0022709 | 0.12381 | 0.0036615 | 0.0014803 | 0.0019932 | -0.0015935 | -0.041534 | 0.14537 | 0.0048984 | -0.004014 | -0.002384 | -0.0027302 | 0.0030869 | -28.2028 | -2.0645 | -120.7855 | -2.5314 | -2.5177 | -120.1492 | -2.6138 | 0.90179 | 2.7832 | 2.2339 | 2.3163 | 2.3071 | 2.0096 | 2.1194 | -0.14191 | -4.6555 | -5.1224 | 118.1259 | 118.0298 | 0.49438 | 118.1717 | 0.63629 | 122.8775 | 0.19226 | -0.27466 | 122.9507 | 122.7631 | 122.6532 | -0.11444 | -0.2243 | 118.2678 | 118.2541 | 0.073242 | 0.082397 | 118.721 | 0.54932 | 118.5791 | 123.4268 | -123.3765 | -0.35705 | 118.1122 | 122.9599 | 92.4408 | 121.5454
1426.5469 | 123.3948 | -120.5246 | 2.6825 | -0.52307 | 0.0026981 | 0.12317 | 0.0064385 | 0.00041234 | 0.0017794 | 0.0018243 | -0.084259 | 0.1458 | 0.0055392 | 0.0034628 | -0.000675 | -0.0012348 | 9.6064e-05 | -29.3518 | -2.1057 | -120.7535 | -2.5314 | -2.3895 | -119.8517 | -2.4994 | 1.1307 | 2.8244 | 2.298 | 2.5085 | 2.536 | 2.449 | 2.4445 | -0.22888 | -4.7882 | -5.2139 | 118.1351 | 118.0252 | 0.67291 | 118.2541 | 0.90179 | 122.8226 | 0.14191 | -0.17395 | 123.0606 | 122.9691 | 122.9736 | 0.14648 | 0.15106 | 118.364 | 118.222 | 0.23804 | 0.21057 | 118.6478 | 0.52643 | 118.4189 | 123.349 | -123.436 | -0.38452 | 117.9932 | 123.0331 | 91.1728 | 121.6553
1427.4844 | 123.2986 | -120.8084 | 2.4857 | 0.026245 | 0.0014163 | 0.12509 | 0.0032343 | -0.0032193 | 0.0030612 | 0.00011527 | -0.026276 | 0.14623 | 0.0010532 | 0.00089939 | -0.0047338 | -0.0020892 | 0.0024461 | -28.9993 | -2.1332 | -121.0144 | -2.5909 | -2.4216 | -120.163 | -2.4811 | 0.91553 | 2.5772 | 1.9867 | 2.1744 | 2.2202 | 2.124 | 2.0462 | -0.20599 | -4.6188 | -5.0766 | 118.3868 | 118.3273 | 0.64545 | 118.5333 | 0.85144 | 122.7951 | 0.091552 | -0.31128 | 123.0286 | 122.8546 | 122.9324 | 0.05951 | 0.13733 | 118.5928 | 118.4235 | 0.23346 | 0.18768 | 118.8812 | 0.59051 | 118.6752 | 123.3856 | -123.5001 | -0.49896 | 118.2175 | 122.9828 | 91.8091 | 121.7239
1428.5469 | 123.3673 | -120.9091 | 2.3209 | -0.03479 | 0.00098907 | 0.12552 | 2.9918e-05 | -0.00022866 | -0.00035682 | 0.00054267 | -0.020172 | 0.14537 | 0.0031894 | -0.005082 | -0.003025 | -0.0020892 | -0.0037491 | -30.4459 | -2.179 | -121.0419 | -2.5131 | -2.3209 | -120.7169 | -2.4124 | 0.97961 | 2.3941 | 1.886 | 2.1606 | 2.179 | 2.0828 | 2.2018 | -0.13275 | -4.4998 | -4.834 | 118.5883 | 118.4967 | 0.19226 | 118.6295 | 0.32501 | 122.7951 | 0.073242 | -0.16022 | 123.0881 | 123.111 | 122.9919 | 0.31586 | 0.19684 | 118.721 | 118.5287 | 0.29297 | 0.27466 | 118.8629 | 0.50812 | 118.7302 | 123.3032 | -123.3627 | -0.43488 | 118.396 | 123.0698 | 90.4633 | 121.8887
1429.4844 | 123.3444 | -120.4514 | 2.8107 | 0.0033567 | 0.0029117 | 0.12402 | 0.0021661 | -0.00086946 | 0.002634 | 0.00075627 | -0.0018616 | 0.14516 | 0.0023348 | 0.00089939 | -0.0011022 | -0.00059378 | -0.0018265 | -31.636 | -2.1881 | -120.8267 | -2.5131 | -2.3483 | -120.2179 | -2.417 | 1.0986 | 2.7374 | 2.211 | 2.5497 | 2.5269 | 2.5635 | 2.7969 | -0.37537 | -4.9988 | -5.3238 | 118.103 | 118.0344 | 0.23346 | 118.4097 | 0.60883 | 122.6624 | -0.073242 | -0.26092 | 122.9782 | 123.2483 | 123.0148 | 0.58594 | 0.35248 | 118.4784 | 118.3136 | 0.31586 | 0.33874 | 118.6386 | 0.52643 | 118.2632 | 123.1888 | -123.6374 | -0.59967 | 117.9382 | 123.0011 | 88.8153 | 121.55
1430.4844 | 123.4131 | -120.8405 | 2.3712 | -0.050049 | 0.0031253 | 0.12488 | 0.0025933 | 0.0016939 | 0.0011386 | 0.0018243 | 0.013397 | 0.14366 | 0.0048984 | -0.0029458 | -0.0025976 | 0.00026062 | -0.0020401 | -31.691 | -2.2018 | -121.051 | -2.504 | -2.3438 | -120.6299 | -2.3804 | 1.0849 | 2.4811 | 1.9821 | 2.2293 | 2.2888 | 2.2156 | 2.2888 | -0.21057 | -4.5731 | -4.8752 | 118.4967 | 118.4601 | 0.21057 | 118.6707 | 0.42114 | 122.8226 | 0.10986 | -0.14191 | 123.1293 | 123.1293 | 123.056 | 0.3067 | 0.23346 | 118.7073 | 118.5471 | 0.3067 | 0.24719 | 118.8492 | 0.49896 | 118.6386 | 123.3215 | -123.4222 | -0.3891 | 118.3365 | 123.0698 | 89.1495 | 121.9254
1431.5469 | 123.381 | -120.9457 | 2.2659 | 0.010986 | 0.0016299 | 0.12423 | 0.0032343 | -0.00086946 | 0.0011386 | -0.0026617 | -0.014069 | 0.1458 | 0.0046848 | -0.004014 | -0.0028112 | -0.0035846 | -0.00075834 | -29.892 | -2.2751 | -121.1151 | -2.5909 | -2.4582 | -120.6985 | -2.4536 | 0.97504 | 2.4399 | 1.9592 | 2.1378 | 2.2018 | 2.092 | 2.1515 | -0.16937 | -4.541 | -4.8569 | 118.4875 | 118.4921 | 0.24719 | 118.6615 | 0.41656 | 122.905 | 0.17395 | -0.12817 | 123.1476 | 123.0972 | 123.0377 | 0.19226 | 0.13275 | 118.6569 | 118.5242 | 0.24261 | 0.17853 | 118.84 | 0.48065 | 118.6707 | 123.3856 | -123.381 | -0.3067 | 118.3548 | 123.0835 | 91.0538 | 121.9208
1432.4844 | 123.2803 | -120.7764 | 2.4948 | -0.042419 | 0.0012027 | 0.12381 | 0.0021661 | -0.00022866 | 0.00092498 | -0.00031193 | -0.056793 | 0.1443 | 0.0029758 | -0.00038241 | -0.002384 | -0.0048664 | -0.0028945 | -31.5948 | -2.2842 | -121.0098 | -2.6505 | -2.5085 | -120.5841 | -2.5635 | 0.98877 | 2.5864 | 2.0325 | 2.2156 | 2.2842 | 2.1835 | 2.2522 | -0.23346 | -4.7791 | -5.1453 | 118.2678 | 118.2129 | 0.19226 | 118.4463 | 0.42572 | 122.8088 | 0.091553 | -0.27924 | 123.0606 | 123.0286 | 122.9599 | 0.21973 | 0.15106 | 118.5013 | 118.3594 | 0.25177 | 0.1831 | 118.7256 | 0.55389 | 118.4921 | 123.3627 | -123.5046 | -0.46234 | 118.1259 | 122.9919 | 89.1815 | 121.7651
1433.4844 | 123.2529 | -120.8817 | 2.417 | 0.018616 | 0.0031253 | 0.12359 | 0.0036615 | -0.0027921 | 0.0017794 | -0.0028753 | -0.059845 | 0.14452 | 0.0021212 | -0.0031594 | -0.0021704 | -0.00059378 | 0.0015915 | -30.0522 | -2.2293 | -121.1243 | -2.6642 | -2.5269 | -120.7352 | -2.5452 | 0.93384 | 2.5177 | 1.9272 | 2.1057 | 2.124 | 2.0279 | 2.1149 | -0.24262 | -4.6463 | -5.0812 | 118.3548 | 118.3365 | 0.14648 | 118.5791 | 0.3891 | 122.8088 | 0.10071 | -0.31128 | 123.0057 | 122.9965 | 122.9095 | 0.18768 | 0.10071 | 118.5974 | 118.4601 | 0.19684 | 0.17853 | 118.895 | 0.59052 | 118.6523 | 123.3994 | -123.5413 | -0.48981 | 118.2175 | 122.9874 | 90.8295 | 121.8155
1434.4844 | 122.5433 | -44.0964 | 78.5248 | -0.080566 | 0.0016299 | 0.043058 | 0.00024352 | -0.0038603 | -0.0014248 | -0.00031193 | 0.071381 | 0.0037405 | 0.0038302 | 0.038711 | -0.0019568 | -0.0020892 | -0.0018265 | -10.8765 | -1.2314 | -43.9819 | -1.5427 | -1.4465 | -44.2566 | -1.5564 | 4.5822 | 78.0579 | 1.3779 | 78.7811 | 1.5198 | 1.3779 | 1.4328 | 0.11444 | -79.7562 | -80.0674 | 42.6498 | 42.54 | -0.16022 | 42.4255 | -0.27466 | 45.4742 | -0.46692 | 0.25635 | 45.6162 | 45.5292 | 45.4742 | 0.054931 | 0 | 42.5354 | 42.4393 | 0.14191 | 77.4033 | 42.7506 | 76.68 | 42.865 | 122.1542 | -122.5067 | -77.1469 | 42.5537 | 122.8775 | 33.2199 | 48.6786
1435.4844 | 116.8259 | -43.7439 | 78.3508 | -0.43152 | 0.0014163 | 0.041349 | 0.0019525 | -0.0032193 | 0.00028418 | 0.0011835 | 0.05307 | 0.0043815 | 0.004471 | 0.039992 | -0.0015296 | -0.001662 | 0.0041551 | -10.8948 | -1.1673 | -43.9453 | -1.7029 | -1.7349 | -44.4214 | -1.8585 | 2.0279 | 78.2227 | 1.4832 | 78.0945 | 1.2955 | 1.1169 | 1.2222 | -0.20142 | -79.5181 | -80.0537 | 42.009 | 41.8854 | -0.67749 | 42.0868 | -0.47608 | 45.227 | -0.12817 | -0.25635 | 45.0394 | 44.9661 | 44.8608 | -0.26093 | -0.36621 | 42.2104 | 42.2424 | -0.18768 | 76.6113 | 42.778 | 76.7395 | 42.5766 | 121.9666 | -122.2961 | -76.8677 | 42.041 | 121.8384 | 32.8491 | 45.7718
1436.4844 | 122.9187 | -44.0918 | 78.9368 | -0.027161 | 0.0014163 | 0.043699 | -0.00039728 | -0.00086946 | 0.0017794 | -0.0028753 | 0.083588 | 0.0028861 | 0.0036166 | 0.039992 | -0.0032386 | -0.001662 | -0.00075834 | -10.5194 | -1.1124 | -44.3115 | -1.3824 | -1.1993 | -44.1559 | -1.3046 | 2.1652 | 78.8223 | 1.3916 | 79.0695 | 1.7715 | 1.6754 | 1.7029 | -0.21973 | -80.0491 | -80.3192 | 42.8925 | 42.7872 | -0.064087 | 43.0069 | 0.15564 | 45.4834 | -0.11444 | 0.13275 | 45.8633 | 45.7947 | 45.7672 | 0.31128 | 0.28381 | 43.1122 | 42.9291 | 0.37994 | 77.6779 | 43.1992 | 77.4307 | 42.9794 | 122.9141 | -123.2483 | -77.5452 | 42.7094 | 123.1613 | 33.5724 | 46.257
1437.4844 | 94.5374 | -34.3689 | 78.6942 | -0.095825 | -0.0084103 | 0.041349 | -0.011078 | -0.010696 | 7.0582e-05 | -0.0073615 | -0.020172 | -0.013349 | -0.010269 | 0.025893 | -0.029087 | -0.018111 | -0.018489 | -10.5377 | -1.0254 | -43.8354 | -1.474 | -1.561 | -31.9244 | 0.09613 | 1.4328 | 78.3417 | 1.5747 | 67.543 | 1.474 | 0.091553 | 0.09613 | -9.4666 | -79.7195 | -80.1682 | 32.8079 | 34.465 | 2.4445 | 43.9316 | 11.911 | 35.9436 | -0.35248 | -11.1511 | 35.8429 | 34.465 | 34.4604 | -1.4786 | -1.4832 | 42.2745 | 42.3614 | -0.10071 | 65.9683 | 42.8101 | 76.767 | 33.3435 | 112.7106 | -122.5296 | -77.1194 | 32.8949 | 101.9119 | 23.8312 | 35.8017
1438.5469 | 123.0606 | -44.0781 | 78.8086 | -0.072937 | 0.0020573 | 0.041349 | 0.0015253 | 0.00019874 | 0.0022068 | -0.0020209 | 0.059174 | 0.0013907 | 0.005112 | 0.037002 | -0.004093 | -0.0025164 | -0.00097194 | -10.6247 | -1.1215 | -44.3481 | -1.442 | -1.3092 | -44.3344 | -1.3321 | 1.2131 | 79.1016 | 1.5472 | 79.0924 | 1.9089 | 1.799 | 1.8906 | -0.27008 | -79.9301 | -80.2506 | 42.7689 | 42.746 | -0.25635 | 43.0161 | 0.013733 | 45.6253 | 0.29297 | 0.28381 | 45.9869 | 45.9686 | 45.8771 | 0.34332 | 0.25177 | 43.0389 | 42.9062 | 0.36163 | 77.5452 | 43.2266 | 77.5543 | 42.9565 | 123.1796 | -123.1567 | -77.2614 | 42.6361 | 123.1705 | 33.4534 | 45.2911
1439.4844 | 106.2653 | -44.5496 | 78.5294 | -0.48492 | 0.0018435 | 0.042203 | 0.0038751 | -1.486e-05 | -0.00057042 | -0.0022345 | -0.065949 | 0.0037405 | 0.0036166 | 0.041915 | 0.0016748 | -0.0029438 | 0.0020187 | -10.7346 | -1.3412 | -44.3573 | -1.7807 | -1.7761 | -44.6091 | -2.0691 | 0.95215 | 78.8086 | 1.3596 | 78.1357 | 1.4969 | 1.4008 | 1.7578 | 0.19226 | -79.8706 | -80.3101 | 42.7734 | 42.4805 | -0.059509 | 42.2882 | -0.25177 | 45.9091 | 0.27924 | -0.39368 | 46.0464 | 46.3074 | 45.9503 | 0.39825 | 0.041199 | 42.5812 | 42.5766 | 0.13733 | 76.7761 | 43.0161 | 77.449 | 43.2083 | 123.3582 | -122.8867 | -77.1698 | 42.7689 | 122.6852 | 33.815 | 45.5017
1440.5 | 96.0205 | -37.2437 | 78.8498 | -0.26367 | 0.02406 | 0.034086 | -0.0063789 | 0.035233 | -0.012533 | 0.049889 | -0.28873 | 0.014849 | -0.00621 | 0.028029 | -0.028232 | 0.0077374 | -0.017848 | -10.6247 | -1.2405 | -44.0781 | -1.6388 | -1.7303 | -40.1596 | 0.091553 | 1.2589 | 78.8177 | 1.4648 | 75.6226 | 1.6113 | 1.5839 | 0.07782 | -6.8344 | -80.0903 | -80.4886 | 35.5133 | 37.3352 | -2.916 | 44.1696 | 3.9185 | 38.7085 | -0.032043 | -3.2272 | 38.855 | 37.3215 | 38.8275 | -1.387 | 0.11902 | 42.3477 | 42.4393 | 0.14648 | 74.1577 | 42.8375 | 77.3529 | 36.0031 | 116.0614 | -122.9279 | -77.3849 | 35.6049 | 112.8662 | 26.619 | 38.5025
1441.5469 | 123.1064 | -44.2337 | 78.3051 | -0.019531 | 0.00077547 | 0.042631 | 0.0013117 | 0.0025485 | 0.0017794 | -0.0018073 | 0.062225 | 0.0039541 | 0.005112 | 0.039565 | -0.0021704 | -0.0046528 | -0.0013991 | -11.3022 | -1.506 | -44.4946 | -1.8082 | -1.6022 | -44.4443 | -1.6708 | 3.1723 | 78.9093 | 1.5564 | 78.9459 | 1.9684 | 1.8539 | 1.9135 | -0.26093 | -79.8111 | -80.1132 | 42.6315 | 42.5629 | -0.21057 | 42.8238 | 0.050354 | 45.7901 | 0.60425 | 0.64087 | 46.2021 | 46.1472 | 46.0876 | 0.35706 | 0.29755 | 42.8925 | 42.6865 | 0.41199 | 77.3895 | 42.9886 | 77.3529 | 42.7277 | 123.143 | -122.7997 | -76.7487 | 42.4255 | 123.1796 | 32.9315 | 47.406
1442.4844 | 94.3726 | -31.8192 | 78.5797 | -0.24841 | 0.02406 | 0.029813 | -0.012147 | 0.024125 | -0.010183 | -0.0045843 | -0.28873 | 0.014849 | -0.001724 | 0.027816 | 0.10122 | 0.016282 | -0.0097305 | -10.5606 | -1.2497 | -44.2062 | -1.6159 | -1.5747 | -44.7784 | -1.6525 | 5.2094 | 78.8361 | 1.6479 | 73.2971 | 1.8127 | 1.7578 | 0.10071 | -12.3871 | -79.8294 | -80.1956 | 30.2444 | 30.1666 | -12.9593 | 42.5537 | -0.5722 | 33.4671 | 0.25635 | -5.2826 | 33.6319 | 31.9199 | 33.577 | -1.5472 | 0.10986 | 42.6315 | 42.5903 | 0.16479 | 71.6492 | 42.9565 | 77.1881 | 30.5695 | 110.6552 | -122.7859 | -76.9318 | 30.2032 | 105.1163 | 21.2585 | 37.0285
1443.4844 | 123.3948 | -120.6024 | 2.5726 | -0.0042723 | 0.0035525 | 0.12466 | 0.0036615 | -0.0030057 | 0.0015658 | -0.00073913 | -0.01712 | 0.14665 | 0.0040438 | 0.0023948 | -0.0011022 | -0.0010212 | -0.00097194 | -30.7755 | -2.2614 | -120.9824 | -2.7237 | -2.623 | -120.6619 | -2.7878 | 0.98419 | 2.6138 | 2.0325 | 2.2385 | 2.0691 | 1.9226 | 1.9684 | -0.37994 | -4.834 | -5.2963 | 117.9794 | 117.8146 | -0.059509 | 118.1946 | 0.32044 | 122.6349 | 0.041199 | -0.33417 | 122.6715 | 122.5708 | 122.525 | -0.064087 | -0.10986 | 118.3594 | 118.2587 | 0.036621 | 0.20599 | 118.721 | 0.58136 | 118.3411 | 123.2162 | -123.555 | -0.54016 | 117.8787 | 122.8409 | 89.827 | 121.5866
1444.4844 | 123.3719 | -120.8725 | 2.3666 | -0.050049 | 0.0033389 | 0.1253 | 0.0010981 | 0.00062594 | 0.00028418 | 0.00054267 | 0.010345 | 0.14452 | 0.0036166 | -0.0059366 | -0.001316 | -0.00508 | -0.00011754 | -30.5466 | -2.5085 | -121.0464 | -2.8931 | -2.7145 | -120.3918 | -2.8061 | 0.99335 | 2.4994 | 1.9547 | 2.1286 | 2.1561 | 2.0004 | 2.005 | -0.17395 | -4.8752 | -5.2597 | 118.158 | 118.0664 | 0.48065 | 118.2404 | 0.6546 | 122.8271 | 0.13275 | -0.23804 | 123.0286 | 122.8775 | 122.8729 | 0.050354 | 0.045776 | 118.3319 | 118.1534 | 0.20142 | 0.17395 | 118.5379 | 0.54474 | 118.364 | 123.3719 | -123.4131 | -0.41199 | 117.9794 | 123.0011 | 90.3259 | 121.8658
1445.4844 | 123.3856 | -120.6482 | 2.6596 | -0.027161 | -0.0034969 | 0.11996 | 0.0043023 | -0.010696 | -0.00099762 | -0.011848 | -0.21854 | 0.1396 | -0.006851 | -0.0055094 | -0.01392 | -0.018111 | -0.012721 | -30.5923 | -2.3895 | -121.0831 | -2.8061 | -2.7512 | -109.9503 | -3.2318 | 1.1124 | 2.5635 | 2.0187 | 2.3621 | 2.3483 | 2.0096 | 2.4902 | -0.43488 | -5.0491 | -5.4657 | 117.897 | 117.4164 | 10.6979 | 117.8513 | 11.1328 | 122.6669 | -0.09613 | -0.29755 | 122.9965 | 123.1384 | 122.6578 | 0.4715 | -0.009155 | 118.3319 | 118.277 | 0.32959 | 0.34332 | 118.6935 | 0.54474 | 118.2587 | 123.2117 | -123.7427 | -0.64087 | 117.8421 | 123.0103 | 90.0558 | 121.7606
1446.5469 | 123.468 | -120.4651 | 2.7603 | -0.065308 | 0.0039799 | 0.12488 | 0.0030207 | 0.0021213 | 0.0024204 | -0.0022345 | -0.01712 | 0.14324 | 0.0057528 | -0.005082 | -0.0015296 | -0.0044392 | 0.0050095 | -30.5328 | -2.3483 | -120.8771 | -2.6505 | -2.4948 | -120.108 | -2.536 | 1.1078 | 2.8519 | 2.3071 | 2.7649 | 2.6047 | 2.4216 | 2.623 | -0.41199 | -5.1086 | -5.4108 | 117.9703 | 117.9291 | 0.35706 | 118.3411 | 0.76904 | 122.7722 | 0.091553 | 0.004578 | 123.0698 | 123.0881 | 122.8867 | 0.31586 | 0.11444 | 118.3823 | 118.2266 | 0.29755 | 0.45776 | 118.5287 | 0.54474 | 118.1168 | 123.317 | -123.6374 | -0.45319 | 117.8146 | 123.23 | 89.9323 | 121.5729
1447.5 | 123.3902 | -120.8771 | 2.3621 | -0.019531 | 0.0031253 | 0.12616 | 0.0045159 | -0.00086946 | 0.0028476 | -0.0052251 | 0.037811 | 0.14516 | 0.005112 | -0.0082864 | -0.0028112 | -0.0023028 | 9.6064e-05 | -30.5969 | -2.3987 | -121.0876 | -2.742 | -2.6001 | -120.7077 | -2.6367 | 0.97961 | 2.5131 | 1.9958 | 2.1561 | 2.2018 | 2.1378 | 2.2293 | -0.21057 | -4.7607 | -5.1041 | 118.277 | 118.2404 | 0.16937 | 118.4509 | 0.37994 | 122.8729 | 0.15106 | -0.20599 | 123.0789 | 123.1064 | 123.0148 | 0.23346 | 0.14191 | 118.4875 | 118.3456 | 0.20599 | 0.16022 | 118.689 | 0.51727 | 118.4784 | 123.3902 | -123.4497 | -0.36621 | 118.1351 | 123.0331 | 90.2802 | 121.8567
1448.5469 | 123.4131 | -120.8954 | 2.3117 | -0.057678 | 0.00034827 | 0.12381 | 0.0010981 | 0.0029757 | 0.002634 | -0.0015935 | -0.011017 | 0.14516 | 0.005112 | -0.0029458 | -0.003025 | -0.0029438 | -0.00033114 | -30.7022 | -2.4582 | -121.1288 | -2.7328 | -2.5818 | -120.7031 | -2.6321 | 1.0529 | 2.3438 | 1.8173 | 2.1423 | 2.2293 | 2.1698 | 2.211 | -0.23346 | -4.7699 | -5.0446 | 118.3136 | 118.2632 | 0.19226 | 118.4967 | 0.42572 | 122.7127 | 0.032043 | -0.16937 | 123.1247 | 123.1064 | 123.0652 | 0.39368 | 0.35248 | 118.5471 | 118.396 | 0.41199 | 0.32501 | 118.6707 | 0.52643 | 118.4372 | 123.2391 | -123.4406 | -0.49439 | 118.1625 | 123.0377 | 90.1932 | 121.9482
1449.4844 | 123.4543 | -120.52 | 2.5681 | 0.0033567 | 0.0041935 | 0.12317 | -0.0018927 | -0.01326 | -0.0016384 | -0.015693 | -0.30704 | 0.12807 | -0.014328 | -0.018113 | -0.030796 | -0.014266 | -0.0033219 | -29.7455 | -2.1057 | -120.694 | -2.5772 | -2.4902 | -93.7729 | 0.12817 | 0.87891 | 2.9022 | 2.6413 | 2.33 | 2.124 | 0.07782 | 0.086975 | -0.17395 | -4.6738 | -5.1453 | 118.0298 | 120.6482 | 26.7471 | 120.8221 | 26.9211 | 123.1613 | 0.33417 | -0.23804 | 122.644 | 120.607 | 120.5978 | -2.5543 | -2.5635 | 118.2037 | 118.1168 | -0.51727 | -0.31128 | 118.5883 | 0.26093 | 118.4143 | 123.4222 | -123.262 | 0.073242 | 117.9428 | 122.85 | 90.7745 | 121.3989
1450.5469 | 123.4634 | -120.9503 | 2.1881 | -0.042419 | 0.0035525 | 0.12488 | 0.0028069 | -0.0047147 | 0.00071138 | -0.0026617 | 0.022552 | 0.14281 | 0.0040438 | -0.0042276 | -0.003025 | -0.0029438 | 0.0039413 | -29.9423 | -2.2614 | -121.1838 | -2.5452 | -2.3895 | -120.6985 | -2.4307 | 0.95215 | 2.3163 | 1.799 | 2.0737 | 2.0874 | 2.0554 | 2.1149 | -0.23346 | -4.4495 | -4.7333 | 118.5608 | 118.5196 | 0.25177 | 118.7531 | 0.48523 | 122.7493 | 0.12817 | -0.11444 | 123.0377 | 123.0652 | 123.0057 | 0.31586 | 0.25635 | 118.7943 | 118.6386 | 0.28839 | 0.27466 | 118.9224 | 0.51727 | 118.689 | 123.2666 | -123.3719 | -0.3891 | 118.4052 | 123.024 | 91.008 | 121.9025
1451.5 | 123.4177 | -120.5521 | 2.6825 | 0.010986 | 0.0052615 | 0.12317 | 0.0010981 | 0.0027621 | 0.0017794 | -0.00031193 | 0.010345 | 0.14089 | 0.0027622 | -0.0018778 | -0.002384 | -0.0018756 | -0.00097194 | -30.3268 | -2.3026 | -120.7031 | -2.6413 | -2.4948 | -120.3323 | -2.5085 | 1.1948 | 2.8198 | 2.3071 | 2.5726 | 2.5772 | 2.4994 | 2.5452 | -0.15106 | -4.985 | -5.3238 | 118.0573 | 118.0435 | 0.21973 | 118.1946 | 0.37079 | 122.8592 | 0.13733 | -0.10986 | 123.1293 | 123.0972 | 123.0515 | 0.23804 | 0.19226 | 118.2083 | 118.0618 | 0.27008 | 0.2655 | 118.4006 | 0.51269 | 118.2495 | 123.3719 | -123.3856 | -0.37537 | 117.9108 | 123.1247 | 90.2252 | 121.7468
1452.5625 | 123.4131 | -120.7581 | 2.4353 | -0.13397 | 0.0041935 | 0.12573 | 0.0036615 | 0.0014803 | 0.0017794 | -0.0013799 | -0.044586 | 0.14302 | 0.006821 | -0.0044412 | -0.002384 | -0.0014484 | 0.00073706 | -29.7775 | -2.3392 | -120.9869 | -2.6184 | -2.4765 | -120.3506 | -2.5223 | 1.0025 | 2.536 | 2.0325 | 2.3254 | 2.3209 | 2.211 | 2.3209 | -0.22888 | -4.7745 | -5.0537 | 118.2816 | 118.2358 | 0.40741 | 118.4647 | 0.63629 | 122.7905 | 0.10071 | -0.10986 | 123.0789 | 123.0789 | 122.9691 | 0.28839 | 0.17853 | 118.5104 | 118.3685 | 0.28839 | 0.29297 | 118.6478 | 0.50354 | 118.4189 | 123.2941 | -123.4222 | -0.40283 | 118.1396 | 123.0835 | 90.9805 | 121.7606
1453.4844 | 123.2758 | -120.5887 | 2.6779 | -0.088196 | 0.00077547 | 0.11932 | 0.0049433 | -0.012191 | -0.0037746 | -0.017402 | -0.1636 | 0.14986 | -0.0053556 | -0.005082 | -0.0025976 | -0.013839 | -0.0043899 | -30.162 | -2.3346 | -120.8405 | -2.7924 | -2.655 | -119.0826 | -3.0029 | 0.9201 | 2.774 | 2.0966 | 2.4078 | 2.3254 | 2.1835 | 2.0737 | -0.25177 | -5.0125 | -5.4703 | 117.9337 | 117.5858 | 1.506 | 117.8375 | 1.7578 | 122.6852 | 0.096131 | -0.27008 | 122.9141 | 122.6624 | 122.7722 | -0.022889 | 0.086975 | 118.1854 | 118.0481 | 0.22888 | 0.31128 | 118.5059 | 0.67749 | 118.2541 | 123.3627 | -123.5184 | -0.58136 | 117.7963 | 122.9965 | 90.4266 | 121.5088
1454.4844 | 123.3673 | -120.3461 | 2.7832 | 0.0033567 | 0.0022709 | 0.12039 | 0.0032343 | 0.0023349 | 0.0017794 | 0.00075627 | -0.21243 | 0.13576 | 0.0036166 | 0.0060264 | -0.0028112 | -0.0055072 | -0.0058853 | -29.9057 | -2.3026 | -120.5978 | -2.742 | -2.5818 | -117.6636 | -2.9663 | 1.1215 | 2.8931 | 2.3163 | 2.4902 | 2.4994 | 2.2934 | 2.179 | -0.25177 | -5.0858 | -5.5252 | 117.7643 | 117.3798 | 2.6825 | 117.6315 | 2.9343 | 122.6624 | 0.10986 | -0.29297 | 122.8455 | 122.525 | 122.6395 | -0.13733 | -0.022888 | 118.0161 | 117.8558 | 0.18311 | 0.17395 | 118.2953 | 0.57678 | 118.0435 | 123.2391 | -123.381 | -0.46692 | 117.6041 | 122.8363 | 90.4404 | 121.4676
1455.4844 | 123.2941 | -120.8771 | 2.3666 | -0.057678 | 0.0026981 | 0.12594 | 0.0036615 | -0.012619 | 0.0015658 | -0.014838 | -0.14224 | 0.13811 | -0.0030058 | -0.0055094 | -0.0090064 | -0.01512 | -0.010158 | -30.3864 | -2.3621 | -121.0831 | -2.829 | -2.655 | -116.0431 | -3.1036 | 0.80109 | 2.5269 | 1.9318 | 2.1011 | 2.037 | 1.9501 | 1.8448 | -0.20599 | -4.7287 | -5.1956 | 118.222 | 117.7734 | 4.834 | 117.9794 | 5.04 | 122.8088 | 0.16022 | -0.2655 | 122.9141 | 122.7219 | 122.8271 | -0.086975 | 0.01831 | 118.428 | 118.2541 | 0.10529 | 0.16937 | 118.721 | 0.59509 | 118.515 | 123.4039 | -123.4497 | -0.43488 | 118.0481 | 122.9782 | 90.4907 | 121.6782
1456.4844 | 123.2849 | -120.9137 | 2.3804 | -0.03479 | 0.0022709 | 0.12445 | 0.0034479 | 0.00041234 | -0.00035682 | 0.0016107 | -0.020172 | 0.14281 | 0.005112 | -0.0010232 | -0.0019568 | 0.001115 | 0.0022323 | -29.8645 | -2.2705 | -121.1426 | -2.7512 | -2.5681 | -120.9824 | -2.5497 | 0.90637 | 2.4536 | 1.8631 | 2.124 | 2.1881 | 2.0416 | 1.9867 | -0.22888 | -4.6509 | -5.1315 | 118.3456 | 118.364 | -0.068665 | 118.5928 | 0.16022 | 122.7768 | 0.073242 | -0.25635 | 123.1018 | 122.9004 | 122.9553 | 0.1236 | 0.17853 | 118.5745 | 118.3914 | 0.32501 | 0.26093 | 118.8721 | 0.59051 | 118.6432 | 123.3673 | -123.5229 | -0.51727 | 118.1625 | 123.0377 | 91.0492 | 121.8201
1457.5625 | 123.4131 | -120.7809 | 2.3758 | -0.027161 | 0.0029117 | 0.12274 | 0.0017389 | 0.0023349 | -0.00035682 | -0.00052553 | 0.019501 | 0.1411 | 0.0042574 | -0.0038004 | -0.0015296 | -0.0018756 | -0.00054474 | -29.6722 | -3.0075 | -120.6436 | -3.3371 | -2.124 | -120.4422 | -2.1881 | 1.0208 | 2.6459 | 2.1973 | 2.2797 | 2.3209 | 2.2247 | 2.3026 | 0.13733 | -5.3833 | -5.7129 | 118.6569 | 118.5928 | 0.33875 | 118.4555 | 0.20142 | 122.9782 | 0.27008 | -0.09613 | 123.1018 | 123.0835 | 123.0057 | 0.10528 | 0.027465 | 118.5196 | 117.3065 | 0.1236 | 0.082397 | 117.6361 | 0.44861 | 117.7734 | 123.4268 | -123.0194 | -0.17853 | 117.4438 | 123.0606 | 91.1087 | 121.8018
1458.4844 | 123.2758 | -120.8359 | 2.4078 | -0.050049 | -0.00071993 | 0.11676 | 0.0047295 | -0.015609 | -0.0050564 | -0.016975 | -0.28567 | 0.011431 | -0.0074918 | -0.011064 | -0.0094336 | -0.0059344 | -0.011653 | -30.6335 | -2.655 | -121.1105 | -3.0853 | -2.1103 | -120.2728 | -2.211 | 0.94299 | 2.4719 | 1.9455 | 2.1881 | 2.1744 | 2.0462 | 2.0737 | -0.27466 | -5.0629 | -5.4932 | 118.7256 | 118.6249 | 0.56305 | 118.8995 | 0.83771 | 122.7814 | 0.064087 | -0.21973 | 123.0103 | 122.9095 | 122.8821 | 0.12817 | 0.10071 | 119.0002 | 118.0252 | 0.22888 | 0.24261 | 118.4555 | 0.52643 | 118.1808 | 123.3078 | -123.5184 | -0.46234 | 117.7505 | 123.024 | 90.2023 | 121.7789
1459.4844 | 123.3536 | -120.7169 | 2.4994 | -0.080566 | 0.0012027 | 0.12445 | 0.0032343 | 0.00083954 | 0.00092498 | 0.0022517 | -0.10562 | 0.14559 | 0.003403 | -0.0020914 | -0.0034522 | -0.0010212 | 0.0015915 | -31.1874 | -2.4857 | -121.0236 | -2.9343 | -2.4261 | -120.9229 | -2.4445 | 1.0025 | 2.5543 | 2.0325 | 2.3026 | 2.3209 | 2.2247 | 2.3621 | -0.3067 | -4.985 | -5.4337 | 118.2907 | 118.2724 | -0.20599 | 118.5791 | 0.10071 | 122.7493 | 0.054931 | -0.19684 | 123.0377 | 123.0789 | 122.9416 | 0.32959 | 0.19226 | 118.5974 | 118.0893 | 0.28839 | 0.27008 | 118.5379 | 0.52185 | 118.2312 | 123.2712 | -123.523 | -0.46692 | 117.7826 | 123.0194 | 89.5294 | 121.7194
1460.5469 | 123.2803 | -120.6573 | 2.623 | -0.027161 | 0.0039799 | 0.12445 | 0.0019525 | 0.00041234 | 7.0582e-05 | -0.0011663 | -0.062897 | 0.14495 | 0.0048984 | -0.0014504 | -0.0019568 | -0.0029438 | 0.0028733 | -30.4367 | -2.5085 | -120.7764 | -2.9526 | -2.2385 | -120.5246 | -2.2797 | 0.92468 | 2.6596 | 2.1103 | 2.3026 | 2.449 | 2.3529 | 2.4536 | -0.11902 | -5.1315 | -5.5756 | 118.4189 | 118.3777 | 0.13275 | 118.4967 | 0.25177 | 122.7676 | 0.036621 | -0.32044 | 123.1064 | 123.111 | 123.0103 | 0.34332 | 0.24261 | 118.5379 | 117.8238 | 0.33874 | 0.19226 | 118.2678 | 0.54932 | 118.1488 | 123.317 | -123.3994 | -0.51269 | 117.7048 | 122.9599 | 90.2206 | 121.582
1461.4844 | 123.3307 | -121.2341 | 1.9913 | -0.042419 | 0.0039799 | 0.12723 | 0.0043023 | -0.00022866 | 0.0030612 | 0.00011527 | -0.099518 | 0.1458 | 0.0012668 | 0.0023948 | -0.003025 | -0.0012348 | 0.0037277 | -30.574 | -2.4033 | -121.5866 | -2.8473 | -2.3849 | -121.1472 | -2.4216 | 0.73242 | 2.0828 | 1.5564 | 1.799 | 1.8173 | 1.7258 | 1.8356 | -0.35248 | -4.3945 | -4.8386 | 118.8492 | 118.8126 | 0.086975 | 119.165 | 0.43945 | 122.7905 | 0.091553 | -0.19226 | 123.0515 | 123.0698 | 122.9599 | 0.27924 | 0.16937 | 119.2017 | 118.7393 | 0.26093 | 0.24262 | 119.1833 | 0.52643 | 118.8309 | 123.317 | -123.5779 | -0.43488 | 118.3868 | 123.0331 | 90.6601 | 121.9666
1462.5 | 123.2758 | -120.9686 | 2.3346 | -0.042419 | 0.0035525 | 0.12295 | 0.0030207 | -1.486e-05 | 0.00028418 | -0.0024481 | -0.11478 | 0.14452 | 0.0036166 | 0.00389 | -0.0021704 | -0.0010212 | 0.00030966 | -30.5832 | -2.3666 | -121.0327 | -2.829 | -2.2888 | -120.2499 | -2.3117 | 0.93842 | 2.6825 | 2.1332 | 2.0462 | 2.179 | 2.0096 | 2.0279 | -0.064087 | -4.7012 | -5.1636 | 118.6798 | 118.6569 | 0.71869 | 118.721 | 0.78278 | 123.1018 | 0.3479 | -0.28839 | 123.1476 | 122.9965 | 122.9782 | -0.10529 | -0.1236 | 118.7439 | 118.2037 | 0.045776 | -0.086975 | 118.6661 | 0.54932 | 118.602 | 123.6511 | -123.3673 | -0.20142 | 118.1396 | 123.0148 | 90.3854 | 121.907
1463.5625 | 123.2574 | -121.1472 | 2.1378 | -0.027161 | 0.0026981 | 0.12381 | 0.0036615 | 0.0014803 | 0.0030612 | -0.00095273 | -0.11783 | 0.14623 | 0.0027622 | 0.004531 | -0.000675 | 0.00026062 | 0.00073706 | -31.6772 | -2.3621 | -121.5042 | -2.8198 | -2.2476 | -120.9778 | -2.2705 | 0.75531 | 2.1744 | 1.6022 | 1.8631 | 1.8997 | 1.7715 | 1.9089 | -0.35706 | -4.4998 | -4.9576 | 118.8995 | 118.8766 | 0.16937 | 119.2337 | 0.52643 | 122.7493 | 0.036621 | -0.27466 | 123.0469 | 123.056 | 122.9187 | 0.3067 | 0.16937 | 119.2566 | 118.6844 | 0.29755 | 0.26092 | 119.1422 | 0.5722 | 118.7851 | 123.3215 | -123.642 | -0.53558 | 118.3273 | 123.0103 | 89.4699 | 121.9025
1464.4844 | 94.5099 | -30.1483 | 62.6129 | -0.26367 | 0.023847 | 0.11206 | 0.055572 | 0.035233 | 0.055613 | 0.049889 | -0.28873 | -0.00074552 | -0.00044215 | 0.042556 | 0.26336 | 0.015855 | 0.033208 | -11.3937 | -1.5518 | -33.5129 | -1.6205 | -1.6022 | -45.0119 | -1.8585 | 5.2277 | 78.0624 | 0.46692 | 76.8906 | 0.71869 | 0.56763 | 0.44403 | -3.3646 | -64.1647 | -64.2334 | 28.5461 | 28.2898 | -14.8636 | 31.6544 | -11.499 | 30.6152 | 15.4495 | 14.2776 | 30.867 | 30.5923 | 30.7159 | -0.022888 | 0.10071 | 31.9107 | 31.8924 | 0.25177 | 76.4236 | 31.9611 | 77.5955 | 28.5965 | 108.2108 | -96.1258 | -62.146 | 28.5278 | 107.0389 | 18.7546 | 35.376
1465.5469 | 111.0168 | -45.0348 | 66.6641 | -0.24841 | 0.02406 | 0.11334 | 0.065185 | 0.036515 | -0.0048428 | -0.0090703 | -0.27957 | -0.0037363 | -0.011551 | 0.037643 | -0.012211 | -0.011061 | -0.013576 | 0.091553 | 0.17395 | -32.9498 | 0.09613 | 0.091553 | -27.3239 | 0.091553 | 5.2048 | 60.7819 | 0.44861 | 69.4748 | 0.64545 | 0.45776 | 0.60883 | 12.085 | -66.4902 | -66.568 | 45.1263 | 45.1263 | 17.7109 | 33.0414 | 5.6259 | 45.4834 | -5.8823 | 2.8107 | 45.6802 | 45.6436 | 45.4926 | 0.16022 | 0.009156 | 33.0414 | 33.046 | 0.19684 | 69.0262 | 33.1238 | 60.3333 | 45.2087 | 105.8167 | -99.614 | -66.2155 | 45.1309 | 114.5096 | 45.1263 | 50.2396
1466.4844 | 94.2993 | -34.4009 | 58.1497 | -0.26367 | 0.023847 | 0.11291 | 0.065826 | 0.034592 | -0.0048428 | 0.049889 | -0.29178 | 0.014849 | 0.013657 | 0.042129 | 0.26379 | 0.016069 | 0.033849 | 0.086975 | -1.506 | -36.7081 | 0.09613 | 0.09613 | -22.6044 | 0.086975 | 4.8065 | 67.2272 | 0.54932 | 54.3182 | 0.09613 | 0.09613 | 0.091553 | -2.3071 | -59.6558 | -58.0536 | 34.4971 | 34.4879 | 11.7966 | 36.795 | 14.1037 | 34.9503 | 9.0775 | -3.8315 | 34.4971 | 34.4925 | 34.4971 | -0.45776 | -0.45319 | 36.8042 | 36.8042 | -0.45319 | 53.7689 | 35.202 | 66.6779 | 32.8949 | 101.6281 | -94.8578 | -57.6004 | 34.4971 | 88.7192 | 34.4879 | 39.2075
1467.5625 | 93.924 | -32.8033 | 61.1526 | -0.25604 | 0.024274 | 0.11291 | 0.065826 | 0.035019 | 0.055399 | 0.050103 | -0.28567 | 0.013994 | 0.011307 | 0.041915 | 0.26529 | 0.01735 | 0.034917 | 0.091553 | 0.09613 | -24.3805 | 0.10071 | 0.091553 | -26.033 | 0.086975 | 0.10071 | 59.0149 | 1.7532 | 62.9745 | 0.84228 | 0.054932 | 0.082397 | 8.4229 | -61.0565 | -61.0519 | 32.8949 | 32.8903 | 6.7703 | 24.4675 | -1.6525 | 34.5566 | -2.1378 | 1.8219 | 33.6456 | 32.8857 | 32.8583 | -1.6708 | -1.6983 | 24.472 | 24.4812 | -0.91095 | 61.2213 | 24.4766 | 57.2617 | 32.8995 | 91.8182 | -85.5331 | -59.3994 | 32.9041 | 95.7779 | 32.8949 | 32.9041
1468.4844 | 94.1757 | -31.2332 | 56.1768 | -0.2713 | 0.023847 | 0.11249 | 0.065826 | 0.035019 | 0.055185 | 0.049889 | -0.28567 | 0.014849 | 0.013657 | 0.042129 | 0.264 | 0.015855 | 0.033421 | 0.09613 | 0.10071 | -16.777 | 0.10071 | 0.086975 | -21.6797 | 0.082397 | 0.091553 | 53.4897 | 5.0537 | 57.3807 | 0.10529 | 0.091553 | 0.091553 | 14.4562 | -56.0761 | -56.0761 | 31.3202 | 31.3156 | 9.5535 | 16.8594 | -4.9026 | 36.2869 | -2.6871 | 1.2039 | 31.3385 | 31.3248 | 31.3248 | -4.9622 | -4.9622 | 16.864 | 16.8777 | -4.9484 | 52.327 | 16.8777 | 48.436 | 31.3339 | 84.7229 | -72.9538 | -51.123 | 31.3339 | 88.6139 | 31.3293 | 31.3248
1469.4844 | 96.0159 | -37.8937 | 66.3986 | -0.25604 | 0.023847 | 0.11313 | 0.065826 | 0.034806 | -0.012747 | 0.049889 | -0.28873 | 0.015062 | -0.002792 | 0.039352 | 0.20825 | 0.016923 | 0.033635 | -2.6093 | -1.474 | -41.2354 | 0.09613 | 0.091553 | -26.5778 | 0.086975 | 1.8723 | 70.6604 | 0.83313 | 62.0728 | 1.0803 | 0.10986 | 0.082397 | -3.3417 | -67.8726 | -66.3025 | 37.9852 | 37.9807 | 11.3159 | 41.3223 | 14.6576 | 38.7268 | 4.2618 | -4.3259 | 38.974 | 37.9761 | 38.0035 | -0.75073 | -0.72327 | 41.3269 | 41.3315 | 0.24719 | 61.2396 | 39.7614 | 69.8273 | 36.4197 | 108.5541 | -107.634 | -65.5655 | 37.9898 | 99.9664 | 35.2844 | 39.7659
1470.5469 | 122.7859 | -43.9362 | 77.8931 | -0.1416 | 0.0022709 | 0.043058 | 0.0025933 | 0.00041234 | -0.0012112 | -0.0022345 | 0.05307 | 0.0011771 | 0.0025484 | 0.03572 | -0.0019568 | -0.0029438 | 0.0011643 | -11.586 | -1.03 | -44.0918 | -1.3824 | -1.2909 | -44.3024 | -1.3962 | 1.8539 | 78.1906 | 1.0574 | 78.479 | 1.2085 | 1.0345 | 1.0895 | -0.15564 | -78.923 | -79.2755 | 42.6453 | 42.54 | -0.36621 | 42.6956 | -0.21057 | 44.9936 | 0.29755 | 0.58594 | 45.1447 | 45.0256 | 44.9707 | 0.032044 | -0.022888 | 42.8009 | 42.7094 | 0.15106 | 77.4216 | 43.0618 | 77.1332 | 42.9062 | 122.1268 | -121.9849 | -76.8356 | 42.5537 | 122.4152 | 32.3502 | 45.7901
1471.4844 | 103.4088 | -44.5999 | 78.0991 | -0.25604 | 0.024274 | 0.034727 | -0.0085151 | 0.036942 | -0.0093288 | -0.0090703 | -0.29788 | -0.010572 | -0.014114 | 0.029738 | -0.018833 | -0.016188 | -0.015285 | -12.0621 | -1.1032 | -44.2474 | -1.7761 | -1.561 | -30.455 | 0.091553 | 2.4628 | 77.9343 | 0.86975 | 72.5098 | 0.80566 | 0.82398 | 0.036621 | 0.35248 | -79.2023 | -79.8752 | 43.0389 | 44.6915 | 14.1449 | 44.339 | 13.7924 | 45.4697 | -0.16479 | -5.5893 | 45.4056 | 44.6365 | 45.4239 | -0.83313 | -0.045776 | 42.6865 | 42.4713 | -0.064087 | 71.64 | 43.1442 | 77.0645 | 43.4967 | 122.5342 | -122.3465 | -77.2293 | 42.8238 | 117.1097 | 32.5378 | 47.0627
1472.5 | 98.822 | -39.8026 | 72.0108 | -0.50781 | -0.0013607 | 0.038785 | -0.00082468 | -0.0042875 | 0.0019932 | -0.0013799 | -0.3284 | -0.012922 | -0.005142 | 0.04042 | -0.0070838 | -0.01213 | -0.0088761 | -12.0483 | -1.1261 | -44.252 | -1.6388 | -1.767 | -39.2395 | -1.5564 | 2.5681 | 78.1906 | 0.97961 | 71.3379 | 1.0986 | 1.0345 | 0.10529 | -4.4495 | -73.1369 | -73.6496 | 38.0356 | 38.2462 | 0.56305 | 42.6956 | 5.0125 | 40.7822 | 6.1798 | -0.67291 | 40.9012 | 39.9078 | 40.8371 | -0.87433 | 0.054932 | 42.485 | 42.6132 | 0.11902 | 70.3583 | 43.1259 | 77.211 | 38.6765 | 117.9932 | -116.2628 | -71.0312 | 38.1638 | 111.1404 | 27.7542 | 42.3706
1473.4844 | 94.249 | -33.2153 | 78.566 | -0.2713 | 0.02406 | 0.035367 | -0.012574 | 0.033524 | -0.011252 | -0.0075751 | -0.28567 | 0.014635 | 0.01323 | 0.03807 | 0.264 | 0.015855 | 0.033421 | -11.8698 | -1.0254 | -44.1513 | -1.561 | -1.6479 | -31.0547 | 0.091553 | 1.9684 | 78.3005 | 0.95673 | 52.8671 | 1.149 | 0.09613 | 0.091553 | -10.936 | -79.5914 | -80.127 | 31.5674 | 33.3069 | 2.1606 | 44.2429 | 13.0966 | 34.1721 | -0.2655 | -25.6989 | 34.3643 | 33.3069 | 33.3115 | -0.86517 | -0.8606 | 42.5034 | 42.5903 | 0.19226 | 51.9104 | 43.1259 | 77.3438 | 32.1899 | 111.5158 | -122.7173 | -77.6093 | 31.6544 | 86.0825 | 21.3455 | 35.1837
1474.5469 | 123.1155 | -44.4901 | 78.6118 | -0.088196 | 0.0024845 | 0.043058 | 0.0021661 | -0.0025785 | 0.0011386 | -0.0011663 | 0.065277 | 0.0026725 | 0.0019076 | 0.036361 | -0.001316 | -0.0020892 | -0.00075834 | -12.1536 | -1.1627 | -44.7235 | -1.5198 | -1.3687 | -44.7647 | -1.387 | 1.918 | 78.7308 | 0.80566 | 78.6896 | 1.149 | 1.0483 | 1.1353 | -0.23346 | -79.7745 | -80.1315 | 43.1213 | 43.103 | -0.27466 | 43.3365 | -0.041198 | 45.2957 | 0.11902 | 0.07782 | 45.639 | 45.6253 | 45.5383 | 0.32959 | 0.24261 | 43.3548 | 43.2037 | 0.34332 | 77.8839 | 43.5608 | 77.9251 | 43.3273 | 123.2208 | -123.3353 | -77.8061 | 42.9703 | 123.1796 | 32.3364 | 46.4081
1475.4844 | 95.9473 | -35.9116 | 78.6758 | -0.25604 | 0.023847 | 0.038358 | 0.00067072 | 0.034806 | -0.012533 | 0.049889 | -0.28567 | 0.014635 | -0.0023648 | 0.028243 | 0.055081 | 0.015641 | -0.0052445 | -12.149 | -1.2085 | -44.4214 | -1.6296 | -1.7258 | -38.53 | 0.24719 | 1.8585 | 78.511 | 0.96588 | 70.5917 | 1.0483 | 1.0803 | 0.09613 | -8.5098 | -79.8843 | -80.3055 | 34.1858 | 36.1588 | -2.6184 | 44.6686 | 5.8914 | 36.8774 | -0.16479 | -8.0841 | 36.9598 | 36.0077 | 36.9919 | -0.86975 | 0.11444 | 42.6956 | 42.7917 | 0.082398 | 69.6259 | 43.2129 | 77.5452 | 34.7031 | 114.4226 | -123.0972 | -77.71 | 34.2819 | 106.5033 | 23.7625 | 37.7701
1476.4844 | 93.9514 | -30.6427 | 52.7618 | -0.24841 | 0.023633 | 0.11313 | 0.065399 | 0.035019 | -0.010824 | 0.049889 | -0.28873 | 0.014849 | 0.013443 | 0.042556 | 0.26358 | 0.015855 | 0.033635 | 0.09613 | -1.4099 | -39.1342 | 0.09613 | 0.086975 | -22.673 | 0.091553 | 1.9135 | 65.2771 | 0.8194 | 55.1743 | 0.11444 | 0.091553 | 0.091553 | -8.4915 | -54.1718 | -52.6657 | 30.7297 | 30.7343 | 7.9697 | 39.2258 | 16.4612 | 31.4621 | 12.5153 | 2.4124 | 30.7571 | 30.7343 | 30.7343 | -0.72784 | -0.72784 | 39.2212 | 39.2303 | -0.70496 | 54.3549 | 37.7243 | 64.4577 | 29.2328 | 95.9198 | -91.8961 | -51.9424 | 30.7388 | 85.817 | 30.7388 | 32.5562
1477.5469 | 123.3902 | -120.8633 | 2.3529 | -0.011902 | 0.0031253 | 0.12402 | 0.0025933 | -0.0027921 | 0.0028476 | -0.0026617 | -0.020172 | 0.14388 | 0.00083965 | -0.0055094 | -0.0025976 | -0.0063618 | -0.00033114 | -32.3639 | -2.2934 | -121.1655 | -2.6276 | -2.4261 | -120.7718 | -2.4811 | 1.0437 | 2.536 | 1.9958 | 2.1378 | 2.1744 | 2.0966 | 2.1423 | -0.30212 | -4.6463 | -4.9805 | 118.4372 | 118.3823 | 0.091552 | 118.6844 | 0.39368 | 122.8592 | 0.18311 | -0.21515 | 123.0377 | 123.0057 | 122.9599 | 0.14648 | 0.10071 | 118.7393 | 118.5379 | 0.17853 | 0.14191 | 118.8721 | 0.54016 | 118.5699 | 123.3994 | -123.5184 | -0.35705 | 118.2358 | 123.0011 | 88.4994 | 121.907
1478.4844 | 123.3353 | -120.6848 | 2.5131 | -0.050049 | 0.0024845 | 0.12295 | 0.0038751 | -0.0012967 | 0.00071138 | -0.0020209 | -0.056793 | 0.14516 | 0.0074618 | -0.006791 | -0.0019568 | -0.0046528 | 0.0062913 | -31.2653 | -2.1881 | -120.7809 | -2.6413 | -2.4857 | -120.5841 | -2.4994 | 1.0391 | 2.6917 | 2.1469 | 2.1423 | 2.1332 | 1.9821 | 2.1469 | -0.096131 | -4.7012 | -5.1544 | 118.1992 | 118.1854 | 0.10071 | 118.2816 | 0.19684 | 122.8317 | 0.17853 | -0.37079 | 122.818 | 122.8317 | 122.6669 | 0 | -0.1648 | 118.2953 | 118.1396 | -0.013733 | -0.004578 | 118.5928 | 0.54474 | 118.4967 | 123.3765 | -123.2941 | -0.36621 | 118.0435 | 122.8271 | 89.4196 | 121.7239
1479.5469 | 123.2895 | -120.7535 | 2.5497 | -0.2713 | 0.023633 | 0.12253 | 0.0034479 | -0.0017239 | -0.0084744 | -0.0077887 | -0.2399 | 0.12978 | -0.0074918 | -0.012986 | -0.0077246 | -0.014693 | -0.0058853 | -31.1508 | -2.2247 | -121.225 | -2.6779 | -2.5497 | -120.6573 | -2.5864 | 0.9613 | 2.4628 | 1.8814 | 2.3621 | 2.4033 | 2.0508 | 2.0462 | -0.4715 | -4.7745 | -5.2277 | 118.2037 | 118.1671 | 0.09613 | 118.6386 | 0.56763 | 122.6349 | -0.086975 | -0.18768 | 123.1567 | 122.7997 | 122.8043 | 0.16479 | 0.16937 | 118.6752 | 118.5471 | 0.52185 | 0.48065 | 119.0002 | 0.58136 | 118.5287 | 123.2162 | -123.7747 | -0.66833 | 118.0756 | 123.1155 | 89.6027 | 121.7148
1480.4844 | 123.3261 | -120.5383 | 2.6047 | -0.43152 | -0.011401 | 0.11035 | 0.0034479 | -0.0062101 | 0.00092498 | -0.0026617 | -0.1636 | 0.13576 | -0.0066374 | -0.0059366 | -0.0081518 | -0.015975 | -0.0084487 | -30.7251 | -2.2064 | -120.639 | -2.6138 | -2.4536 | -120.0073 | -2.5085 | 1.0849 | 2.8702 | 2.3346 | 2.3483 | 2.3209 | 2.1194 | 2.2522 | -0.10071 | -4.8111 | -5.2185 | 118.0847 | 118.0298 | 0.53101 | 118.1305 | 0.63171 | 122.8729 | 0.2655 | -0.25635 | 122.8592 | 122.7905 | 122.6578 | -0.082398 | -0.21515 | 118.1854 | 118.0252 | -0.013733 | 0.013733 | 118.4326 | 0.53558 | 118.3319 | 123.4085 | -123.2437 | -0.27008 | 117.9245 | 122.8867 | 89.8132 | 121.6232
1481.4844 | 116.5146 | -44.0002 | 78.2227 | -0.2713 | -0.010119 | 0.03729 | -0.0023199 | -0.0057829 | 0.0019932 | -0.0037299 | -0.15445 | 0.0016043 | 0.0031894 | 0.043624 | 0.0008204 | -0.0046528 | -0.0011855 | -11.2976 | -0.82398 | -44.838 | -1.2314 | -1.0849 | -44.6182 | -1.1078 | 4.921 | 77.9205 | 0.58136 | 78.2867 | 0.72327 | 0.44861 | 0.48523 | -0.83771 | -79.0466 | -79.454 | 42.9153 | 42.8925 | -0.61798 | 43.7302 | 0.21973 | 44.5816 | -0.30212 | 0.064087 | 44.7235 | 44.4855 | 44.4489 | -0.096131 | -0.13275 | 43.7531 | 43.6066 | 0.14191 | 77.7054 | 44.014 | 77.3392 | 43.1763 | 121.9208 | -123.0606 | -77.6413 | 42.7689 | 122.287 | 32.7026 | 48.9212
1482.5469 | 107.6477 | -44.4534 | 73.439 | -0.43915 | 0.0022709 | 0.042417 | 0.0030207 | -0.00086946 | 0.0017794 | 0.0011835 | -0.026276 | 0.0048087 | 0.0057528 | 0.04106 | -0.0002478 | -0.001662 | 0.0030869 | -11.1282 | -0.81024 | -44.0094 | -1.2817 | -1.1307 | -44.339 | -1.1444 | 2.2202 | 78.241 | 0.60883 | 78.1494 | 0.74158 | 0.43945 | 0.44403 | 0.44403 | -74.2493 | -74.7208 | 43.3228 | 43.309 | 0.11444 | 42.865 | -0.32959 | 45.0623 | 4.8019 | 4.7104 | 45.195 | 44.8975 | 44.8929 | -0.16479 | -0.16937 | 42.8787 | 42.7277 | 0.13275 | 77.5406 | 43.1992 | 77.6321 | 43.6432 | 122.6944 | -117.4484 | -72.8302 | 43.1717 | 122.6028 | 33.3252 | 46.6736
1483.4844 | 94.3634 | -32.9819 | 58.6395 | -0.25604 | 0.02406 | 0.11291 | 0.065826 | 0.034592 | -0.0033474 | 0.050103 | -0.28873 | 0.014422 | 0.013443 | 0.042342 | 0.26336 | 0.016069 | 0.033635 | -6.0837 | -1.2634 | -37.7106 | -1.474 | -1.4191 | -33.8242 | -1.7166 | 2.2842 | 77.4765 | 0.66376 | 52.3041 | 0.082397 | 0.091553 | 0.09613 | -4.7287 | -59.903 | -60.1135 | 31.5628 | 31.2653 | -0.84228 | 35.994 | 3.8864 | 33.6456 | 18.837 | -6.3354 | 33.0643 | 33.078 | 33.0734 | -0.56763 | -0.5722 | 36.2915 | 36.2366 | -0.58136 | 51.6403 | 36.4471 | 76.8127 | 31.7184 | 110.4584 | -96.3501 | -57.9758 | 31.5079 | 85.2859 | 26.8982 | 35.2661
1484.5469 | 123.5138 | -120.7352 | 2.449 | -0.0042723 | 0.0041935 | 0.12445 | 0.0038751 | 0.0010531 | 0.0056248 | -9.8328e-05 | -0.0049134 | 0.14195 | 0.0038302 | -0.0012368 | -0.0019568 | -0.0042254 | 0.0022323 | -31.7047 | -2.179 | -120.9641 | -2.4857 | -2.3117 | -120.2179 | -2.33 | 1.4008 | 2.9434 | 2.2797 | 2.774 | 2.3666 | 2.0691 | 2.2247 | -0.22888 | -4.628 | -4.9347 | 118.4235 | 118.4052 | 0.51727 | 118.634 | 0.74615 | 123.0148 | 0.49438 | 0.32501 | 123.1018 | 122.9599 | 122.8043 | -0.054932 | -0.21057 | 118.6523 | 118.4784 | 0.086975 | 0.49438 | 118.7851 | 0.66376 | 118.5562 | 123.6786 | -123.4131 | -0.16937 | 118.2495 | 123.5092 | 89.0305 | 122.1359
1485.4844 | 123.3902 | -120.9686 | 2.2568 | 0.010986 | -0.0020017 | 0.11761 | -0.0061651 | 0.034378 | -0.0054836 | 0.049889 | -0.28567 | 0.015062 | -0.0021512 | -0.0089272 | 0.26315 | 0.015641 | 0.033208 | -31.7963 | -2.1744 | -121.3303 | -2.6367 | -2.7191 | -98.3734 | -3.0487 | 0.93842 | 2.3712 | 1.8036 | 2.0416 | 1.7349 | 1.918 | 0.11444 | -0.36163 | -4.4312 | -4.8935 | 118.2495 | 117.9199 | 22.5952 | 118.2816 | 22.9568 | 122.7722 | 0.11444 | -0.21515 | 122.7036 | 121.0831 | 122.8867 | -1.6891 | 0.11444 | 118.6111 | 118.6935 | -0.068665 | 0.23804 | 119.1559 | 0.56763 | 118.7943 | 123.3398 | -123.587 | -0.45319 | 118.3319 | 123.0103 | 89.1724 | 121.907
1486.5469 | 123.3627 | -120.8267 | 2.4078 | -0.0042723 | 0.0026981 | 0.12466 | 0.0053705 | 0.0010531 | 0.00071138 | -0.0037299 | 0.0072936 | 0.14281 | 0.0038302 | -0.0014504 | -0.0015296 | -0.003371 | 0.0030869 | -32.6477 | -2.298 | -121.0327 | -2.6459 | -2.4857 | -120.0897 | -2.5452 | 1.0574 | 2.5131 | 1.9684 | 2.1378 | 2.1973 | 2.124 | 2.1652 | -0.20599 | -4.7058 | -5.0537 | 118.3411 | 118.2816 | 0.737 | 118.4875 | 0.94299 | 122.7951 | 0.10529 | -0.27008 | 123.024 | 122.9919 | 122.9507 | 0.19684 | 0.15564 | 118.5471 | 118.3868 | 0.22888 | 0.16937 | 118.7347 | 0.54474 | 118.5287 | 123.3398 | -123.4406 | -0.43945 | 118.1808 | 122.9645 | 88.179 | 121.8842
1487.5 | 123.3902 | -121.0144 | 2.2202 | -0.057678 | 0.0035525 | 0.12509 | 0.0034479 | 0.0027621 | 0.0041294 | -0.00073913 | -0.011017 | 0.14217 | 0.0025484 | 0.0021812 | -0.0011022 | -0.0027302 | 0.0030869 | -32.9224 | -2.2842 | -121.3623 | -2.6459 | -2.4857 | -121.1655 | -2.5314 | 0.99335 | 2.2156 | 1.7258 | 2.0142 | 2.0233 | 1.9913 | 2.1194 | -0.3479 | -4.5044 | -4.866 | 118.5287 | 118.483 | -0.15106 | 118.8309 | 0.19684 | 122.7402 | -0.004578 | -0.20599 | 123.0377 | 123.1338 | 123.0057 | 0.39368 | 0.2655 | 118.8766 | 118.7164 | 0.29755 | 0.28839 | 119.0781 | 0.48981 | 118.7302 | 123.23 | -123.5825 | -0.49438 | 118.3685 | 123.0286 | 88.092 | 122.0078
1488.5469 | 123.4222 | -120.9 | 2.2797 | -0.019531 | 0.0014163 | 0.12402 | 0.0028069 | 0.00041234 | 0.0013522 | 0.0011835 | 0.010345 | 0.1443 | 0.004471 | -0.0042276 | -0.003025 | -0.0031574 | -0.00097194 | -33.2199 | -2.2568 | -121.1563 | -2.5681 | -2.3941 | -120.5063 | -2.4445 | 1.1398 | 2.417 | 1.9501 | 2.1606 | 2.2064 | 2.1194 | 2.1973 | -0.25635 | -4.5364 | -4.8477 | 118.5059 | 118.4555 | 0.39368 | 118.7119 | 0.65002 | 122.85 | 0.13733 | -0.11902 | 123.1064 | 123.0972 | 123.0194 | 0.24719 | 0.16937 | 118.7622 | 118.5883 | 0.25635 | 0.21057 | 118.8995 | 0.46692 | 118.6432 | 123.317 | -123.436 | -0.32959 | 118.3319 | 123.0606 | 87.6801 | 122.0398
1489.4844 | 123.2666 | -121.1288 | 2.1881 | -0.55359 | -0.011401 | 0.11548 | 0.0032343 | -0.010055 | -0.00527 | -0.0082159 | -0.053741 | 0.0084403 | -0.0055692 | -0.0035868 | -0.0066564 | -0.018111 | -0.0058853 | -32.7896 | -2.298 | -121.463 | -2.7512 | -2.6321 | -121.0144 | -2.742 | 0.78735 | 2.1927 | 1.6159 | 1.8951 | 1.8906 | 1.7715 | 1.767 | -0.33417 | -4.4861 | -4.9393 | 118.4967 | 118.3868 | 0.11444 | 118.721 | 0.44861 | 122.7448 | 0.004578 | -0.29297 | 123.0194 | 122.8958 | 122.9004 | 0.15106 | 0.15564 | 118.8309 | 118.7119 | 0.27466 | 0.27924 | 119.165 | 0.57678 | 118.8309 | 123.3215 | -123.6511 | -0.5722 | 118.3777 | 123.024 | 88.3392 | 121.9162
1490.4844 | 123.3124 | -121.1929 | 2.0004 | 0.018616 | 0.0033389 | 0.12359 | 0.0028069 | 0.0040439 | 0.0013522 | -0.0022345 | -0.12698 | 0.14537 | 0.0055392 | -0.005723 | -0.001316 | -0.0023028 | 0.0028733 | -32.3868 | -1.5839 | -121.5591 | -2.0508 | -1.8768 | -121.2204 | -1.8997 | 0.75989 | 2.0416 | 1.4969 | 1.6525 | 1.7258 | 1.6754 | 1.799 | -0.36621 | -3.5843 | -4.0512 | 119.3161 | 119.2932 | -0.027466 | 119.6594 | 0.33875 | 122.6898 | 0.041199 | -0.3479 | 122.9187 | 122.9919 | 122.8683 | 0.30212 | 0.17853 | 119.6823 | 119.5084 | 0.22888 | 0.15564 | 119.9753 | 0.54474 | 119.6091 | 123.2346 | -123.5596 | -0.50354 | 119.1422 | 122.8455 | 88.8062 | 121.9528
1491.5469 | 123.4543 | -121.0007 | 2.179 | -0.072937 | 0.0048343 | 0.12402 | 0.0032343 | -0.0012967 | 0.0024204 | -0.0011663 | -0.075104 | 0.14452 | 0.0042574 | -0.0087136 | -0.0019568 | -0.0029438 | 0.00030966 | -32.2769 | -1.886 | -121.4401 | -2.1698 | -1.973 | -120.9229 | -2.0416 | 1.1078 | 2.1515 | 1.6937 | 2.037 | 2.1103 | 2.0462 | 2.0782 | -0.43945 | -4.0649 | -4.3488 | 119.0277 | 118.959 | 0.077819 | 119.3985 | 0.51727 | 122.6944 | -0.027466 | -0.14191 | 123.111 | 123.0789 | 123.0469 | 0.38452 | 0.35248 | 119.4672 | 119.2703 | 0.41657 | 0.34332 | 119.5541 | 0.45776 | 119.1147 | 123.1522 | -123.6191 | -0.48523 | 118.8309 | 123.0377 | 88.7238 | 122.1085
1492.5 | 123.3215 | -43.8354 | 78.5751 | -0.56885 | -0.011401 | 0.042631 | 0.0028069 | 0.0057529 | -0.00099762 | -0.00052553 | -0.14835 | 0.0048087 | 0.004471 | 0.043197 | -0.0021704 | -0.00080758 | -0.0043899 | -11.7371 | -0.89264 | -44.9066 | -1.3458 | -1.2177 | -44.9524 | -1.2131 | 3.6484 | 78.6026 | 0.35248 | 78.5568 | 0.62714 | 0.49439 | 0.65002 | -1.0712 | -79.4678 | -79.921 | 42.6178 | 42.6224 | -1.1169 | 43.6935 | -0.045777 | 44.1879 | 0.027466 | -0.01831 | 44.4626 | 44.4855 | 44.3298 | 0.29755 | 0.14191 | 43.689 | 43.5608 | 0.27466 | 78.2043 | 44.014 | 78.2501 | 42.9428 | 122.438 | -123.4818 | -78.2227 | 42.4896 | 122.3923 | 32.0984 | 47.4838
1493.5625 | 123.0698 | -44.371 | 78.6804 | -0.072937 | 0.0050479 | 0.045408 | 0.0019525 | 0.00062594 | 0.0032748 | -0.0022345 | -0.084259 | 0.0028861 | 0.0057528 | 0.042129 | -0.0015296 | -0.0018756 | 0.0033005 | -11.5952 | -0.62256 | -44.6503 | -0.9201 | -0.75989 | -44.458 | -0.79651 | 2.4948 | 78.7766 | 0.37994 | 78.7949 | 0.75531 | 0.65002 | 0.73242 | -0.27924 | -79.303 | -79.6005 | 43.6111 | 43.5745 | -0.086975 | 43.8538 | 0.19226 | 44.751 | 0.09613 | 0.11444 | 45.1263 | 45.1035 | 45.0211 | 0.35248 | 0.27008 | 43.8904 | 43.7302 | 0.37537 | 78.4149 | 44.0277 | 78.3966 | 43.7485 | 123.1476 | -123.3307 | -78.3005 | 43.4509 | 123.1659 | 32.7759 | 46.8658
1494.4844 | 108.8196 | -39.2944 | 78.3875 | -0.12634 | -0.0049923 | 0.035367 | 0.0028069 | -0.00065586 | -0.00035682 | -0.0041571 | -0.12393 | 0.0035269 | -0.001724 | 0.03337 | -0.0068702 | -0.018752 | -0.0013991 | -11.7096 | -0.67749 | -44.6503 | -1.062 | -0.9201 | -44.6457 | -0.97046 | 2.4902 | 78.8635 | 0.45319 | 78.7308 | 0.74616 | 0.6134 | 0.72327 | -5.3558 | -79.0649 | -79.4495 | 38.3743 | 38.324 | -5.3513 | 43.6798 | 0.004578 | 39.7476 | 0.47607 | 0.34332 | 40.0406 | 40.0177 | 39.9078 | 0.27008 | 0.16022 | 43.7302 | 43.5883 | 0.29297 | 78.2776 | 43.9728 | 78.4103 | 38.6169 | 118.158 | -123.0377 | -77.9343 | 38.2324 | 118.0252 | 27.5848 | 41.7847
1495.4844 | 116.9861 | -44.3619 | 78.3051 | -0.13397 | -0.0034969 | 0.035367 | 0.0038751 | -1.486e-05 | 7.0582e-05 | 0.00096987 | -0.12393 | 0.0043815 | 0.0023348 | 0.04106 | -0.0015296 | -0.011061 | 0.0024461 | -11.7508 | -0.55847 | -44.6136 | -0.97961 | -0.81482 | -44.6594 | -0.86517 | 1.918 | 78.9185 | 0.44861 | 78.5477 | 0.75073 | 0.61798 | 0.72784 | -0.25177 | -78.8635 | -79.2847 | 43.5471 | 43.4967 | -0.29755 | 43.7485 | -0.045777 | 44.8105 | 0.6134 | 0.24261 | 45.1126 | 45.0897 | 44.9799 | 0.27924 | 0.16937 | 43.7988 | 43.634 | 0.30212 | 78.0991 | 44.0552 | 78.4698 | 43.8034 | 123.2803 | -122.9187 | -77.8564 | 43.3823 | 122.9095 | 32.6111 | 46.2799
1496.5469 | 123.5229 | -120.9045 | 2.1606 | -0.042419 | -0.00050633 | 0.12915 | 0.00088432 | -0.0012967 | 0.00071138 | -0.0041571 | 0.0011902 | 0.14516 | 0.0053256 | -0.0031594 | -0.0017432 | -0.0027302 | 0.00073706 | -34.0759 | -1.5701 | -121.2936 | -1.8494 | -1.6525 | -120.7352 | -1.7258 | 0.98419 | 2.2385 | 1.7441 | 2.037 | 2.1149 | 2.0233 | 2.0828 | -0.3891 | -3.7308 | -4.01 | 119.252 | 119.1788 | 0.16937 | 119.5679 | 0.55847 | 122.6486 | 0.077819 | -0.1236 | 123.0194 | 122.9874 | 122.9279 | 0.33875 | 0.27924 | 119.6411 | 119.4443 | 0.37079 | 0.29297 | 119.7235 | 0.49438 | 119.3344 | 123.143 | -123.4543 | -0.41657 | 119.0552 | 122.9416 | 86.8286 | 121.8887
1497.5 | 122.5159 | -44.3298 | 78.8406 | -0.080566 | 0.0024845 | 0.042203 | 0.0021661 | -0.00086946 | -0.00014322 | -0.00073913 | -0.096466 | 0.0060905 | 0.0029758 | 0.036788 | -0.0008886 | -0.00059378 | 9.6064e-05 | -12.1857 | -0.63171 | -44.6457 | -1.0529 | -0.9201 | -44.5908 | -0.93842 | 1.3824 | 78.9413 | 0.55389 | 78.8635 | 0.87433 | 0.72784 | 0.86517 | -0.31586 | -79.4724 | -79.8935 | 43.4097 | 43.3914 | -0.26093 | 43.7073 | 0.054932 | 44.8837 | 0.10071 | 0.022888 | 45.2042 | 45.195 | 45.0577 | 0.31128 | 0.17395 | 43.7256 | 43.5928 | 0.32044 | 78.3096 | 44.014 | 78.3875 | 43.6981 | 123.2712 | -123.4863 | -78.2867 | 43.277 | 123.1934 | 32.1442 | 45.7123
1498.5625 | 122.8088 | -44.3344 | 78.8315 | -0.080566 | 0.0039799 | 0.046262 | 0.0036615 | 0.0016939 | 0.0041294 | -0.0013799 | -0.10257 | 0.0037405 | 0.0048984 | 0.047042 | -0.004093 | 0.00026062 | 9.6064e-05 | -11.998 | -0.78735 | -44.577 | -1.2177 | -1.1032 | -44.6411 | -1.1169 | 1.2543 | 78.9459 | 0.61798 | 78.8406 | 0.94757 | 0.77362 | 0.93842 | -0.24261 | -79.6188 | -80.0491 | 43.2312 | 43.2175 | -0.3067 | 43.4601 | -0.064087 | 44.9524 | 0.11444 | 0.009155 | 45.282 | 45.2728 | 45.108 | 0.32044 | 0.15564 | 43.4738 | 43.3594 | 0.32959 | 78.2227 | 43.7897 | 78.3279 | 43.5471 | 123.2803 | -123.4085 | -78.2135 | 43.1168 | 123.175 | 32.3364 | 45.5887
1499.4844 | 122.6257 | -44.3573 | 78.804 | -0.057678 | 0.00098907 | 0.042417 | 0.0019525 | 0.0016939 | 7.0582e-05 | -0.0024481 | -0.041534 | 0.0054495 | 0.0029758 | 0.042983 | -0.0017432 | -0.00038018 | 0.0026597 | -12.0255 | -0.69122 | -44.6091 | -1.149 | -0.99335 | -44.632 | -1.0071 | 2.1423 | 78.9597 | 0.6134 | 78.6896 | 0.91553 | 0.79651 | 0.88806 | -0.25177 | -79.4952 | -79.953 | 43.364 | 43.3502 | -0.27466 | 43.602 | -0.022888 | 44.9707 | 0.15564 | -0.11444 | 45.2728 | 45.2454 | 45.1538 | 0.27466 | 0.18311 | 43.6157 | 43.4601 | 0.30212 | 78.0762 | 43.9178 | 78.3463 | 43.6661 | 123.317 | -123.4131 | -78.1906 | 43.2083 | 123.0469 | 32.3318 | 46.4996
1500.5 | 123.317 | -44.2291 | 78.891 | -0.03479 | 0.0044071 | 0.044981 | 0.0040887 | -0.0021513 | 0.0017794 | -0.0020209 | -0.056793 | 0.0050223 | 0.0053256 | 0.043624 | -0.002384 | -0.0012348 | 0.0013779 | -11.8927 | -0.64087 | -44.7327 | -0.96588 | -0.81482 | -44.4122 | -0.86975 | 1.7303 | 78.9871 | 0.71411 | 79.0009 | 1.0941 | 0.98877 | 1.0757 | -0.50354 | -79.5319 | -79.8569 | 43.4143 | 43.3594 | -0.1831 | 43.8629 | 0.32044 | 44.9432 | 0.096131 | 0.10986 | 45.3232 | 45.3049 | 45.2179 | 0.36163 | 0.27466 | 43.9178 | 43.7668 | 0.37994 | 78.2867 | 44.0918 | 78.273 | 43.5883 | 123.2162 | -123.6237 | -78.1769 | 43.2632 | 123.23 | 32.3364 | 45.9595
1501.5625 | 122.7173 | -44.1605 | 78.9688 | -0.011902 | 0.0067569 | 0.043699 | 0.0013117 | 0.0046847 | 0.0013522 | -0.0022345 | -0.047638 | 0.0045951 | 0.0048984 | 0.046187 | -0.004093 | -0.0023028 | 0.0020187 | -12.3367 | -0.58594 | -44.4992 | -1.0071 | -0.88348 | -45.1035 | -0.91553 | 1.5656 | 79.0741 | 0.74616 | 78.7308 | 1.0941 | 0.98419 | 1.0803 | -0.33875 | -79.5547 | -79.9759 | 43.277 | 43.2449 | -0.94299 | 43.5837 | -0.60425 | 44.9066 | 0.10529 | -0.23804 | 45.2545 | 45.2408 | 45.1447 | 0.33417 | 0.23804 | 43.6157 | 43.4921 | 0.3479 | 77.9846 | 43.9133 | 78.3279 | 43.5745 | 123.2346 | -123.468 | -78.2227 | 43.1534 | 122.8912 | 31.8237 | 45.726
1502.4844 | 107.6706 | -44.4305 | 70.5917 | -0.64514 | 0.0018435 | 0.041776 | 0.00024352 | -0.0023649 | -0.00057042 | -0.0020209 | -0.035431 | 0.0037405 | 0.004471 | 0.040847 | 0.0029566 | -0.003371 | 0.0026597 | -11.4899 | -0.56763 | -43.7439 | -1.0345 | -0.87891 | -44.5129 | -0.89264 | 2.0279 | 78.3325 | 0.75989 | 78.1128 | 0.70496 | 0.54474 | 0.63629 | 0.68665 | -71.1594 | -71.6263 | 43.5516 | 43.5379 | -0.082397 | 42.8513 | -0.76904 | 45.1904 | 7.7408 | 7.5211 | 45.1355 | 45.0668 | 44.9753 | -0.1236 | -0.21515 | 42.865 | 42.7094 | -0.054932 | 77.3529 | 43.1763 | 77.5726 | 43.8629 | 122.7631 | -114.3356 | -69.8318 | 43.396 | 122.5433 | 32.9407 | 46.4584
1503.4844 | 113.8184 | -43.9911 | 78.4515 | -0.26367 | -0.0030697 | 0.036863 | -0.011506 | -0.010696 | -0.0012112 | -0.010566 | -0.090363 | 0.00074988 | 0.0019076 | 0.040847 | -0.0038794 | -0.0042254 | -0.00054474 | -11.7279 | -0.66834 | -43.8492 | -1.0895 | -0.96588 | -44.545 | -0.97961 | 1.5839 | 78.3829 | 0.88348 | 78.2227 | 0.85602 | 0.68665 | 0.78735 | 0.14191 | -79.1199 | -79.541 | 43.0252 | 43.0115 | -0.55389 | 42.8696 | -0.6958 | 44.8746 | -0.068664 | -0.22888 | 44.8471 | 44.7784 | 44.6777 | -0.09613 | -0.19684 | 42.8833 | 42.7597 | -0.027466 | 77.3392 | 43.1808 | 77.4994 | 43.3228 | 122.374 | -122.3007 | -77.5681 | 42.9016 | 122.2137 | 32.2632 | 45.575
1504.5469 | 122.6624 | -43.9453 | 78.2181 | -0.057678 | 0.00077547 | 0.041563 | 0.0019525 | -0.0038603 | 0.00049778 | 0.0020379 | 0.031708 | 0.0028861 | 0.003403 | 0.044906 | -0.0028112 | -0.0035846 | 0.00052346 | -11.618 | -0.83313 | -44.3024 | -1.1444 | -0.97046 | -44.3985 | -1.0254 | 1.4374 | 78.9825 | 1.0712 | 79.0054 | 1.4603 | 1.355 | 1.4053 | -0.35706 | -79.0512 | -79.3625 | 42.9749 | 42.9199 | -0.45319 | 43.277 | -0.096131 | 45.0165 | 0.76447 | 0.78735 | 45.4056 | 45.3506 | 45.3003 | 0.33417 | 0.28381 | 43.3319 | 43.158 | 0.3891 | 77.9343 | 43.4692 | 77.9114 | 43.1122 | 122.9279 | -122.5204 | -77.1469 | 42.8009 | 122.9507 | 32.3273 | 45.3827
1505.4844 | 112.2345 | -43.9407 | 78.7308 | -0.36285 | 0.00098907 | 0.043699 | 0.0021661 | -0.0015103 | 7.0582e-05 | -0.0022345 | -0.026276 | 0.0039541 | 0.0042574 | 0.042342 | -0.0002478 | -0.0025164 | 0.0028733 | -11.879 | -0.72784 | -44.1193 | -1.1765 | -1.0391 | -44.426 | -1.0529 | 2.5497 | 78.978 | 1.0025 | 78.3371 | 1.1719 | 1.0254 | 0.9613 | -0.17853 | -79.4586 | -79.9072 | 42.9016 | 42.8879 | -0.48523 | 43.0664 | -0.3067 | 44.9432 | 0.24719 | -0.39368 | 45.1126 | 44.902 | 44.9661 | -0.041198 | 0.022889 | 43.0801 | 42.9428 | 0.16937 | 77.3346 | 43.3914 | 77.9755 | 43.2129 | 122.9187 | -122.85 | -77.7283 | 42.7643 | 122.2778 | 32.0618 | 46.4905
1506.4844 | 123.0652 | -44.0689 | 79.0329 | -0.050049 | 0.0012027 | 0.043485 | 0.0025933 | 0.0014803 | -0.00099762 | 0.0018243 | 0.043915 | 0.0045951 | 0.0036166 | 0.042983 | -0.0034522 | -0.0035846 | -0.00054474 | -11.6592 | -0.71411 | -44.3436 | -0.9613 | -0.78278 | -44.2429 | -0.8606 | 1.0071 | 79.1061 | 1.1353 | 79.1519 | 1.5564 | 1.4511 | 1.5015 | -0.27466 | -79.747 | -79.9942 | 43.2861 | 43.2083 | -0.17395 | 43.483 | 0.10071 | 45.2042 | 0.073242 | 0.11902 | 45.6253 | 45.5704 | 45.52 | 0.36621 | 0.31586 | 43.5608 | 43.3823 | 0.42114 | 78.0167 | 43.6295 | 77.9709 | 43.3548 | 123.175 | -123.3765 | -77.8976 | 43.1076 | 123.2208 | 32.4097 | 45.076
1507.5625 | 101.3718 | -35.5133 | 78.8544 | -0.43915 | -0.0020017 | 0.024686 | 0.070739 | 0.035019 | -0.014242 | 0.049889 | -0.31619 | 0.01549 | 0.013871 | 0.04576 | 0.26529 | 0.015641 | -0.0033219 | -11.7188 | -0.81024 | -44.133 | -1.1948 | -1.0574 | -44.4077 | -1.1078 | 3.3829 | 78.891 | 1.3412 | 74.3958 | 1.5015 | 1.3779 | -0.022888 | -8.6197 | -79.6646 | -80.0491 | 34.4559 | 34.4055 | -8.8943 | 43.0252 | -0.27466 | 36.8546 | 0.036621 | -4.4586 | 37.0148 | 35.4904 | 36.8912 | -1.3641 | 0.036621 | 43.0756 | 42.9382 | 0.16022 | 73.0545 | 43.3228 | 77.5497 | 34.7031 | 114.4043 | -122.9874 | -77.5131 | 34.3185 | 109.9091 | 23.7946 | 38.8962
1508.4844 | 123.1705 | -44.2017 | 78.8269 | 0.026245 | 0.0033389 | 0.044553 | 0.0028069 | 0.0021213 | 0.0015658 | 0.00096987 | 0.025604 | 0.0028861 | 0.003403 | 0.034865 | -0.000675 | -0.0027302 | 0.0022323 | -11.7096 | -0.96588 | -44.4855 | -1.2268 | -1.0529 | -44.4077 | -1.1078 | 2.092 | 78.9871 | 1.2314 | 78.9734 | 1.6296 | 1.5198 | 1.5793 | -0.28381 | -79.7928 | -80.0537 | 43.1488 | 43.0939 | -0.20599 | 43.3777 | 0.07782 | 45.433 | 0.16022 | 0.14648 | 45.8313 | 45.7809 | 45.7214 | 0.3479 | 0.28839 | 43.4326 | 43.2587 | 0.39826 | 77.742 | 43.5196 | 77.7557 | 43.2358 | 123.1888 | -123.3124 | -77.5955 | 42.9749 | 123.175 | 32.4921 | 46.2936
1509.4844 | 119.8929 | -43.6981 | 78.8635 | -0.38574 | 0.0033389 | 0.040708 | 0.0036615 | 0.00062594 | -0.0014248 | -0.0011663 | -0.032379 | 0.0039541 | 0.0048984 | 0.039779 | -0.0025976 | -0.0023028 | -0.0013991 | -11.5814 | -1.0208 | -44.5175 | -1.4603 | -1.3138 | -44.5496 | -1.3412 | 1.3733 | 79.01 | 1.355 | 78.3966 | 1.6159 | 1.3641 | 1.3092 | -0.8194 | -79.8843 | -80.3238 | 42.3843 | 42.3569 | -0.85144 | 43.1763 | -0.032044 | 45.0531 | 0.14648 | -0.46692 | 45.314 | 45.0073 | 45.0623 | -0.045776 | 0.009156 | 43.2037 | 43.0573 | 0.26093 | 77.0416 | 43.4967 | 77.655 | 42.6773 | 122.7081 | -123.381 | -77.5085 | 42.2379 | 122.0947 | 32.1167 | 45.0714
1510.5469 | 123.3856 | -44.3481 | 78.8177 | -0.050049 | 0.0037661 | 0.041776 | 0.0017389 | 0.00083954 | -0.00078402 | -0.0043707 | 0.025604 | 0.0028861 | 0.0059664 | 0.038283 | -0.0028112 | -0.0035846 | 0.0037277 | -11.8698 | -1.2726 | -44.577 | -1.593 | -1.442 | -44.5541 | -1.4648 | 1.9592 | 78.8864 | 1.4328 | 78.9047 | 1.8448 | 1.7487 | 1.8265 | -0.22888 | -80.0903 | -80.4108 | 42.9062 | 42.8833 | -0.20599 | 43.1122 | 0.022888 | 45.7809 | 0.068665 | 0.086975 | 46.1929 | 46.1746 | 46.0968 | 0.39368 | 0.31586 | 43.1351 | 42.984 | 0.41199 | 77.4719 | 43.3044 | 77.4536 | 43.0756 | 123.2346 | -123.3948 | -77.3849 | 42.7551 | 123.2529 | 32.4783 | 46.3074
1511.4844 | 122.4976 | -44.1971 | 78.8361 | -0.095825 | 0.0020573 | 0.042631 | 0.0017389 | -0.0010831 | 0.002634 | 0.0011835 | -0.023224 | 0.0033133 | 0.0023348 | 0.036788 | -0.0038794 | -0.0025164 | -0.0016129 | -11.911 | -1.1673 | -44.6411 | -1.5198 | -1.3687 | -44.5999 | -1.4191 | 1.4008 | 78.9001 | 1.1993 | 78.7949 | 1.506 | 1.4282 | 1.4603 | -0.44403 | -80.0034 | -80.3558 | 42.8284 | 42.778 | -0.40283 | 43.222 | 0.041198 | 45.3964 | 0.064086 | -0.041199 | 45.7031 | 45.6573 | 45.6253 | 0.26093 | 0.22888 | 43.2724 | 43.1213 | 0.3067 | 77.5955 | 43.4738 | 77.7008 | 43.0298 | 123.0972 | -123.4772 | -77.6367 | 42.6773 | 122.9919 | 32.2861 | 45.5978
1512.5625 | 122.8867 | -44.1238 | 78.8818 | -0.23315 | 0.0035525 | 0.045835 | 0.0032343 | 0.0023349 | -0.00057042 | 0.00096987 | -0.062897 | 0.0030997 | 0.0023348 | 0.047256 | -0.0004614 | -0.0012348 | -0.0018265 | -11.8515 | -1.1993 | -44.5404 | -1.506 | -1.3824 | -44.5358 | -1.4282 | 1.1124 | 78.9825 | 1.5106 | 78.9963 | 1.9592 | 1.8082 | 1.9821 | -0.41656 | -80.0812 | -80.3879 | 42.7414 | 42.6956 | -0.41199 | 43.1122 | 0.004577 | 45.6345 | 0.10071 | 0.11444 | 46.0831 | 46.106 | 45.932 | 0.4715 | 0.29755 | 43.158 | 43.0344 | 0.44861 | 77.4857 | 43.3411 | 77.4719 | 42.9245 | 123.1064 | -123.4222 | -77.3712 | 42.6178 | 123.1201 | 32.2723 | 45.2362
1513.4844 | 123.1476 | -44.2337 | 78.7628 | -0.050049 | 0.0016299 | 0.042844 | 0.0032343 | -0.0038603 | 0.0011386 | -0.0020209 | 0.028656 | 0.0033133 | 0.0063938 | 0.035293 | -0.0028112 | -0.0044392 | 0.00052346 | -11.824 | -1.181 | -44.4122 | -1.4603 | -1.2817 | -44.426 | -1.3412 | 1.2726 | 78.9871 | 1.6891 | 79.0466 | 2.1698 | 2.1011 | 2.0828 | -0.17853 | -79.9438 | -80.2231 | 42.952 | 42.8925 | -0.19226 | 43.071 | -0.013733 | 45.9229 | 0.22431 | 0.28381 | 46.4035 | 46.3165 | 46.3348 | 0.39368 | 0.41199 | 43.1305 | 42.952 | 0.48065 | 77.3575 | 43.2312 | 77.298 | 43.0527 | 123.2208 | -123.175 | -77.0737 | 42.7734 | 123.2803 | 32.4097 | 45.5063
1514.4844 | 122.4976 | -43.9682 | 78.6438 | -0.1416 | 0.0029117 | 0.043485 | 0.0051569 | -0.0032193 | 0.0022068 | -0.0018073 | -0.038483 | 0.0028861 | 0.0025484 | 0.041701 | -0.0015296 | -0.0035846 | 0.0050095 | -11.9659 | -1.1765 | -44.5358 | -1.6022 | -1.4557 | -44.577 | -1.4923 | 1.68 | 79.0054 | 1.5427 | 78.8681 | 1.8127 | 1.6754 | 1.7212 | -0.56763 | -79.8203 | -80.246 | 42.5125 | 42.4759 | -0.60882 | 43.0435 | -0.041198 | 45.5109 | 0.36163 | 0.2243 | 45.7809 | 45.6894 | 45.6436 | 0.17853 | 0.13275 | 43.0801 | 42.9337 | 0.27008 | 77.3254 | 43.3594 | 77.4628 | 42.7917 | 122.9736 | -123.1796 | -77.1011 | 42.366 | 122.8363 | 32.0023 | 45.6482
1515.4844 | 122.5296 | -43.9774 | 79.0512 | -0.11871 | 0.0029117 | 0.041135 | 0.0023797 | -0.0027921 | 0.00092498 | -0.00095273 | -0.020172 | 0.0048087 | 0.0040438 | 0.047683 | -0.0025976 | -0.00059378 | 0.0039413 | -11.6638 | -1.1765 | -44.4214 | -1.5747 | -1.4236 | -44.4168 | -1.4557 | 1.3733 | 79.1382 | 1.9135 | 78.9642 | 2.2568 | 2.0554 | 2.1469 | -0.44403 | -80.2277 | -80.6259 | 42.5537 | 42.5217 | -0.43945 | 42.9657 | 0.004578 | 45.8908 | 0.086976 | -0.086975 | 46.2341 | 46.1243 | 46.0327 | 0.23346 | 0.14191 | 42.9977 | 42.8467 | 0.34332 | 77.0508 | 43.2449 | 77.2247 | 42.8009 | 123.1155 | -123.4726 | -77.1378 | 42.4026 | 122.9416 | 32.3135 | 45.3506
1516.4844 | 123.317 | -44.2017 | 78.9642 | -0.027161 | 0.0014163 | 0.042417 | 0.0023797 | -0.0034329 | 0.00071138 | -0.00052553 | 0.043915 | 0.0030997 | 0.0042574 | 0.041701 | -0.0036658 | -0.0010212 | -0.0026809 | -11.9385 | -1.387 | -44.577 | -1.6571 | -1.4694 | -44.4443 | -1.5289 | 1.6434 | 78.9185 | 1.8768 | 79.0237 | 2.4857 | 2.449 | 2.5955 | -0.37537 | -80.3513 | -80.6213 | 42.7322 | 42.6727 | -0.24262 | 43.0481 | 0.13275 | 46.0785 | -0.045776 | 0.05951 | 46.6873 | 46.7972 | 46.6507 | 0.71869 | 0.57221 | 43.1076 | 42.9199 | 0.60883 | 77.1469 | 43.19 | 77.0416 | 42.8146 | 123.1201 | -123.5413 | -77.0874 | 42.5446 | 123.2254 | 32.2632 | 45.845
1517.5625 | 122.9324 | -44.3848 | 78.772 | 0.026245 | 0.0026981 | 0.041135 | 0.0034479 | 0.0029757 | 0.00028418 | -0.0024481 | -0.011017 | 0.0030997 | 0.0053256 | 0.045333 | -0.0019568 | -0.0018756 | 0.00073706 | -11.6684 | -1.4786 | -44.6869 | -1.7899 | -1.6525 | -44.664 | -1.6846 | 1.6754 | 78.8406 | 1.561 | 78.7354 | 1.8906 | 1.799 | 1.8631 | -0.30212 | -80.2506 | -80.5618 | 42.7322 | 42.7002 | -0.27923 | 43.0023 | 0.022889 | 45.9457 | 0.068664 | -0.036621 | 46.2753 | 46.2479 | 46.1838 | 0.30212 | 0.23804 | 43.0344 | 42.897 | 0.32959 | 77.1744 | 43.2083 | 77.2797 | 42.9062 | 123.2254 | -123.4589 | -77.211 | 42.5949 | 123.1201 | 32.7164 | 46.0602
1518.4844 | 123.3536 | -44.3573 | 78.804 | -0.11108 | 0.0037661 | 0.043272 | 0.0034479 | -1.486e-05 | -0.00078402 | -0.0020209 | -0.041534 | 0.0022453 | 0.0046848 | 0.039565 | -0.003025 | -0.0025164 | 0.0022323 | -11.7279 | -1.4786 | -44.5953 | -1.7807 | -1.6159 | -44.5953 | -1.6983 | 5.3879 | 78.8956 | 1.8173 | 78.8727 | 2.1423 | 2.0233 | 2.1332 | -0.23804 | -80.2826 | -80.5847 | 42.7414 | 42.659 | -0.23804 | 42.897 | 0 | 46.1746 | 0.091553 | 0.068665 | 46.4996 | 46.4905 | 46.3806 | 0.31586 | 0.20599 | 42.9794 | 42.8146 | 0.32501 | 77.0554 | 43.1168 | 77.0782 | 42.8787 | 123.2529 | -123.3994 | -76.9867 | 42.5766 | 123.23 | 32.6294 | 49.7452
1519.4844 | 123.4497 | -44.2474 | 78.9185 | -0.042419 | 0.0022709 | 0.042417 | 0.0017389 | -0.0017239 | -0.00078402 | -0.00095273 | 0.004242 | 0.0026725 | 0.005112 | 0.038283 | -0.0045202 | -0.0010212 | -0.0048171 | -11.5265 | -1.4923 | -44.4855 | -1.7624 | -1.5793 | -44.4672 | -1.6525 | 4.0558 | 79.0054 | 2.2202 | 79.01 | 2.4811 | 2.5269 | 2.4902 | -0.23804 | -80.4108 | -80.6808 | 42.6682 | 42.5949 | -0.21973 | 42.8329 | 0.018311 | 46.4676 | 0.086975 | 0.091553 | 46.7285 | 46.7377 | 46.7743 | 0.27008 | 0.3067 | 42.9062 | 42.7231 | 0.26092 | 76.7899 | 42.9932 | 76.7853 | 42.7551 | 123.2529 | -123.4039 | -76.6983 | 42.485 | 123.2574 | 32.7209 | 48.3032
1520.5469 | 123.3673 | -44.3481 | 78.8452 | -0.042419 | 0.0014163 | 0.042203 | 0.0038751 | 0.00083954 | 0.0013522 | 0.00011527 | -0.053741 | 0.00010888 | 0.0021212 | 0.041488 | -0.002384 | -0.0023028 | -0.0011855 | -11.8835 | -1.5152 | -44.5999 | -1.8356 | -1.7075 | -44.5679 | -1.7441 | 1.3779 | 78.978 | 2.0874 | 78.9185 | 2.3529 | 2.2293 | 2.243 | -0.25177 | -80.3604 | -80.6808 | 42.6407 | 42.6041 | -0.21973 | 42.8558 | 0.032044 | 46.4355 | 0.13275 | 0.073242 | 46.7011 | 46.5912 | 46.5775 | 0.15564 | 0.14191 | 42.8925 | 42.7643 | 0.2655 | 76.8311 | 43.0847 | 76.8906 | 42.8329 | 123.3261 | -123.4451 | -76.7578 | 42.5125 | 123.2666 | 32.4646 | 45.726
1521.4844 | 123.3719 | -44.4351 | 78.7399 | -0.072937 | 0.0020573 | 0.043272 | 0.0034479 | -0.0049283 | 0.0022068 | 0.00054267 | -0.011017 | 0.0026725 | 0.0053256 | 0.041488 | -0.0028112 | -0.0018756 | -0.00054474 | -11.8607 | -1.5335 | -44.7006 | -1.8265 | -1.6754 | -44.6548 | -1.7258 | 1.4969 | 78.8086 | 1.68 | 78.7766 | 2.0691 | 1.9501 | 2.0462 | -0.2655 | -80.2734 | -80.5664 | 42.7597 | 42.7094 | -0.21973 | 42.9749 | 0.045777 | 46.1151 | 0.068665 | 0.036621 | 46.5042 | 46.4813 | 46.3852 | 0.36621 | 0.27008 | 43.0252 | 42.8741 | 0.3891 | 77.0966 | 43.1671 | 77.1286 | 42.9016 | 123.2437 | -123.4406 | -77.0599 | 42.6086 | 123.2117 | 32.5745 | 45.932
1522.5625 | 122.644 | -44.133 | 78.7628 | -0.3476 | 0.0026981 | 0.041563 | 0.0038751 | 0.00062594 | -0.00035682 | -0.00095273 | -0.099518 | 0.0020315 | 0.0014804 | 0.039992 | -0.0028112 | 4.7018e-05 | -0.00054474 | -12.0712 | -1.4694 | -44.7372 | -1.9089 | -1.7853 | -44.7281 | -1.799 | 1.5289 | 78.8498 | 1.5518 | 78.7628 | 1.8585 | 1.8127 | 1.8814 | -0.60425 | -80.2322 | -80.6717 | 42.3477 | 42.334 | -0.59509 | 42.9382 | 0.009156 | 45.6848 | 0.086975 | 0 | 45.9915 | 46.0144 | 45.9457 | 0.32959 | 0.26092 | 42.952 | 42.8284 | 0.3067 | 77.211 | 43.2678 | 77.298 | 42.6636 | 122.9828 | -123.5001 | -77.211 | 42.2241 | 122.8958 | 32.0618 | 45.6619
1523.4844 | 123.4131 | -44.2703 | 78.9139 | -0.080566 | 0.0039799 | 0.04199 | 0.0036615 | -0.0034329 | -0.0012112 | -0.0015935 | 0.010345 | 0.0026725 | 0.0036166 | 0.042129 | -0.0025976 | -0.0025164 | 0.00030966 | -12.1262 | -1.5701 | -44.5862 | -1.8311 | -1.6571 | -44.4809 | -1.7075 | 1.6434 | 78.9459 | 1.9775 | 78.9642 | 2.4811 | 2.3529 | 2.4673 | -0.31586 | -80.484 | -80.7449 | 42.6132 | 42.5629 | -0.21057 | 42.8787 | 0.10529 | 46.2479 | 0.032044 | 0.050354 | 46.7514 | 46.7377 | 46.6232 | 0.48981 | 0.37537 | 42.9291 | 42.7551 | 0.50354 | 76.9867 | 43.0161 | 76.9684 | 42.7002 | 123.2162 | -123.5001 | -76.9363 | 42.4393 | 123.2346 | 32.1442 | 45.9137
1524.5469 | 123.3719 | -44.3298 | 78.8132 | -0.088196 | 0.0020573 | 0.042203 | 0.0030207 | -0.0036465 | -0.00035682 | -0.0018073 | -0.020172 | 0.0030997 | 0.0036166 | 0.041274 | -0.002384 | -0.00059378 | 0.0033005 | -12.1033 | -1.5427 | -44.5358 | -1.8951 | -1.7532 | -45.1126 | -1.7899 | 1.3275 | 78.9459 | 2.0966 | 78.9001 | 2.3483 | 2.2888 | 2.3071 | -0.20599 | -80.3558 | -80.7083 | 42.5766 | 42.54 | -0.78278 | 42.746 | -0.57678 | 46.4264 | 0.13275 | 0.086975 | 46.6782 | 46.637 | 46.6187 | 0.21057 | 0.19226 | 42.7826 | 42.6407 | 0.25177 | 76.8036 | 42.9932 | 76.8494 | 42.7872 | 123.2758 | -123.349 | -76.7166 | 42.4347 | 123.23 | 32.2266 | 45.6573
1525.4844 | 123.3902 | -44.4168 | 78.6896 | -0.042419 | 0.0014163 | 0.044767 | 0.0013117 | -0.0012967 | 0.0013522 | -0.0045843 | -0.056793 | 0.0037405 | 0.0040438 | 0.039352 | -0.002384 | -0.0037982 | 0.0013779 | -11.9705 | -1.5289 | -44.664 | -1.8768 | -1.7532 | -44.7144 | -1.7578 | 2.3483 | 78.8223 | 1.561 | 78.7582 | 1.9318 | 1.7761 | 1.8768 | -0.24719 | -80.2185 | -80.5664 | 42.6636 | 42.659 | -0.29755 | 42.9062 | -0.050354 | 45.9778 | 0.13275 | 0.068665 | 46.3486 | 46.2936 | 46.1929 | 0.31586 | 0.21515 | 42.9108 | 42.7872 | 0.37079 | 77.1973 | 43.1351 | 77.2614 | 42.8879 | 123.2391 | -123.3536 | -77.1286 | 42.54 | 123.175 | 32.4463 | 46.7651
1526.4844 | 123.3948 | -44.3527 | 78.772 | -0.080566 | 0.0063297 | 0.042417 | 0.0043023 | -0.0021513 | 0.0011386 | -0.0020209 | -0.078156 | 0.0018179 | 0.0046848 | 0.042129 | -0.0036658 | 0.00068782 | 9.6064e-05 | -12.0346 | -1.5244 | -44.6915 | -1.7944 | -1.6617 | -44.664 | -1.7349 | 1.7395 | 78.8773 | 1.7303 | 78.9368 | 2.1881 | 2.1332 | 2.3392 | -0.33875 | -80.2963 | -80.5664 | 42.691 | 42.6178 | -0.31128 | 42.9565 | 0.027466 | 46.0831 | 0.10528 | 0.16479 | 46.5408 | 46.6919 | 46.4859 | 0.60882 | 0.40283 | 43.0298 | 42.897 | 0.45776 | 77.2064 | 43.1671 | 77.1469 | 42.8284 | 123.23 | -123.4634 | -77.0416 | 42.5583 | 123.2895 | 32.3181 | 46.0922
1527.5 | 122.7631 | -44.3756 | 78.2181 | -0.072937 | 0.0024845 | 0.043485 | 0.0047295 | 0.0010531 | -0.00078402 | -0.0043707 | -0.081207 | 0.00032248 | 0.0036166 | 0.038497 | -0.0032386 | -0.0035846 | 0.00095066 | -12.0941 | -1.5884 | -44.751 | -2.0096 | -1.8997 | -44.7922 | -1.9135 | 1.3733 | 78.8269 | 1.6388 | 78.6667 | 1.8723 | 1.7303 | 1.8219 | -0.37537 | -79.8065 | -80.2277 | 42.4759 | 42.4622 | -0.41656 | 42.8375 | -0.041198 | 46.0144 | 0.60882 | 0.44861 | 46.2479 | 46.1975 | 46.106 | 0.1831 | 0.091553 | 42.8513 | 42.7414 | 0.23346 | 77.0279 | 43.1625 | 77.1881 | 42.7872 | 123.2025 | -122.9691 | -76.5793 | 42.366 | 123.0423 | 32.2815 | 45.7489
1528.4844 | 123.3582 | -44.2932 | 78.8773 | -0.057678 | 0.0029117 | 0.042844 | 0.0028069 | 0.00062594 | 0.00092498 | -0.00073913 | -0.0018616 | 0.0033133 | 0.0055392 | 0.036788 | -0.0036658 | -0.0018756 | -0.00033114 | -12.0895 | -1.6296 | -44.6915 | -1.9867 | -1.8311 | -44.6411 | -1.8539 | 1.8906 | 78.9413 | 2.0416 | 78.9413 | 2.6505 | 2.6459 | 2.655 | -0.39825 | -80.5069 | -80.864 | 42.4622 | 42.4393 | -0.3479 | 42.8375 | 0.050354 | 46.3348 | 0.064087 | 0.064087 | 46.9437 | 46.9482 | 46.9391 | 0.6134 | 0.60425 | 42.8604 | 42.7048 | 0.60883 | 76.8997 | 43.0618 | 76.8997 | 42.6636 | 123.2346 | -123.5687 | -76.8356 | 42.3065 | 123.2346 | 32.2037 | 46.1838
1529.4844 | 123.4039 | -44.5358 | 78.598 | -0.065308 | 0.0024845 | 0.043058 | 0.0030207 | -0.0030057 | 0.0013522 | 0.00096987 | -0.0018616 | 0.0041679 | 0.0046848 | 0.041701 | -0.0021704 | -0.0025164 | 0.0020187 | -11.8011 | -1.68 | -44.7739 | -1.9592 | -1.8265 | -44.751 | -1.8631 | 2.0782 | 78.7125 | 1.3962 | 78.7125 | 1.8127 | 1.7029 | 1.7624 | -0.23804 | -80.278 | -80.5573 | 42.7094 | 42.6727 | -0.21515 | 42.9108 | 0.022888 | 45.932 | 0.11444 | 0.11444 | 46.3486 | 46.2982 | 46.2387 | 0.36621 | 0.3067 | 42.9474 | 42.8146 | 0.41656 | 77.3163 | 43.0939 | 77.3163 | 42.8558 | 123.2483 | -123.3719 | -77.2018 | 42.5766 | 123.2483 | 32.7347 | 46.6141
1530.5469 | 123.3719 | -44.3619 | 78.8223 | -0.12634 | 0.0050479 | 0.042631 | 0.0030207 | -0.0015103 | 0.002634 | -0.0015935 | -0.081207 | 0.0024589 | 0.0046848 | 0.036788 | -0.0002478 | -0.00080758 | -0.0020401 | -12.0758 | -1.7166 | -44.6686 | -2.005 | -1.8585 | -44.7372 | -1.918 | 2.0554 | 78.7354 | 1.6205 | 78.8544 | 2.3254 | 2.1881 | 2.3758 | -0.3067 | -80.5389 | -80.8273 | 42.5034 | 42.4438 | -0.37537 | 42.7505 | -0.068665 | 45.9824 | -0.086975 | 0.032043 | 46.6873 | 46.7377 | 46.55 | 0.75531 | 0.56763 | 42.8101 | 42.6636 | 0.70496 | 77.2339 | 42.952 | 77.1149 | 42.6453 | 123.0972 | -123.4909 | -77.2018 | 42.3569 | 123.2162 | 32.2861 | 46.4172
1531.4844 | 123.4543 | -44.4992 | 78.6301 | -0.027161 | 0.0024845 | 0.04199 | 0.0013117 | -0.0015103 | 0.0030612 | -0.0015935 | -0.023224 | 0.0024589 | 0.0038302 | 0.042129 | -0.0032386 | -0.0020892 | -0.0013991 | -11.8011 | -1.7212 | -44.7372 | -1.9775 | -1.8311 | -44.696 | -1.8814 | 1.886 | 78.7308 | 1.6022 | 78.772 | 2.0416 | 1.9135 | 1.9638 | -0.23804 | -80.3513 | -80.6076 | 42.6682 | 42.6178 | -0.19684 | 42.8558 | 0.041199 | 46.1014 | 0.10071 | 0.14191 | 46.5408 | 46.463 | 46.4127 | 0.36163 | 0.31128 | 42.9062 | 42.7597 | 0.43945 | 77.1698 | 43.0161 | 77.1286 | 42.778 | 123.23 | -123.3673 | -77.0279 | 42.5217 | 123.2712 | 32.6981 | 46.3852
1532.4844 | 123.3582 | -44.4992 | 78.6255 | -0.019531 | 0.0022709 | 0.043912 | 0.0049433 | -0.00086946 | 0.0017794 | -0.0047979 | -0.059845 | 0.0033133 | 0.0046848 | 0.040633 | -0.0019568 | -0.00016658 | -0.0018265 | -11.8286 | -1.6983 | -44.7418 | -2.0142 | -1.8814 | -44.7968 | -1.9272 | 1.4648 | 78.7445 | 1.4786 | 78.6987 | 1.8356 | 1.7303 | 1.8082 | -0.24261 | -80.3238 | -80.6396 | 42.6178 | 42.572 | -0.29755 | 42.8146 | -0.054932 | 45.9778 | 0.11902 | 0.073242 | 46.3348 | 46.3074 | 46.2296 | 0.32959 | 0.25177 | 42.8604 | 42.7277 | 0.35705 | 77.2202 | 43.0435 | 77.2659 | 42.8009 | 123.2437 | -123.3673 | -77.1469 | 42.485 | 123.1979 | 32.6706 | 45.9641
1533.5625 | 123.3994 | -44.4855 | 78.6621 | -0.0042723 | 0.0024845 | 0.041776 | 0.0036615 | -0.0038603 | 0.0011386 | -0.0015935 | -0.01712 | 0.0024589 | 0.0046848 | 0.036147 | -0.002384 | -0.0037982 | -0.00097194 | -12.0346 | -1.6479 | -44.7189 | -1.9363 | -1.7715 | -44.6365 | -1.8356 | 2.1103 | 78.7674 | 1.5427 | 78.772 | 1.8677 | 1.7807 | 1.7944 | -0.23346 | -80.3101 | -80.5984 | 42.7139 | 42.6498 | -0.15106 | 42.8833 | 0.082397 | 46.0281 | 0.10529 | 0.10986 | 46.3532 | 46.2799 | 46.2662 | 0.25177 | 0.23804 | 42.9474 | 42.7826 | 0.32501 | 77.2293 | 43.071 | 77.2247 | 42.8375 | 123.2529 | -123.381 | -77.1194 | 42.5491 | 123.2574 | 32.4509 | 46.5958
1534.4844 | 123.4131 | -44.5221 | 78.6301 | -0.15686 | 0.0035525 | 0.040922 | 0.0028069 | -0.0010831 | 0.0039158 | -0.0018073 | -0.093414 | 0.0039541 | 0.005112 | 0.043838 | -0.0034522 | -0.0023028 | -0.0013991 | -12.149 | -1.6663 | -44.8105 | -1.9363 | -1.8082 | -44.8013 | -1.8768 | 1.8448 | 78.6987 | 1.4099 | 78.7262 | 1.7807 | 1.68 | 1.7807 | -0.28839 | -80.2963 | -80.5664 | 42.7139 | 42.6453 | -0.27924 | 42.9337 | 0.009155 | 45.932 | 0.068664 | 0.09613 | 46.3028 | 46.3028 | 46.2021 | 0.37079 | 0.27008 | 43.0023 | 42.8741 | 0.37079 | 77.3163 | 43.1442 | 77.2888 | 42.8558 | 123.2208 | -123.4406 | -77.2202 | 42.5858 | 123.2483 | 32.373 | 46.3669
1535.4844 | 123.4085 | -44.4855 | 78.653 | -0.057678 | 0.0016299 | 0.041776 | 0.0025933 | -0.0047147 | 0.0011386 | 0.00075627 | 0.010345 | 0.0045951 | 0.0057528 | 0.038924 | -0.000675 | -0.0020892 | -0.0020401 | -12.0895 | -1.6571 | -44.7418 | -1.973 | -1.8082 | -44.7464 | -1.8448 | 1.6342 | 78.7903 | 1.442 | 78.7857 | 1.9318 | 1.7944 | 1.8539 | -0.25635 | -80.3101 | -80.6259 | 42.6773 | 42.6407 | -0.26092 | 42.897 | -0.004578 | 45.9274 | 0.13733 | 0.13275 | 46.4172 | 46.3394 | 46.2799 | 0.41199 | 0.35248 | 42.9337 | 42.7689 | 0.48981 | 77.3438 | 43.0847 | 77.3483 | 42.8284 | 123.2758 | -123.3948 | -77.211 | 42.5125 | 123.2712 | 32.3959 | 46.1197
1536.4844 | 123.3719 | -44.4534 | 78.7308 | -0.042419 | 0.0012027 | 0.04199 | 0.0021661 | 0.00062594 | 0.0015658 | -0.0015935 | -0.044586 | 0.0022453 | 0.0040438 | 0.040847 | -0.0032386 | -0.00080758 | -0.0026809 | -12.1765 | -1.6846 | -44.6823 | -2.0142 | -1.8768 | -44.7372 | -1.9226 | 1.6571 | 78.8132 | 1.7166 | 78.7949 | 2.092 | 1.9775 | 2.0737 | -0.22888 | -80.4153 | -80.7449 | 42.5766 | 42.5308 | -0.28381 | 42.7597 | -0.054932 | 46.17 | 0.082397 | 0.064087 | 46.5454 | 46.5271 | 46.431 | 0.35706 | 0.26092 | 42.8055 | 42.6682 | 0.37537 | 77.0782 | 42.9977 | 77.0966 | 42.7689 | 123.2666 | -123.4131 | -77.0142 | 42.4393 | 123.2483 | 32.2769 | 46.1105
1537.5 | 123.23 | -44.4534 | 78.7582 | -0.072937 | 0.0022709 | 0.043058 | 0.0051569 | 0.0025485 | 7.0582e-05 | -0.00073913 | -0.10257 | 0.0039541 | 0.0048984 | 0.042556 | -0.0019568 | -0.00059378 | -0.0024673 | -12.1536 | -1.5793 | -44.696 | -2.0233 | -1.8951 | -44.7327 | -1.9226 | 1.9272 | 78.891 | 1.6434 | 78.7582 | 1.9318 | 1.8402 | 1.9318 | -0.24262 | -80.3375 | -80.7816 | 42.5583 | 42.5308 | -0.27924 | 42.7734 | -0.036621 | 46.0968 | 0.13275 | 0 | 46.3852 | 46.3852 | 46.2936 | 0.28839 | 0.19684 | 42.8009 | 42.6727 | 0.28839 | 77.1149 | 43.1168 | 77.2476 | 42.8741 | 123.3444 | -123.4543 | -77.1149 | 42.4301 | 123.2117 | 32.2998 | 46.3806
1538.5469 | 123.3719 | -44.2337 | 78.9093 | -0.080566 | 0.0041935 | 0.042417 | 0.0040887 | 0.0014803 | -0.00014322 | -0.00073913 | -0.056793 | 0.0033133 | 0.0055392 | 0.04106 | -0.0028112 | -0.001662 | 0.0056503 | -12.0712 | -1.561 | -44.5633 | -1.8539 | -1.68 | -44.6045 | -1.7395 | 1.5793 | 78.9963 | 1.8906 | 79.0146 | 2.4628 | 2.4078 | 2.4719 | -0.32959 | -80.4703 | -80.7632 | 42.5537 | 42.4942 | -0.37079 | 42.8238 | -0.041199 | 46.1243 | 0.086975 | 0.10529 | 46.6965 | 46.7056 | 46.6415 | 0.58136 | 0.51727 | 42.8833 | 42.7094 | 0.57221 | 77.124 | 43.0023 | 77.1057 | 42.6727 | 123.23 | -123.4726 | -77.0187 | 42.3798 | 123.2483 | 32.1625 | 45.813
1539.4844 | 123.4131 | -44.1467 | 79.0237 | 0.010986 | 0.0018435 | 0.042417 | 0.0013117 | -1.486e-05 | -0.00078402 | -0.00031193 | 0.004242 | 0.0026725 | 0.0036166 | 0.040847 | -0.0043066 | -0.0012348 | -0.0018265 | -12.0483 | -1.593 | -44.3939 | -1.8677 | -1.6937 | -44.3481 | -1.7487 | 1.7258 | 79.0421 | 2.2385 | 79.1107 | 2.9388 | 2.6779 | 2.7145 | -0.24719 | -80.6168 | -80.8914 | 42.453 | 42.3981 | -0.20142 | 42.6453 | 0.045776 | 46.3852 | 0.01831 | 0.086975 | 47.0856 | 46.8613 | 46.8246 | 0.47607 | 0.43945 | 42.7002 | 42.5262 | 0.70038 | 76.8723 | 42.8009 | 76.8036 | 42.5537 | 123.1888 | -123.4177 | -76.7853 | 42.2791 | 123.2574 | 32.0984 | 45.8725
1540.4844 | 123.3719 | -44.3253 | 78.8452 | -0.065308 | 0.0029117 | 0.041563 | 0.0036615 | 0.00083954 | 0.0034884 | 0.00054267 | -0.041534 | 0.0041679 | 0.005112 | 0.042129 | -0.0049476 | -0.0014484 | 0.0028733 | -12.0758 | -1.5793 | -44.5221 | -1.8997 | -1.7624 | -44.632 | -1.8036 | 1.9043 | 78.8864 | 1.7944 | 78.9001 | 2.1423 | 2.0325 | 2.1561 | -0.19684 | -80.4245 | -80.7449 | 42.5629 | 42.5217 | -0.3067 | 42.7185 | -0.10986 | 46.1197 | 0.041199 | 0.054931 | 46.4676 | 46.4813 | 46.3577 | 0.36163 | 0.23804 | 42.7597 | 42.6224 | 0.3479 | 77.1057 | 42.9428 | 77.092 | 42.746 | 123.2117 | -123.3673 | -77.0508 | 42.4255 | 123.2254 | 32.2495 | 46.2296
1541.5625 | 123.317 | -44.4351 | 78.804 | -0.050049 | 0.0026981 | 0.039854 | 0.0032343 | -0.0012967 | 0.00092498 | -0.00052553 | -0.056793 | 0.0024589 | 0.004471 | 0.038924 | -0.0032386 | -0.0014484 | -0.00033114 | -12.0209 | -1.6342 | -44.6182 | -1.9638 | -1.8173 | -44.6136 | -1.8723 | 2.1606 | 78.923 | 1.6891 | 78.7994 | 1.9775 | 1.8768 | 1.9775 | -0.18311 | -80.4382 | -80.7678 | 42.6178 | 42.5629 | -0.17853 | 42.746 | 0.004578 | 46.1243 | 0.11902 | -0.004578 | 46.4127 | 46.4127 | 46.312 | 0.28839 | 0.18768 | 42.8009 | 42.6544 | 0.28839 | 77.1103 | 42.984 | 77.2339 | 42.8009 | 123.3582 | -123.4222 | -77.1149 | 42.4713 | 123.2346 | 32.4142 | 46.5958
1542.5 | 123.2986 | -44.2978 | 78.9551 | -0.0042723 | 0.0024845 | 0.043485 | 0.0030207 | -1.486e-05 | 0.00028418 | 0.00096987 | -0.056793 | 0.0037405 | 0.005112 | 0.039992 | -0.0019568 | -0.0020892 | 0.00073706 | -11.8881 | -1.5472 | -44.5496 | -1.973 | -1.8402 | -44.7006 | -1.8723 | 1.6205 | 79.0558 | 2.1378 | 78.8956 | 2.2842 | 2.2476 | 2.2888 | -0.25177 | -80.5023 | -80.928 | 42.4576 | 42.4255 | -0.40283 | 42.6773 | -0.15106 | 46.4355 | 0.10071 | -0.059509 | 46.582 | 46.5866 | 46.5454 | 0.15106 | 0.10986 | 42.7094 | 42.5766 | 0.14649 | 76.7578 | 43.0023 | 76.918 | 42.7505 | 123.3536 | -123.5046 | -76.8173 | 42.3248 | 123.1934 | 32.4097 | 45.9183
1543.5469 | 123.3765 | -44.3573 | 78.8223 | -0.11108 | 0.0035525 | 0.043272 | 0.0023797 | -0.0017239 | -0.00035682 | -0.0022345 | -0.056793 | 0.0037405 | 0.00618 | 0.039779 | -0.0015296 | -0.0012348 | 0.00052346 | -11.9476 | -1.5747 | -44.6228 | -1.8906 | -1.767 | -44.6823 | -1.7853 | 1.593 | 78.8406 | 1.5335 | 78.8818 | 2.037 | 1.9455 | 2.0554 | -0.2655 | -80.397 | -80.7129 | 42.5903 | 42.572 | -0.32501 | 42.8375 | -0.059509 | 45.8908 | 0.01831 | 0.059509 | 46.3943 | 46.4127 | 46.3028 | 0.52185 | 0.41199 | 42.8558 | 42.7322 | 0.50354 | 77.3483 | 43.0481 | 77.3071 | 42.7826 | 123.1979 | -123.4451 | -77.2888 | 42.4667 | 123.2391 | 32.4097 | 45.9503
1544.4844 | 123.3856 | -44.3619 | 78.7857 | -0.080566 | 0.0024845 | 0.044981 | 0.0025933 | -0.0038603 | 0.00092498 | -0.0043707 | -0.020172 | 0.0045951 | 0.00618 | 0.038283 | -0.0019568 | -0.001662 | 0.0015915 | -12.1078 | -1.6159 | -44.5541 | -1.9592 | -1.8356 | -44.5679 | -1.8585 | 1.5198 | 78.9505 | 1.9958 | 78.8544 | 2.0828 | 1.9867 | 2.0279 | -0.19226 | -80.4016 | -80.7449 | 42.5262 | 42.5034 | -0.20599 | 42.6956 | -0.013733 | 46.3577 | 0.16479 | 0.068664 | 46.4447 | 46.3898 | 46.3486 | 0.032043 | -0.009156 | 42.7185 | 42.5949 | 0.086975 | 76.8585 | 42.9382 | 76.9547 | 42.746 | 123.3124 | -123.3398 | -76.7899 | 42.4026 | 123.2162 | 32.254 | 45.8817
1545.5625 | 123.4039 | -44.4168 | 78.7491 | -0.072937 | 0.00077547 | 0.043272 | 0.0047295 | 0.0025485 | 7.0582e-05 | -9.8328e-05 | -0.029327 | 0.0033133 | 0.0023348 | 0.039352 | -0.0045202 | -0.0020892 | 0.00030966 | -11.8378 | -1.712 | -44.6732 | -1.9775 | -1.8173 | -44.6411 | -1.886 | 1.6891 | 78.8086 | 1.7303 | 78.8406 | 2.1652 | 2.037 | 2.1194 | -0.25635 | -80.4611 | -80.7266 | 42.5995 | 42.5308 | -0.2243 | 42.7872 | 0.032044 | 46.1472 | 0.05951 | 0.091553 | 46.582 | 46.5363 | 46.4539 | 0.3891 | 0.3067 | 42.8558 | 42.6956 | 0.43487 | 77.1103 | 42.9611 | 77.0782 | 42.7048 | 123.2254 | -123.4222 | -77.0187 | 42.4393 | 123.2574 | 32.579 | 46.106
1546.4844 | 123.4177 | -44.3253 | 78.8177 | -0.042419 | 0.0041935 | 0.043485 | 0.0038751 | 0.0012667 | 0.0019932 | -0.0015935 | -0.062897 | 0.0026725 | 0.0025484 | 0.037643 | -0.0021704 | -0.00080758 | -0.0031081 | -12.149 | -1.6663 | -44.5908 | -1.9455 | -1.7899 | -44.5908 | -1.8539 | 1.8402 | 78.8773 | 1.9135 | 78.9322 | 2.2842 | 2.1469 | 2.2614 | -0.2655 | -80.484 | -80.7632 | 42.5354 | 42.4713 | -0.2655 | 42.7368 | 0 | 46.2387 | 0.059509 | 0.11444 | 46.6095 | 46.5866 | 46.4722 | 0.3479 | 0.23346 | 42.8009 | 42.6453 | 0.37079 | 77.0187 | 42.9245 | 76.9638 | 42.659 | 123.2025 | -123.4085 | -76.9043 | 42.3798 | 123.2574 | 32.1762 | 46.1655
1547.4844 | 123.4222 | -44.3619 | 78.8177 | -0.072937 | 0.00013467 | 0.041349 | 0.0036615 | -1.486e-05 | 7.0582e-05 | -0.0024481 | -0.011017 | 0.0016043 | 0.0042574 | 0.038924 | -0.002384 | -0.001662 | 0.0011643 | -12.1399 | -1.6525 | -44.696 | -1.9318 | -1.8036 | -44.6136 | -1.8402 | 1.8631 | 78.9139 | 1.7395 | 78.8864 | 2.1332 | 2.1057 | 2.2659 | -0.33417 | -80.4703 | -80.7495 | 42.5583 | 42.5217 | -0.25177 | 42.8558 | 0.082398 | 46.1014 | 0.09613 | 0.068665 | 46.4951 | 46.6278 | 46.4676 | 0.52643 | 0.36621 | 42.8925 | 42.7643 | 0.39368 | 77.1469 | 43.0435 | 77.1744 | 42.7094 | 123.2758 | -123.5138 | -77.0782 | 42.4301 | 123.2483 | 32.222 | 46.225
1548.4844 | 123.3994 | -44.5358 | 78.6072 | -0.011902 | 0.0039799 | 0.045621 | 0.0021661 | 0.0027621 | 7.0582e-05 | -0.0028753 | -0.026276 | 0.0037405 | 0.003403 | 0.035934 | -0.0036658 | -0.0012348 | 9.6064e-05 | -12.1811 | -1.6754 | -44.7418 | -2.0096 | -1.8677 | -44.7601 | -1.9135 | 2.1652 | 78.7537 | 1.5289 | 78.7262 | 1.9043 | 1.3824 | 1.8768 | -0.20599 | -80.2826 | -80.6168 | 42.6682 | 42.6224 | -0.2243 | 42.8284 | -0.018311 | 46.0648 | 0.14648 | 0.11902 | 46.4401 | 46.4127 | 45.9183 | 0.3479 | -0.14648 | 42.8741 | 42.7322 | 0.37537 | 77.1973 | 43.0664 | 77.2247 | 42.8604 | 123.2895 | -123.349 | -77.0782 | 42.5262 | 123.262 | 32.3547 | 46.7011
1549.4844 | 123.4177 | -44.4489 | 78.6987 | -0.050049 | 0.0012027 | 0.04199 | 0.0017389 | 0.00041234 | -0.00035682 | -0.0024481 | -0.0079652 | 0.0016043 | 0.0029758 | 0.041488 | -0.002384 | -0.0035846 | -0.0028945 | -11.8378 | -1.7029 | -44.7189 | -1.9547 | -1.7853 | -44.632 | -1.8539 | 2.2614 | 78.7811 | 1.5656 | 78.804 | 1.973 | 1.8997 | 1.9226 | -0.27008 | -80.4016 | -80.6534 | 42.6636 | 42.5949 | -0.1831 | 42.865 | 0.086975 | 46.0144 | 0.082398 | 0.10529 | 46.4218 | 46.3715 | 46.3486 | 0.35705 | 0.33417 | 42.9337 | 42.7643 | 0.40741 | 77.2385 | 43.0161 | 77.2156 | 42.746 | 123.23 | -123.4177 | -77.1332 | 42.4942 | 123.2529 | 32.6111 | 46.7102
1550.5469 | 122.85 | -44.2978 | 78.9093 | -0.26367 | -0.0022153 | 0.045408 | 0.0040887 | -0.0034329 | 0.00092498 | -0.0018073 | -0.11783 | 0.0045951 | 0.0029758 | 0.044478 | -0.0043066 | 4.7018e-05 | -0.00075834 | -11.9934 | -1.2314 | -44.5358 | -1.6434 | -1.5244 | -44.5496 | -1.561 | 3.2547 | 79.0283 | 1.5884 | 78.9551 | 1.8585 | 1.7487 | 1.799 | -0.23804 | -80.1407 | -80.5527 | 42.7734 | 42.7368 | -0.25177 | 42.9749 | -0.013733 | 45.8862 | 0.11902 | 0.045776 | 46.1563 | 46.0968 | 46.0464 | 0.21057 | 0.16022 | 43.0115 | 42.8925 | 0.27008 | 77.3666 | 43.3044 | 77.4399 | 43.0664 | 123.3261 | -123.4451 | -77.3209 | 42.6544 | 123.2529 | 32.3044 | 47.5525
1551.4844 | 123.381 | -44.1513 | 79.0009 | -0.03479 | 0.0029117 | 0.042844 | 0.0032343 | 0.0016939 | 0.0011386 | -0.0028753 | -0.056793 | 0.00053628 | 0.0046848 | 0.041488 | -0.0034522 | -0.0018756 | -0.0020401 | -11.9522 | -1.355 | -44.426 | -1.6571 | -1.4648 | -44.371 | -1.5381 | 1.4786 | 79.0741 | 1.8494 | 79.097 | 2.2385 | 2.1011 | 2.2156 | -0.27466 | -80.3558 | -80.658 | 42.6865 | 42.6132 | -0.21973 | 42.8879 | 0.054931 | 46.0007 | 0.073243 | 0.096131 | 46.3898 | 46.3669 | 46.2524 | 0.36621 | 0.25177 | 42.9611 | 42.7689 | 0.3891 | 77.2476 | 43.071 | 77.2247 | 42.7963 | 123.2254 | -123.4268 | -77.1515 | 42.4942 | 123.2483 | 32.1991 | 45.6299
1552.5625 | 122.8043 | -44.1925 | 79.0329 | -0.401 | -0.0058469 | 0.038145 | -0.0021063 | -0.0064237 | -0.010611 | -0.010993 | -0.14529 | -0.0011727 | -0.0025784 | 0.029738 | -0.0047338 | -0.019393 | -0.00075834 | -12.0483 | -1.3641 | -44.5084 | -1.7487 | -1.6022 | -44.4717 | -1.6708 | 0.97504 | 79.129 | 1.8997 | 79.0466 | 2.2751 | 2.2659 | 2.3209 | -0.31586 | -80.397 | -80.7816 | 42.5903 | 42.5217 | -0.27924 | 42.8375 | 0.036621 | 46.0922 | 0.09613 | 0.013733 | 46.4676 | 46.5134 | 46.4584 | 0.42114 | 0.36621 | 42.9062 | 42.7597 | 0.37537 | 77.1469 | 43.1442 | 77.2293 | 42.8284 | 123.3215 | -123.5413 | -77.1332 | 42.4438 | 123.2391 | 32.1442 | 45.1675
1553.4844 | 123.4039 | -44.3115 | 78.8452 | 0.018616 | 0.0016299 | 0.043058 | 0.0013117 | 0.0016939 | 0.00028418 | 0.0018243 | 0.004242 | 0.0035269 | 0.00618 | 0.039352 | -0.002384 | -0.0027302 | -0.0024673 | -11.7691 | -1.4786 | -44.5404 | -1.7349 | -1.5884 | -44.4809 | -1.6205 | 1.0483 | 78.9642 | 1.6205 | 78.9734 | 2.0279 | 1.9272 | 1.9684 | -0.22888 | -80.3238 | -80.5801 | 42.7231 | 42.691 | -0.16937 | 42.9199 | 0.059509 | 45.932 | 0.11902 | 0.12817 | 46.3394 | 46.2799 | 46.2387 | 0.3479 | 0.3067 | 42.952 | 42.8055 | 0.40741 | 77.3529 | 43.0618 | 77.3438 | 42.8329 | 123.2758 | -123.3856 | -77.2247 | 42.5766 | 123.2849 | 32.5424 | 45.3598
1554.4844 | 123.3627 | -44.3573 | 78.8315 | -0.03479 | 0.0024845 | 0.043912 | 0.0025933 | 0.00062594 | 0.0022068 | -0.0015935 | -0.01712 | 0.0037405 | 0.0042574 | 0.03807 | -0.0025976 | 4.7018e-05 | -0.0035355 | -11.7966 | -1.4694 | -44.5953 | -1.8219 | -1.6663 | -44.5953 | -1.6937 | 1.0529 | 78.9047 | 1.5472 | 78.8544 | 1.886 | 1.7715 | 1.8448 | -0.23804 | -80.3009 | -80.6534 | 42.691 | 42.6636 | -0.23804 | 42.9016 | 0 | 45.9045 | 0.073242 | 0.022888 | 46.2433 | 46.2021 | 46.1288 | 0.29755 | 0.2243 | 42.9291 | 42.7734 | 0.33874 | 77.3071 | 43.1259 | 77.3575 | 42.8879 | 123.262 | -123.4268 | -77.2842 | 42.5354 | 123.2117 | 32.5607 | 45.4102
1555.5625 | 123.3627 | -44.3069 | 78.9139 | -0.0042723 | 0.0033389 | 0.044767 | 0.0019525 | -0.00022866 | -0.00014322 | -0.0018073 | -0.023224 | 0.0041679 | 0.005112 | 0.036788 | -0.0036658 | -0.0018756 | -0.00011754 | -11.1923 | -1.3779 | -44.5267 | -1.6663 | -1.506 | -44.3939 | -1.5747 | 1.0391 | 79.0054 | 1.5015 | 78.9459 | 1.8814 | 1.7395 | 1.8402 | -0.21973 | -80.2917 | -80.5801 | 42.8009 | 42.7322 | -0.086975 | 42.952 | 0.13275 | 45.8084 | 0.091553 | 0.032044 | 46.1884 | 46.1472 | 46.0464 | 0.33874 | 0.23804 | 43.0206 | 42.8604 | 0.37994 | 77.4445 | 43.1488 | 77.504 | 42.9291 | 123.3124 | -123.4406 | -77.4124 | 42.6407 | 123.2529 | 33.1146 | 45.3461
1556.4844 | 123.3856 | -44.2017 | 78.9688 | -0.011902 | 0.0048343 | 0.043699 | 0.0038751 | 0.0010531 | 0.0015658 | -0.0020209 | -0.0079652 | 0.0033133 | 0.0059664 | 0.042129 | -0.0004614 | -0.0018756 | -0.0026809 | -11.705 | -1.3733 | -44.4717 | -1.6846 | -1.5564 | -44.5038 | -1.5839 | 1.0483 | 79.0192 | 1.5564 | 79.01 | 2.0782 | 1.9135 | 2.0233 | -0.27008 | -80.3421 | -80.6534 | 42.6453 | 42.6178 | -0.30212 | 42.8879 | -0.032043 | 45.7581 | 0.050354 | 0.041199 | 46.2799 | 46.225 | 46.1151 | 0.46692 | 0.35706 | 42.9153 | 42.7872 | 0.52185 | 77.4536 | 43.0984 | 77.4628 | 42.8284 | 123.2208 | -123.4406 | -77.4124 | 42.5171 | 123.2117 | 32.4966 | 45.2499
1557.5625 | 123.317 | -44.2062 | 79.0421 | -0.60699 | -0.013965 | 0.033018 | -0.0070197 | 0.035447 | -0.010824 | 0.049889 | -0.13919 | -0.0043771 | -0.0055692 | 0.026107 | -0.0047338 | -0.006148 | 0.0011643 | -11.3892 | -1.3596 | -44.4946 | -1.7395 | -1.593 | -44.5862 | -1.68 | 0.96588 | 79.1061 | 1.7075 | 78.9734 | 2.1469 | 2.0737 | 2.179 | -0.28839 | -80.4016 | -80.7816 | 42.6132 | 42.5262 | -0.37994 | 42.8146 | -0.091553 | 45.9137 | 0.064087 | -0.068664 | 46.3531 | 46.3852 | 46.2799 | 0.4715 | 0.36621 | 42.9016 | 42.7551 | 0.43945 | 77.2659 | 43.1351 | 77.3987 | 42.8467 | 123.3124 | -123.5367 | -77.3346 | 42.4667 | 123.1796 | 32.8171 | 45.1721
1558.4844 | 123.4039 | -44.1879 | 78.9642 | -0.10345 | 0.0029117 | 0.044126 | 0.00045712 | -0.0030057 | 0.0015658 | -0.0033025 | -0.035431 | 0.0037405 | 0.0036166 | 0.040206 | -0.0011022 | -0.001662 | 0.0011643 | -11.5448 | -1.4099 | -44.426 | -1.7075 | -1.561 | -44.3802 | -1.6113 | 1.4557 | 79.1016 | 1.9775 | 79.1107 | 2.2522 | 2.1149 | 2.2247 | -0.23804 | -80.3741 | -80.6717 | 42.627 | 42.5766 | -0.19226 | 42.8146 | 0.045776 | 46.1655 | 0.13733 | 0.14649 | 46.4401 | 46.4127 | 46.3028 | 0.24719 | 0.13733 | 42.865 | 42.7185 | 0.27466 | 77.1332 | 43.0161 | 77.124 | 42.778 | 123.2895 | -123.3902 | -76.9867 | 42.4805 | 123.2986 | 32.6431 | 45.6436
1559.5625 | 123.3719 | -44.3436 | 78.8818 | -0.080566 | 0.0044071 | 0.043912 | 0.0015253 | -0.0012967 | 0.0019932 | 0.00075627 | -0.014069 | 0.0041679 | 0.004471 | 0.038497 | -0.0025976 | -0.0027302 | 0.0013779 | -11.1557 | -1.3138 | -44.5129 | -1.6296 | -1.5518 | -44.4992 | -1.6296 | 1.3 | 79.0054 | 1.4786 | 78.9139 | 1.7944 | 1.7258 | 1.7899 | -0.16937 | -80.1956 | -80.5115 | 42.7917 | 42.7139 | -0.15564 | 42.8833 | 0.013732 | 45.8221 | 0.1236 | 0.032043 | 46.138 | 46.1334 | 46.0693 | 0.31128 | 0.24719 | 42.9611 | 42.8833 | 0.31586 | 77.4353 | 43.1992 | 77.5269 | 43.0298 | 123.349 | -123.3948 | -77.4033 | 42.7139 | 123.2574 | 33.1879 | 45.6436
1560.4844 | 123.4131 | -44.2703 | 78.8727 | -0.019531 | 0.0039799 | 0.043699 | 0.0017389 | 0.0010531 | 0.0019932 | -0.0015935 | 0.004242 | 0.0022453 | 0.0038302 | 0.044051 | -0.0028112 | -0.0020892 | -0.00097194 | -11.0504 | -1.355 | -44.5129 | -1.6022 | -1.4603 | -44.4626 | -1.5106 | 1.2955 | 79.0146 | 1.5106 | 79.0192 | 1.9455 | 1.8265 | 1.8906 | -0.24261 | -80.2277 | -80.4749 | 42.8101 | 42.7597 | -0.19226 | 43.0023 | 0.050354 | 45.7809 | 0.14191 | 0.14648 | 46.2158 | 46.1609 | 46.0968 | 0.37994 | 0.31586 | 43.0527 | 42.9108 | 0.43488 | 77.5085 | 43.158 | 77.504 | 42.9153 | 123.2849 | -123.3856 | -77.3621 | 42.6682 | 123.2895 | 33.2199 | 45.5658
1561.4844 | 123.3856 | -44.2841 | 78.8818 | -0.042419 | 0.0022709 | 0.041135 | 0.0021661 | -0.0023649 | 0.0011386 | -9.8328e-05 | -0.023224 | 0.0039541 | 0.0066074 | 0.039565 | -0.000675 | -0.0031574 | 0.0013779 | -11.1832 | -1.3733 | -44.545 | -1.6708 | -1.5884 | -44.5679 | -1.6296 | 2.4216 | 78.9551 | 1.5656 | 78.9322 | 1.9089 | 1.8036 | 1.8768 | -0.26093 | -80.2551 | -80.5527 | 42.6956 | 42.6544 | -0.28381 | 42.9153 | -0.022888 | 45.8496 | 0.073242 | 0.050354 | 46.1929 | 46.1609 | 46.0876 | 0.31128 | 0.23804 | 42.9565 | 42.8741 | 0.34332 | 77.3666 | 43.1717 | 77.3895 | 42.9108 | 123.2391 | -123.4268 | -77.3163 | 42.6132 | 123.2162 | 33.1009 | 46.7056
1562.4844 | 123.3582 | -44.2154 | 79.01 | -0.03479 | 0.0050479 | 0.043058 | 0.0021661 | 0.00083954 | -0.00035682 | -0.0013799 | -0.029327 | 0.0033133 | 0.004471 | 0.041915 | -0.001316 | -0.0018756 | -0.0016129 | -11.3113 | -1.4557 | -44.4489 | -1.7441 | -1.6022 | -44.4855 | -1.6617 | 2.1194 | 79.0237 | 1.6937 | 78.9825 | 2.2522 | 2.0416 | 2.2064 | -0.23346 | -80.4657 | -80.7541 | 42.6132 | 42.5537 | -0.27008 | 42.7872 | -0.036621 | 45.9091 | 0.013733 | -0.027466 | 46.4676 | 46.4218 | 46.257 | 0.5127 | 0.3479 | 42.8467 | 42.7048 | 0.55847 | 77.2888 | 42.9932 | 77.33 | 42.7597 | 123.2391 | -123.4589 | -77.3163 | 42.4713 | 123.1979 | 32.9041 | 46.3348
1563.5469 | 123.3994 | -44.0002 | 79.184 | -0.088196 | 0.0026981 | 0.043912 | 0.0030207 | -0.00044226 | 0.0011386 | -0.00073913 | -0.072052 | 0.0026725 | 0.0055392 | 0.042556 | -0.0028112 | -0.00038018 | 0.00052346 | -11.3617 | -1.3916 | -44.3573 | -1.68 | -1.5427 | -44.4122 | -1.5884 | 2.0187 | 79.0833 | 1.8265 | 79.303 | 2.8564 | 2.8748 | 3.0167 | -0.35706 | -80.5756 | -80.864 | 42.4576 | 42.4118 | -0.41199 | 42.7689 | -0.054931 | 45.8267 | -0.10071 | 0.11902 | 46.8567 | 47.0169 | 46.875 | 1.1902 | 1.0483 | 42.8146 | 42.6773 | 1.03 | 77.4765 | 42.9657 | 77.2568 | 42.6086 | 123.0835 | -123.5413 | -77.3575 | 42.3203 | 123.3032 | 32.6386 | 46.019
1564.4844 | 123.3856 | -44.2474 | 78.9185 | -0.12634 | 0.0029117 | 0.040281 | 0.0015253 | 0.0010531 | 7.0582e-05 | -9.8328e-05 | -0.0049134 | 0.0018179 | 0.0036166 | 0.037215 | -0.0017432 | -0.00016658 | 0.0020187 | -11.4212 | -1.3596 | -44.4443 | -1.7029 | -1.5747 | -44.4672 | -1.593 | 1.8631 | 79.0375 | 1.6113 | 79.0237 | 1.9409 | 1.8265 | 1.8723 | -0.19684 | -80.278 | -80.6213 | 42.6727 | 42.6544 | -0.21973 | 42.8513 | -0.022888 | 45.8588 | 0.11902 | 0.10529 | 46.1884 | 46.1197 | 46.0739 | 0.26092 | 0.21515 | 42.8696 | 42.7414 | 0.32959 | 77.4124 | 43.0847 | 77.4261 | 42.8879 | 123.2849 | -123.3627 | -77.3071 | 42.5446 | 123.2712 | 32.8262 | 46.1105
1565.4844 | 123.4222 | -43.9316 | 79.2252 | -0.03479 | 0.0037661 | 0.043058 | 0.0036615 | -0.0015103 | 0.00092498 | -0.00052553 | -0.014069 | 0.0056631 | 0.005112 | 0.042342 | -0.0015296 | -0.0025164 | -0.00097194 | -11.2564 | -1.3824 | -44.1971 | -1.6937 | -1.561 | -44.252 | -1.561 | 2.8748 | 79.3945 | 2.6138 | 79.3533 | 3.1128 | 2.8564 | 2.9755 | -0.2655 | -80.6076 | -80.9189 | 42.3706 | 42.3706 | -0.32043 | 42.6361 | -0.054931 | 46.5454 | 0.16937 | 0.12817 | 47.0444 | 46.907 | 46.788 | 0.36163 | 0.24261 | 42.6361 | 42.5034 | 0.49896 | 76.7395 | 42.8146 | 76.7807 | 42.5491 | 123.3261 | -123.4222 | -76.6113 | 42.2379 | 123.2849 | 32.6752 | 46.8063
1566.5469 | 123.3215 | -44.2154 | 79.01 | -0.065308 | 0.0046207 | 0.044126 | 0.0034479 | -0.0015103 | 0.002634 | -0.0018073 | -0.10867 | 0.0037405 | 0.00618 | 0.03807 | -0.0025976 | -0.0010212 | -0.0018265 | -11.4304 | -1.3779 | -44.4855 | -1.8082 | -1.6983 | -44.4946 | -1.7166 | 2.4628 | 79.1656 | 1.8906 | 79.0283 | 2.1698 | 2.0004 | 2.1652 | -0.27008 | -80.3879 | -80.8182 | 42.5171 | 42.4988 | -0.27924 | 42.7689 | -0.009155 | 46.106 | 0.15564 | 0.01831 | 46.3852 | 46.3806 | 46.2158 | 0.27466 | 0.10986 | 42.7872 | 42.6773 | 0.27924 | 77.1378 | 43.1076 | 77.2751 | 42.8375 | 123.381 | -123.4955 | -77.1194 | 42.4072 | 123.2437 | 32.785 | 46.6782
1567.5 | 123.3627 | -43.927 | 79.2068 | -0.050049 | 0.0048343 | 0.043058 | 0.0019525 | -0.00065586 | 0.0030612 | -0.0033025 | -0.026276 | 0.0026725 | 0.0027622 | 0.03572 | -0.0021704 | -0.00080758 | -0.0041763 | -11.38 | -1.4145 | -44.2657 | -1.6937 | -1.5335 | -44.2154 | -1.5976 | 2.4445 | 79.3076 | 2.4307 | 79.303 | 2.8198 | 2.7786 | 2.829 | -0.33874 | -80.6213 | -80.9006 | 42.3935 | 42.3294 | -0.28839 | 42.6682 | 0.050354 | 46.3577 | 0.10071 | 0.096131 | 46.7468 | 46.756 | 46.7056 | 0.39825 | 0.3479 | 42.7322 | 42.572 | 0.3891 | 76.8723 | 42.8513 | 76.8768 | 42.5125 | 123.2346 | -123.4726 | -76.7761 | 42.2333 | 123.23 | 32.547 | 46.3715
1568.4844 | 123.3765 | -44.1788 | 78.9734 | -0.11108 | 0.0037661 | 0.043272 | 0.0040887 | 0.0042575 | -0.0012112 | -0.0035163 | -0.059845 | 0.0033133 | 0.0038302 | 0.04106 | -0.0034522 | -0.0018756 | 0.0039413 | -11.4029 | -1.4328 | -44.458 | -1.7258 | -1.5793 | -44.458 | -1.6388 | 2.7969 | 79.0649 | 1.8631 | 79.0787 | 2.211 | 2.1011 | 2.1927 | -0.27924 | -80.4062 | -80.6992 | 42.5995 | 42.54 | -0.27924 | 42.8192 | 0 | 46.0419 | 0.091552 | 0.10529 | 46.3898 | 46.3715 | 46.2799 | 0.32959 | 0.23804 | 42.8787 | 42.7322 | 0.3479 | 77.2156 | 43.0252 | 77.2018 | 42.746 | 123.2437 | -123.4314 | -77.1103 | 42.453 | 123.2574 | 32.7759 | 46.9757
1569.4844 | 123.4268 | -44.2703 | 78.8864 | -0.011902 | 0.0046207 | 0.043912 | 0.0034479 | -0.0032193 | 0.00092498 | -0.0011663 | -0.0079652 | 0.0041679 | 0.005112 | 0.04341 | -0.0038794 | -0.003371 | 9.6064e-05 | -11.5356 | -1.4877 | -44.5587 | -1.7395 | -1.5701 | -44.4122 | -1.6388 | 2.4445 | 78.9963 | 1.6663 | 79.0237 | 2.0737 | 1.973 | 1.9867 | -0.28839 | -80.3741 | -80.6259 | 42.7002 | 42.6315 | -0.14191 | 42.9199 | 0.14648 | 45.9366 | 0.10986 | 0.13733 | 46.344 | 46.257 | 46.2433 | 0.32043 | 0.3067 | 42.9886 | 42.8192 | 0.40741 | 77.3575 | 43.071 | 77.33 | 42.7826 | 123.2666 | -123.4451 | -77.2202 | 42.5308 | 123.2941 | 32.7347 | 46.7148
1570.5625 | 123.4085 | -44.2886 | 78.8956 | -0.088196 | 0.0056889 | 0.04199 | 0.0025933 | -0.0034329 | 0.0013522 | -0.0022345 | -0.0079652 | 0.0043815 | 0.0076754 | 0.038711 | -0.0015296 | -0.003371 | -0.0031081 | -11.911 | -1.506 | -44.6091 | -1.8173 | -1.6983 | -44.5862 | -1.7258 | 2.7145 | 78.978 | 1.4832 | 78.9459 | 1.9089 | 1.8173 | 1.8951 | -0.32044 | -80.4016 | -80.7129 | 42.5903 | 42.5629 | -0.29755 | 42.8833 | 0.022888 | 45.7718 | 0.082397 | 0.050354 | 46.1975 | 46.1838 | 46.106 | 0.41199 | 0.33417 | 42.9108 | 42.7917 | 0.42572 | 77.4628 | 43.103 | 77.4948 | 42.7826 | 123.2666 | -123.5046 | -77.4124 | 42.4713 | 123.2346 | 32.3776 | 47.0032
1571.4844 | 123.4268 | -44.1788 | 78.9642 | -0.10345 | 0.0037661 | 0.043699 | 0.0025933 | 0.0025485 | 7.0582e-05 | -0.00073913 | -0.0079652 | 0.0048087 | 0.0046848 | 0.04042 | -3.4196e-05 | -0.0029438 | 0.00095066 | -11.824 | -1.4648 | -44.4397 | -1.7807 | -1.6571 | -44.4443 | -1.6617 | 1.6067 | 79.1245 | 1.8173 | 79.0924 | 2.2751 | 2.0828 | 2.1606 | -0.26093 | -80.4291 | -80.7449 | 42.5217 | 42.5171 | -0.2655 | 42.778 | -0.004578 | 45.9961 | 0.16022 | 0.12817 | 46.4539 | 46.3394 | 46.2616 | 0.34332 | 0.2655 | 42.7826 | 42.659 | 0.45776 | 77.2751 | 42.9749 | 77.3071 | 42.7139 | 123.3032 | -123.4039 | -77.1469 | 42.3981 | 123.2712 | 32.3547 | 45.7855
1572.5625 | 123.3032 | -44.1788 | 79.0695 | 0.0033567 | 0.0041935 | 0.043912 | 0.0040887 | 0.0021213 | -0.0014248 | -0.0024481 | -0.075104 | 0.0058767 | 0.006821 | 0.045333 | -0.0025976 | -0.0014484 | -0.0024673 | -11.8057 | -1.4557 | -44.5358 | -1.8539 | -1.7624 | -44.4626 | -1.7715 | 1.6342 | 79.0878 | 1.7944 | 79.0421 | 2.2568 | 2.1927 | 2.1606 | -0.35706 | -80.5252 | -80.9235 | 42.4164 | 42.4072 | -0.28381 | 42.7643 | 0.073243 | 45.9732 | 0.018311 | -0.027466 | 46.4355 | 46.3394 | 46.3715 | 0.36621 | 0.39825 | 42.7734 | 42.6819 | 0.46234 | 77.2476 | 43.0801 | 77.2934 | 42.7231 | 123.2666 | -123.6053 | -77.2751 | 42.3248 | 123.2208 | 32.373 | 45.813
1573.4844 | 123.3856 | -44.252 | 78.9413 | -0.042419 | 0.0041935 | 0.041135 | 0.0025933 | -1.486e-05 | 0.00071138 | -0.0011663 | 0.0011902 | 0.0039541 | 0.0040438 | 0.034652 | -0.0036658 | -0.00080758 | -0.00054474 | -11.705 | -1.4877 | -44.4717 | -1.8219 | -1.68 | -44.4305 | -1.7166 | 1.8677 | 79.0833 | 1.9272 | 79.0054 | 2.0966 | 1.9501 | 2.0645 | -0.21973 | -80.4291 | -80.7632 | 42.572 | 42.5354 | -0.17853 | 42.7551 | 0.041199 | 46.1792 | 0.14191 | 0.064087 | 46.3486 | 46.3165 | 46.2021 | 0.13733 | 0.022888 | 42.7917 | 42.6498 | 0.16937 | 77.0782 | 42.984 | 77.1561 | 42.7643 | 123.3353 | -123.4131 | -77.0142 | 42.4301 | 123.2574 | 32.547 | 46.1197
1574.5469 | 123.2849 | -44.101 | 79.097 | -0.019531 | 0.00077547 | 0.044981 | -0.00061088 | -0.014328 | -0.00035682 | -0.0097113 | -0.13614 | 0.0033133 | 0.0055392 | 0.038711 | -0.0002478 | -0.012984 | 0.00052346 | -11.6364 | -1.4694 | -44.4855 | -1.8768 | -1.7624 | -44.4305 | -1.8082 | 2.2659 | 79.2435 | 2.1286 | 78.9871 | 2.33 | 2.1149 | 2.2797 | -0.38452 | -80.5664 | -80.9738 | 42.3386 | 42.2928 | -0.32959 | 42.6773 | 0.054932 | 46.2296 | 0.14648 | -0.10986 | 46.431 | 46.3806 | 46.2158 | 0.15106 | -0.013733 | 42.7231 | 42.6086 | 0.20142 | 76.8585 | 43.0161 | 77.1149 | 42.6315 | 123.3444 | -123.5825 | -76.9684 | 42.2241 | 123.0881 | 32.4646 | 46.3669
1575.4844 | 123.4314 | -44.1879 | 78.9871 | -0.0042723 | 0.0046207 | 0.044553 | 0.0010981 | -0.0015103 | -0.00078402 | -9.8328e-05 | 0.019501 | 0.0028861 | 0.0040438 | 0.036147 | -3.4196e-05 | -0.0023028 | 0.00073706 | -11.9339 | -1.4832 | -44.545 | -1.8173 | -1.6525 | -44.4443 | -1.6708 | 1.9226 | 79.0512 | 1.7075 | 79.0833 | 2.2385 | 2.1469 | 2.179 | -0.35706 | -80.4703 | -80.8044 | 42.5354 | 42.5171 | -0.25635 | 42.8741 | 0.10071 | 45.8954 | 0.064086 | 0.09613 | 46.4264 | 46.3669 | 46.3348 | 0.4715 | 0.43945 | 42.8925 | 42.7277 | 0.53101 | 77.3758 | 43.0618 | 77.3438 | 42.7048 | 123.2391 | -123.5321 | -77.2797 | 42.3706 | 123.2712 | 32.254 | 46.1105
1576.4844 | 123.4039 | -44.2154 | 78.9139 | -0.088196 | 0.0048343 | 0.042844 | 0.0025933 | 0.0021213 | 0.0011386 | 0.00032907 | -0.053741 | 0.0020315 | 0.0059664 | 0.039138 | -0.0019568 | 4.7018e-05 | 0.0022323 | -11.8378 | -1.5015 | -44.4901 | -1.7899 | -1.6251 | -44.4901 | -1.7029 | 1.9363 | 79.0329 | 1.6937 | 79.0466 | 2.1011 | 1.9501 | 2.0508 | -0.27466 | -80.4153 | -80.7037 | 42.5903 | 42.5125 | -0.27466 | 42.7872 | 0 | 45.9091 | 0.11902 | 0.13275 | 46.3165 | 46.2662 | 46.1655 | 0.35706 | 0.25635 | 42.865 | 42.7002 | 0.40741 | 77.3529 | 42.9886 | 77.3392 | 42.7139 | 123.2483 | -123.4039 | -77.2202 | 42.4255 | 123.262 | 32.3776 | 46.1517
1577.5625 | 123.3032 | -44.3527 | 78.8864 | -0.0042723 | 0.0029117 | 0.043699 | 0.0038751 | -0.0092007 | -0.00035682 | -0.017188 | -0.13004 | 0.0045951 | 0.0059664 | 0.035293 | -0.0011022 | -0.015334 | 0.0015915 | -11.998 | -1.506 | -44.6274 | -1.9135 | -1.8127 | -44.696 | -1.8631 | 2.1194 | 79.0054 | 1.4786 | 78.8727 | 1.7303 | 1.5472 | 1.7212 | -0.27466 | -80.3925 | -80.7999 | 42.54 | 42.4896 | -0.34332 | 42.7643 | -0.068665 | 45.8313 | 0.11902 | -0.013733 | 46.0831 | 46.0739 | 45.9 | 0.24261 | 0.068664 | 42.8146 | 42.7139 | 0.25177 | 77.3941 | 43.1213 | 77.5269 | 42.8467 | 123.3582 | -123.5138 | -77.4078 | 42.4393 | 123.2254 | 32.3547 | 46.4722
1578.4844 | 123.4268 | -44.101 | 79.0466 | -0.042419 | 0.0033389 | 0.043699 | 0.0010981 | 0.0016939 | 0.0022068 | -0.00095273 | -0.035431 | 0.0035269 | 0.0042574 | 0.040206 | -0.003025 | -0.0018756 | 9.6064e-05 | -11.8927 | -1.5335 | -44.2245 | -1.8219 | -1.68 | -44.252 | -1.7624 | 1.6434 | 79.2114 | 2.5314 | 79.2389 | 2.71 | 2.9114 | 2.7969 | -0.1236 | -80.5801 | -80.8685 | 42.421 | 42.3386 | -0.15106 | 42.4622 | -0.027466 | 46.6324 | 0.16479 | 0.19226 | 46.8109 | 46.8979 | 47.0123 | 0.2655 | 0.37994 | 42.5446 | 42.4026 | 0.17853 | 76.7075 | 42.691 | 76.68 | 42.5674 | 123.3124 | -123.2712 | -76.5152 | 42.2791 | 123.3398 | 32.2083 | 45.7443
1579.5 | 123.2758 | -44.5496 | 78.7399 | -0.019531 | 0.0050479 | 0.042203 | 0.0053705 | -0.0017239 | -0.0012112 | -0.0082159 | -0.10257 | 0.0037405 | 0.003403 | 0.048965 | -0.000675 | -0.0072162 | -0.0016129 | -12.1582 | -1.5152 | -44.5953 | -1.9501 | -1.8356 | -44.7098 | -1.8951 | 1.8127 | 79.0192 | 1.5335 | 78.8361 | 1.7853 | 1.5335 | 1.7532 | -0.045776 | -80.2551 | -80.69 | 42.7139 | 42.6544 | -0.16022 | 42.7002 | -0.11444 | 46.0831 | 0.27924 | 0.096131 | 46.3348 | 46.3028 | 46.0831 | 0.21973 | 0 | 42.7597 | 42.6453 | 0.25177 | 77.3026 | 43.0801 | 77.4857 | 43.0344 | 123.5687 | -123.3353 | -77.2064 | 42.5995 | 123.3856 | 32.3914 | 46.3623
1580.5469 | 123.3215 | -44.2062 | 78.9871 | -0.027161 | 0.0033389 | 0.043272 | 0.0030207 | 0.0053255 | 0.0013522 | 0.0039607 | -0.096466 | 0.0045951 | 0.0042574 | 0.04341 | -0.0038794 | -0.00016658 | -0.00033114 | -12.0712 | -1.4832 | -44.2932 | -1.9135 | -1.8173 | -44.4855 | -1.8539 | 1.6983 | 79.2068 | 2.1881 | 79.0878 | 2.3666 | 2.1057 | 2.2522 | -0.086975 | -80.4703 | -80.9006 | 42.3889 | 42.3523 | -0.27924 | 42.4393 | -0.19226 | 46.3943 | 0.21973 | 0.10071 | 46.5729 | 46.4584 | 46.312 | 0.064087 | -0.082397 | 42.4759 | 42.3798 | 0.17853 | 76.8997 | 42.8101 | 77.0187 | 42.7231 | 123.4131 | -123.2803 | -76.799 | 42.2928 | 123.2941 | 32.135 | 45.9045
1581.4844 | 123.3994 | -44.3253 | 78.8406 | 0.010986 | 0.0050479 | 0.042631 | 2.9918e-05 | -0.0034329 | 0.0015658 | -0.0018073 | 0.016449 | 0.0020315 | 0.0031894 | 0.03572 | -0.0015296 | -0.00059378 | 0.0022323 | -12.0483 | -1.5244 | -44.5953 | -1.8723 | -1.7349 | -44.5496 | -1.7395 | 1.8448 | 78.9688 | 1.5335 | 78.9642 | 1.9775 | 1.8265 | 1.9135 | -0.27008 | -80.365 | -80.7129 | 42.5903 | 42.5858 | -0.2243 | 42.8558 | 0.045776 | 45.8588 | 0.12817 | 0.1236 | 46.3028 | 46.2387 | 46.1517 | 0.37994 | 0.29297 | 42.8604 | 42.7231 | 0.44403 | 77.4307 | 43.071 | 77.4353 | 42.8009 | 123.2941 | -123.436 | -77.3071 | 42.453 | 123.2895 | 32.2769 | 46.17
1582.4844 | 123.3856 | -44.2062 | 78.9734 | -0.065308 | 0.0041935 | 0.040708 | 0.0032343 | -0.0042875 | 0.00071138 | -0.0011663 | 0.016449 | 0.0028861 | 0.0040438 | 0.037429 | -0.0025976 | -0.0031574 | 0.00030966 | -12.0255 | -1.5198 | -44.3756 | -1.8631 | -1.7258 | -44.4305 | -1.7441 | 1.5884 | 79.1336 | 2.0828 | 79.0558 | 2.2064 | 2.243 | 2.2568 | -0.16937 | -80.4932 | -80.8365 | 42.4805 | 42.4622 | -0.2243 | 42.6315 | -0.054932 | 46.2891 | 0.16022 | 0.082397 | 46.4127 | 46.463 | 46.4493 | 0.17395 | 0.16022 | 42.6498 | 42.5125 | 0.1236 | 76.973 | 42.8558 | 77.0508 | 42.6865 | 123.3398 | -123.349 | -76.8906 | 42.3431 | 123.262 | 32.1808 | 45.7947
1583.4844 | 123.4131 | -44.2703 | 78.8956 | -0.080566 | 0.0029117 | 0.043912 | 0.0015253 | -0.0012967 | 0.0013522 | -0.00031193 | 0.013397 | 0.0033133 | 0.0048984 | 0.031875 | -0.0032386 | -0.003371 | 0.0013779 | -12.0941 | -1.5656 | -44.5221 | -1.8723 | -1.6983 | -44.4855 | -1.7349 | 1.9592 | 78.9871 | 1.6754 | 79.0237 | 2.1057 | 1.9867 | 2.0645 | -0.25177 | -80.4611 | -80.7678 | 42.572 | 42.5354 | -0.21515 | 42.7872 | 0.036621 | 45.9457 | 0.091553 | 0.12817 | 46.376 | 46.3348 | 46.257 | 0.3891 | 0.31128 | 42.8238 | 42.6498 | 0.4303 | 77.3483 | 42.9565 | 77.3117 | 42.7048 | 123.2574 | -123.4177 | -77.2202 | 42.3981 | 123.2941 | 32.1762 | 46.2296
1584.5625 | 123.3261 | -44.2886 | 78.9597 | -0.050049 | 0.0022709 | 0.044767 | 0.0034479 | -0.0030057 | 7.0582e-05 | -0.00052553 | -0.05069 | 0.0041679 | 0.0029758 | 0.040633 | -0.0034522 | -0.0018756 | -0.00075834 | -11.9202 | -1.5198 | -44.2703 | -1.918 | -1.767 | -44.545 | -1.8036 | 1.9363 | 79.0741 | 1.9455 | 78.9459 | 2.092 | 1.9272 | 2.0508 | 0.01831 | -80.4794 | -80.8777 | 42.5217 | 42.485 | -0.25635 | 42.4667 | -0.27466 | 46.2341 | 0.11444 | -0.013733 | 46.3806 | 46.3394 | 46.2158 | 0.10529 | -0.018311 | 42.5034 | 42.3523 | 0.14648 | 77.0004 | 42.7505 | 77.1286 | 42.7689 | 123.3627 | -123.23 | -77.0142 | 42.3706 | 123.2346 | 32.3685 | 46.225
1585.4844 | 123.436 | -44.1605 | 78.9734 | -0.03479 | 0.0052615 | 0.042417 | 0.0036615 | 0.0014803 | -0.001852 | -0.0022345 | 0.0072936 | 0.0052359 | 0.0040438 | 0.035934 | -0.002384 | -0.003371 | -0.0011855 | -12.0438 | -1.5381 | -44.4717 | -1.8173 | -1.6525 | -44.4214 | -1.6846 | 1.5701 | 79.0421 | 1.7899 | 79.097 | 2.1835 | 2.092 | 2.1652 | -0.31128 | -80.5115 | -80.7907 | 42.5079 | 42.4759 | -0.26093 | 42.7872 | 0.050354 | 45.9503 | 0.068664 | 0.1236 | 46.344 | 46.3257 | 46.2524 | 0.37537 | 0.30212 | 42.8192 | 42.6544 | 0.39368 | 77.3071 | 42.9337 | 77.2522 | 42.6224 | 123.2025 | -123.4451 | -77.1835 | 42.3431 | 123.2574 | 32.1167 | 45.7306
1586.5469 | 123.3948 | -43.9041 | 79.2526 | -0.11108 | 0.0031253 | 0.04434 | 0.0045159 | -0.0019377 | -0.00057042 | -0.0022345 | -0.023224 | 0.0013907 | 0.0053256 | 0.039138 | -0.0028112 | -0.00059378 | 0.0024461 | -11.8744 | -1.5015 | -44.1284 | -1.8036 | -1.6479 | -44.2886 | -1.7166 | 1.3733 | 79.3121 | 2.6184 | 79.3991 | 2.9114 | 3.2547 | 3.4378 | -0.2243 | -80.7541 | -81.0562 | 42.2562 | 42.1875 | -0.38452 | 42.4118 | -0.16022 | 46.5225 | 0.059509 | 0.14648 | 46.8155 | 47.3419 | 47.1588 | 0.8194 | 0.63629 | 42.4805 | 42.3248 | 0.29297 | 76.7807 | 42.627 | 76.6937 | 42.4026 | 123.2162 | -123.381 | -76.6342 | 42.1005 | 123.3032 | 32.0297 | 45.2774
1587.5 | 123.3261 | -44.3253 | 78.9093 | -0.011902 | 0.0035525 | 0.042417 | 0.0028069 | 0.0029757 | 0.0015658 | 0.00032907 | -0.05069 | 0.0028861 | 0.0048984 | 0.039565 | -0.0034522 | -0.0018756 | -0.0020401 | -11.7508 | -1.506 | -44.5084 | -1.9501 | -1.799 | -44.6091 | -1.8173 | 1.1124 | 79.0421 | 1.6937 | 78.8864 | 1.8631 | 1.7899 | 1.8539 | -0.18311 | -80.4153 | -80.8594 | 42.5262 | 42.5079 | -0.28381 | 42.691 | -0.10071 | 46.019 | 0.13275 | -0.022888 | 46.1884 | 46.1792 | 46.1151 | 0.16022 | 0.09613 | 42.7094 | 42.5583 | 0.16937 | 77.1927 | 43.0023 | 77.3483 | 42.8192 | 123.3673 | -123.4177 | -77.2156 | 42.3752 | 123.2117 | 32.5745 | 45.4376
1588.4844 | 123.4314 | -44.2383 | 78.891 | -0.11871 | 0.0033389 | 0.044767 | 0.0010981 | 0.00019874 | 0.0015658 | -0.00031193 | -0.05069 | 0.0024589 | 0.0046848 | 0.04341 | -0.0038794 | -0.001662 | -0.0020401 | -11.6226 | -1.5564 | -44.339 | -1.8127 | -1.6754 | -44.5175 | -1.7441 | 2.3895 | 79.0054 | 1.7532 | 79.0604 | 2.1332 | 2.0966 | 2.1057 | -0.10071 | -80.4474 | -80.7037 | 42.5629 | 42.4942 | -0.27924 | 42.5949 | -0.17853 | 45.9915 | 0.11444 | 0.16937 | 46.3715 | 46.344 | 46.3348 | 0.35248 | 0.34332 | 42.6636 | 42.5262 | 0.37994 | 77.3071 | 42.7826 | 77.2522 | 42.6819 | 123.2437 | -123.23 | -77.1378 | 42.4255 | 123.2986 | 32.6157 | 46.6278
1589.5625 | 123.3124 | -44.3069 | 78.9459 | 0.018616 | 0.0037661 | 0.042631 | 0.0030207 | -0.00065586 | 0.0015658 | 0.0011835 | -0.038483 | 0.0041679 | 0.0023348 | 0.042556 | -0.0034522 | -0.0010212 | 0.0015915 | -11.5723 | -1.4923 | -44.5404 | -1.8997 | -1.7532 | -44.545 | -1.7807 | 1.4603 | 79.0375 | 1.5656 | 78.9139 | 1.9684 | 1.8402 | 1.9226 | -0.23346 | -80.4382 | -80.8456 | 42.5537 | 42.5262 | -0.23804 | 42.7597 | -0.004578 | 45.8725 | 0.091553 | -0.032044 | 46.2753 | 46.2296 | 46.1472 | 0.35705 | 0.27466 | 42.7872 | 42.6407 | 0.40283 | 77.3483 | 43.0481 | 77.4719 | 42.8146 | 123.3444 | -123.4863 | -77.3804 | 42.4072 | 123.2208 | 32.7347 | 45.7672
1590.4844 | 123.3994 | -44.2749 | 78.9185 | -0.12634 | 0.0026981 | 0.04199 | 0.0013117 | 0.00062594 | 0.002634 | -0.0024481 | -0.020172 | 0.0045951 | 0.0072482 | 0.037643 | -0.0028112 | -0.0018756 | -0.0011855 | -11.2518 | -1.5198 | -44.5221 | -1.8539 | -1.7303 | -44.5496 | -1.7395 | 1.9547 | 79.0283 | 1.6617 | 78.9825 | 2.0187 | 1.8768 | 1.973 | -0.24719 | -80.4382 | -80.7724 | 42.5446 | 42.5354 | -0.27466 | 42.7826 | -0.027466 | 45.9366 | 0.10986 | 0.064087 | 46.2936 | 46.2479 | 46.1517 | 0.31128 | 0.21515 | 42.7917 | 42.6682 | 0.35706 | 77.3209 | 43.0023 | 77.3666 | 42.7551 | 123.3032 | -123.4406 | -77.2568 | 42.421 | 123.2574 | 33.0231 | 46.2296
1591.5469 | 123.3078 | -44.2612 | 79.0146 | -0.0042723 | 0.0048343 | 0.044981 | 0.0045159 | -0.0064237 | 0.0017794 | -0.010352 | -0.11172 | 0.0056631 | 0.00618 | 0.037215 | 0.0014612 | -0.014479 | -0.00033114 | -11.3297 | -1.5015 | -44.5129 | -1.9409 | -1.8219 | -44.5633 | -1.8631 | 1.5015 | 79.097 | 1.8082 | 78.9368 | 2.1103 | 2.1194 | 2.1286 | -0.25177 | -80.5161 | -80.9555 | 42.4393 | 42.3981 | -0.30212 | 42.6498 | -0.050354 | 46.0693 | 0.082398 | -0.077819 | 46.3715 | 46.3898 | 46.3806 | 0.32043 | 0.31128 | 42.691 | 42.572 | 0.30212 | 77.1286 | 43.0115 | 77.2888 | 42.7597 | 123.3582 | -123.5275 | -77.2064 | 42.3203 | 123.1979 | 32.9315 | 45.7626
1592.4844 | 123.4451 | -44.2245 | 78.9413 | -0.057678 | 0.0050479 | 0.042203 | 0.0028069 | -0.00044226 | -0.002493 | -0.00073913 | 0.0072936 | 0.0016043 | 0.0048984 | 0.038497 | -0.0011022 | -0.0044392 | 0.00030966 | -11.2885 | -1.5106 | -44.458 | -1.8311 | -1.6846 | -44.4672 | -1.7029 | 1.5289 | 79.0604 | 1.7944 | 79.0283 | 2.1515 | 2.0508 | 2.0828 | -0.23346 | -80.452 | -80.7724 | 42.54 | 42.5217 | -0.24262 | 42.7551 | -0.009155 | 46.019 | 0.11902 | 0.086975 | 46.376 | 46.3074 | 46.2753 | 0.28839 | 0.25635 | 42.7734 | 42.627 | 0.35706 | 77.2339 | 42.9474 | 77.2659 | 42.7139 | 123.2849 | -123.3994 | -77.1469 | 42.3935 | 123.2529 | 32.9361 | 45.7535
1593.4844 | 123.4543 | -44.2154 | 78.9551 | -0.019531 | 0.0041935 | 0.04434 | 0.0017389 | -0.0015103 | 7.0582e-05 | -0.0024481 | -0.011017 | 0.0022453 | 0.005112 | 0.039992 | -0.0028112 | -0.0023028 | -0.00075834 | -11.5036 | -1.5244 | -44.4855 | -1.8448 | -1.6983 | -44.4809 | -1.712 | 1.561 | 79.0558 | 1.6388 | 79.0558 | 2.0325 | 1.8951 | 1.9638 | -0.27008 | -80.4794 | -80.7999 | 42.5171 | 42.5034 | -0.2655 | 42.7734 | 0.004578 | 45.8542 | 0.10071 | 0.10071 | 46.2479 | 46.1792 | 46.1105 | 0.32501 | 0.25635 | 42.7872 | 42.6407 | 0.39368 | 77.417 | 42.9611 | 77.417 | 42.691 | 123.2712 | -123.4406 | -77.3163 | 42.3706 | 123.2712 | 32.7118 | 45.7764
1594.5625 | 123.381 | -44.2749 | 78.9551 | -0.050049 | 0.0035525 | 0.042844 | 0.0038751 | -0.0040739 | 0.0019932 | 0.00054267 | -0.011017 | 0.0041679 | 0.0040438 | 0.044051 | -0.0028112 | -0.0029438 | 9.6064e-05 | -11.4258 | -1.5427 | -44.5358 | -1.8631 | -1.7212 | -44.5541 | -1.7441 | 1.3412 | 79.0237 | 1.5472 | 78.9963 | 1.8997 | 1.7899 | 1.8814 | -0.26093 | -80.4977 | -80.8182 | 42.5537 | 42.5308 | -0.27924 | 42.7917 | -0.01831 | 45.8221 | 0.068665 | 0.041199 | 46.1746 | 46.1563 | 46.0648 | 0.33417 | 0.24261 | 42.8146 | 42.6727 | 0.35248 | 77.449 | 42.9932 | 77.4765 | 42.7322 | 123.2986 | -123.4909 | -77.4078 | 42.4118 | 123.2712 | 32.8491 | 45.6161
1595.4844 | 123.3856 | -44.2841 | 78.8773 | -0.050049 | 0.0033389 | 0.043485 | 0.0030207 | 0.00062594 | 0.00071138 | -0.00095273 | -0.0079652 | 0.0037405 | 0.0025484 | 0.039992 | -0.002384 | -0.0012348 | -0.0058853 | -11.4578 | -1.5335 | -44.5496 | -1.8677 | -1.7303 | -44.5816 | -1.7578 | 1.3184 | 78.9551 | 1.474 | 78.9551 | 1.8356 | 1.6663 | 1.7899 | -0.2655 | -80.4108 | -80.7449 | 42.5537 | 42.5262 | -0.29755 | 42.7917 | -0.032043 | 45.7581 | 0.07782 | 0.07782 | 46.1197 | 46.0739 | 45.9503 | 0.31586 | 0.19226 | 42.8192 | 42.6819 | 0.36163 | 77.4811 | 43.0161 | 77.4811 | 42.7506 | 123.2391 | -123.4268 | -77.4033 | 42.4164 | 123.2391 | 32.8262 | 45.6024
1596.4844 | 123.4268 | -43.8812 | 79.2709 | -0.03479 | 0.0054751 | 0.041135 | 0.0038751 | -0.00044226 | 0.0015658 | 0.00011527 | -0.069 | 0.0033133 | 0.0063938 | 0.039565 | -0.0019568 | -0.001662 | -0.0016129 | -11.4441 | -1.5335 | -44.2291 | -1.8082 | -1.6571 | -44.2474 | -1.7166 | 1.3138 | 79.335 | 2.6001 | 79.4266 | 3.2135 | 3.0258 | 3.186 | -0.3479 | -80.8044 | -81.0791 | 42.2241 | 42.1646 | -0.36621 | 42.5125 | -0.018311 | 46.4813 | 0.064087 | 0.15564 | 47.0947 | 47.0673 | 46.907 | 0.58594 | 0.42572 | 42.572 | 42.421 | 0.6134 | 76.8265 | 42.6956 | 76.7349 | 42.3477 | 123.2162 | -123.5001 | -76.6708 | 42.0731 | 123.3078 | 32.4371 | 45.195
1597.5 | 123.3215 | -44.22 | 79.0375 | 0.0033567 | 0.0029117 | 0.041776 | 0.0040887 | -0.0015103 | 0.0013522 | 0.0011835 | -0.032379 | 0.0024589 | 0.0042574 | 0.039779 | -0.002384 | -0.0020892 | -0.0033219 | -11.5036 | -1.5427 | -44.4168 | -1.9043 | -1.7715 | -44.4351 | -1.8265 | 1.2634 | 79.1702 | 1.9547 | 79.01 | 2.2018 | 2.0462 | 2.1011 | -0.19684 | -80.5801 | -80.9418 | 42.4484 | 42.3935 | -0.21515 | 42.5903 | -0.018311 | 46.1746 | 0.13275 | -0.027466 | 46.4218 | 46.3211 | 46.2662 | 0.14648 | 0.091553 | 42.6453 | 42.5125 | 0.24719 | 77.0554 | 42.8741 | 77.2156 | 42.6773 | 123.3902 | -123.4543 | -77.0828 | 42.3157 | 123.23 | 32.7164 | 45.4834
1598.4844 | 123.4314 | -44.2932 | 78.8727 | -0.12634 | 0.0031253 | 0.044126 | 0.0038751 | 0.0016939 | 0.0013522 | -0.00073913 | -0.075104 | 0.0022453 | 0.0072482 | 0.039565 | -0.0034522 | -0.0010212 | 0.00030966 | -10.9451 | -1.5701 | -44.5312 | -1.8402 | -1.6891 | -44.5724 | -1.7715 | 1.3275 | 78.9825 | 1.5747 | 78.9825 | 1.9684 | 1.8631 | 1.9547 | -0.23804 | -80.4428 | -80.7129 | 42.6041 | 42.5217 | -0.27924 | 42.7597 | -0.041199 | 45.8679 | 0.10986 | 0.10986 | 46.2616 | 46.2479 | 46.1563 | 0.37994 | 0.28839 | 42.8421 | 42.691 | 0.39368 | 77.4078 | 42.9611 | 77.4078 | 42.7231 | 123.2758 | -123.4039 | -77.298 | 42.453 | 123.2758 | 33.3481 | 45.6207
1599.5625 | 123.3353 | -44.2795 | 78.9825 | -0.011902 | 0.0020573 | 0.041776 | 0.0036615 | -0.00044226 | 0.00049778 | 0.0013971 | -0.035431 | 0.00096348 | 0.0031894 | 0.038497 | -0.002384 | 0.00068782 | 0.0024461 | -11.0504 | -1.5381 | -44.4992 | -1.9363 | -1.7853 | -44.5724 | -1.8036 | 1.1627 | 79.129 | 1.6983 | 78.9505 | 2.005 | 1.8906 | 1.9638 | -0.21973 | -80.5206 | -80.9189 | 42.4942 | 42.4759 | -0.29297 | 42.6956 | -0.073242 | 45.9778 | 0.14648 | -0.032044 | 46.2845 | 46.2433 | 46.17 | 0.2655 | 0.19226 | 42.7139 | 42.5629 | 0.3067 | 77.2522 | 42.9611 | 77.4307 | 42.7414 | 123.4085 | -123.4818 | -77.2842 | 42.3431 | 123.23 | 33.2291 | 45.4422
1600.4844 | 123.3856 | -44.1467 | 79.0283 | -0.065308 | 0.0024845 | 0.044767 | 0.0017389 | 0.00041234 | 0.0028476 | -0.0011663 | -0.041534 | 0.0035269 | 0.0029758 | 0.042556 | -0.002384 | 0.00047422 | -0.00054474 | -10.9863 | -1.5701 | -44.4122 | -1.8402 | -1.68 | -44.4077 | -1.7578 | 2.5955 | 79.1473 | 2.0187 | 79.1107 | 2.3895 | 2.2705 | 2.417 | -0.2655 | -80.5984 | -80.8685 | 42.4667 | 42.3889 | -0.26093 | 42.6544 | 0.004577 | 46.1655 | 0.11902 | 0.082398 | 46.5363 | 46.5637 | 46.4172 | 0.39825 | 0.25177 | 42.7322 | 42.572 | 0.37079 | 77.092 | 42.8421 | 77.1286 | 42.5766 | 123.2941 | -123.4406 | -77.0096 | 42.3065 | 123.2574 | 33.1604 | 46.7422
1601.5469 | 123.3398 | -44.2657 | 78.9963 | -0.072937 | 0.0050479 | 0.041563 | 0.0043023 | 0.0019077 | 0.00028418 | 0.00096987 | -0.12088 | 0.0033133 | 0.0063938 | 0.048965 | -0.0019568 | -0.00059378 | 0.00073706 | -11.0962 | -1.5518 | -44.5129 | -1.9775 | -1.8677 | -44.6136 | -1.8951 | 1.4145 | 79.1336 | 1.8127 | 78.9871 | 2.124 | 1.9913 | 2.1469 | -0.24719 | -80.5481 | -80.9738 | 42.3981 | 42.3706 | -0.3479 | 42.6178 | -0.10071 | 46.0785 | 0.13733 | -0.009155 | 46.3898 | 46.4127 | 46.257 | 0.33417 | 0.17853 | 42.6453 | 42.5354 | 0.31128 | 77.1744 | 42.9611 | 77.3209 | 42.7139 | 123.3994 | -123.5092 | -77.1835 | 42.2882 | 123.2529 | 33.1696 | 45.6802
1602.4844 | 123.3902 | -44.0231 | 79.1565 | -0.095825 | 0.0035525 | 0.045194 | 0.0019525 | 0.0023349 | 0.0015658 | -0.0022345 | -0.020172 | 0.0024589 | 0.0029758 | 0.039992 | -0.0034522 | -0.001662 | -0.00097194 | -11.2289 | -1.5976 | -44.3619 | -1.9272 | -1.7624 | -44.3848 | -1.8036 | 1.7349 | 79.2892 | 2.504 | 79.2984 | 2.948 | 2.9343 | 2.9068 | -0.33875 | -80.7541 | -81.0837 | 42.2607 | 42.2195 | -0.36163 | 42.5583 | -0.022889 | 46.5271 | 0.13275 | 0.14191 | 46.9711 | 46.9299 | 46.9574 | 0.40283 | 0.4303 | 42.5995 | 42.4347 | 0.44403 | 76.7944 | 42.7643 | 76.7853 | 42.4255 | 123.3124 | -123.5184 | -76.6525 | 42.0959 | 123.3215 | 32.7942 | 45.7581
1603.4844 | 123.4268 | -44.2108 | 78.9642 | -0.072937 | 0.0048343 | 0.043699 | 0.0019525 | -0.0030057 | 0.0019932 | 0.0011835 | 0.019501 | 0.0037405 | 0.0036166 | 0.033584 | -0.001316 | -0.0020892 | 0.0022323 | -11.0046 | -1.5793 | -44.2932 | -1.9089 | -1.7441 | -44.339 | -1.7807 | 1.6159 | 79.1656 | 2.1973 | 79.1016 | 2.3209 | 2.2476 | 2.1469 | -0.082398 | -80.5435 | -80.8731 | 42.4667 | 42.4301 | -0.12817 | 42.5125 | -0.045776 | 46.4081 | 0.20142 | 0.13733 | 46.5317 | 46.3577 | 46.4584 | -0.050354 | 0.050354 | 42.5491 | 42.3843 | 0.1236 | 76.9043 | 42.7139 | 76.9684 | 42.6315 | 123.3765 | -123.2574 | -76.767 | 42.3019 | 123.3124 | 33.2062 | 45.8267
1604.4844 | 123.4177 | -44.1376 | 79.0329 | -0.072937 | 0.0061161 | 0.042631 | 0.0036615 | 0.00041234 | 0.0030612 | -0.00031193 | -0.047638 | 0.0024589 | 0.0036166 | 0.040633 | -0.002384 | -0.00016658 | 0.00030966 | -11.3022 | -1.5656 | -44.4397 | -1.8585 | -1.6754 | -44.458 | -1.767 | 1.7166 | 79.0924 | 1.8539 | 79.1199 | 2.3346 | 2.1973 | 2.4033 | -0.30212 | -80.5984 | -80.8914 | 42.4622 | 42.3706 | -0.32043 | 42.6727 | -0.018311 | 45.9915 | 0.059509 | 0.086975 | 46.4722 | 46.5408 | 46.3348 | 0.54932 | 0.34332 | 42.7643 | 42.5812 | 0.48065 | 77.2659 | 42.8741 | 77.2385 | 42.572 | 123.23 | -123.4726 | -77.179 | 42.2791 | 123.2574 | 32.8354 | 45.8542
1605.4844 | 123.4406 | -44.2154 | 78.9734 | -0.050049 | 0.0029117 | 0.043485 | 0.0036615 | 0.0021213 | 0.002634 | 0.00032907 | 0.0011902 | 0.0041679 | 0.005112 | 0.038283 | -0.0021704 | -0.0020892 | -0.00097194 | -11.1328 | -1.561 | -44.458 | -1.8585 | -1.6891 | -44.426 | -1.7395 | 1.1948 | 79.097 | 1.8494 | 79.1107 | 2.2476 | 2.1561 | 2.2064 | -0.24262 | -80.5344 | -80.8319 | 42.5262 | 42.4759 | -0.21057 | 42.7185 | 0.032044 | 46.0648 | 0.1236 | 0.13733 | 46.463 | 46.4218 | 46.3715 | 0.35706 | 0.3067 | 42.7689 | 42.5995 | 0.39826 | 77.2614 | 42.897 | 77.2476 | 42.6544 | 123.3124 | -123.4314 | -77.124 | 42.3569 | 123.3261 | 33.0826 | 45.4102
1606.4844 | 123.4589 | -44.2841 | 78.891 | -0.050049 | 0.0039799 | 0.043058 | 0.0045159 | -0.0034329 | 0.0024204 | 0.0022517 | -0.072052 | 0.00096348 | 0.0046848 | 0.040206 | -0.000675 | -0.00038018 | -0.0011855 | -11.4304 | -1.6571 | -44.5312 | -1.9272 | -1.7761 | -44.5496 | -1.8356 | 1.1307 | 79.0466 | 1.6891 | 79.0375 | 2.037 | 1.9226 | 2.0279 | -0.24719 | -80.5481 | -80.8182 | 42.5079 | 42.4484 | -0.2655 | 42.6956 | -0.018311 | 45.9732 | 0.15564 | 0.14648 | 46.3211 | 46.312 | 46.2067 | 0.33875 | 0.23346 | 42.7551 | 42.6041 | 0.3479 | 77.3483 | 42.8741 | 77.3575 | 42.627 | 123.3307 | -123.4222 | -77.2018 | 42.3569 | 123.3215 | 32.8537 | 45.4147
1607.5469 | 123.4497 | -44.1605 | 78.9688 | -0.065308 | 0.0052615 | 0.043912 | 0.0045159 | -0.00086946 | -0.0033474 | -0.0024481 | -0.05069 | 0.0041679 | 0.0029758 | 0.041915 | -0.0021704 | -0.00059378 | -0.00097194 | -11.1832 | -1.6434 | -44.4763 | -1.9272 | -1.7853 | -44.4489 | -1.8448 | 1.3779 | 79.0878 | 1.9638 | 79.097 | 2.3163 | 2.1927 | 2.3117 | -0.31586 | -80.6122 | -80.896 | 42.3752 | 42.3157 | -0.28839 | 42.6315 | 0.027465 | 46.1243 | 0.11902 | 0.12817 | 46.4767 | 46.4722 | 46.3531 | 0.3479 | 0.22888 | 42.691 | 42.5491 | 0.35248 | 77.1332 | 42.8329 | 77.124 | 42.5171 | 123.2483 | -123.4451 | -77.005 | 42.2333 | 123.2574 | 32.9773 | 45.5383
1608.4844 | 123.4589 | -44.22 | 78.9139 | -0.088196 | 0.0041935 | 0.042844 | 0.0036615 | -0.0025785 | 0.0037022 | 0.0013971 | -0.075104 | 0.0037405 | 0.003403 | 0.043197 | -0.002384 | 0.00026062 | -0.0037491 | -11.1557 | -1.6571 | -44.5267 | -1.9409 | -1.7807 | -44.5221 | -1.8402 | 1.3687 | 79.0237 | 1.7899 | 79.0649 | 2.1835 | 2.0325 | 2.1698 | -0.3067 | -80.571 | -80.8548 | 42.4393 | 42.3798 | -0.30212 | 42.6865 | 0.004577 | 46.0098 | 0.10986 | 0.15106 | 46.4035 | 46.3898 | 46.2524 | 0.37994 | 0.24262 | 42.746 | 42.5858 | 0.39368 | 77.2751 | 42.8696 | 77.2339 | 42.5629 | 123.2437 | -123.4406 | -77.124 | 42.2791 | 123.2849 | 33.0643 | 45.5887
1609.4844 | 123.4177 | -44.1513 | 79.0512 | -0.019531 | 0.0031253 | 0.043912 | 0.0017389 | 0.0014803 | 0.0013522 | -0.0035163 | -0.0018616 | 0.0028861 | 0.0042574 | 0.043197 | -0.003025 | -0.0031574 | 0.0020187 | -11.1603 | -1.6388 | -44.458 | -1.9455 | -1.7944 | -44.4031 | -1.8219 | 1.3367 | 79.1428 | 2.1881 | 79.1382 | 2.623 | 2.4078 | 2.4994 | -0.3067 | -80.69 | -80.9967 | 42.3569 | 42.3294 | -0.25177 | 42.6361 | 0.054932 | 46.3394 | 0.091553 | 0.086976 | 46.7743 | 46.6507 | 46.5591 | 0.31128 | 0.21973 | 42.6636 | 42.5125 | 0.43488 | 76.9501 | 42.8192 | 76.9547 | 42.5125 | 123.2941 | -123.5092 | -76.8631 | 42.2058 | 123.2895 | 32.991 | 45.488
1610.4844 | 123.4131 | -43.8034 | 79.4037 | -0.050049 | 0.0029117 | 0.042844 | 0.0023797 | -0.0021513 | -0.00057042 | -0.0013799 | -0.0018616 | 0.0052359 | 0.0048984 | 0.040847 | -0.0015296 | -0.001662 | 0.0037277 | -10.7712 | -1.6205 | -44.22 | -1.9547 | -1.7807 | -44.1376 | -1.8127 | 0.98419 | 79.3991 | 3.0396 | 79.5959 | 3.9093 | 4.335 | 3.9185 | -0.41656 | -81.0242 | -81.3583 | 42.0227 | 41.9907 | -0.33417 | 42.4072 | 0.082398 | 46.843 | -0.004578 | 0.19226 | 47.7127 | 47.7219 | 48.1384 | 0.87891 | 1.2955 | 42.4393 | 42.2653 | 0.86975 | 76.5564 | 42.5995 | 76.3596 | 42.1829 | 123.2025 | -123.6237 | -76.3641 | 41.8488 | 123.3994 | 33.0322 | 44.7876
1611.4844 | 123.4039 | -44.3069 | 78.891 | -0.088196 | 0.0050479 | 0.041135 | 0.0047295 | 0.0029757 | -0.0012112 | 0.00032907 | -0.01712 | 0.0030997 | 0.006821 | 0.041274 | -0.0015296 | -0.00059378 | 0.00095066 | -10.8765 | -1.6022 | -44.5175 | -1.9272 | -1.7761 | -44.6045 | -1.799 | 1.0437 | 79.01 | 1.7715 | 78.9688 | 2.1149 | 1.9821 | 2.0691 | -0.21057 | -80.4932 | -80.8182 | 42.5308 | 42.5079 | -0.29755 | 42.7185 | -0.086975 | 46.0785 | 0.11902 | 0.07782 | 46.4218 | 46.376 | 46.2891 | 0.29755 | 0.21057 | 42.7414 | 42.5903 | 0.34332 | 77.1973 | 42.9153 | 77.2385 | 42.7048 | 123.317 | -123.4085 | -77.1194 | 42.3798 | 123.2758 | 33.4305 | 45.3506
1612.5625 | 123.4497 | -44.3161 | 78.8452 | -0.027161 | 0.0039799 | 0.042417 | 0.0017389 | -0.0021513 | -0.00014322 | 0.00011527 | -0.029327 | 0.0013907 | 0.003403 | 0.043197 | -0.0021704 | -0.0027302 | -0.00011754 | -10.8902 | -1.5976 | -44.5679 | -1.8677 | -1.6937 | -44.5267 | -1.767 | 1.0529 | 78.9688 | 1.5244 | 78.9825 | 1.9363 | 1.8082 | 1.8585 | -0.25177 | -80.4428 | -80.7129 | 42.6224 | 42.5491 | -0.21057 | 42.8009 | 0.041199 | 45.8405 | 0.1236 | 0.13733 | 46.2524 | 46.1746 | 46.1243 | 0.33417 | 0.28381 | 42.8741 | 42.7002 | 0.41199 | 77.4582 | 42.9703 | 77.4445 | 42.7185 | 123.2849 | -123.4131 | -77.3209 | 42.4484 | 123.2986 | 33.4259 | 45.369
1613.4844 | 123.4314 | -44.2474 | 78.9322 | -0.03479 | 0.0048343 | 0.044553 | 0.0043023 | -0.00065586 | 0.0015658 | -0.0024481 | -0.01712 | 0.0024589 | 0.0021212 | 0.037002 | -0.002384 | -0.00038018 | -0.0046035 | -10.9314 | -1.6113 | -44.5175 | -1.9409 | -1.8127 | -44.5633 | -1.8311 | 1.181 | 79.0146 | 1.7075 | 78.9917 | 2.1149 | 1.9958 | 2.0828 | -0.27008 | -80.5435 | -80.8731 | 42.4347 | 42.4164 | -0.31586 | 42.6865 | -0.045776 | 45.9549 | 0.082397 | 0.059509 | 46.3623 | 46.3303 | 46.2433 | 0.37537 | 0.28839 | 42.7048 | 42.5766 | 0.40741 | 77.2842 | 42.9062 | 77.3071 | 42.6361 | 123.262 | -123.4497 | -77.2247 | 42.3065 | 123.2391 | 33.316 | 45.4285
1614.4844 | 123.4085 | -44.339 | 78.8223 | -0.095825 | 0.0035525 | 0.042631 | 0.0025933 | 0.0040439 | -0.00057042 | 0.0011835 | -0.044586 | 0.0033133 | 0.0053256 | 0.039779 | -0.004093 | -0.0010212 | -0.00033114 | -11.0413 | -1.6708 | -44.5816 | -1.9592 | -1.799 | -44.6091 | -1.8677 | 1.3 | 78.9459 | 1.6296 | 78.923 | 1.9455 | 1.8311 | 1.9272 | -0.24262 | -80.4932 | -80.7816 | 42.54 | 42.4713 | -0.27008 | 42.7139 | -0.027466 | 45.9686 | 0.1236 | 0.10071 | 46.2845 | 46.2662 | 46.17 | 0.29755 | 0.20142 | 42.7826 | 42.6224 | 0.31586 | 77.2934 | 42.9108 | 77.3163 | 42.6682 | 123.2849 | -123.4039 | -77.1927 | 42.3798 | 123.262 | 33.2977 | 45.639
1615.5469 | 123.468 | -44.1971 | 78.9688 | -0.088196 | 0.0041935 | 0.045408 | 0.0028069 | 0.0021213 | 0.00028418 | 0.0013971 | -0.090363 | 0.0037405 | 0.0029758 | 0.042769 | -0.004093 | -0.0010212 | -0.0035355 | -10.9451 | -1.6617 | -44.4763 | -1.9135 | -1.7761 | -44.4809 | -1.8402 | 1.2726 | 79.0558 | 1.8906 | 79.0878 | 2.2888 | 2.1515 | 2.2751 | -0.27923 | -80.6305 | -80.8823 | 42.421 | 42.3569 | -0.28381 | 42.6361 | -0.004578 | 46.0876 | 0.086975 | 0.11902 | 46.4859 | 46.4722 | 46.3486 | 0.38452 | 0.26093 | 42.7002 | 42.5629 | 0.39825 | 77.1973 | 42.8146 | 77.1652 | 42.5354 | 123.2529 | -123.4451 | -77.0782 | 42.2836 | 123.2849 | 33.252 | 45.4697
1616.4844 | 123.4177 | -44.2108 | 78.923 | -0.095825 | 0.0050479 | 0.043912 | 0.0040887 | -0.0021513 | 0.00028418 | 0.00054267 | -0.056793 | 0.0024589 | 0.0027622 | 0.039992 | -0.0032386 | -0.0014484 | 0.0028733 | -11.0001 | -1.6754 | -44.4763 | -1.9363 | -1.7807 | -44.5312 | -1.8585 | 1.2543 | 79.0329 | 1.8494 | 79.0512 | 2.2293 | 2.124 | 2.2293 | -0.2655 | -80.5984 | -80.8594 | 42.4301 | 42.3523 | -0.32044 | 42.6178 | -0.054932 | 46.0602 | 0.10986 | 0.12817 | 46.4401 | 46.4401 | 46.3348 | 0.37994 | 0.27466 | 42.6956 | 42.54 | 0.37994 | 77.2018 | 42.8009 | 77.1835 | 42.5354 | 123.2437 | -123.3994 | -77.0737 | 42.2745 | 123.262 | 33.2108 | 45.4651
1617.5 | 123.3765 | -44.1193 | 79.1016 | -0.072937 | 0.0050479 | 0.044126 | 0.0017389 | 0.00019874 | -0.00057042 | -0.00073913 | -0.032379 | 0.0041679 | 0.0048984 | 0.041488 | -0.0008886 | 0.00047422 | 0.0013779 | -11.2198 | -1.6251 | -44.3573 | -1.8997 | -1.7487 | -44.3344 | -1.8127 | 1.4923 | 79.1565 | 2.1561 | 79.1107 | 2.5406 | 2.3666 | 2.4857 | -0.23804 | -80.7266 | -81.0013 | 42.3706 | 42.3065 | -0.21515 | 42.5446 | 0.022888 | 46.2753 | 0.054932 | 0.009156 | 46.6599 | 46.6049 | 46.4859 | 0.32959 | 0.21057 | 42.6086 | 42.4576 | 0.38452 | 76.9547 | 42.7322 | 77.0004 | 42.4942 | 123.2758 | -123.4589 | -76.9455 | 42.2195 | 123.23 | 32.8995 | 45.6116
1618.5469 | 123.317 | -44.1193 | 79.1428 | -0.027161 | 0.0052615 | 0.043485 | 0.0045159 | -0.0074919 | -0.0020658 | -0.0058661 | -0.12393 | 0.0039541 | 0.0057528 | 0.041274 | -0.0004614 | -0.014052 | -0.00011754 | -11.3937 | -1.4648 | -44.3893 | -1.8585 | -1.7395 | -44.4489 | -1.799 | 1.7578 | 79.2755 | 2.0737 | 79.129 | 2.3987 | 2.2247 | 2.3895 | -0.27008 | -80.6076 | -81.0013 | 42.3798 | 42.3203 | -0.32959 | 42.5903 | -0.05951 | 46.1929 | 0.13275 | -0.013733 | 46.5179 | 46.5088 | 46.344 | 0.31586 | 0.15106 | 42.6498 | 42.5308 | 0.32501 | 77.0554 | 42.9245 | 77.2018 | 42.6544 | 123.3948 | -123.5321 | -77.0691 | 42.2607 | 123.2483 | 32.7255 | 45.8771
1619.4844 | 123.4863 | -120.2225 | 3.0304 | -0.011902 | 0.0033389 | 0.12787 | 0.0025933 | -0.0025785 | 7.0582e-05 | -0.0037299 | -0.041534 | 0.14495 | 0.004471 | -0.00059601 | -0.0017432 | -0.0014484 | 0.0018051 | -31.8832 | -2.5269 | -120.6985 | -2.8564 | -2.7054 | -120.4376 | -2.7603 | 0.99792 | 2.8473 | 2.3621 | 2.7969 | 3.0121 | 2.8519 | 2.7557 | -0.47607 | -5.5573 | -5.8868 | 117.5171 | 117.4622 | -0.21515 | 117.9382 | 0.26093 | 122.5845 | -0.18311 | -0.23346 | 123.2346 | 122.9782 | 123.0743 | 0.39368 | 0.48981 | 117.9932 | 117.8421 | 0.65002 | 0.43487 | 118.1717 | 0.48523 | 117.6956 | 123.0698 | -123.7289 | -0.66833 | 117.366 | 123.0194 | 88.3392 | 121.2204
1620.4844 | 123.5962 | -120.2911 | 2.9755 | -0.057678 | 0.0022709 | 0.1253 | 0.0019525 | 0.0012667 | -0.00035682 | 0.0016107 | -0.044586 | 0.14366 | 0.0025484 | -0.0038004 | -0.0028112 | -0.0031574 | -0.0022537 | -31.4301 | -2.4811 | -120.8405 | -2.7466 | -2.5726 | -120.2454 | -2.6184 | 0.85602 | 2.9205 | 2.3941 | 2.9114 | 3.0762 | 2.7557 | 2.8473 | -0.54932 | -5.4565 | -5.722 | 117.7185 | 117.6727 | 0.045777 | 118.222 | 0.59509 | 122.6852 | -0.054932 | -0.064087 | 123.3673 | 123.1384 | 123.0469 | 0.45319 | 0.36163 | 118.2678 | 118.0939 | 0.68207 | 0.51727 | 118.3594 | 0.52643 | 117.8101 | 123.2117 | -123.8159 | -0.58136 | 117.5446 | 123.2025 | 88.8611 | 121.1472
1621.4844 | 123.4909 | -120.8176 | 2.4033 | -0.027161 | 0.0035525 | 0.1253 | 0.0030207 | -0.00022866 | -0.00014322 | 0.0037469 | -0.047638 | 0.14601 | 0.0042574 | -0.004014 | -0.0019568 | -0.0010212 | -0.0013991 | -31.311 | -2.5223 | -120.7947 | -2.8381 | -2.6871 | -120.8908 | -2.7145 | 0.78278 | 2.6001 | 2.124 | 2.3346 | 2.3254 | 2.2659 | 2.3392 | 0.022888 | -4.9255 | -5.2414 | 118.1305 | 118.103 | -0.073242 | 118.0801 | -0.09613 | 122.9416 | 0.19684 | -0.068664 | 123.143 | 123.1567 | 123.0835 | 0.21515 | 0.14191 | 118.1076 | 117.9565 | 0.20142 | 0.21057 | 118.2724 | 0.47607 | 118.2953 | 123.4177 | -123.1979 | -0.27924 | 117.9794 | 123.1522 | 89.5065 | 121.6003
1622.5469 | 123.3902 | -120.8679 | 2.4765 | -0.0042723 | 0.0035525 | 0.12488 | 0.0043023 | 0.0019077 | 0.0019932 | -0.0026617 | -0.1575 | 0.14644 | 0.0046848 | 0.0032492 | -0.0038794 | -0.00059378 | 0.0018051 | -31.3568 | -2.3163 | -120.7672 | -2.7328 | -2.6093 | -120.2087 | -2.6459 | 0.54932 | 3.0212 | 2.4628 | 2.3621 | 2.3804 | 2.0233 | 2.1194 | 0.10071 | -4.7928 | -5.2093 | 118.2587 | 118.222 | 0.65918 | 118.1213 | 0.55847 | 123.3307 | 0.54474 | -0.11444 | 123.2483 | 122.9874 | 122.8912 | -0.34332 | -0.43945 | 118.158 | 118.0344 | -0.082398 | -0.10071 | 118.4509 | 0.55847 | 118.5516 | 123.8892 | -123.2437 | -0.013732 | 118.1351 | 123.23 | 89.5111 | 121.4172
1623.4844 | 123.4039 | -121.0236 | 2.2659 | -0.10345 | 0.0046207 | 0.12637 | 0.0032343 | 0.0019077 | 0.0017794 | -0.00095273 | -0.078156 | 0.1443 | 0.0038302 | 0.001113 | -0.0017432 | -0.0029438 | -0.0022537 | -30.3085 | -2.3666 | -121.0281 | -2.6825 | -2.5085 | -120.5795 | -2.5726 | 0.82398 | 2.5635 | 2.0737 | 2.1149 | 2.1194 | 2.0187 | 2.1286 | -0.004577 | -4.6326 | -4.9484 | 118.515 | 118.4509 | 0.44403 | 118.4555 | 0.44861 | 123.0972 | 0.29755 | -0.15106 | 123.143 | 123.1522 | 123.0423 | 0.054932 | -0.054931 | 118.5196 | 118.3456 | 0.045777 | 0.041199 | 118.6615 | 0.48981 | 118.6569 | 123.587 | -123.2941 | -0.19226 | 118.3411 | 123.1384 | 90.715 | 121.8475
1624.5469 | 123.3536 | -120.6757 | 2.7374 | -0.080566 | 0.0035525 | 0.12616 | 0.0023797 | 0.0027621 | 0.00049778 | 0.0018243 | -0.17581 | 0.14516 | 0.0042574 | -0.0012368 | -0.0034522 | 0.001756 | -0.0043899 | -31.3339 | -2.3254 | -120.7489 | -2.7786 | -2.6413 | -120.9824 | -2.6688 | 1.6617 | 2.8381 | 2.2568 | 2.7878 | 2.6184 | 2.4124 | 2.4902 | -0.073242 | -5.0629 | -5.5161 | 118.0344 | 118.0069 | -0.3067 | 118.0801 | -0.23346 | 122.9324 | 0.10071 | 0.050354 | 123.2941 | 123.1659 | 123.0881 | 0.23346 | 0.15564 | 118.1076 | 117.9703 | 0.36163 | 0.53101 | 118.4235 | 0.58136 | 118.3502 | 123.5138 | -123.4863 | -0.48065 | 117.897 | 123.4634 | 89.3417 | 122.3373
1625.4844 | 123.4634 | -120.8771 | 2.4536 | -0.027161 | 0.0035525 | 0.12402 | 0.00045712 | 0.0014803 | 7.0582e-05 | 0.00075627 | -0.041534 | 0.14687 | 0.0031894 | 0.0030356 | -0.0011022 | -0.0023028 | 0.00030966 | -31.1646 | -2.3575 | -120.9137 | -2.7603 | -2.6459 | -120.4834 | -2.5635 | 1.1078 | 2.7466 | 2.2064 | 2.3346 | 2.2659 | 2.1515 | 2.2339 | -0.036621 | -4.8111 | -5.2139 | 118.2312 | 118.3136 | 0.39368 | 118.3502 | 0.4303 | 123.0835 | 0.29297 | -0.11902 | 123.143 | 123.111 | 123.0286 | 0.027466 | -0.054932 | 118.2678 | 118.1534 | 0.059509 | 0.12817 | 118.5562 | 0.54016 | 118.5196 | 123.6237 | -123.3673 | -0.24719 | 118.1168 | 123.2117 | 89.7125 | 121.9849
1626.5469 | 123.468 | -120.2271 | 3.1128 | -0.027161 | 0.0048343 | 0.12637 | 0.0057977 | 0.00041234 | 0.0030612 | -0.00031193 | -0.13614 | 0.15093 | 0.0036166 | 0.00068579 | -0.0015296 | -0.00059378 | -0.0013991 | -30.5054 | -2.3346 | -120.7352 | -2.7832 | -2.6688 | -120.3735 | -2.6596 | 1.0849 | 3.0075 | 2.3849 | 2.948 | 2.71 | 2.3071 | 2.6047 | -0.50812 | -5.4474 | -5.896 | 117.5583 | 117.5674 | -0.14648 | 118.0756 | 0.36163 | 122.612 | -0.10529 | -0.16479 | 122.937 | 122.8317 | 122.5342 | 0.21973 | -0.07782 | 118.0664 | 117.952 | 0.32501 | 0.56305 | 118.4006 | 0.62256 | 117.8925 | 123.2346 | -123.848 | -0.72784 | 117.4438 | 123.175 | 89.7217 | 121.312
1627.4844 | 123.4634 | -120.7031 | 2.5818 | -0.050049 | 0.0033389 | 0.12594 | 0.0038751 | -0.00022866 | 0.00049778 | -0.0041571 | -0.023224 | 0.14452 | 0.00618 | -0.004014 | -0.0011022 | -0.001662 | -0.00097194 | -30.4688 | -2.4124 | -121.019 | -2.6733 | -2.5085 | -120.5109 | -2.5223 | 1.181 | 2.655 | 2.0874 | 2.4673 | 2.4536 | 2.3483 | 2.4033 | -0.31586 | -4.9942 | -5.2551 | 118.1946 | 118.1808 | 0.19226 | 118.4967 | 0.50812 | 122.7905 | 0.073242 | -0.11444 | 123.1567 | 123.1064 | 123.0515 | 0.31586 | 0.26093 | 118.5104 | 118.3456 | 0.36621 | 0.37994 | 118.6066 | 0.56763 | 118.2907 | 123.3582 | -123.6008 | -0.49438 | 118.0298 | 123.1705 | 90.2344 | 121.8842
1628.4844 | 123.23 | -44.458 | 78.7033 | -0.095825 | 0.0037661 | 0.043485 | 0.0030207 | 0.0038303 | 0.00092498 | -0.00095273 | -0.075104 | 0.0033133 | 0.0031894 | 0.041488 | -0.002384 | -0.00038018 | -0.00054474 | -10.9039 | -0.90637 | -44.7281 | -1.2589 | -1.1032 | -44.7327 | -1.1444 | 1.7441 | 78.7857 | 0.50354 | 78.8406 | 0.88806 | 0.76446 | 0.88806 | -0.27008 | -79.6097 | -79.9622 | 43.3548 | 43.3136 | -0.27466 | 43.5837 | -0.004578 | 44.9615 | 0.082398 | 0.13733 | 45.3461 | 45.3461 | 45.2225 | 0.38452 | 0.26092 | 43.6249 | 43.4692 | 0.38452 | 78.3371 | 43.8217 | 78.2822 | 43.5516 | 123.2437 | -123.4314 | -78.1998 | 43.1992 | 123.2986 | 33.5541 | 46.2021
1629.4844 | 123.3627 | -44.3848 | 78.804 | -0.080566 | 0.0037661 | 0.044126 | 0.00088432 | -0.0042875 | 0.0015658 | -0.0022345 | -0.0079652 | 0.0035269 | 0.0040438 | 0.040633 | -0.0043066 | 4.7018e-05 | 0.0022323 | -10.881 | -0.91095 | -44.6365 | -1.2497 | -1.1032 | -44.632 | -1.1215 | 1.7532 | 78.891 | 0.5127 | 78.8864 | 0.91553 | 0.74158 | 0.81482 | -0.25177 | -79.715 | -80.0537 | 43.2816 | 43.2632 | -0.24719 | 43.515 | 0.004578 | 44.8975 | 0.086975 | 0.082398 | 45.3003 | 45.1996 | 45.1263 | 0.30212 | 0.22888 | 43.5333 | 43.3868 | 0.40283 | 78.3737 | 43.7256 | 78.3783 | 43.4738 | 123.2758 | -123.4406 | -78.2913 | 43.1351 | 123.2712 | 33.5037 | 46.138
1630.5469 | 123.262 | -44.2703 | 78.978 | 0.0033567 | 0.0035525 | 0.043272 | 0.0030207 | 0.0010531 | 0.0015658 | -0.0020209 | -0.13614 | 0.0035269 | 0.001694 | 0.039992 | -0.0038794 | -0.010421 | -0.00054474 | -10.8765 | -0.87433 | -44.5312 | -1.3 | -1.1673 | -44.5312 | -1.2268 | 1.6754 | 79.0695 | 0.54474 | 78.9459 | 0.83771 | 0.68207 | 0.81024 | -0.26093 | -79.8523 | -80.278 | 43.103 | 43.0435 | -0.26093 | 43.3044 | 0 | 44.8151 | 0.091553 | -0.032043 | 45.108 | 45.0806 | 44.9524 | 0.2655 | 0.13733 | 43.364 | 43.2312 | 0.29297 | 78.4012 | 43.6569 | 78.5248 | 43.396 | 123.3398 | -123.5092 | -78.4332 | 42.9703 | 123.2162 | 33.3939 | 45.9457
1631.4844 | 123.4177 | -44.3756 | 78.7903 | -0.042419 | -7.913e-05 | 0.045621 | 0.0032343 | 0.00062594 | -0.00057042 | -0.0018073 | -0.0049134 | 0.0022453 | 0.004471 | 0.041488 | -0.0036658 | -0.0031574 | 0.00052346 | -10.9589 | -0.9201 | -44.6411 | -1.1948 | -1.0345 | -44.6182 | -1.0803 | 1.8906 | 78.891 | 0.64087 | 78.9139 | 1.0254 | 0.93842 | 1.0025 | -0.2655 | -79.7104 | -79.985 | 43.3411 | 43.2953 | -0.24262 | 43.5608 | 0.022888 | 45.0165 | 0.10071 | 0.1236 | 45.401 | 45.3781 | 45.314 | 0.36163 | 0.29755 | 43.6066 | 43.4463 | 0.38452 | 78.273 | 43.721 | 78.2501 | 43.4555 | 123.2666 | -123.4314 | -78.1494 | 43.1808 | 123.2895 | 33.4167 | 46.2662
1632.4844 | 123.3398 | -44.371 | 78.7994 | -0.03479 | 0.0044071 | 0.042631 | 0.0025933 | -0.0023649 | -0.00014322 | 0.00032907 | -0.035431 | 0.0028861 | 0.0036166 | 0.038711 | -0.0038794 | -0.0018756 | -0.00054474 | -10.9222 | -0.89264 | -44.6411 | -1.1353 | -0.97504 | -44.6732 | -1.0391 | 2.0004 | 78.8773 | 0.54932 | 78.8773 | 0.92468 | 0.79651 | 0.90179 | -0.27008 | -79.6921 | -79.9347 | 43.396 | 43.3319 | -0.30212 | 43.602 | -0.032044 | 44.9203 | 0.07782 | 0.07782 | 45.2957 | 45.2728 | 45.1675 | 0.35248 | 0.24719 | 43.6661 | 43.5059 | 0.37537 | 78.3279 | 43.7485 | 78.3279 | 43.4784 | 123.2483 | -123.4406 | -78.2501 | 43.2358 | 123.2483 | 33.4488 | 46.3715
1633.5469 | 123.3307 | -44.3756 | 78.8544 | -0.095825 | -0.0011471 | 0.044981 | 0.0040887 | 0.0029757 | 0.0013522 | 0.00032907 | -0.099518 | 0.0039541 | 0.0029758 | 0.048537 | -0.0053748 | -0.00080758 | 0.0020187 | -11.0321 | -0.8606 | -44.6182 | -1.2634 | -1.1398 | -44.7281 | -1.1536 | 2.0966 | 78.9459 | 0.54932 | 78.8544 | 0.88348 | 0.74616 | 0.85144 | -0.24262 | -79.715 | -80.1178 | 43.2358 | 43.222 | -0.35248 | 43.4647 | -0.10986 | 44.9249 | 0.091553 | 0 | 45.2591 | 45.227 | 45.1218 | 0.30212 | 0.19684 | 43.4784 | 43.3548 | 0.33417 | 78.3051 | 43.7576 | 78.3966 | 43.515 | 123.3215 | -123.4726 | -78.3051 | 43.1122 | 123.23 | 33.3435 | 46.4722
1634.4844 | 123.056 | -44.3436 | 78.8727 | -0.065308 | 0.0035525 | 0.044767 | 0.0040887 | 0.0031893 | 7.0582e-05 | -0.0011663 | -0.13614 | 0.0024589 | 0.0029758 | 0.042556 | -0.0038794 | 4.7018e-05 | 9.6064e-05 | -11.0779 | -0.83313 | -44.6182 | -1.268 | -1.1307 | -44.7144 | -1.1627 | 1.9775 | 78.9734 | 0.56305 | 78.8498 | 0.86975 | 0.72784 | 0.84686 | -0.27466 | -79.7058 | -80.1407 | 43.2129 | 43.1808 | -0.37079 | 43.4555 | -0.09613 | 44.9066 | 0.10071 | -0.022889 | 45.2133 | 45.1904 | 45.0714 | 0.28381 | 0.1648 | 43.4875 | 43.3502 | 0.3067 | 78.2867 | 43.7851 | 78.4103 | 43.5104 | 123.317 | -123.4909 | -78.3096 | 43.0756 | 123.1934 | 33.2657 | 46.3211
1635.4844 | 123.4085 | -44.3024 | 78.8406 | -0.03479 | 0.0052615 | 0.045408 | 0.0034479 | 0.0031893 | 0.0024204 | 0.00011527 | -0.069 | 0.0030997 | 0.001694 | 0.040633 | -0.0008886 | -0.0014484 | -0.0033219 | -11.0367 | -0.88348 | -44.5633 | -1.1627 | -1.0117 | -44.5999 | -1.0757 | 1.6571 | 78.9734 | 0.63171 | 78.9825 | 1.0162 | 0.90637 | 1.0071 | -0.26093 | -79.7241 | -80.0034 | 43.2907 | 43.2266 | -0.29755 | 43.4875 | -0.036622 | 44.9341 | 0.13275 | 0.14191 | 45.3186 | 45.3094 | 45.2087 | 0.37537 | 0.27466 | 43.5516 | 43.4006 | 0.38452 | 78.3508 | 43.6798 | 78.3417 | 43.4189 | 123.2758 | -123.4039 | -78.2089 | 43.1396 | 123.2849 | 33.2657 | 45.9595
1636.5469 | 123.317 | -44.3436 | 78.9001 | -0.050049 | 0.0037661 | 0.041135 | 0.0043023 | -0.0021513 | -0.0012112 | 0.00032907 | -0.069 | 0.0043815 | 0.00618 | 0.04341 | -0.0032386 | -0.0025164 | 0.0022323 | -11.0458 | -0.85602 | -44.5953 | -1.2909 | -1.1581 | -44.6457 | -1.1673 | 0.97504 | 78.9917 | 0.63629 | 78.8818 | 0.9613 | 0.82398 | 0.92468 | -0.25177 | -79.7562 | -80.191 | 43.1854 | 43.1763 | -0.30212 | 43.428 | -0.050354 | 44.9799 | 0.091553 | -0.01831 | 45.3049 | 45.2683 | 45.1675 | 0.28839 | 0.18768 | 43.4372 | 43.3044 | 0.32501 | 78.2455 | 43.7393 | 78.3554 | 43.4875 | 123.3353 | -123.4955 | -78.2639 | 43.0527 | 123.2254 | 33.2977 | 45.3186
1637.4844 | 123.3902 | -44.2978 | 78.8773 | -0.057678 | 0.0063297 | 0.043272 | 0.0040887 | 0.00041234 | 0.00071138 | -0.0018073 | 0.0011902 | 0.0052359 | 0.003403 | 0.038711 | -0.0017432 | -0.001662 | 0.0018051 | -11.055 | -0.91095 | -44.5541 | -1.1902 | -1.0162 | -44.5404 | -1.0849 | 0.99335 | 78.9963 | 0.76446 | 78.9963 | 1.1078 | 1.0117 | 1.0757 | -0.25635 | -79.7882 | -80.0674 | 43.2816 | 43.2129 | -0.24261 | 43.4692 | 0.013733 | 45.0623 | 0.11902 | 0.11902 | 45.4056 | 45.3735 | 45.3094 | 0.31128 | 0.24719 | 43.5379 | 43.364 | 0.34332 | 78.2318 | 43.6432 | 78.2318 | 43.3868 | 123.2941 | -123.4314 | -78.1128 | 43.1076 | 123.2941 | 33.2428 | 45.2911
1638.4844 | 123.4131 | -44.2841 | 78.9093 | -0.1416 | 0.0035525 | 0.044126 | 0.0034479 | 0.0025485 | 0.0011386 | 0.00032907 | -0.029327 | 0.0030997 | 0.0012668 | 0.044906 | -0.0032386 | -0.0029438 | -0.0028945 | -11.0138 | -0.85144 | -44.5496 | -1.1627 | -1.0071 | -44.5358 | -1.062 | 1.149 | 78.9597 | 0.74158 | 79.0009 | 1.1169 | 0.98877 | 1.0941 | -0.2655 | -79.7607 | -80.072 | 43.277 | 43.222 | -0.25177 | 43.4875 | 0.013733 | 45.0256 | 0.050354 | 0.091552 | 45.401 | 45.3781 | 45.2728 | 0.35248 | 0.24719 | 43.5425 | 43.3868 | 0.37537 | 78.2593 | 43.6981 | 78.2181 | 43.4326 | 123.2437 | -123.4589 | -78.1677 | 43.1213 | 123.2849 | 33.2703 | 45.433
1639.4844 | 123.3582 | -44.2291 | 78.9459 | -0.14923 | 0.0050479 | 0.043272 | 0.0025933 | -0.0012967 | -0.0022794 | -0.0058661 | -0.023224 | 0.0011771 | 0.0025484 | 0.04811 | -0.0049476 | -0.0027302 | -0.0011855 | -11.0138 | -0.86975 | -44.4809 | -1.0666 | -0.95215 | -44.7006 | -1.0483 | 1.1536 | 79.0192 | 0.7782 | 78.9963 | 1.1353 | 1.0025 | 1.0941 | -0.25177 | -79.8157 | -80.0125 | 43.277 | 43.1808 | -0.4715 | 43.4326 | -0.21973 | 45.0073 | 0.073242 | 0.050354 | 45.3644 | 45.3232 | 45.2316 | 0.31586 | 0.2243 | 43.5287 | 43.4143 | 0.35706 | 78.2181 | 43.6111 | 78.241 | 43.3594 | 123.2483 | -123.4268 | -78.1677 | 43.1625 | 123.2254 | 33.2153 | 45.3827
1640.4844 | 123.4222 | -44.1971 | 78.9597 | -0.065308 | 0.0044071 | 0.047117 | 0.0015253 | 0.0014803 | 0.0041294 | -0.0013799 | -0.078156 | 0.0018179 | 0.0038302 | 0.04106 | -0.002384 | -0.0018756 | 0.0041551 | -10.9772 | -0.89264 | -44.5038 | -1.1398 | -1.0208 | -44.4809 | -1.0757 | 1.1536 | 79.0512 | 0.86975 | 79.097 | 1.2497 | 1.1169 | 1.2451 | -0.3067 | -79.8523 | -80.0995 | 43.1763 | 43.1213 | -0.28381 | 43.428 | 0.022888 | 45.0668 | 0.091552 | 0.13733 | 45.4468 | 45.4422 | 45.314 | 0.37537 | 0.24719 | 43.483 | 43.364 | 0.37994 | 78.2272 | 43.6111 | 78.1815 | 43.3044 | 123.2483 | -123.4634 | -78.0899 | 43.0573 | 123.2941 | 33.2199 | 45.3506
1641.5469 | 123.3994 | -44.2291 | 78.9368 | -0.050049 | 0.0012027 | 0.044553 | 0.0051569 | -1.486e-05 | 0.00092498 | -0.00052553 | -0.096466 | 0.0037405 | 0.004471 | 0.046401 | -0.0028112 | 4.7018e-05 | 0.00095066 | -11.1053 | -0.8606 | -44.5221 | -1.2085 | -1.0803 | -44.5587 | -1.1215 | 1.0895 | 79.0375 | 0.80109 | 79.0649 | 1.181 | 1.0437 | 1.149 | -0.29297 | -79.7974 | -80.1453 | 43.1488 | 43.1076 | -0.32959 | 43.4006 | -0.036621 | 45.0302 | 0.10071 | 0.12817 | 45.4102 | 45.3781 | 45.2728 | 0.3479 | 0.24262 | 43.4418 | 43.3136 | 0.37994 | 78.2639 | 43.6615 | 78.2364 | 43.3685 | 123.2666 | -123.4589 | -78.1357 | 43.0206 | 123.2941 | 33.1238 | 45.3186
1642.4844 | 123.4222 | -44.1559 | 78.978 | -0.011902 | 0.0035525 | 0.044126 | 0.0040887 | 0.0025485 | 0.0015658 | -9.8328e-05 | -0.072052 | 0.0033133 | 0.0027622 | 0.044051 | -0.001316 | 4.7018e-05 | -0.0026809 | -11.0458 | -0.89722 | -44.4626 | -1.181 | -1.03 | -44.4855 | -1.0757 | 1.6617 | 79.0878 | 0.87891 | 79.1107 | 1.2543 | 1.1536 | 1.2451 | -0.3067 | -79.8752 | -80.159 | 43.1259 | 43.0801 | -0.32959 | 43.3868 | -0.022889 | 45.0348 | 0.10986 | 0.13275 | 45.4102 | 45.401 | 45.3094 | 0.36621 | 0.27466 | 43.4326 | 43.2816 | 0.37537 | 78.2318 | 43.5654 | 78.2089 | 43.2587 | 123.2437 | -123.4406 | -78.0991 | 42.9749 | 123.2666 | 33.11 | 45.8176
1643.4844 | 123.4222 | -44.1559 | 79.0421 | -0.019531 | 0.0052615 | 0.04669 | 0.0025933 | -1.486e-05 | 0.0015658 | -9.8328e-05 | -0.044586 | 0.0039541 | 0.0046848 | 0.046187 | -0.0038794 | 0.00026062 | -0.0013991 | -10.9589 | -0.88806 | -44.4214 | -1.1719 | -1.0025 | -44.4305 | -1.0757 | 1.3596 | 79.1153 | 0.93842 | 79.1016 | 1.2863 | 1.1444 | 1.2131 | -0.2655 | -79.9301 | -80.2139 | 43.1534 | 43.0801 | -0.27466 | 43.3456 | -0.009155 | 45.0943 | 0.073242 | 0.059509 | 45.4422 | 45.369 | 45.3003 | 0.27466 | 0.20599 | 43.4189 | 43.2495 | 0.3479 | 78.1631 | 43.5333 | 78.1769 | 43.2678 | 123.2712 | -123.4634 | -78.1036 | 42.984 | 123.2574 | 33.197 | 45.5154
1644.5469 | 123.2986 | -44.2108 | 79.0054 | -0.019531 | 0.0039799 | 0.043272 | 0.0053705 | -0.00044226 | 0.00092498 | 0.00032907 | -0.11478 | 0.0041679 | 0.0055392 | 0.046828 | -0.003025 | -0.0020892 | -0.0039627 | -11.1649 | -0.87891 | -44.5084 | -1.3229 | -1.1993 | -44.5633 | -1.2222 | 1.2726 | 79.1565 | 0.8606 | 78.9963 | 1.1444 | 1.0025 | 1.1307 | -0.29755 | -79.8843 | -80.3284 | 43.0115 | 42.9886 | -0.35248 | 43.2861 | -0.054931 | 45.0714 | 0.15106 | -0.009155 | 45.3552 | 45.3415 | 45.2133 | 0.27008 | 0.14191 | 43.309 | 43.1854 | 0.28381 | 78.1357 | 43.6295 | 78.2959 | 43.3319 | 123.3673 | -123.5138 | -78.1448 | 42.8879 | 123.2071 | 33.046 | 45.4834
1645.4844 | 123.3994 | -44.1605 | 79.0237 | -0.095825 | 0.0031253 | 0.044981 | 0.0030207 | 0.00083954 | 0.0013522 | -0.00031193 | -0.032379 | 0.0039541 | 0.0046848 | 0.037429 | -0.002384 | -0.0012348 | 0.0020187 | -10.9955 | -0.95215 | -44.4168 | -1.2222 | -1.0529 | -44.4122 | -1.1398 | 1.5564 | 79.1016 | 0.93842 | 79.1199 | 1.3184 | 1.1948 | 1.2955 | -0.25635 | -79.9759 | -80.246 | 43.1076 | 43.0206 | -0.25177 | 43.277 | 0.004578 | 45.0989 | 0.077819 | 0.09613 | 45.4788 | 45.4559 | 45.3552 | 0.35706 | 0.25635 | 43.364 | 43.1946 | 0.37994 | 78.1815 | 43.4647 | 78.1631 | 43.2083 | 123.262 | -123.4406 | -78.0853 | 42.9382 | 123.2803 | 33.165 | 45.7169
1646.4844 | 123.4314 | -44.2154 | 78.9322 | -0.080566 | 0.0052615 | 0.045621 | 0.0021661 | 0.00019874 | 0.0030612 | -9.8328e-05 | -0.044586 | 0.0043815 | 0.0036166 | 0.042129 | -0.0043066 | -0.0020892 | 0.0018051 | -10.9909 | -0.96588 | -44.4397 | -1.2314 | -1.0803 | -44.4992 | -1.1444 | 1.3458 | 79.0421 | 1.0391 | 79.0649 | 1.3962 | 1.2909 | 1.3687 | -0.2243 | -79.8981 | -80.1636 | 43.1351 | 43.071 | -0.28381 | 43.2953 | -0.05951 | 45.2545 | 0.10986 | 0.13275 | 45.6116 | 45.5841 | 45.5063 | 0.32959 | 0.25177 | 43.3594 | 43.2083 | 0.35706 | 78.0258 | 43.4738 | 78.0029 | 43.2495 | 123.2574 | -123.3719 | -77.8931 | 42.984 | 123.2803 | 33.2245 | 45.5612
1647.4844 | 123.4314 | -44.1467 | 79.0237 | -0.065308 | 0.0039799 | 0.043699 | 0.0017389 | -0.0055691 | -0.00014322 | 0.00011527 | -0.011017 | 0.0033133 | 0.0040438 | 0.044906 | -0.002384 | -0.0018756 | -0.0026809 | -10.9314 | -0.97504 | -44.4122 | -1.3092 | -1.149 | -44.426 | -1.1856 | 1.3275 | 79.1153 | 1.0986 | 79.1061 | 1.5015 | 1.3824 | 1.4465 | -0.2655 | -79.9988 | -80.3329 | 42.9977 | 42.9611 | -0.27923 | 43.2266 | -0.013733 | 45.2454 | 0.091552 | 0.082397 | 45.6482 | 45.5933 | 45.5292 | 0.3479 | 0.28381 | 43.2632 | 43.103 | 0.40283 | 78.0075 | 43.4372 | 78.0167 | 43.1717 | 123.262 | -123.436 | -77.9251 | 42.8375 | 123.2529 | 33.2153 | 45.4742
1648.5469 | 123.3582 | -44.2245 | 79.0375 | -0.03479 | 0.0048343 | 0.043485 | 0.0045159 | -0.00065586 | 0.00049778 | -0.0020209 | -0.072052 | 0.0071585 | 0.0038302 | 0.042129 | -0.0038794 | -0.00059378 | 0.0037277 | -10.936 | -0.98877 | -44.5129 | -1.4099 | -1.3092 | -44.5267 | -1.3184 | 1.1169 | 79.1336 | 1.0757 | 79.0054 | 1.4099 | 1.2634 | 1.3458 | -0.28839 | -80.0262 | -80.4474 | 42.9153 | 42.9062 | -0.30212 | 43.1946 | -0.013733 | 45.3003 | 0.09613 | -0.032044 | 45.6345 | 45.5704 | 45.488 | 0.27008 | 0.18768 | 43.2037 | 43.103 | 0.33417 | 77.9297 | 43.5242 | 78.0579 | 43.2358 | 123.3582 | -123.5504 | -77.9617 | 42.8146 | 123.23 | 33.2886 | 45.3415
1649.4844 | 123.4314 | -44.1788 | 78.9917 | -0.080566 | 0.0044071 | 0.043485 | 0.0030207 | 0.0019077 | 0.0017794 | -0.00052553 | -0.075104 | 0.0037405 | 0.0038302 | 0.045119 | -0.0025976 | -0.0025164 | 0.0035141 | -11.0275 | -1.0986 | -44.4443 | -1.4008 | -1.236 | -44.4489 | -1.3046 | 1.1993 | 79.0878 | 1.2085 | 79.129 | 1.5747 | 1.4374 | 1.5793 | -0.2655 | -80.0903 | -80.3925 | 42.9428 | 42.8741 | -0.27008 | 43.1396 | -0.004578 | 45.3873 | 0.096131 | 0.13733 | 45.7535 | 45.7581 | 45.6162 | 0.37079 | 0.22888 | 43.2083 | 43.0435 | 0.36621 | 77.9205 | 43.3456 | 77.8793 | 43.0801 | 123.2666 | -123.436 | -77.7832 | 42.778 | 123.3078 | 33.1512 | 45.3781
1650.4844 | 123.381 | -44.2703 | 78.9322 | -0.03479 | 0.0041935 | 0.042844 | 0.0021661 | 0.00041234 | 0.0017794 | 0.0020379 | -0.093414 | 0.0060905 | 0.0055392 | 0.047896 | -0.003025 | 4.7018e-05 | 0.0035141 | -11.1328 | -1.1765 | -44.5221 | -1.6342 | -1.4328 | -44.6777 | -1.4969 | 1.0254 | 79.0558 | 1.149 | 78.978 | 1.4923 | 1.4008 | 1.4832 | -0.25177 | -80.1086 | -80.5664 | 42.8375 | 42.7734 | -0.40741 | 43.0252 | -0.15564 | 45.4193 | 0.1236 | 0.045776 | 45.7626 | 45.7535 | 45.6711 | 0.33417 | 0.25177 | 43.0893 | 42.8879 | 0.34332 | 77.829 | 43.3456 | 77.9068 | 43.0939 | 123.3261 | -123.4543 | -77.7832 | 42.6361 | 123.2483 | 33.1375 | 45.2957
1651.4844 | 123.3994 | -44.2932 | 78.8864 | -0.065308 | 0.0061161 | 0.041563 | 0.0021661 | 0.0010531 | 7.0582e-05 | -0.00073913 | 0.019501 | 0.0024589 | 0.004471 | 0.04042 | -0.0008886 | -0.001662 | 0.0018051 | -11.1603 | -1.2772 | -44.5404 | -1.6159 | -1.4648 | -44.5679 | -1.5152 | 1.8814 | 79.0283 | 1.2543 | 78.9459 | 1.6159 | 1.506 | 1.5839 | -0.24719 | -80.1636 | -80.5023 | 42.8284 | 42.778 | -0.27466 | 43.0252 | -0.027466 | 45.5475 | 0.14191 | 0.059509 | 45.9091 | 45.8771 | 45.7993 | 0.32959 | 0.25177 | 43.0756 | 42.9245 | 0.36163 | 77.6917 | 43.2632 | 77.774 | 43.0161 | 123.3215 | -123.4268 | -77.6321 | 42.6773 | 123.2391 | 33.1329 | 46.1746
1652.5469 | 123.3673 | -44.4763 | 78.7033 | -0.11108 | 0.0031253 | 0.043485 | 0.0030207 | -0.0017239 | 0.0015658 | -0.00095273 | -0.069 | 0.0026725 | 0.0055392 | 0.042983 | -0.0036658 | 0.00090142 | -0.00097194 | -11.2244 | -1.5015 | -44.7327 | -2.2156 | -1.9409 | -44.9158 | -1.8173 | 1.2268 | 78.8544 | 1.1856 | 78.8086 | 1.5564 | 1.4282 | 1.5381 | -0.25635 | -80.2048 | -80.9189 | 42.5354 | 42.659 | -0.43945 | 42.9153 | -0.1831 | 45.6619 | 0.15106 | 0.10529 | 46.0327 | 46.0144 | 45.9045 | 0.35248 | 0.24262 | 42.7917 | 42.5171 | 0.37079 | 77.623 | 43.2312 | 77.6688 | 42.9749 | 123.3307 | -123.436 | -77.5177 | 42.2607 | 123.2849 | 33.252 | 45.7031
1653.4844 | 123.4039 | -44.4443 | 78.7308 | -0.10345 | 0.0026981 | 0.043912 | 0.0019525 | 0.00062594 | 0.0017794 | -9.8328e-05 | 0.004242 | 0.0030997 | 0.0059664 | 0.04106 | -0.0028112 | -0.0025164 | -0.0011855 | -11.1145 | -1.5884 | -44.7052 | -1.8997 | -1.7578 | -44.7601 | -1.7853 | 1.9089 | 78.8315 | 1.2772 | 78.7949 | 1.6296 | 1.5152 | 1.6022 | -0.26093 | -80.3192 | -80.6305 | 42.6865 | 42.659 | -0.31586 | 42.9199 | -0.054932 | 45.7214 | 0.10071 | 0.064087 | 46.0739 | 46.0464 | 45.9595 | 0.32501 | 0.23804 | 42.9474 | 42.8055 | 0.35248 | 77.5177 | 43.1168 | 77.5543 | 42.8558 | 123.2758 | -123.436 | -77.4536 | 42.5446 | 123.2391 | 33.3298 | 46.3531
1654.5469 | 123.3398 | -44.4992 | 78.7582 | -0.027161 | 0.0037661 | 0.045194 | 0.0036615 | 0.00041234 | 0.00071138 | -0.0020209 | -0.10257 | 0.0037405 | 0.0046848 | 0.04042 | -0.0043066 | 0.00047422 | -0.0020401 | -11.1511 | -1.5244 | -44.6823 | -1.9592 | -1.8265 | -44.8105 | -1.8539 | 1.5381 | 78.891 | 1.2772 | 78.7674 | 1.6342 | 1.506 | 1.593 | -0.18311 | -80.2826 | -80.7175 | 42.6727 | 42.6453 | -0.31128 | 42.8284 | -0.12817 | 45.7764 | 0.13275 | 0.009155 | 46.1334 | 46.0922 | 46.0052 | 0.31586 | 0.22888 | 42.8558 | 42.7231 | 0.35705 | 77.4902 | 43.158 | 77.6138 | 42.9749 | 123.3902 | -123.4406 | -77.4811 | 42.54 | 123.2666 | 33.3481 | 46.0373
1655.4844 | 123.2849 | -44.4122 | 78.7308 | -0.080566 | 0.0046207 | 0.043912 | 0.0028069 | -0.00044226 | 7.0582e-05 | 0.0011835 | -0.032379 | 0.0030997 | 0.0019076 | 0.042129 | -0.0021704 | -0.0023028 | 0.00095066 | -11.0825 | -1.5656 | -44.6777 | -1.8448 | -1.6663 | -44.6777 | -1.7441 | 1.8311 | 78.8773 | 1.3641 | 78.9047 | 1.7487 | 1.6251 | 1.7395 | -0.2655 | -80.2963 | -80.5756 | 42.746 | 42.6682 | -0.2655 | 42.9337 | 0 | 45.7764 | 0.14648 | 0.17395 | 46.1609 | 46.1517 | 46.0373 | 0.37537 | 0.26093 | 43.0115 | 42.8329 | 0.38452 | 77.5406 | 43.1122 | 77.5131 | 42.8467 | 123.2895 | -123.4085 | -77.3666 | 42.5674 | 123.317 | 33.3298 | 46.2433
1656.5469 | 123.4589 | -119.751 | 3.4836 | -0.03479 | 0.00034827 | 0.12552 | 0.0047295 | 0.0023349 | -0.002493 | 0.00096987 | -0.13004 | 0.14665 | 0.0031894 | 0.0047446 | -0.003025 | -0.006789 | -0.0035355 | -30.8487 | -2.6596 | -120.0668 | -3.0762 | -2.9297 | -119.5816 | -3.0121 | 1.1765 | 3.653 | 3.1036 | 3.241 | 3.0167 | 2.9846 | 3.2913 | -0.31586 | -6.1432 | -6.5598 | 116.8213 | 116.7389 | 0.16937 | 117.0547 | 0.48523 | 122.8546 | 0.16937 | -0.24262 | 122.7676 | 123.0423 | 122.7356 | 0.18768 | -0.11902 | 117.1371 | 116.9907 | -0.086975 | 0.13733 | 117.4072 | 0.54932 | 117.0914 | 123.4039 | -123.5504 | -0.37994 | 116.6748 | 122.9919 | 88.9023 | 120.9274
1657.5 | 123.5458 | -120.4742 | 2.7557 | -0.057678 | 0.0041935 | 0.12594 | 0.0019525 | -0.00022866 | -0.00035682 | -0.0020209 | 0.0072936 | 0.14452 | 0.005112 | -0.0035868 | -0.0021704 | -0.0023028 | -0.00033114 | -29.7134 | -2.3987 | -120.5246 | -2.7054 | -2.5085 | -120.3415 | -2.5772 | 1.0483 | 2.8702 | 2.3712 | 2.6596 | 2.5909 | 2.5681 | 2.6779 | -0.050354 | -5.1544 | -5.4611 | 117.9657 | 117.897 | 0.13275 | 117.9474 | 0.1831 | 122.8455 | 0.11444 | -0.09613 | 123.0652 | 123.1522 | 123.0423 | 0.3067 | 0.19684 | 118.0161 | 117.8192 | 0.21973 | 0.28839 | 118.1259 | 0.49896 | 118.0756 | 123.3444 | -123.2803 | -0.38452 | 117.7689 | 123.1338 | 90.7608 | 121.5225
1658.4844 | 123.4634 | -120.7809 | 2.4994 | -0.050049 | 0.0041935 | 0.12701 | 0.0040887 | 0.0021213 | 0.0017794 | -0.0067205 | 0.059174 | 0.14495 | 0.0036166 | 0.0026084 | -0.001316 | -0.0040118 | 0.00095066 | -30.0613 | -2.4765 | -120.9641 | -2.9938 | -2.4857 | -121.138 | -2.8015 | 0.88806 | 2.5589 | 2.0691 | 2.3621 | 2.3804 | 2.3026 | 2.3987 | -0.1831 | -4.9759 | -5.4932 | 118.2953 | 117.9794 | -0.35706 | 118.1625 | -0.17395 | 122.85 | 0.059509 | -0.13733 | 123.1613 | 123.1796 | 123.0835 | 0.32959 | 0.23346 | 118.4784 | 117.9703 | 0.31128 | 0.29297 | 118.4875 | 0.48981 | 118.3044 | 123.3398 | -123.4634 | -0.4303 | 117.7872 | 123.143 | 90.7196 | 121.669
1659.5469 | 123.3673 | -120.6894 | 2.6505 | 0.033875 | 0.0037661 | 0.12744 | 0.0053705 | 0.0034029 | 0.00049778 | 0.0011835 | -0.14529 | 0.14601 | 0.0021212 | 0.0030356 | -0.0028112 | 0.00068782 | -0.0011855 | -30.0293 | -2.417 | -121.0419 | -2.8656 | -2.7237 | -120.6619 | -2.7924 | 0.93384 | 2.7557 | 2.1881 | 2.3849 | 2.3758 | 2.2522 | 2.417 | -0.35248 | -5.0674 | -5.5161 | 117.9657 | 117.897 | 0.027466 | 118.2495 | 0.37994 | 122.8775 | 0.10528 | -0.2655 | 123.0652 | 123.1064 | 122.9416 | 0.22888 | 0.064087 | 118.3182 | 118.1763 | 0.18768 | 0.19684 | 118.6249 | 0.56763 | 118.2724 | 123.4451 | -123.6923 | -0.46234 | 117.8238 | 123.0743 | 90.6601 | 121.6232
1660.5 | 123.3856 | -120.8542 | 2.504 | -0.027161 | 0.0037661 | 0.12552 | 0.0038751 | -0.0012967 | 0.0015658 | -0.0045843 | -0.032379 | 0.14409 | 0.003403 | 0.005599 | -0.0043066 | -0.0027302 | 0.0024461 | -29.9377 | -2.3621 | -121.1197 | -2.6917 | -2.5314 | -120.6757 | -2.5864 | 0.99335 | 2.5772 | 2.0279 | 2.2247 | 2.2705 | 2.2064 | 2.2888 | -0.2655 | -4.866 | -5.1956 | 118.3228 | 118.2678 | 0.17853 | 118.5333 | 0.44403 | 122.8821 | 0.073242 | -0.27924 | 123.1247 | 123.143 | 123.0606 | 0.26092 | 0.17853 | 118.5883 | 118.428 | 0.24261 | 0.19684 | 118.7576 | 0.54932 | 118.4921 | 123.4314 | -123.6237 | -0.47607 | 118.1625 | 123.0789 | 90.9164 | 121.8475
1661.5625 | 123.4222 | -120.5704 | 2.7695 | -0.065308 | 0.0061161 | 0.12317 | 0.0047295 | 0.00019874 | 0.002634 | -0.0011663 | -0.023224 | 0.14473 | 0.003403 | 0.00089939 | -0.0025976 | -0.0018756 | 0.0024461 | -29.8416 | -2.4536 | -121.0739 | -2.7969 | -2.6688 | -120.4514 | -2.6505 | 1.0986 | 2.8381 | 2.3621 | 2.6688 | 2.7054 | 2.5497 | 2.5589 | -0.50354 | -5.2231 | -5.5664 | 117.9016 | 117.9199 | 0.11902 | 118.4235 | 0.62256 | 122.9324 | 0.068665 | -0.10071 | 123.2758 | 123.1293 | 123.1201 | 0.19684 | 0.18768 | 118.4052 | 118.277 | 0.34332 | 0.3067 | 118.6203 | 0.47607 | 118.1168 | 123.4085 | -123.8434 | -0.40741 | 117.7734 | 123.2391 | 90.7288 | 121.669
1662.4844 | 123.4406 | -120.4926 | 2.7878 | -0.057678 | 0.0046207 | 0.12445 | 0.0015253 | -0.00044226 | 0.00071138 | -0.0020209 | -0.035431 | 0.14366 | 0.005112 | -0.0025186 | -0.0021704 | -0.0020892 | 9.6064e-05 | -29.9835 | -2.4719 | -120.6207 | -2.774 | -2.6367 | -120.5704 | -2.6505 | 1.0162 | 2.7283 | 2.3941 | 2.5909 | 2.7878 | 2.7374 | 2.742 | -0.12817 | -5.2597 | -5.5618 | 117.8558 | 117.8421 | -0.07782 | 117.9703 | 0.050354 | 122.8867 | -0.05951 | -0.19684 | 123.2803 | 123.2346 | 123.23 | 0.3479 | 0.34332 | 117.984 | 117.8467 | 0.39368 | 0.19684 | 118.1488 | 0.33417 | 118.0206 | 123.2208 | -123.4085 | -0.39368 | 117.7185 | 123.0835 | 90.509 | 121.5088
1663.4844 | 123.4177 | -120.9778 | 2.2888 | -0.072937 | 0.0048343 | 0.12701 | 0.0045159 | -0.00022866 | 0.0024204 | -0.0022345 | -0.078156 | 0.14473 | 0.0023348 | -0.0029458 | -0.0017432 | 0.00068782 | 0.0022323 | -30.3955 | -2.4353 | -121.225 | -2.71 | -2.536 | -120.9549 | -2.5818 | 0.93384 | 2.4353 | 1.8906 | 2.1744 | 2.2064 | 2.124 | 2.2202 | -0.24719 | -4.7241 | -4.9988 | 118.4418 | 118.396 | 0.022888 | 118.6432 | 0.27008 | 122.8683 | 0.14649 | -0.11444 | 123.1842 | 123.1979 | 123.1018 | 0.32959 | 0.23346 | 118.689 | 118.515 | 0.31586 | 0.28381 | 118.7897 | 0.54474 | 118.5425 | 123.4131 | -123.5138 | -0.39825 | 118.2678 | 123.1522 | 90.5823 | 121.9116
1664.5469 | 123.3765 | -120.401 | 2.9388 | -0.050049 | 0.0026981 | 0.12509 | 0.0040887 | -0.00086946 | -0.0016384 | -0.0033025 | -0.1575 | 0.1443 | 0.0038302 | 0.002822 | -0.0025976 | -0.0052936 | -0.0048171 | -30.0018 | -2.3026 | -120.9 | -2.5955 | -2.4033 | -120.4651 | -2.4719 | 1.0712 | 2.9938 | 2.5497 | 2.9434 | 2.8152 | 2.861 | 2.8885 | -0.49896 | -5.2414 | -5.5344 | 117.9977 | 117.9291 | -0.064087 | 118.428 | 0.43488 | 122.9507 | 0.054931 | 0.004577 | 123.2162 | 123.2895 | 123.262 | 0.33874 | 0.31128 | 118.4967 | 118.3044 | 0.2655 | 0.39368 | 118.5974 | 0.44403 | 118.0984 | 123.3948 | -123.8388 | -0.3891 | 117.8055 | 123.3444 | 90.3992 | 121.4722
1665.5 | 123.3261 | -120.5154 | 2.8336 | -0.057678 | 0.0016299 | 0.12509 | 0.0034479 | 0.0038303 | 0.0011386 | -0.00052553 | -0.13614 | 0.14302 | 0.0048984 | 0.004531 | -0.0021704 | -0.0018756 | -0.0018265 | -29.8691 | -2.3209 | -120.694 | -2.7283 | -2.5772 | -120.5658 | -2.6367 | 1.1444 | 2.9984 | 2.6184 | 2.6093 | 2.7054 | 2.4857 | 2.5314 | -0.17853 | -5.1544 | -5.5618 | 117.9382 | 117.8787 | -0.050354 | 118.0573 | 0.12817 | 123.1338 | 0.1648 | -0.2243 | 123.2208 | 123.0469 | 123.0011 | -0.086975 | -0.13275 | 118.1168 | 117.9657 | 0.086975 | -0.009155 | 118.3731 | 0.37994 | 118.1946 | 123.5138 | -123.5275 | -0.21515 | 117.7872 | 123.1247 | 90.6464 | 121.6599
1666.5469 | 123.3856 | -120.3003 | 3.067 | -0.019531 | 0.0052615 | 0.12616 | 0.0028069 | -0.0015103 | -0.0014248 | 0.00011527 | -0.12088 | 0.1396 | 0.0055392 | 0.0017538 | -0.0028112 | -0.0025164 | 0.0030869 | -29.9835 | -2.0462 | -120.7993 | -2.4719 | -2.3346 | -120.694 | -2.3666 | 0.9201 | 2.8198 | 2.33 | 2.9297 | 2.9663 | 2.7283 | 2.8519 | -0.49896 | -5.1132 | -5.5389 | 117.9657 | 117.9337 | -0.39368 | 118.4326 | 0.10529 | 122.6303 | -0.24719 | -0.13733 | 123.2666 | 123.1522 | 123.0286 | 0.52185 | 0.39825 | 118.4647 | 118.3273 | 0.63629 | 0.59967 | 118.7531 | 0.48981 | 118.2541 | 123.1201 | -123.8663 | -0.737 | 117.8284 | 123.23 | 90.3168 | 121.2204
1667.4844 | 123.4497 | -120.8633 | 2.4078 | -0.019531 | 0.0018435 | 0.12317 | 0.0028069 | 0.0012667 | 0.00028418 | -0.0028753 | 0.016449 | 0.14238 | 0.003403 | -0.0070046 | -0.001316 | -0.0042254 | -0.0020401 | -29.8599 | -2.3666 | -121.1288 | -2.6276 | -2.4353 | -120.7031 | -2.4902 | 1.0574 | 2.504 | 2.0004 | 2.2797 | 2.3529 | 2.2842 | 2.3254 | -0.2655 | -4.7745 | -5.0354 | 118.428 | 118.3731 | 0.16022 | 118.6386 | 0.42572 | 122.8638 | 0.09613 | -0.12817 | 123.2162 | 123.1888 | 123.1476 | 0.32501 | 0.28381 | 118.6935 | 118.5013 | 0.35248 | 0.27924 | 118.7622 | 0.50354 | 118.4967 | 123.3673 | -123.5367 | -0.40741 | 118.2358 | 123.143 | 91.0034 | 121.9208
1668.5469 | 123.3856 | -120.1721 | 3.1723 | -0.072937 | 0.0022709 | 0.12573 | 0.0049433 | 0.00041234 | 0.0013522 | 0.0011835 | -0.12088 | 0.1458 | 0.0029758 | 0.00389 | -0.002384 | -0.0023028 | 0.0015915 | -29.9835 | -2.5818 | -120.9595 | -2.98 | -2.8519 | -119.4489 | -2.8748 | 0.87433 | 3.5202 | 2.8427 | 3.0945 | 3.1403 | 2.9297 | 2.8839 | -0.78735 | -5.7541 | -6.1523 | 117.3203 | 117.2974 | 0.72327 | 118.0847 | 1.5106 | 123.0148 | 0.3479 | -0.07782 | 123.3124 | 123.056 | 123.1018 | 0.041199 | 0.086975 | 118.1076 | 117.9794 | 0.29755 | 0.25177 | 118.3777 | 0.67749 | 117.5903 | 123.6923 | -124.1318 | -0.32959 | 117.1921 | 123.2666 | 90.1886 | 121.0464
1669.4844 | 123.4039 | -120.726 | 2.5177 | 0.049133 | 0.0046207 | 0.12509 | 0.0023797 | -0.0019377 | -0.00099762 | -0.0018073 | -0.072052 | 0.1443 | 0.005112 | -0.003373 | 0.0001794 | -0.0018756 | 0.00052346 | -29.8096 | -2.3209 | -121.0739 | -2.6093 | -2.4445 | -120.694 | -2.4948 | 1.0117 | 2.5452 | 2.0645 | 2.3895 | 2.4353 | 2.3346 | 2.417 | -0.3479 | -4.8386 | -5.127 | 118.2816 | 118.2312 | 0.032043 | 118.5791 | 0.37994 | 122.7905 | 0.027466 | -0.12817 | 123.1613 | 123.143 | 123.0606 | 0.35248 | 0.27008 | 118.6295 | 118.4647 | 0.37079 | 0.32501 | 118.7531 | 0.48065 | 118.4052 | 123.2712 | -123.5916 | -0.45319 | 118.1168 | 123.1155 | 90.9164 | 121.7377
1670.5469 | 123.4268 | -120.6665 | 2.5818 | -0.065308 | 0.0026981 | 0.12658 | 0.0038751 | 0.0044711 | 0.00071138 | -0.0039435 | -0.11172 | 0.14623 | 0.0025484 | 0.00068579 | -0.0028112 | -0.00059378 | 0.0020187 | -29.6997 | -2.3849 | -121.0831 | -2.6779 | -2.5314 | -120.6573 | -2.5955 | 1.0849 | 2.6093 | 2.1286 | 2.4628 | 2.4948 | 2.3804 | 2.4628 | -0.41656 | -4.9667 | -5.2597 | 118.1351 | 118.071 | 0.009155 | 118.4875 | 0.42572 | 122.7951 | 0.027466 | -0.11902 | 123.1613 | 123.1293 | 123.0469 | 0.33417 | 0.25177 | 118.5516 | 118.4052 | 0.36621 | 0.33417 | 118.6981 | 0.48065 | 118.2816 | 123.2758 | -123.6649 | -0.45319 | 117.9886 | 123.1293 | 90.9668 | 121.7514
1671.4844 | 123.3261 | -120.401 | 2.8839 | -0.10345 | 0.0035525 | 0.12359 | 2.9918e-05 | -0.0025785 | 0.0015658 | -0.0037299 | -0.026276 | 0.14388 | 0.0019076 | -0.00059601 | -0.0025976 | -0.0025164 | -0.0037491 | -29.7043 | -2.3209 | -120.9915 | -2.5909 | -2.4353 | -120.5887 | -2.4628 | 1.3367 | 2.6917 | 2.1927 | 2.5223 | 2.5726 | 2.7466 | 2.6505 | -0.59052 | -5.2048 | -5.4749 | 117.9657 | 117.9382 | -0.18768 | 118.5287 | 0.40283 | 122.5937 | -0.19226 | -0.36163 | 122.9736 | 123.0515 | 123.1476 | 0.45776 | 0.55389 | 118.5562 | 118.4006 | 0.37994 | 0.32959 | 118.6707 | 0.49896 | 118.0801 | 123.0927 | -123.8754 | -0.69122 | 117.8101 | 122.9233 | 90.6967 | 121.7377
1672.4844 | 123.3353 | -120.8313 | 2.4673 | -0.057678 | 0.0056889 | 0.12573 | 0.0043023 | 0.0038303 | 0.0017794 | -0.0020209 | -0.1514 | 0.1379 | 0.00618 | -0.00038241 | -0.0062292 | 0.00026062 | -0.0041763 | -29.7592 | -2.3621 | -121.1151 | -2.774 | -2.6184 | -120.8221 | -2.6871 | 0.92926 | 2.5818 | 1.9043 | 2.2247 | 2.1423 | 1.9775 | 2.1011 | -0.28381 | -4.8294 | -5.2414 | 118.2129 | 118.1442 | 0.009155 | 118.428 | 0.29297 | 122.7356 | 0.11444 | -0.24262 | 122.9736 | 122.9324 | 122.8088 | 0.19684 | 0.073242 | 118.4967 | 118.3411 | 0.23804 | 0.32043 | 118.7531 | 0.67749 | 118.4692 | 123.4131 | -123.5825 | -0.56305 | 118.0573 | 123.056 | 91.0721 | 121.7606
1673.5469 | 123.381 | -120.5017 | 2.7328 | -0.057678 | 0.0031253 | 0.12359 | 0.0053705 | 0.0016939 | 0.0017794 | 0.0016107 | -0.11783 | 0.14452 | 0.0040438 | -0.002305 | -0.0034522 | 0.00090142 | -0.0022537 | -29.8141 | -2.4124 | -120.5704 | -2.8152 | -2.6413 | -120.2316 | -2.7008 | 0.87891 | 2.9388 | 2.2934 | 2.6093 | 2.5131 | 2.417 | 2.4765 | -0.068665 | -5.1453 | -5.5481 | 117.8604 | 117.8009 | 0.27008 | 117.8696 | 0.33875 | 122.7951 | 0.20599 | -0.1236 | 123.0148 | 122.9782 | 122.9187 | 0.1831 | 0.1236 | 117.9291 | 117.7551 | 0.21973 | 0.31586 | 118.158 | 0.64545 | 118.0893 | 123.4406 | -123.3032 | -0.43945 | 117.6865 | 123.111 | 90.6876 | 121.3806
1674.4844 | 123.4085 | -120.7947 | 2.4399 | -0.03479 | 0.0031253 | 0.12509 | 0.0034479 | -0.0034329 | 0.0032748 | -0.0022345 | -0.026276 | 0.14366 | 0.0014804 | -0.0025186 | -0.002384 | -0.0023028 | -0.0028945 | -29.924 | -2.4857 | -121.0739 | -2.8427 | -2.6779 | -120.7169 | -2.7008 | 0.98419 | 2.5497 | 1.9958 | 2.1652 | 2.2797 | 2.179 | 2.243 | -0.27924 | -4.9255 | -5.2826 | 118.1168 | 118.0939 | 0.07782 | 118.3731 | 0.35706 | 122.7905 | 0.10986 | -0.27466 | 123.0743 | 123.0377 | 122.9736 | 0.24719 | 0.18311 | 118.396 | 118.2312 | 0.28381 | 0.16937 | 118.5883 | 0.55389 | 118.309 | 123.3444 | -123.5138 | -0.44403 | 117.952 | 122.9599 | 90.8707 | 121.7789
1675.5 | 123.3765 | -120.8359 | 2.4994 | -0.042419 | 0.0035525 | 0.12637 | 0.0038751 | -0.0021513 | 0.00049778 | 0.0024653 | -0.13309 | 0.14623 | 0.0053256 | -0.00080961 | -0.0038794 | -0.0012348 | 0.0018051 | -30.0156 | -2.4307 | -121.1838 | -2.8885 | -2.7466 | -120.8496 | -2.7786 | 0.86517 | 2.5497 | 1.886 | 2.3209 | 2.1011 | 1.9684 | 2.124 | -0.3479 | -4.9301 | -5.3879 | 118.0893 | 118.0573 | -0.013733 | 118.4052 | 0.33417 | 122.7219 | 0.050354 | -0.17853 | 122.937 | 122.9599 | 122.8043 | 0.23804 | 0.082398 | 118.4372 | 118.2953 | 0.21515 | 0.43488 | 118.7531 | 0.66376 | 118.4052 | 123.3856 | -123.6832 | -0.6134 | 117.9474 | 123.1567 | 90.8203 | 121.701
1676.4844 | 123.4177 | -120.6802 | 2.5818 | -0.072937 | 0.0054751 | 0.12253 | 0.0030207 | 0.0014803 | 0.0017794 | -0.0013799 | -0.056793 | 0.14281 | 0.0031894 | -0.003373 | -0.0019568 | -0.0027302 | 0.0037277 | -29.8553 | -2.5177 | -120.8176 | -2.829 | -2.6505 | -120.4697 | -2.7328 | 1.1124 | 2.7328 | 2.243 | 2.4765 | 2.4811 | 2.2156 | 2.3392 | -0.13733 | -5.0995 | -5.4108 | 118.0298 | 117.9474 | 0.21057 | 118.0847 | 0.3479 | 122.9233 | 0.15106 | -0.10529 | 123.1613 | 123.0194 | 122.8958 | 0.09613 | -0.027466 | 118.1671 | 117.9886 | 0.23804 | 0.23346 | 118.2999 | 0.48981 | 118.1625 | 123.4131 | -123.3994 | -0.33874 | 117.8513 | 123.1567 | 90.8249 | 121.7926
1677.4844 | 123.3582 | -120.9229 | 2.3987 | -0.042419 | 0.0031253 | 0.12552 | 0.0030207 | -0.0015103 | 0.00049778 | -9.8328e-05 | -0.14224 | 0.14345 | 0.0021212 | 0.0049582 | -0.0028112 | -0.0014484 | 0.0022323 | -29.9881 | -2.8519 | -121.2112 | -3.3096 | -3.1677 | -120.6253 | -3.1311 | 0.96588 | 2.5177 | 1.9455 | 2.1378 | 2.1835 | 2.0462 | 2.1606 | -0.28839 | -5.2506 | -5.7083 | 117.7551 | 117.7917 | 0.29755 | 118.0801 | 0.58594 | 122.8683 | 0.11902 | -0.26093 | 123.1064 | 123.0835 | 122.9691 | 0.21515 | 0.10071 | 118.0435 | 117.9016 | 0.23804 | 0.19226 | 118.3594 | 0.5722 | 118.071 | 123.4406 | -123.6099 | -0.45319 | 117.6132 | 123.0606 | 90.9348 | 121.8887
1678.5469 | 123.3719 | -120.1996 | 3.2135 | -0.11108 | 0.0041935 | 0.12445 | 0.0030207 | 0.0029757 | 0.0013522 | -0.0030889 | -0.075104 | 0.14302 | 0.0055392 | -0.0012368 | -0.0017432 | -0.00059378 | 0.00073706 | -29.8599 | -2.7512 | -120.6299 | -3.035 | -2.8336 | -120.3232 | -2.9388 | 1.2817 | 2.9846 | 2.4857 | 2.9343 | 3.1815 | 3.0212 | 2.861 | -0.4303 | -5.9647 | -6.2485 | 117.366 | 117.2607 | -0.1236 | 117.691 | 0.3067 | 122.6852 | -0.22888 | -0.27924 | 123.381 | 123.0606 | 123.2208 | 0.37537 | 0.53558 | 117.7963 | 117.5949 | 0.6958 | 0.44861 | 117.8787 | 0.49896 | 117.4484 | 123.1842 | -123.8434 | -0.72784 | 117.1646 | 123.1338 | 90.3397 | 121.4813
1679.4844 | 123.4085 | -121.0007 | 2.2842 | -0.088196 | 0.0035525 | 0.12359 | 0.0038751 | -0.0045011 | 0.002634 | -0.0015935 | -0.035431 | 0.14388 | 0.0036166 | 0.0032492 | -0.0021704 | -0.00080758 | -0.00097194 | -29.9561 | -2.6733 | -121.2845 | -2.9709 | -2.7924 | -120.8542 | -2.8564 | 1.0666 | 2.3438 | 1.8494 | 2.1149 | 2.179 | 2.1011 | 2.1606 | -0.28381 | -4.9576 | -5.2551 | 118.2083 | 118.1442 | 0.14648 | 118.428 | 0.4303 | 122.85 | 0.059509 | -0.16937 | 123.1796 | 123.1613 | 123.1018 | 0.31128 | 0.25177 | 118.4921 | 118.3136 | 0.32959 | 0.2655 | 118.6111 | 0.49439 | 118.3273 | 123.3444 | -123.5687 | -0.43488 | 118.0298 | 123.1155 | 91.0446 | 122.0673
1680.5625 | 123.2895 | -120.5658 | 2.7008 | -0.057678 | 0.0033389 | 0.12253 | 0.0060113 | -0.00065586 | 0.00092498 | 0.0011835 | -0.16055 | 0.1443 | 0.0059664 | 0.0023948 | -0.0038794 | -0.0023028 | 0.0018051 | -29.9332 | -2.5955 | -120.8817 | -3.0579 | -2.9388 | -120.6345 | -2.9572 | 1.0803 | 2.8244 | 2.2568 | 2.4536 | 2.4719 | 2.3483 | 2.4857 | -0.31586 | -5.2963 | -5.7587 | 117.627 | 117.6086 | -0.068664 | 117.9245 | 0.24719 | 122.8226 | 0.1236 | -0.24719 | 123.0377 | 123.0515 | 122.9141 | 0.22888 | 0.091553 | 117.9428 | 117.8238 | 0.21515 | 0.19684 | 118.2861 | 0.56763 | 117.9703 | 123.3902 | -123.5825 | -0.44403 | 117.5079 | 123.0194 | 90.6326 | 121.6461
1681.4844 | 123.4222 | -120.575 | 2.6871 | -0.027161 | 0.0026981 | 0.12274 | 0.0032343 | -0.0040739 | 7.0582e-05 | -0.0013799 | -0.023224 | 0.14003 | 0.0048984 | -0.0027322 | -0.0038794 | -0.0042254 | -0.0026809 | -29.6402 | -2.6047 | -120.8588 | -2.9068 | -2.7283 | -120.4147 | -2.7969 | 1.4053 | 2.742 | 2.2522 | 2.5406 | 2.5864 | 2.4765 | 2.5406 | -0.28381 | -5.2917 | -5.5939 | 117.8467 | 117.778 | 0.16022 | 118.0618 | 0.44403 | 122.8271 | 0.054931 | -0.14648 | 123.1613 | 123.1155 | 123.0515 | 0.28839 | 0.2243 | 118.1305 | 117.952 | 0.33417 | 0.28839 | 118.2541 | 0.48981 | 117.9703 | 123.317 | -123.5458 | -0.43488 | 117.6682 | 123.1155 | 90.9348 | 121.9803
1682.5469 | 123.3902 | -120.4147 | 2.9755 | 0.10254 | 0.0029117 | 0.12594 | 0.0036615 | 0.00062594 | -0.001852 | -0.00095273 | -0.13004 | 0.14388 | 0.0046848 | 0.00389 | -0.0025976 | -0.0010212 | 0.0022323 | -29.7363 | -2.6688 | -120.694 | -3.0487 | -2.9251 | -120.369 | -2.9663 | 1.3962 | 3.0396 | 2.4994 | 3.0121 | 2.9297 | 2.8107 | 2.6917 | -0.27924 | -5.6442 | -6.0242 | 117.4896 | 117.4484 | 0.045776 | 117.7277 | 0.32501 | 122.9141 | 0.064087 | 0.036621 | 123.3444 | 123.1064 | 123.2254 | 0.19226 | 0.31128 | 117.7689 | 117.6453 | 0.4303 | 0.51269 | 118.0252 | 0.54016 | 117.746 | 123.4543 | -123.6694 | -0.47607 | 117.366 | 123.4268 | 90.6784 | 121.8109
1683.4844 | 123.4177 | -119.0506 | 4.3671 | -0.027161 | 0.0022709 | 0.12402 | 0.0017389 | 0.0010531 | -0.00057042 | 0.00096987 | -0.044586 | 0.14366 | 0.004471 | -0.0025186 | -0.0019568 | -0.0027302 | 0.00030966 | -29.2053 | -2.6505 | -119.5267 | -2.9205 | -2.7374 | -118.9178 | -2.8061 | 2.2156 | 4.1565 | 3.6438 | 4.4403 | 4.5136 | 4.3991 | 4.1153 | -0.47607 | -7.0175 | -7.2876 | 116.3132 | 116.2445 | 0.13275 | 116.7206 | 0.60883 | 122.6944 | -0.21057 | 0.073243 | 123.5641 | 123.1659 | 123.4497 | 0.4715 | 0.75531 | 116.7892 | 116.6061 | 0.86975 | 0.79651 | 116.8762 | 0.5127 | 116.4001 | 123.2071 | -123.8937 | -0.72327 | 116.1301 | 123.4909 | 89.8453 | 121.2662
1684.4844 | 123.3856 | -119.6045 | 3.685 | -0.095825 | 0.0037661 | 0.12103 | 0.0045159 | -0.0019377 | 7.0582e-05 | 0.0026789 | -0.01712 | 0.14153 | 0.0038302 | -0.0012368 | -0.0034522 | -0.0031574 | -0.00033114 | -29.5166 | -2.7878 | -119.4214 | -3.1448 | -2.98 | -119.2383 | -3.0121 | 1.6983 | 4.0192 | 3.5934 | 3.7262 | 3.9001 | 3.5751 | 3.5019 | 0.1831 | -6.4728 | -6.8298 | 116.6244 | 116.5924 | 0.36621 | 116.4093 | 0.18311 | 123.1979 | 0.33417 | 0.041198 | 123.5046 | 123.1064 | 123.1796 | -0.091553 | -0.018311 | 116.4413 | 116.2766 | 0.3067 | 0.13275 | 116.6336 | 0.42572 | 116.8167 | 123.6237 | -123.1064 | -0.091553 | 116.4597 | 123.3307 | 90.0879 | 121.3028
1685.5469 | 123.381 | -120.9366 | 2.3392 | -0.057678 | 0.0050479 | 0.12338 | 0.0032343 | -1.486e-05 | 0.0011386 | -0.0026617 | -0.093414 | 0.14409 | 0.0038302 | -0.0025186 | -0.003025 | -0.0020892 | 0.0020187 | -29.8828 | -2.7969 | -121.2524 | -3.1174 | -2.9709 | -120.8633 | -3.0533 | 0.97504 | 2.3849 | 1.9089 | 2.1561 | 2.2064 | 2.1057 | 2.1973 | -0.31586 | -5.1361 | -5.4565 | 117.9657 | 117.8833 | 0.073242 | 118.1992 | 0.3891 | 122.8455 | 0.045777 | -0.1831 | 123.143 | 123.1338 | 123.0423 | 0.28839 | 0.19684 | 118.2816 | 118.1351 | 0.29755 | 0.24719 | 118.4555 | 0.47607 | 118.1396 | 123.3215 | -123.5916 | -0.4303 | 117.8192 | 123.0927 | 91.0538 | 121.9116
1686.4844 | 123.4131 | -120.2637 | 2.9205 | -0.050049 | 0.0033389 | 0.12616 | 0.0038751 | 0.00062594 | 0.002634 | -0.0067205 | -0.05069 | 0.1426 | 0.0031894 | 0.00047219 | -0.0032386 | -0.0031574 | -0.00033114 | -29.3838 | -2.8473 | -120.9778 | -3.1403 | -2.9709 | -120.433 | -3.0304 | 1.3 | 2.6413 | 2.1744 | 2.6642 | 2.5955 | 2.8793 | 3.1357 | -0.71411 | -5.7678 | -6.0608 | 117.2928 | 117.2333 | -0.16937 | 117.9474 | 0.54474 | 122.438 | -0.27924 | -0.25635 | 122.8592 | 123.3994 | 123.143 | 0.9613 | 0.70496 | 118.0069 | 117.8375 | 0.42114 | 0.48981 | 118.1305 | 0.46692 | 117.4164 | 122.905 | -123.8983 | -0.74616 | 117.1234 | 122.9279 | 90.8798 | 121.5637
1687.5469 | 123.4268 | -120.0577 | 3.1952 | -0.050049 | 0.0037661 | 0.12466 | 0.0045159 | -0.0010831 | 0.00028418 | -0.0050115 | -0.05069 | 0.14046 | 0.0042574 | -0.0044412 | -0.003025 | -0.0012348 | -0.0011855 | -29.7684 | -2.8473 | -120.607 | -3.1357 | -2.948 | -120.1126 | -3.0121 | 1.9867 | 3.1769 | 2.623 | 3.2272 | 3.035 | 2.8793 | 3.1815 | -0.54932 | -6.0425 | -6.3309 | 117.1097 | 117.0456 | -0.054932 | 117.5949 | 0.49438 | 122.6807 | -0.01831 | 0.032044 | 123.0927 | 123.2391 | 122.937 | 0.55847 | 0.25635 | 117.659 | 117.4713 | 0.41199 | 0.60425 | 117.7597 | 0.55389 | 117.2104 | 123.2346 | -123.8022 | -0.5722 | 116.922 | 123.2849 | 90.2893 | 122.0444
1688.4844 | 123.4406 | -120.6345 | 2.6093 | -0.050049 | 0.0063297 | 0.12423 | 0.0030207 | -0.0034329 | 0.0017794 | 0.00032907 | -0.053741 | 0.14302 | 0.005112 | 0.00389 | -0.0034522 | -0.0010212 | -0.00011754 | -29.718 | -2.829 | -120.7993 | -3.0899 | -2.9297 | -120.4605 | -2.9846 | 1.2085 | 2.742 | 2.2705 | 2.4628 | 2.5726 | 2.4811 | 2.5772 | -0.16479 | -5.4382 | -5.6992 | 117.7048 | 117.6498 | 0.17395 | 117.8146 | 0.33875 | 122.905 | 0.13275 | -0.14648 | 123.2071 | 123.2117 | 123.1155 | 0.3067 | 0.21057 | 117.8696 | 117.7094 | 0.30212 | 0.19226 | 117.9703 | 0.4715 | 117.8055 | 123.3765 | -123.4085 | -0.33874 | 117.5446 | 123.0972 | 90.9164 | 121.843
1689.5469 | 123.349 | -120.9045 | 2.3666 | -0.011902 | 0.0039799 | 0.12338 | 0.0034479 | 0.0023349 | -0.001852 | -0.0018073 | -0.056793 | 0.1426 | 0.0014804 | 0.0019674 | -0.0038794 | -0.0040118 | -0.00054474 | -29.6906 | -2.9388 | -121.2021 | -3.2181 | -3.0716 | -120.7535 | -3.1265 | 1.062 | 2.449 | 1.9318 | 2.0554 | 2.4353 | 2.1881 | 2.2064 | -0.29755 | -5.3055 | -5.5847 | 117.8329 | 117.778 | 0.15106 | 118.0756 | 0.44861 | 122.8363 | 0.082398 | -0.31128 | 123.3398 | 123.111 | 123.0927 | 0.27466 | 0.25635 | 118.1305 | 117.984 | 0.50354 | 0.1236 | 118.2632 | 0.51727 | 117.9657 | 123.3536 | -123.5687 | -0.43488 | 117.6865 | 122.9599 | 91.214 | 121.9666
1690.4844 | 123.4863 | -120.1996 | 3.067 | -0.050049 | 0.0041935 | 0.12188 | 0.0045159 | -0.0021513 | 0.00049778 | -0.00031193 | -0.053741 | 0.14174 | 0.0027622 | 0.00089939 | -0.0047338 | -0.001662 | -0.0035355 | -29.8004 | -3.1311 | -120.3644 | -3.4103 | -3.2593 | -120.2179 | -3.3234 | 1.355 | 3.2089 | 2.7191 | 2.9572 | 2.9846 | 2.8885 | 2.9114 | -0.16479 | -6.1981 | -6.4774 | 116.9403 | 116.8762 | -0.018311 | 117.041 | 0.14648 | 122.9187 | 0.14191 | -0.10986 | 123.1842 | 123.111 | 123.0881 | 0.19226 | 0.16937 | 117.1051 | 116.954 | 0.2655 | 0.23804 | 117.2333 | 0.48981 | 117.0685 | 123.4085 | -123.4314 | -0.3479 | 116.7892 | 123.1567 | 90.3992 | 121.5546
1691.5469 | 123.3994 | -120.8405 | 2.3758 | -0.0042723 | 0.0026981 | 0.12423 | 0.0040887 | -0.0034329 | 0.0019932 | -0.0030889 | -0.053741 | 0.14153 | 0.0042574 | -0.004014 | -0.0028112 | -0.0020892 | 0.0041551 | -5.8044 | -3.0808 | -121.1929 | -3.3646 | -3.2227 | -120.7581 | -3.241 | 1.0345 | 2.4536 | 1.973 | 2.2659 | 2.3209 | 2.2339 | 2.3071 | -0.35248 | -5.4565 | -5.7404 | 117.6178 | 117.5995 | 0.082397 | 117.952 | 0.43488 | 122.8134 | 0.07782 | -0.10986 | 123.1613 | 123.1476 | 123.0743 | 0.33417 | 0.26093 | 117.9703 | 117.8284 | 0.3479 | 0.29297 | 118.1122 | 0.48065 | 117.7597 | 123.2941 | -123.5687 | -0.40283 | 117.4759 | 123.1064 | 115.036 | 121.875
1692.4844 | 123.349 | -120.2682 | 2.9938 | -0.011902 | 0.0044071 | 0.12274 | 0.0038751 | 0.0040439 | 0.0017794 | -0.0011663 | -0.15445 | 0.14644 | 0.004471 | 0.0036764 | -0.002384 | -0.00016658 | -0.00054474 | -5.5801 | -3.2089 | -120.3049 | -3.6026 | -3.479 | -120.2362 | -3.5202 | 1.3733 | 3.2364 | 2.7832 | 2.8931 | 2.9022 | 2.5818 | 2.8107 | -0.036621 | -6.2027 | -6.5964 | 116.7892 | 116.748 | 0.032044 | 116.7847 | 0.068665 | 123.0515 | 0.24261 | -0.10071 | 123.1705 | 123.0789 | 122.85 | 0.027466 | -0.20142 | 116.8259 | 116.7023 | 0.11902 | 0.10986 | 117.0959 | 0.45319 | 117.0593 | 123.5046 | -123.2986 | -0.21057 | 116.6656 | 123.1613 | 114.6881 | 121.6415
1693.4844 | 123.3398 | -120.8588 | 2.4719 | -0.072937 | 0.0026981 | 0.12445 | 0.0040887 | -0.0010831 | 0.00092498 | 0.00011527 | -0.12088 | 0.1443 | 0.004471 | 0.00025839 | -0.0036658 | -0.0031574 | -0.0016129 | -6.3812 | -3.1723 | -121.1472 | -3.6301 | -3.5019 | -120.7214 | -3.5294 | 1.0071 | 2.5223 | 1.973 | 2.2202 | 2.2751 | 2.1286 | 2.2614 | -0.28839 | -5.6442 | -6.102 | 117.3569 | 117.3294 | 0.13733 | 117.6178 | 0.42572 | 122.8317 | 0.050354 | -0.25177 | 123.1339 | 123.1201 | 122.9874 | 0.28839 | 0.15564 | 117.6453 | 117.5171 | 0.30212 | 0.24719 | 117.9749 | 0.54932 | 117.6865 | 123.381 | -123.6191 | -0.49896 | 117.2287 | 123.0789 | 114.4775 | 121.8658
1694.5469 | 123.3994 | -120.8862 | 2.4445 | -0.072937 | 0.0014163 | 0.12381 | 0.0028069 | -0.00044226 | 0.00092498 | -0.0035163 | -0.047638 | 0.14324 | 0.0042574 | -0.00038241 | -0.0002478 | -0.0040118 | 0.0018051 | -3.4195 | -3.1174 | -121.0785 | -3.5065 | -3.3691 | -120.7352 | -3.392 | 1.0208 | 2.5269 | 2.0279 | 2.3026 | 2.4078 | 2.2888 | 2.179 | -0.19226 | -5.5618 | -5.9509 | 117.5171 | 117.4942 | 0.15106 | 117.6865 | 0.34332 | 122.9141 | 0.082397 | -0.14191 | 123.2941 | 123.0652 | 123.175 | 0.15106 | 0.26092 | 117.7094 | 117.572 | 0.37994 | 0.27466 | 117.9611 | 0.49896 | 117.7689 | 123.4131 | -123.5229 | -0.41656 | 117.3798 | 123.1888 | 117.4667 | 121.907
1695.4844 | 123.1934 | -119.8471 | 3.5065 | 0.018616 | 0.0048343 | 0.12167 | 0.0036615 | 0.0034029 | 0.0011386 | 0.0026789 | -0.081207 | 0.14452 | 0.0059664 | 0.00068579 | -0.002384 | -0.0018756 | -0.0024673 | -3.7674 | -3.447 | -120.2866 | -3.8864 | -3.7582 | -120.6207 | -3.772 | 1.2634 | 3.1357 | 2.5955 | 3.5889 | 3.3188 | 3.0899 | 3.2959 | -0.43945 | -6.9534 | -7.3929 | 116.0889 | 116.0751 | -0.77362 | 116.5146 | -0.33417 | 122.4426 | -0.37079 | 0.082397 | 123.1659 | 123.143 | 122.937 | 0.70038 | 0.49438 | 116.5283 | 116.4001 | 0.72327 | 0.99335 | 116.8396 | 0.54016 | 116.4001 | 122.9828 | -123.793 | -0.91095 | 115.9607 | 123.436 | 116.0797 | 121.1105
1696.5469 | 123.349 | -119.957 | 3.2959 | -0.065308 | 0.0024845 | 0.12188 | 0.0062249 | 0.0021213 | -0.00078402 | 0.0011835 | -0.059845 | 0.14452 | 0.0031894 | -0.0018778 | -0.0021704 | -0.0018756 | 0.0018051 | -5.3238 | -2.4536 | -120.2087 | -2.774 | -2.623 | -120.3278 | -2.6871 | 1.4465 | 3.447 | 2.9755 | 3.2455 | 2.8839 | 2.9984 | 3.0579 | -0.25177 | -5.7495 | -6.0699 | 117.334 | 117.2699 | -0.37079 | 117.5217 | -0.11902 | 122.9324 | 0.15106 | -0.050354 | 122.8409 | 123.0148 | 122.9553 | 0.082397 | 0.022888 | 117.5858 | 117.4347 | -0.091553 | 0.27008 | 117.7551 | 0.4715 | 117.5034 | 123.4039 | -123.5046 | -0.32043 | 117.1829 | 123.2025 | 114.6332 | 121.4035
1697.4844 | 123.3032 | -120.1218 | 3.2227 | -0.057678 | 0.00034827 | 0.12274 | 0.0085749 | 0.0023349 | 0.0013522 | -0.00052553 | -0.1514 | 0.1443 | 0.0076754 | 0.0034628 | -0.0015296 | -0.00059378 | 0.0018051 | -3.1311 | -2.4124 | -120.3186 | -2.774 | -2.6276 | -119.9432 | -2.7237 | 1.474 | 3.2822 | 2.8381 | 3.0212 | 3.154 | 2.9617 | 2.9572 | -0.19684 | -5.6351 | -5.9967 | 117.4942 | 117.3981 | 0.17853 | 117.5949 | 0.37537 | 122.9599 | 0.05951 | -0.20142 | 123.2758 | 123.0789 | 123.0835 | 0.11902 | 0.1236 | 117.691 | 117.5446 | 0.31586 | 0.18311 | 117.9062 | 0.44403 | 117.7094 | 123.4039 | -123.5413 | -0.38452 | 117.3477 | 123.143 | 116.9907 | 121.5958
1698.5469 | 123.3627 | -118.7988 | 4.4861 | -0.088196 | -0.0032833 | 0.1206 | 0.011779 | 0.0019077 | 0.00071138 | -0.0024481 | -0.035431 | 0.14217 | 0.0048984 | 0.0026084 | -0.0032386 | -0.0020892 | 0.0020187 | -2.7969 | -2.5314 | -118.6935 | -2.8381 | -2.6688 | -118.3548 | -2.7328 | 2.2568 | 4.7195 | 4.3076 | 4.0558 | 4.3991 | 4.2801 | 4.3671 | 0.10529 | -7.0175 | -7.3242 | 116.1301 | 116.066 | 0.44403 | 115.9607 | 0.33874 | 123.1064 | 0.23346 | -0.4303 | 123.1979 | 123.1659 | 123.0789 | 0.059509 | -0.027466 | 116.0248 | 115.8554 | 0.091553 | -0.25177 | 116.1621 | 0.41199 | 116.2674 | 123.5184 | -123.1796 | -0.17853 | 115.9607 | 122.8546 | 116.0019 | 121.0556
1699.4844 | 123.2986 | -120.7901 | 2.5131 | -0.088196 | -0.0071285 | 0.12466 | 0.016052 | 0.0021213 | 0.0015658 | 0.00096987 | -0.15445 | 0.14238 | 0.0027622 | 0.00389 | -0.0045202 | 0.001756 | 0.00052346 | -3.4607 | -2.861 | -121.1288 | -3.3508 | -3.2318 | -120.7443 | -3.2501 | 0.94757 | 2.6093 | 2.0554 | 2.1606 | 2.4628 | 2.2385 | 2.2705 | -0.33875 | -5.3741 | -5.864 | 117.5583 | 117.54 | 0.045776 | 117.8787 | 0.38452 | 122.8455 | 0.09613 | -0.35248 | 123.2529 | 123.0606 | 123.0286 | 0.21515 | 0.1831 | 117.897 | 117.778 | 0.40741 | 0.10529 | 118.2678 | 0.55389 | 117.9291 | 123.3994 | -123.642 | -0.45776 | 117.4393 | 122.9507 | 117.3294 | 121.7377
1700.5469 | 123.3673 | -120.1172 | 3.1631 | -0.080566 | -0.01781 | 0.12274 | 0.023101 | -0.00065586 | 0.0019932 | 0.0013971 | -0.062897 | 0.14025 | 0.0031894 | 0.0023948 | -0.0004614 | -0.0023028 | 0.0028733 | -3.3051 | -2.8519 | -120.5154 | -3.2043 | -3.0396 | -120.3644 | -3.0762 | 1.268 | 2.9755 | 2.4719 | 3.0396 | 2.9984 | 3.2455 | 3.0853 | -0.39825 | -6.015 | -6.3675 | 117.0776 | 117.041 | -0.24719 | 117.4393 | 0.15106 | 122.5891 | -0.18768 | -0.1236 | 123.1155 | 123.2025 | 123.3627 | 0.6134 | 0.77362 | 117.4759 | 117.3111 | 0.52643 | 0.56763 | 117.6636 | 0.50354 | 117.2653 | 123.0927 | -123.6786 | -0.69122 | 116.9128 | 123.1567 | 116.8121 | 121.3852
1701.4844 | 123.1155 | -119.9249 | 3.3463 | -0.027161 | 0.0033389 | 0.12167 | 0.0030207 | 0.00041234 | 0.0019932 | -0.0013799 | -0.093414 | 0.14345 | 0.0048984 | -0.0020914 | -0.002384 | 4.7018e-05 | -0.00011754 | -2.98 | -2.4261 | -120.4102 | -2.8839 | -2.7191 | -120.3644 | -2.7466 | 1.4008 | 3.1128 | 2.5955 | 2.9205 | 3.0853 | 2.98 | 3.1815 | -0.48523 | -5.7724 | -6.2302 | 117.2058 | 117.1783 | -0.43945 | 117.6636 | 0.045776 | 122.5204 | -0.23346 | -0.42572 | 123.0103 | 123.1064 | 122.905 | 0.58594 | 0.38452 | 117.691 | 117.5262 | 0.48981 | 0.32501 | 117.984 | 0.51727 | 117.4988 | 123.0377 | -123.7564 | -0.75073 | 117.041 | 122.8455 | 116.9449 | 121.3257
1702.4844 | 123.317 | -120.6848 | 2.5909 | -0.019531 | 0.0059025 | 0.12359 | 0.0028069 | -0.0012967 | 7.0582e-05 | -0.00031193 | -0.05069 | 0.14131 | 0.0059664 | 0.0049582 | -0.0047338 | -0.0014484 | -0.0024673 | -2.8061 | -2.536 | -120.813 | -2.8931 | -2.7466 | -120.5566 | -2.7878 | 1.0849 | 2.7008 | 2.1927 | 2.3346 | 2.3941 | 2.298 | 2.3529 | -0.12817 | -5.127 | -5.484 | 117.9382 | 117.897 | 0.12817 | 118.0252 | 0.25635 | 122.8775 | 0.10986 | -0.25635 | 123.0789 | 123.0377 | 122.9828 | 0.16022 | 0.10529 | 118.0664 | 117.9199 | 0.20142 | 0.14191 | 118.277 | 0.50812 | 118.1488 | 123.3856 | -123.4039 | -0.39825 | 117.7917 | 123.0194 | 117.8787 | 121.7697
1703.5469 | 123.3902 | -120.2225 | 2.9984 | -0.011902 | -0.0064877 | 0.12402 | 0.011352 | -0.0027921 | -0.0014248 | -0.0026617 | -0.059845 | 0.14067 | 0.0036166 | -0.0016642 | -0.0036658 | -0.001662 | 0.00052346 | -2.7237 | -2.4536 | -120.1859 | -2.7466 | -2.5864 | -119.5358 | -2.6321 | 1.3184 | 3.4149 | 2.9388 | 2.8061 | 2.9297 | 2.8564 | 2.916 | 0.036621 | -5.452 | -5.7449 | 117.6361 | 117.5903 | 0.68664 | 117.5537 | 0.65002 | 123.1613 | 0.41656 | -0.19226 | 123.1522 | 123.1384 | 123.0789 | -0.022888 | -0.082398 | 117.5995 | 117.4393 | -0.009156 | -0.13275 | 117.7322 | 0.47607 | 117.7689 | 123.6374 | -123.1842 | -0.059509 | 117.4759 | 123.0286 | 117.4988 | 121.5408
1704.4844 | 123.381 | -120.2637 | 2.9617 | 0.0033567 | -0.0094785 | 0.12274 | 0.015197 | -0.0027921 | 0.00049778 | -0.0041571 | -0.035431 | 0.14131 | 0.004471 | -0.0027322 | -0.0028112 | -0.0031574 | -0.00075834 | -2.9617 | -2.7328 | -120.8313 | -2.948 | -2.8015 | -120.6802 | -2.916 | 1.1993 | 2.7832 | 2.298 | 2.6642 | 2.8656 | 2.8564 | 2.7878 | -0.56763 | -5.6946 | -5.9097 | 117.4622 | 117.3477 | -0.41657 | 117.9153 | 0.15106 | 122.5616 | -0.17853 | -0.29755 | 123.1293 | 123.0515 | 123.1201 | 0.48981 | 0.55847 | 118.0298 | 117.8833 | 0.56763 | 0.36621 | 118.0984 | 0.48523 | 117.5308 | 123.0469 | -123.793 | -0.66376 | 117.3157 | 122.9279 | 117.3019 | 121.463
1705.5469 | 123.436 | -120.2316 | 3.1265 | -0.050049 | -0.018237 | 0.12359 | 0.026092 | 0.00083954 | 0.00028418 | -0.0020209 | -0.0018616 | 0.14238 | 0.0053256 | -0.0048684 | -0.0045202 | -0.0018756 | -0.0022537 | -2.7969 | -2.5452 | -120.4697 | -2.8519 | -2.6596 | -119.8425 | -2.7283 | 1.7441 | 3.2913 | 2.7283 | 3.1448 | 3.0853 | 2.7374 | 2.7649 | -0.23804 | -5.6717 | -5.9784 | 117.572 | 117.5034 | 0.3891 | 117.7414 | 0.62714 | 122.9599 | 0.16479 | 0.01831 | 123.317 | 122.9965 | 122.9691 | 0.036622 | 0.009156 | 117.8101 | 117.6178 | 0.35706 | 0.41657 | 117.9245 | 0.56305 | 117.6865 | 123.5229 | -123.5962 | -0.39826 | 117.3798 | 123.3765 | 117.4347 | 121.9757
1706.4844 | 123.3627 | -120.6436 | 2.6459 | -0.019531 | -0.018237 | 0.12231 | 0.026946 | 0.0014803 | 0.0013522 | -0.0013799 | -0.053741 | 0.14217 | 0.0042574 | 4.4788e-05 | -0.0028112 | -0.0025164 | 0.0022323 | -2.7695 | -2.5543 | -120.8084 | -2.8564 | -2.6962 | -120.4834 | -2.7649 | 1.1307 | 2.742 | 2.2385 | 2.4307 | 2.4811 | 2.3758 | 2.4719 | -0.1648 | -5.2002 | -5.5023 | 117.9474 | 117.8787 | 0.16022 | 118.0435 | 0.32501 | 122.8821 | 0.09613 | -0.21515 | 123.1247 | 123.1155 | 123.0194 | 0.23346 | 0.13733 | 118.1122 | 117.952 | 0.24261 | 0.19226 | 118.2541 | 0.50354 | 118.0893 | 123.3856 | -123.4543 | -0.40741 | 117.7872 | 123.0743 | 117.8741 | 121.7743
1707.4844 | 123.2666 | -120.0851 | 3.1677 | -0.019531 | -0.015033 | 0.12338 | 0.026733 | 0.0029757 | 0.0013522 | 0.0011835 | -0.18192 | 0.14238 | 0.0027622 | 0.0049582 | -0.0015296 | -0.00038018 | -0.00054474 | -2.8839 | -2.5681 | -120.2911 | -3.0487 | -2.8793 | -120.0806 | -2.9388 | 1.3275 | 3.3783 | 2.8519 | 2.861 | 2.8381 | 2.7878 | 2.9617 | -0.20599 | -5.7358 | -6.2164 | 117.2058 | 117.1463 | 0.004578 | 117.3523 | 0.21057 | 122.937 | 0.21057 | -0.3067 | 122.9233 | 123.0469 | 122.8729 | 0.10986 | -0.064087 | 117.4118 | 117.2424 | -0.013733 | 0.009155 | 117.7231 | 0.52643 | 117.5171 | 123.4634 | -123.4589 | -0.31586 | 117.0364 | 122.9462 | 117.2012 | 121.4127
1708.5469 | 123.4085 | -119.9066 | 3.3966 | -0.088196 | -0.02016 | 0.12338 | 0.027374 | -0.0010831 | 0.00028418 | 0.0020379 | -0.035431 | 0.14217 | 0.004471 | 0.00068579 | -0.0021704 | -0.0025164 | 0.0043687 | -2.7878 | -2.4857 | -120.3873 | -2.8427 | -2.6962 | -120.2042 | -2.71 | 1.5289 | 3.1448 | 2.6138 | 3.3691 | 3.1311 | 3.2089 | 3.3783 | -0.48065 | -5.8823 | -6.2393 | 117.2104 | 117.1967 | -0.29755 | 117.6773 | 0.18311 | 122.5204 | -0.25177 | -0.027465 | 123.0377 | 123.2849 | 123.1155 | 0.76447 | 0.59509 | 117.691 | 117.5446 | 0.51727 | 0.75531 | 117.9016 | 0.53101 | 117.421 | 123.0515 | -123.7839 | -0.78277 | 117.0639 | 123.2758 | 117.1188 | 121.4355
1709.4844 | 123.317 | -120.4193 | 2.8702 | 0.033875 | -0.018451 | 0.12103 | 0.028442 | 0.0031893 | 0.0022068 | 0.00054267 | -0.11172 | 0.14153 | 0.0029758 | 0.004531 | -0.0025976 | -0.001662 | 9.6064e-05 | -2.8793 | -2.5177 | -120.7443 | -3.0029 | -2.8702 | -120.3094 | -2.9022 | 1.1398 | 2.9572 | 2.3712 | 2.6184 | 2.7145 | 2.5864 | 2.6642 | -0.32501 | -5.3879 | -5.8731 | 117.5491 | 117.5171 | 0.10986 | 117.8421 | 0.43488 | 122.7905 | 0.086975 | -0.25177 | 123.1339 | 123.0835 | 123.0057 | 0.29297 | 0.21515 | 117.8741 | 117.7414 | 0.34332 | 0.24719 | 118.2266 | 0.58594 | 117.9016 | 123.3765 | -123.6145 | -0.49896 | 117.4164 | 123.0377 | 117.54 | 121.5591
1710.4844 | 123.2437 | -120.7855 | 2.5314 | -0.011902 | -0.022296 | 0.12146 | 0.030151 | 0.0034029 | -0.00014322 | -0.0011663 | -0.093414 | 0.14345 | 0.0042574 | 0.0019674 | -0.000675 | -0.0042254 | 0.0015915 | -3.0853 | -2.7283 | -121.1288 | -3.1998 | -3.0579 | -120.7397 | -3.067 | 0.9613 | 2.5543 | 1.9867 | 2.298 | 2.1011 | 2.1469 | 2.2614 | -0.34332 | -5.2597 | -5.7312 | 117.7277 | 117.7185 | 0.045776 | 118.0618 | 0.3891 | 122.7722 | 0.022888 | -0.23346 | 122.8867 | 123.0469 | 122.9324 | 0.27466 | 0.16022 | 118.071 | 117.9291 | 0.11444 | 0.31128 | 118.4006 | 0.56763 | 118.0573 | 123.3398 | -123.6603 | -0.54474 | 117.5858 | 123.0835 | 117.7002 | 121.7468
1711.4844 | 123.3215 | -120.2225 | 3.0853 | -0.0042723 | -0.023578 | 0.12231 | 0.030151 | 0.0051119 | 0.0024204 | -0.00073913 | -0.10867 | 0.14217 | 0.003403 | -0.00059601 | -0.003025 | -0.0040118 | -0.0018265 | -2.8976 | -2.5772 | -120.6024 | -3.0075 | -2.8564 | -120.2866 | -2.9068 | 1.2726 | 3.0441 | 2.4628 | 2.8931 | 2.8931 | 2.7786 | 2.9114 | -0.37994 | -5.6625 | -6.0928 | 117.366 | 117.3157 | -0.064087 | 117.6956 | 0.31586 | 122.6852 | -0.041199 | -0.19226 | 123.1155 | 123.1338 | 123.0011 | 0.44861 | 0.31586 | 117.746 | 117.5949 | 0.4303 | 0.4303 | 118.0252 | 0.58136 | 117.6453 | 123.2666 | -123.6877 | -0.62256 | 117.215 | 123.1155 | 117.3248 | 121.4951
1712.4844 | 123.4085 | -120.5292 | 2.7054 | -0.027161 | -0.020373 | 0.12103 | 0.026306 | 0.0019077 | 0.0028476 | -0.0035163 | -0.01712 | 0.14089 | 0.0046848 | -0.005082 | -0.002384 | -0.0029438 | 0.00095066 | -2.8931 | -2.7603 | -120.8954 | -3.0945 | -2.861 | -120.4468 | -2.9572 | 1.268 | 2.7557 | 2.2293 | 2.5269 | 2.6093 | 2.4994 | 2.5726 | -0.36621 | -5.4657 | -5.7999 | 117.6682 | 117.572 | 0.082398 | 117.9382 | 0.44861 | 122.7585 | 0.050354 | -0.17853 | 123.1384 | 123.1018 | 123.0286 | 0.34332 | 0.27008 | 118.0344 | 117.8009 | 0.37994 | 0.29755 | 118.1351 | 0.52643 | 117.7689 | 123.2849 | -123.6008 | -0.47607 | 117.4347 | 123.056 | 117.6361 | 121.7972
1713.4844 | 123.2803 | -120.4285 | 2.8244 | -0.019531 | -0.016101 | 0.12402 | 0.024597 | -0.00044226 | -0.00014322 | -0.0015935 | -0.1514 | 0.14345 | 0.0023348 | 0.00047219 | -0.002384 | -0.0014484 | -0.0035355 | -2.6596 | -2.3438 | -120.195 | -2.7832 | -2.6093 | -120.5383 | -2.7008 | 1.3458 | 3.2227 | 2.6825 | 2.5589 | 2.5681 | 2.4307 | 2.5635 | 0.23346 | -5.1682 | -5.6076 | 117.8192 | 117.7277 | -0.10986 | 117.4942 | -0.34332 | 123.111 | 0.39825 | -0.2655 | 122.9965 | 122.9919 | 122.8592 | -0.11902 | -0.25177 | 117.5858 | 117.4118 | -0.11444 | -0.1236 | 117.8513 | 0.54016 | 118.0847 | 123.6511 | -123.0194 | -0.14191 | 117.6453 | 122.9874 | 117.7689 | 121.7743
1714.5469 | 123.4222 | -120.4651 | 2.774 | -0.027161 | -0.019092 | 0.12317 | 0.024169 | -0.00044226 | -0.00014322 | -0.00073913 | -0.011017 | 0.14217 | 0.0036166 | -0.0035868 | -0.0017432 | -0.0018756 | 0.0020187 | -3.186 | -2.4857 | -120.7306 | -2.8107 | -2.6093 | -120.2591 | -2.6596 | 1.2222 | 2.8336 | 2.2888 | 2.6138 | 2.6413 | 2.6138 | 2.6459 | -0.2655 | -5.2597 | -5.5847 | 117.8558 | 117.8055 | 0.20599 | 118.071 | 0.4715 | 122.7539 | 0.059509 | -0.16022 | 123.1064 | 123.111 | 123.0789 | 0.35706 | 0.32501 | 118.1213 | 117.9199 | 0.35248 | 0.32501 | 118.2449 | 0.54474 | 117.9794 | 123.2986 | -123.5046 | -0.48523 | 117.6544 | 123.0789 | 117.2791 | 121.6873
1715.4844 | 123.3261 | -119.7144 | 3.5522 | 0.0033567 | -0.015033 | 0.12103 | 0.022247 | -0.0012967 | 0.00092498 | -0.00095273 | -0.081207 | 0.14217 | 0.0040438 | -0.0014504 | -0.004093 | -0.0020892 | -0.0035355 | -3.2455 | -2.536 | -119.957 | -2.9663 | -2.8473 | -119.3802 | -2.8976 | 1.3504 | 3.6209 | 3.0945 | 3.3234 | 3.3737 | 3.273 | 3.3417 | -0.24262 | -6.0883 | -6.5186 | 116.8671 | 116.8167 | 0.33417 | 117.0593 | 0.57678 | 122.8088 | 0.068665 | -0.22888 | 123.0881 | 123.056 | 122.9874 | 0.24719 | 0.17853 | 117.1097 | 116.9907 | 0.27924 | 0.22888 | 117.421 | 0.52643 | 117.1783 | 123.3353 | -123.5092 | -0.45776 | 116.748 | 123.0377 | 116.4688 | 121.0648
1716.4844 | 123.3902 | -120.3964 | 2.9022 | -0.027161 | -0.012256 | 0.12231 | 0.018615 | -0.00044226 | 0.0011386 | -0.0026617 | -0.0079652 | 0.14217 | 0.0059664 | -0.0012368 | -0.0025976 | -0.0037982 | -0.00075834 | -3.653 | -2.6688 | -120.5109 | -2.9938 | -2.8152 | -120.4422 | -2.8839 | 1.4694 | 3.035 | 2.5085 | 2.7603 | 2.742 | 2.6184 | 2.742 | -0.11444 | -5.571 | -5.896 | 117.5812 | 117.5125 | -0.045777 | 117.627 | 0.068664 | 122.905 | 0.13275 | -0.14191 | 123.1384 | 123.1384 | 123.0148 | 0.23346 | 0.10986 | 117.6956 | 117.5171 | 0.23346 | 0.25177 | 117.8421 | 0.52643 | 117.7277 | 123.4314 | -123.4131 | -0.39368 | 117.4026 | 123.1567 | 116.7435 | 121.8658
1717.5469 | 123.3902 | -119.9203 | 3.3188 | -0.03479 | -0.011188 | 0.12103 | 0.017974 | -0.0010831 | 0.0022068 | -0.00073913 | -0.12088 | 0.1396 | 0.0031894 | -0.0070046 | -0.0043066 | -0.0037982 | 0.00095066 | -2.9526 | -2.6505 | -120.2866 | -2.9572 | -2.8656 | -119.4901 | -2.9892 | 1.5381 | 3.3875 | 2.8198 | 3.2913 | 3.3142 | 3.1403 | 3.1952 | -0.36621 | -5.9692 | -6.2759 | 117.0547 | 116.9312 | 0.4303 | 117.2974 | 0.79651 | 122.7402 | 0.068664 | -0.027466 | 123.2346 | 123.1155 | 123.0606 | 0.37537 | 0.32043 | 117.421 | 117.3294 | 0.49438 | 0.4715 | 117.6361 | 0.56763 | 117.2699 | 123.3078 | -123.6053 | -0.49896 | 116.9632 | 123.2117 | 116.9678 | 121.4584
1718.4844 | 123.3673 | -120.4468 | 2.8336 | -0.072937 | -0.0071285 | 0.1221 | 0.015411 | 0.0016939 | 0.0034884 | -0.0024481 | -0.035431 | 0.14153 | 0.0053256 | -0.00080961 | -0.0025976 | -0.0010212 | 0.00052346 | -2.8976 | -2.6779 | -120.6253 | -2.9709 | -2.8015 | -120.401 | -2.8473 | 1.2543 | 2.9205 | 2.3712 | 2.6642 | 2.6825 | 2.6047 | 2.6596 | -0.17853 | -5.5115 | -5.8044 | 117.6453 | 117.5995 | 0.045776 | 117.778 | 0.2243 | 122.818 | 0.086975 | -0.16937 | 123.1293 | 123.1064 | 123.0515 | 0.28839 | 0.23346 | 117.8238 | 117.6544 | 0.31128 | 0.29297 | 117.9474 | 0.54932 | 117.7689 | 123.3673 | -123.4589 | -0.46234 | 117.4759 | 123.111 | 117.5491 | 121.701
1719.4844 | 123.2986 | -120.2271 | 3.0533 | -0.042419 | -0.0043515 | 0.12188 | 0.012634 | -0.00044226 | -0.0022794 | 0.00075627 | -0.090363 | 0.14217 | 0.0057528 | -0.00080961 | -0.0015296 | -0.001662 | -0.00075834 | -2.9755 | -2.5909 | -120.6024 | -3.067 | -2.9297 | -120.2408 | -2.9572 | 1.1993 | 3.0396 | 2.4399 | 2.8198 | 2.8107 | 2.6871 | 2.7878 | -0.37537 | -5.6442 | -6.1203 | 117.2974 | 117.2699 | -0.013733 | 117.6453 | 0.36163 | 122.6669 | -0.013733 | -0.23346 | 123.0377 | 123.0148 | 122.9141 | 0.3479 | 0.24719 | 117.6727 | 117.5354 | 0.37079 | 0.37994 | 118.0115 | 0.59967 | 117.6361 | 123.2666 | -123.6557 | -0.6134 | 117.16 | 123.0469 | 117.2516 | 121.4264
1720.4844 | 123.0927 | -120.2911 | 3.0029 | -0.03479 | -0.0062741 | 0.1221 | 0.015411 | 0.00019874 | 0.00049778 | -0.0028753 | -0.053741 | 0.14067 | 0.0040438 | 0.0015402 | -0.003025 | -0.0014484 | 0.00052346 | -3.0533 | -2.6917 | -120.5154 | -3.1631 | -2.9938 | -120.3049 | -3.035 | 1.0483 | 2.9938 | 2.4353 | 2.6138 | 2.8656 | 2.8885 | 2.7924 | -0.2243 | -5.6946 | -6.1661 | 117.2974 | 117.2562 | -0.013733 | 117.4805 | 0.21057 | 122.7264 | -0.009156 | -0.3891 | 123.1567 | 123.0835 | 123.1796 | 0.35705 | 0.45319 | 117.5217 | 117.3523 | 0.4303 | 0.17853 | 117.8238 | 0.55847 | 117.5995 | 123.2849 | -123.5184 | -0.56763 | 117.128 | 122.905 | 117.2379 | 121.3394
1721.4844 | 123.3353 | -120.1538 | 3.1219 | -0.011902 | -0.0081967 | 0.12231 | 0.015411 | 0.0025485 | 0.0034884 | 0.00011527 | -0.056793 | 0.14153 | 0.004471 | -0.0020914 | -0.0034522 | -0.00059378 | -0.00075834 | -3.1036 | -2.6871 | -120.4285 | -3.1952 | -3.0624 | -119.8425 | -3.067 | 1.2314 | 3.3646 | 2.7557 | 2.8427 | 2.8473 | 2.7512 | 2.8336 | -0.27466 | -5.809 | -6.3171 | 117.0914 | 117.0868 | 0.31128 | 117.3614 | 0.58594 | 122.9095 | 0.24261 | -0.27924 | 123.0011 | 122.9874 | 122.905 | 0.07782 | -0.004577 | 117.366 | 117.2333 | 0.091553 | 0.086975 | 117.7414 | 0.60883 | 117.4667 | 123.5184 | -123.5504 | -0.36621 | 116.9586 | 122.9965 | 117.0502 | 121.3852
1722.5469 | 123.2574 | -119.838 | 3.4744 | -0.050049 | 0.010175 | 0.12488 | 0.0025933 | 0.0046847 | 0.0017794 | -0.0030889 | -0.11478 | 0.14067 | 0.003403 | -0.00059601 | -0.003025 | 0.00026062 | 0.0013779 | -3.2867 | -2.9572 | -120.0989 | -3.3966 | -3.2639 | -119.7784 | -3.3051 | 1.3504 | 3.479 | 2.8976 | 3.2135 | 3.1815 | 3.0808 | 3.1952 | -0.26093 | -6.4316 | -6.871 | 116.5741 | 116.5329 | 0.05951 | 116.7938 | 0.32044 | 122.7356 | 0.004578 | -0.26092 | 123.0194 | 123.0331 | 122.9187 | 0.29755 | 0.18311 | 116.835 | 116.7023 | 0.28381 | 0.31586 | 117.1417 | 0.58136 | 116.8808 | 123.317 | -123.5733 | -0.57678 | 116.4413 | 123.0515 | 116.5512 | 121.1884
1723.4844 | 123.2941 | -120.4742 | 2.8198 | -0.057678 | -0.00050633 | 0.12381 | 0.0092157 | -0.00086946 | 0.00071138 | 0.0024653 | -0.069 | 0.14174 | 0.0031894 | -0.0025186 | -0.0032386 | -0.001662 | -0.00054474 | -2.7924 | -2.4857 | -120.7214 | -2.9755 | -2.8107 | -120.4102 | -2.8519 | 1.1307 | 2.9114 | 2.3163 | 2.5452 | 2.5726 | 2.4719 | 2.5589 | -0.24719 | -5.3055 | -5.7953 | 117.6636 | 117.6224 | 0.064087 | 117.8696 | 0.31128 | 122.7905 | 0.091553 | -0.27466 | 123.0469 | 123.0331 | 122.9462 | 0.24261 | 0.15564 | 117.9108 | 117.746 | 0.25635 | 0.22888 | 118.2358 | 0.59509 | 117.9886 | 123.3856 | -123.5413 | -0.50354 | 117.4988 | 123.0194 | 117.6819 | 121.6049
1724.5469 | 123.4222 | -119.7372 | 3.3966 | -0.10345 | 0.0033389 | 0.12402 | 0.0055841 | 0.0012667 | -0.00014322 | -0.00073913 | -0.084259 | 0.13939 | 0.0040438 | -0.0027322 | -0.0060156 | -0.0010212 | -0.0028945 | -2.8381 | -2.5681 | -120.2499 | -2.8748 | -2.71 | -119.8517 | -2.7786 | 1.355 | 3.3783 | 2.8793 | 3.2455 | 3.3325 | 3.1769 | 3.3234 | -0.51269 | -5.9647 | -6.2714 | 117.0273 | 116.9586 | -0.11444 | 117.4713 | 0.39825 | 122.6166 | -0.01831 | -0.15106 | 123.0698 | 123.0606 | 122.9141 | 0.44403 | 0.29755 | 117.54 | 117.3752 | 0.45319 | 0.36621 | 117.6819 | 0.49896 | 117.1692 | 123.1155 | -123.6465 | -0.51727 | 116.8625 | 122.9828 | 116.8991 | 121.0922
1725.4844 | 123.349 | -120.0531 | 3.2135 | -0.0042723 | 0.0052615 | 0.12103 | 0.0049433 | -0.0010831 | 7.0582e-05 | 0.0011835 | -0.096466 | 0.14324 | 0.0040438 | -0.0046548 | -0.0036658 | -0.0018756 | 0.0018051 | -2.8839 | -2.5085 | -120.4422 | -2.9892 | -2.829 | -120.0119 | -2.8702 | 1.2772 | 3.2959 | 2.6871 | 2.948 | 2.9709 | 2.8427 | 2.9846 | -0.3891 | -5.722 | -6.2027 | 117.2241 | 117.1829 | 0.041199 | 117.572 | 0.4303 | 122.7402 | 0.082397 | -0.2655 | 123.024 | 123.0377 | 122.8958 | 0.29755 | 0.15564 | 117.6132 | 117.453 | 0.28381 | 0.26093 | 117.9337 | 0.60883 | 117.5446 | 123.349 | -123.6557 | -0.52643 | 117.0639 | 123.0011 | 117.1692 | 121.3303
1726.5469 | 123.3902 | -120.2499 | 2.9205 | -0.027161 | 0.0024845 | 0.12188 | 0.0030207 | -0.0059965 | -0.0022794 | -0.0018073 | -0.078156 | 0.1411 | 0.001694 | -0.0031594 | -0.003025 | -0.0010212 | 0.0039413 | -2.8152 | -2.5772 | -119.9936 | -2.8931 | -2.948 | -120.0531 | -2.7786 | 1.1627 | 2.9846 | 2.5818 | 2.7924 | 2.9846 | 2.7191 | 2.71 | 0.25635 | -5.4977 | -5.8136 | 117.3019 | 117.4713 | 0.19684 | 117.215 | -0.05951 | 122.8317 | 0.064087 | -0.12817 | 123.2346 | 122.9599 | 122.9691 | 0.12817 | 0.13733 | 117.0456 | 117.1005 | 0.40283 | 0.21057 | 117.4164 | 0.40283 | 117.6727 | 123.2346 | -122.9141 | -0.33875 | 117.3569 | 123.0423 | 117.4347 | 121.4127
1727.4844 | 123.3307 | -119.6732 | 3.598 | -0.057678 | 0.0026981 | 0.11953 | 0.0034479 | 0.00062594 | 0.00092498 | -0.00073913 | -0.11172 | 0.14067 | 0.0042574 | 0.0032492 | -0.003025 | -0.001662 | 0.0013779 | -2.7969 | -2.4765 | -120.1447 | -2.8976 | -2.7328 | -122.5662 | -2.8107 | 1.5472 | 3.5477 | 2.9526 | 3.2776 | 3.6942 | 3.5706 | 3.3096 | -0.4715 | -6.0745 | -6.4957 | 116.9403 | 116.8625 | -2.8931 | 117.334 | -2.4216 | 122.6257 | -0.050354 | -0.32043 | 123.3673 | 122.9828 | 123.2437 | 0.35705 | 0.61798 | 117.4118 | 117.247 | 0.74158 | 0.32501 | 117.6682 | 0.59509 | 117.1967 | 123.2208 | -123.7427 | -0.64545 | 116.7755 | 122.9507 | 116.8762 | 121.2204
1728.5469 | 123.3536 | -119.8334 | 3.4332 | -0.019531 | 0.0052615 | 0.12317 | 0.0036615 | 0.0029757 | 0.00071138 | -0.0020209 | -0.020172 | 0.14174 | 0.0057528 | 4.4788e-05 | -0.0034522 | -0.0018756 | -0.00054474 | -2.8793 | -2.623 | -120.0577 | -2.9388 | -2.7695 | -119.3985 | -2.8336 | 1.3962 | 3.6392 | 3.1036 | 3.2822 | 3.2455 | 3.2089 | 3.2547 | -0.2243 | -6.0562 | -6.3721 | 117.0639 | 116.9998 | 0.43488 | 117.2241 | 0.65918 | 122.937 | 0.20599 | -0.15106 | 123.0789 | 123.0881 | 123.0423 | 0.15106 | 0.10528 | 117.2882 | 117.1188 | 0.14191 | 0.17853 | 117.4347 | 0.53558 | 117.2104 | 123.4726 | -123.4909 | -0.32959 | 116.8945 | 123.1155 | 116.954 | 121.2296
1729.4844 | 123.3261 | -119.8059 | 3.4836 | 0.041504 | 0.00098907 | 0.12103 | 0.0028069 | 0.00041234 | 0.00092498 | -0.0020209 | -0.096466 | 0.14046 | 0.001694 | -0.0020914 | -0.003025 | -0.00038018 | 0.0026597 | -3.0441 | -2.6413 | -120.163 | -3.1036 | -2.9663 | -119.7968 | -2.9846 | 1.4603 | 3.5431 | 2.9388 | 3.1815 | 3.2272 | 3.1219 | 3.2593 | -0.35706 | -6.1249 | -6.5872 | 116.8396 | 116.8213 | 0.009155 | 117.1783 | 0.36621 | 122.7448 | 0.059509 | -0.30212 | 123.0331 | 123.0652 | 122.9279 | 0.32043 | 0.18311 | 117.1967 | 117.0593 | 0.28839 | 0.24262 | 117.5217 | 0.60425 | 117.1646 | 123.349 | -123.6465 | -0.54474 | 116.7023 | 122.9874 | 116.7618 | 121.2662
1730.4844 | 123.3856 | -119.9982 | 3.241 | -0.26367 | 0.0014163 | 0.12253 | 0.0057977 | -0.0019377 | 7.0582e-05 | -0.0011663 | -0.0018616 | 0.14131 | 0.0053256 | -0.0010232 | -0.0038794 | -0.0025164 | 0.0041551 | -2.9205 | -2.6917 | -120.3049 | -2.98 | -2.8015 | -119.8471 | -2.8793 | 1.6525 | 3.3463 | 2.7878 | 3.1815 | 3.1219 | 2.9984 | 3.0716 | -0.3067 | -5.9326 | -6.221 | 117.1967 | 117.1188 | 0.15106 | 117.4255 | 0.45776 | 122.7859 | 0.10528 | -0.059509 | 123.1201 | 123.0698 | 122.9965 | 0.28381 | 0.21057 | 117.5034 | 117.3248 | 0.33417 | 0.39368 | 117.6132 | 0.55847 | 117.3065 | 123.3444 | -123.5458 | -0.45319 | 117.0181 | 123.1796 | 117.0776 | 121.6507
1731.4844 | 123.381 | -120.0439 | 3.2867 | 0.0033567 | 0.00013467 | 0.12231 | 0.0075067 | -0.0021513 | 0.00071138 | -0.0026617 | -0.053741 | 0.14131 | 0.0042574 | -0.0080728 | -0.0015296 | -0.001662 | 0.0018051 | -3.0167 | -2.6459 | -120.5063 | -3.1311 | -2.9663 | -120.1355 | -2.98 | 1.3962 | 3.241 | 2.5955 | 2.9526 | 2.948 | 2.8381 | 3.0487 | -0.46234 | -5.9326 | -6.4178 | 117.0776 | 117.0639 | -0.091553 | 117.5262 | 0.37079 | 122.6395 | -0.045776 | -0.33417 | 122.9919 | 123.0927 | 122.8821 | 0.45319 | 0.24261 | 117.54 | 117.3752 | 0.35248 | 0.35706 | 117.8604 | 0.64545 | 117.3981 | 123.2849 | -123.793 | -0.69122 | 116.9128 | 122.9965 | 117.0273 | 121.4401
1732.5625 | 123.2803 | -120.2271 | 3.0716 | -0.027161 | 0.00013467 | 0.12188 | 0.0098565 | 0.0012667 | 0.0019932 | 0.0022517 | -0.12088 | 0.14302 | 0.0055392 | -0.00038241 | -0.002384 | -0.00038018 | -0.00054474 | -3.0121 | -2.7191 | -120.4147 | -3.1494 | -2.9892 | -120.3049 | -3.0579 | 1.2726 | 3.1952 | 2.5772 | 2.7786 | 2.7374 | 2.6505 | 2.7786 | -0.18768 | -5.7907 | -6.221 | 117.2379 | 117.1692 | -0.07782 | 117.3569 | 0.10986 | 122.8043 | 0.1236 | -0.29297 | 122.9645 | 123.0057 | 122.8775 | 0.20142 | 0.073243 | 117.4255 | 117.2653 | 0.16022 | 0.20142 | 117.6956 | 0.61798 | 117.5079 | 123.4222 | -123.4863 | -0.49439 | 117.0776 | 123.0057 | 117.215 | 121.4996
1733.4844 | 123.3398 | -120.2957 | 2.98 | -0.027161 | -0.0032833 | 0.12146 | 0.010284 | 0.0014803 | -0.00057042 | -9.8328e-05 | -0.096466 | 0.1411 | 0.0036166 | 0.001113 | -0.0028112 | -0.0018756 | -0.0018265 | -3.067 | -2.7237 | -120.575 | -3.1723 | -3.0304 | -120.1126 | -3.0533 | 1.3 | 3.0991 | 2.5131 | 2.742 | 2.8015 | 2.6505 | 2.742 | -0.27924 | -5.7037 | -6.1523 | 117.2653 | 117.2424 | 0.1831 | 117.5217 | 0.46234 | 122.8088 | 0.11902 | -0.23804 | 123.0972 | 123.0377 | 122.9462 | 0.22888 | 0.13733 | 117.5446 | 117.4026 | 0.28839 | 0.22888 | 117.8513 | 0.58594 | 117.572 | 123.3948 | -123.555 | -0.46692 | 117.1234 | 123.0377 | 117.2287 | 121.5958
1734.5469 | 123.4039 | -120.4102 | 2.8381 | -0.057678 | -0.0084103 | 0.12039 | 0.012847 | -0.0042875 | 0.0011386 | -0.0020209 | -0.0018616 | 0.1411 | 0.0059664 | -0.0035868 | -0.0021704 | -0.0020892 | -0.0018265 | -2.7054 | -2.4399 | -120.6665 | -2.7695 | -2.6001 | -120.3049 | -2.6276 | 1.3504 | 2.9251 | 2.4033 | 2.7145 | 2.7878 | 2.6871 | 2.742 | -0.25635 | -5.278 | -5.6076 | 117.8101 | 117.7826 | 0.10528 | 118.0389 | 0.36163 | 122.8134 | 0.086975 | -0.1236 | 123.1979 | 123.1522 | 123.0972 | 0.33875 | 0.28381 | 118.0664 | 117.897 | 0.38452 | 0.31128 | 118.2266 | 0.52185 | 117.9703 | 123.3353 | -123.5046 | -0.43488 | 117.6407 | 123.1247 | 117.7048 | 121.7606
1735.4844 | 123.3582 | -120.0897 | 3.1815 | -0.0042723 | -0.0039243 | 0.12338 | 0.01477 | 0.00083954 | -0.00014322 | -0.00052553 | -0.11783 | 0.14366 | 0.0048984 | -0.002305 | -0.0011022 | -0.0020892 | 0.00030966 | -2.7328 | -2.449 | -120.6802 | -2.861 | -2.6962 | -120.1309 | -2.7649 | 1.4145 | 3.1403 | 2.5681 | 2.9434 | 3.0945 | 2.9068 | 2.9617 | -0.59052 | -5.6305 | -6.0425 | 117.3935 | 117.3248 | -0.041198 | 117.9153 | 0.54932 | 122.6578 | -0.041199 | -0.23804 | 123.1842 | 123.0515 | 122.9965 | 0.39368 | 0.33874 | 117.984 | 117.8192 | 0.52643 | 0.37537 | 118.2312 | 0.5722 | 117.6407 | 123.23 | -123.8617 | -0.6134 | 117.2287 | 123.0331 | 117.3569 | 121.5042
1736.5469 | 123.3673 | -120.6436 | 2.6184 | -0.065308 | -0.0037107 | 0.12253 | 0.010498 | 0.00062594 | -0.00099762 | -0.0075751 | -0.023224 | 0.14302 | 0.0031894 | -0.0014504 | -0.0034522 | -0.0020892 | -0.0028945 | -2.8793 | -2.6001 | -121.0007 | -3.1174 | -2.829 | -120.7993 | -2.8198 | 1.0941 | 2.5818 | 2.092 | 2.417 | 2.4811 | 2.3621 | 2.4628 | -0.35706 | -5.2185 | -5.7358 | 117.8146 | 117.8238 | -0.15564 | 118.1808 | 0.20142 | 122.7356 | -0.036621 | -0.20142 | 123.1247 | 123.1064 | 123.0057 | 0.37079 | 0.27008 | 118.1717 | 117.8833 | 0.3891 | 0.32501 | 118.4006 | 0.48981 | 118.0435 | 123.2254 | -123.6191 | -0.52643 | 117.5262 | 123.0606 | 117.7643 | 121.7377
1737.4844 | 123.2849 | -120.6116 | 2.7283 | -0.011902 | -0.0043515 | 0.12039 | 0.011138 | 0.0019077 | -0.00078402 | 0.00011527 | -0.10562 | 0.14153 | 0.0057528 | -0.003373 | -0.003025 | 0.00090142 | 0.00073706 | -2.7878 | -2.4353 | -120.8862 | -2.948 | -2.8107 | -120.4605 | -2.7878 | 1.0986 | 2.7924 | 2.2202 | 2.4902 | 2.4902 | 2.3895 | 2.449 | -0.27466 | -5.1636 | -5.6763 | 117.8009 | 117.8238 | 0.15106 | 118.0984 | 0.42572 | 122.8317 | 0.064087 | -0.23804 | 123.1018 | 123.0606 | 123.0011 | 0.22888 | 0.16937 | 118.0756 | 117.9382 | 0.27008 | 0.27008 | 118.4509 | 0.5722 | 118.1763 | 123.4039 | -123.6145 | -0.50812 | 117.6636 | 123.1018 | 117.8238 | 121.7102
1738.4844 | 123.2803 | -120.3964 | 2.9388 | -0.027161 | -0.0026425 | 0.12146 | 0.0079339 | -0.0010831 | -0.0014248 | 0.0013971 | -0.026276 | 0.14345 | 0.003403 | -0.0012368 | -0.0032386 | -0.0035846 | 0.0020187 | -2.8748 | -2.5497 | -120.6802 | -2.9938 | -2.8015 | -120.4514 | -2.8793 | 1.1856 | 2.9205 | 2.3712 | 2.6917 | 2.8152 | 2.6505 | 2.6917 | -0.28381 | -5.4886 | -5.9326 | 117.5949 | 117.5171 | -0.054932 | 117.8009 | 0.22888 | 122.7676 | -0.018311 | -0.24719 | 123.2117 | 123.0881 | 123.0469 | 0.32043 | 0.27924 | 117.8787 | 117.6865 | 0.44403 | 0.32043 | 118.1305 | 0.54932 | 117.8467 | 123.317 | -123.6191 | -0.56763 | 117.4026 | 123.0881 | 117.5217 | 121.582
1739.4844 | 123.3078 | -120.5658 | 2.6825 | -0.03479 | 0.00034827 | 0.12274 | 0.0075067 | 0.0042575 | 7.0582e-05 | 0.0013971 | -0.093414 | 0.14131 | 0.00618 | 0.0013266 | -0.0051612 | 0.00026062 | 0.0011643 | -2.948 | -2.6367 | -120.9045 | -3.0533 | -2.9114 | -120.5292 | -2.948 | 1.1581 | 2.742 | 2.2339 | 2.4536 | 2.5223 | 2.3849 | 2.4902 | -0.33874 | -5.3192 | -5.7358 | 117.6544 | 117.6178 | 0.036621 | 117.9565 | 0.37537 | 122.7997 | 0.059509 | -0.22888 | 123.0881 | 123.056 | 122.9507 | 0.25635 | 0.15106 | 117.9932 | 117.8513 | 0.28839 | 0.21973 | 118.2678 | 0.50812 | 117.9291 | 123.3078 | -123.587 | -0.44861 | 117.5125 | 123.0194 | 117.6178 | 121.7239
1740.4844 | 123.2986 | -120.6024 | 2.7237 | -0.0042723 | 0.0024845 | 0.12018 | 0.0053705 | 0.0014803 | -0.001852 | -0.0015935 | -0.062897 | 0.14153 | 0.005112 | -0.0099954 | -0.0015296 | -0.00038018 | -0.0028945 | -2.4078 | -2.0416 | -120.9 | -2.5223 | -2.3758 | -120.5704 | -2.3849 | 1.3321 | 2.8061 | 2.2476 | 2.449 | 2.4673 | 2.3575 | 2.4307 | -0.29755 | -4.7653 | -5.246 | 118.2266 | 118.2175 | 0.032043 | 118.515 | 0.32959 | 122.85 | 0.082397 | -0.27466 | 123.0698 | 123.0331 | 122.9599 | 0.1831 | 0.10986 | 118.5242 | 118.3777 | 0.21973 | 0.20142 | 118.8583 | 0.55847 | 118.5608 | 123.4085 | -123.6237 | -0.47607 | 118.0801 | 123.0515 | 118.1946 | 121.9345
1741.5469 | 123.3215 | -120.1538 | 3.1128 | -0.0042723 | 0.0039799 | 0.12231 | 0.0030207 | 0.0012667 | 0.0032748 | 0.00096987 | -0.029327 | 0.14217 | 0.004471 | -0.0097818 | -0.0008886 | -0.0012348 | -0.0037491 | -2.3438 | -2.1057 | -120.4926 | -2.4445 | -2.2522 | -119.9844 | -2.3071 | 1.3916 | 3.1586 | 2.6184 | 2.8748 | 2.948 | 2.8656 | 2.9617 | -0.33875 | -5.2185 | -5.5573 | 117.9016 | 117.8467 | 0.16937 | 118.1854 | 0.50812 | 122.7722 | 0.045776 | -0.23804 | 123.1018 | 123.1155 | 123.0194 | 0.34332 | 0.24719 | 118.2404 | 118.0481 | 0.32959 | 0.25635 | 118.3868 | 0.54016 | 118.0481 | 123.3124 | -123.6053 | -0.49438 | 117.7094 | 123.0286 | 117.8101 | 121.5454
1742.4844 | 123.2712 | -120.2545 | 3.0487 | -0.057678 | 0.0020573 | 0.12253 | 0.0025933 | -0.0017239 | 0.00071138 | -0.00073913 | -0.093414 | 0.1411 | 0.0042574 | -0.002305 | -0.003025 | -0.00038018 | 0.0013779 | -2.4994 | -2.1423 | -120.5887 | -2.6047 | -2.449 | -120.2179 | -2.4994 | 1.2085 | 3.0808 | 2.4857 | 2.6825 | 2.8427 | 2.6184 | 2.7603 | -0.33417 | -5.191 | -5.6534 | 117.8055 | 117.7551 | 0.036621 | 118.0893 | 0.37079 | 122.7402 | 0.032044 | -0.36621 | 123.0972 | 123.0148 | 122.8729 | 0.27466 | 0.13275 | 118.1396 | 117.984 | 0.35706 | 0.19684 | 118.4463 | 0.59509 | 118.1122 | 123.3353 | -123.6374 | -0.56305 | 117.6498 | 122.937 | 117.7551 | 121.463
1743.5469 | 123.2758 | -120.3735 | 2.9663 | -0.042419 | 0.0031253 | 0.12231 | 0.0036615 | 0.0012667 | 0.00092498 | -0.00095273 | -0.044586 | 0.14238 | 0.0042574 | 4.4788e-05 | -0.0021704 | -0.0027302 | -0.0013991 | -2.4033 | -2.1194 | -120.6711 | -2.5497 | -2.3895 | -120.3598 | -2.4216 | 1.1719 | 2.98 | 2.3895 | 2.6733 | 2.6962 | 2.6047 | 2.6825 | -0.29755 | -5.0858 | -5.5161 | 117.984 | 117.952 | 0.013733 | 118.2495 | 0.31128 | 122.7631 | 0.013733 | -0.29297 | 123.0698 | 123.056 | 122.9782 | 0.29297 | 0.21515 | 118.2816 | 118.1213 | 0.3067 | 0.28381 | 118.5516 | 0.59052 | 118.2541 | 123.3536 | -123.6374 | -0.57678 | 117.8238 | 123.0469 | 117.9703 | 121.5454
1744.4844 | 123.317 | -120.6528 | 2.6367 | 0.010986 | 0.00098907 | 0.12295 | 0.0053705 | -0.0017239 | -0.00035682 | -0.00073913 | -0.059845 | 0.14302 | 0.0059664 | -0.0061502 | -0.0025976 | -0.0059344 | 0.0015915 | -2.4765 | -2.124 | -121.019 | -2.5726 | -2.4261 | -120.5887 | -2.4628 | 1.0025 | 2.6917 | 2.0874 | 2.4261 | 2.2339 | 2.1378 | 2.3392 | -0.36621 | -4.7607 | -5.2094 | 118.2266 | 118.19 | 0.064087 | 118.5562 | 0.4303 | 122.7402 | 0.054931 | -0.21057 | 122.8867 | 122.9919 | 122.7905 | 0.25177 | 0.050354 | 118.5928 | 118.4463 | 0.14649 | 0.33874 | 118.895 | 0.60425 | 118.5287 | 123.3444 | -123.6557 | -0.54932 | 118.0801 | 123.0789 | 118.1763 | 121.6553
1745.5469 | 123.3627 | -120.6848 | 2.5681 | -0.0042723 | 0.0039799 | 0.12466 | 0.0053705 | 0.0010531 | 0.0015658 | 0.0018243 | -0.014069 | 0.14217 | 0.003403 | -0.00016881 | -0.0034522 | -0.0018756 | -0.0035355 | -2.4445 | -2.2202 | -121.0052 | -2.5223 | -2.3621 | -120.5658 | -2.4216 | 1.1627 | 2.6321 | 2.1103 | 2.3666 | 2.4399 | 2.3209 | 2.417 | -0.32044 | -4.7882 | -5.0903 | 118.3228 | 118.2632 | 0.11902 | 118.5837 | 0.43945 | 122.7951 | 0.064087 | -0.20142 | 123.1247 | 123.1018 | 123.0057 | 0.3067 | 0.21057 | 118.6432 | 118.483 | 0.32959 | 0.25635 | 118.7851 | 0.52185 | 118.4647 | 123.317 | -123.5733 | -0.45776 | 118.1625 | 123.0515 | 118.2404 | 121.8475
1746.4844 | 123.2346 | -120.5292 | 2.7832 | -0.050049 | 0.0033389 | 0.12188 | 0.0019525 | 0.00062594 | 7.0582e-05 | -0.0015935 | -0.065949 | 0.14046 | 0.0038302 | -0.002305 | -0.0032386 | -0.0018756 | 0.0015915 | -2.5406 | -2.2018 | -120.8954 | -2.6413 | -2.4948 | -120.5017 | -2.5223 | 1.1124 | 2.8336 | 2.2156 | 2.4628 | 2.4536 | 2.7054 | 2.6825 | -0.36621 | -4.985 | -5.4245 | 118.0344 | 118.0069 | 0.027466 | 118.3731 | 0.39368 | 122.7448 | 0.050354 | -0.32043 | 122.9828 | 123.2117 | 123.2346 | 0.46692 | 0.48981 | 118.4006 | 118.2541 | 0.23804 | 0.24719 | 118.6935 | 0.61798 | 118.3273 | 123.3627 | -123.6786 | -0.56763 | 117.8879 | 122.9919 | 117.9886 | 121.6415
1747.4844 | 123.2941 | -120.2637 | 3.0624 | -0.03479 | 0.0044071 | 0.12146 | 0.0030207 | 0.00041234 | 0.00049778 | -0.0026617 | -0.13004 | 0.14238 | 0.0040438 | 0.0043174 | -0.0025976 | -0.00080758 | -0.0018265 | -2.4811 | -2.1698 | -120.6436 | -2.5681 | -2.417 | -120.2225 | -2.4902 | 1.3138 | 3.0579 | 2.504 | 2.7832 | 2.8244 | 2.7191 | 2.8061 | -0.37994 | -5.2322 | -5.6305 | 117.8467 | 117.7734 | 0.041199 | 118.1534 | 0.42114 | 122.7676 | -0.004578 | -0.27924 | 123.0881 | 123.0698 | 122.9828 | 0.30212 | 0.21515 | 118.2266 | 118.0756 | 0.32044 | 0.27924 | 118.4738 | 0.55389 | 118.0939 | 123.3215 | -123.7061 | -0.55847 | 117.6956 | 123.0469 | 117.7826 | 121.5775
1748.4844 | 123.3307 | -120.488 | 2.7924 | 0.0033567 | 0.0039799 | 0.12188 | 0.0023797 | 0.0025485 | 7.0582e-05 | 0.00054267 | -0.10562 | 0.1426 | 0.0048984 | -0.0046548 | -0.003025 | -0.00059378 | -0.00054474 | -2.5177 | -2.2385 | -120.8313 | -2.6276 | -2.4628 | -120.4147 | -2.5406 | 1.2405 | 2.8656 | 2.3117 | 2.5497 | 2.5726 | 2.4582 | 2.5635 | -0.34332 | -5.0308 | -5.4199 | 118.0252 | 117.9474 | 0.073242 | 118.2907 | 0.41657 | 122.7997 | 0.073243 | -0.24261 | 123.0606 | 123.0515 | 122.9462 | 0.25177 | 0.14648 | 118.3685 | 118.2037 | 0.26092 | 0.23804 | 118.5928 | 0.55389 | 118.2495 | 123.3536 | -123.6237 | -0.48065 | 117.8604 | 123.0377 | 117.9703 | 121.7285
1749.4844 | 123.2986 | -120.1813 | 3.1082 | -0.065308 | 0.0059025 | 0.1206 | 0.0038751 | -0.00086946 | -0.00014322 | -9.8328e-05 | -0.12088 | 0.14174 | 0.0038302 | 0.0058126 | -0.0011022 | -0.00016658 | 0.00030966 | -2.5635 | -2.2614 | -120.607 | -2.6779 | -2.4994 | -120.1447 | -2.5726 | 1.3321 | 3.0716 | 2.5314 | 2.8336 | 2.8427 | 2.7924 | 2.8839 | -0.42572 | -5.3696 | -5.7861 | 117.6819 | 117.6086 | 0.036621 | 118.0344 | 0.46234 | 122.7127 | -0.036621 | -0.27466 | 123.024 | 123.0652 | 122.9736 | 0.35248 | 0.26093 | 118.1076 | 117.9291 | 0.31128 | 0.30212 | 118.3456 | 0.54016 | 117.9199 | 123.2529 | -123.7152 | -0.57678 | 117.5034 | 123.0148 | 117.6178 | 121.5134
1750.4844 | 123.3215 | -120.3598 | 2.9526 | -0.019531 | 0.0054751 | 0.12231 | 0.0040887 | -1.486e-05 | -0.00057042 | -0.0022345 | -0.065949 | 0.14174 | 0.0053256 | -0.0020914 | -0.0036658 | -0.0027302 | 0.0011643 | -2.4948 | -2.1103 | -120.6619 | -2.5909 | -2.4399 | -120.2957 | -2.4582 | 1.236 | 3.0396 | 2.449 | 2.6962 | 2.7466 | 2.6184 | 2.7008 | -0.30212 | -5.0629 | -5.5435 | 117.9199 | 117.9016 | 0.064087 | 118.2037 | 0.36621 | 122.8088 | 0.086975 | -0.25635 | 123.1064 | 123.0606 | 122.9782 | 0.25177 | 0.16937 | 118.222 | 118.071 | 0.29755 | 0.24719 | 118.5516 | 0.59051 | 118.2495 | 123.3994 | -123.6145 | -0.50354 | 117.7689 | 123.056 | 117.865 | 121.5958
1751.4844 | 123.2941 | -120.3644 | 2.9343 | -0.11871 | 0.0029117 | 0.12402 | 0.0055841 | -0.00086946 | 0.0032748 | -9.8328e-05 | -0.19412 | 0.14366 | 0.0031894 | -0.005082 | -0.0043066 | -0.001662 | 0.0033005 | -2.536 | -2.1835 | -120.7214 | -2.6413 | -2.4948 | -120.401 | -2.5452 | 1.1627 | 2.9709 | 2.4216 | 2.6367 | 2.7054 | 2.5543 | 2.7145 | -0.35706 | -5.1178 | -5.5756 | 117.8696 | 117.8192 | -0.036621 | 118.1763 | 0.32044 | 122.7859 | 0.036621 | -0.29755 | 123.0698 | 123.0789 | 122.9187 | 0.29297 | 0.13275 | 118.2266 | 118.0801 | 0.28381 | 0.21515 | 118.5379 | 0.54932 | 118.1808 | 123.3353 | -123.6557 | -0.51269 | 117.7231 | 123.0011 | 117.8284 | 121.5271
1752.5469 | 123.3215 | -120.401 | 2.8793 | -0.03479 | 0.0041935 | 0.12146 | 0.00067072 | 0.00083954 | 0.0017794 | -0.0041571 | -0.10562 | 0.14174 | 0.003403 | 0.0021812 | -0.0028112 | 4.7018e-05 | 0.0041551 | -2.4811 | -2.1881 | -120.6894 | -2.5955 | -2.4307 | -120.3506 | -2.4857 | 1.268 | 2.948 | 2.4261 | 2.6596 | 2.7008 | 2.5955 | 2.7054 | -0.28839 | -5.0674 | -5.4749 | 117.9703 | 117.9153 | 0.050354 | 118.2037 | 0.33875 | 122.8271 | 0.068665 | -0.21973 | 123.1018 | 123.1064 | 122.9965 | 0.27924 | 0.16937 | 118.2587 | 118.0939 | 0.27466 | 0.23346 | 118.5013 | 0.52185 | 118.2129 | 123.349 | -123.5687 | -0.45319 | 117.8055 | 123.0606 | 117.9199 | 121.669
1753.4844 | 123.2849 | -120.3278 | 2.9617 | 0.0033567 | 0.0059025 | 0.12231 | 0.0043023 | 0.00083954 | 0.0015658 | -0.00031193 | -0.10562 | 0.14238 | 0.0029758 | -0.0029458 | -0.0032386 | -0.0018756 | 0.0018051 | -2.4628 | -2.1423 | -120.5933 | -2.5772 | -2.4307 | -120.2682 | -2.504 | 1.2268 | 3.0624 | 2.5223 | 2.7054 | 2.71 | 2.6184 | 2.742 | -0.2655 | -5.1041 | -5.5389 | 117.897 | 117.8238 | 0.059509 | 118.0893 | 0.32501 | 122.85 | 0.10071 | -0.25635 | 123.0377 | 123.0698 | 122.9462 | 0.21973 | 0.09613 | 118.1625 | 118.0161 | 0.18768 | 0.1831 | 118.4509 | 0.54016 | 118.1854 | 123.3902 | -123.555 | -0.43945 | 117.7506 | 123.0331 | 117.865 | 121.5546
1754.5469 | 123.2895 | -120.3094 | 2.98 | -0.057678 | 0.0029117 | 0.12167 | 0.0021661 | -0.0030057 | -0.0012112 | 0.0011835 | -0.011017 | 0.14153 | 0.0036166 | -0.0014504 | -0.0034522 | -0.0025164 | 0.0011643 | -2.5589 | -2.2797 | -120.6024 | -2.7328 | -2.5269 | -120.0439 | -2.5635 | 1.3184 | 3.1677 | 2.6047 | 2.6642 | 2.7603 | 2.6688 | 2.7466 | -0.29297 | -5.2597 | -5.7129 | 117.7826 | 117.746 | 0.2655 | 118.0389 | 0.55847 | 122.9141 | 0.18768 | -0.31586 | 123.0698 | 123.056 | 122.9782 | 0.14191 | 0.064087 | 118.0756 | 117.8696 | 0.15564 | 0.05951 | 118.3228 | 0.56305 | 118.0298 | 123.4772 | -123.5825 | -0.37537 | 117.5766 | 122.9736 | 117.7505 | 121.6278
1755.4844 | 123.2666 | -120.4697 | 2.8336 | -0.019531 | 0.0035525 | 0.12295 | 0.0038751 | 0.0057529 | 0.002634 | -0.0035163 | -0.090363 | 0.14281 | 0.0036166 | -0.00016881 | -0.0043066 | -0.003371 | 0.00052346 | -2.5452 | -2.2064 | -120.7397 | -2.6779 | -2.536 | -120.488 | -2.5543 | 0.9613 | 2.9205 | 2.3621 | 2.5909 | 2.5681 | 2.4399 | 2.6093 | -0.27008 | -5.04 | -5.5115 | 117.9337 | 117.9153 | -0.01831 | 118.1854 | 0.25177 | 122.8317 | 0.086975 | -0.24261 | 123.0377 | 123.0789 | 122.9095 | 0.24719 | 0.077819 | 118.2037 | 118.0618 | 0.20599 | 0.22888 | 118.5333 | 0.55847 | 118.2632 | 123.3902 | -123.5733 | -0.4715 | 117.7917 | 123.0606 | 117.9245 | 121.431
1756.5625 | 123.3719 | -120.4514 | 2.7786 | 0.10254 | 0.0065433 | 0.12253 | 0.0019525 | -0.0025785 | 0.0011386 | -9.8328e-05 | -0.029327 | 0.14153 | 0.0040438 | -0.0027322 | -0.002384 | -0.0018756 | -0.0020401 | -3.5202 | -2.1515 | -120.6985 | -2.4445 | -2.2476 | -120.4239 | -2.3209 | 1.2405 | 2.8381 | 2.3346 | 2.6413 | 2.6871 | 2.5589 | 2.6779 | -0.24719 | -4.9301 | -5.2231 | 118.2037 | 118.1305 | 0.027466 | 118.3777 | 0.27466 | 122.786 | 0.05951 | -0.13733 | 123.1384 | 123.1293 | 123.0103 | 0.34332 | 0.2243 | 118.4509 | 118.2541 | 0.35248 | 0.3067 | 118.5471 | 0.50354 | 118.2999 | 123.2895 | -123.4772 | -0.44403 | 118.0069 | 123.0927 | 116.9312 | 121.6919
1757.4844 | 123.3032 | -120.3644 | 2.9022 | 0.0033567 | 0.0054751 | 0.12423 | 0.0036615 | 0.00019874 | 0.0011386 | 0.00096987 | -0.10867 | 0.1426 | 0.0040438 | -0.0048684 | -0.0038794 | -0.0010212 | -0.0024673 | -2.6047 | -2.211 | -120.6299 | -2.6642 | -2.5131 | -120.1721 | -2.5909 | 1.2314 | 2.9938 | 2.4399 | 2.655 | 2.6596 | 2.5681 | 2.6825 | -0.2655 | -5.1132 | -5.5664 | 117.8513 | 117.7734 | 0.19226 | 118.0389 | 0.45776 | 122.8043 | 0.091552 | -0.24719 | 123.024 | 123.0469 | 122.9324 | 0.24261 | 0.12817 | 118.1168 | 117.9657 | 0.21973 | 0.21515 | 118.4189 | 0.55389 | 118.1534 | 123.3582 | -123.5321 | -0.46234 | 117.7002 | 123.0194 | 117.7597 | 121.5958
1758.4844 | 123.2895 | -120.3278 | 2.9755 | -0.080566 | 0.0050479 | 0.12103 | 0.0028069 | -0.0025785 | -0.00057042 | -0.0024481 | -0.053741 | 0.14089 | 0.006821 | -0.0012368 | -0.002384 | -0.0025164 | 0.00030966 | -2.5818 | -2.1881 | -120.6299 | -2.6642 | -2.5223 | -120.5338 | -2.5177 | 1.236 | 3.067 | 2.449 | 2.7145 | 2.7237 | 2.6367 | 2.7145 | -0.30212 | -5.1636 | -5.6396 | 117.8055 | 117.8101 | -0.20599 | 118.1122 | 0.096131 | 122.7768 | 0.091553 | -0.26093 | 123.0515 | 123.0423 | 122.9645 | 0.2655 | 0.18768 | 118.1076 | 117.9657 | 0.27466 | 0.2655 | 118.4418 | 0.61798 | 118.1396 | 123.3948 | -123.6053 | -0.52643 | 117.6636 | 123.0423 | 117.746 | 121.5637
1759.4844 | 123.3124 | -120.1675 | 3.1494 | -0.057678 | 0.0039799 | 0.1206 | 0.0043023 | 0.0012667 | -0.00099762 | -0.0013799 | -0.087311 | 0.14046 | 0.0046848 | 0.0021812 | -0.0021704 | -0.0023028 | 0.0015915 | -2.3529 | -2.0325 | -120.5612 | -2.4399 | -2.2568 | -120.0668 | -2.3346 | 1.3275 | 3.0945 | 2.5497 | 2.9251 | 2.9068 | 2.8336 | 2.9205 | -0.39368 | -5.1819 | -5.5893 | 117.9108 | 117.8329 | 0.10071 | 118.2266 | 0.49438 | 122.7173 | -0.054932 | -0.2243 | 123.0743 | 123.0881 | 123.0011 | 0.37079 | 0.28381 | 118.3044 | 118.1213 | 0.35705 | 0.37537 | 118.5287 | 0.54474 | 118.1351 | 123.262 | -123.7106 | -0.59967 | 117.7277 | 123.0927 | 117.8146 | 121.4951
1760.5469 | 123.3719 | -120.1767 | 3.067 | -0.088196 | 0.0029117 | 0.12167 | 0.0034479 | 0.0019077 | -0.00014322 | -0.0015935 | -0.0018616 | 0.14195 | 0.003403 | -0.0087136 | -0.0028112 | -0.0040118 | 0.0011643 | -2.5635 | -2.0279 | -120.433 | -2.3849 | -2.2247 | -120.076 | -2.243 | 1.3412 | 3.154 | 2.6505 | 2.8839 | 2.9205 | 2.8336 | 2.9251 | -0.25635 | -5.0949 | -5.452 | 117.952 | 117.9337 | 0.10071 | 118.19 | 0.35705 | 122.8271 | 0.086975 | -0.18311 | 123.0972 | 123.1018 | 123.0103 | 0.27466 | 0.1831 | 118.2083 | 118.0481 | 0.27008 | 0.23346 | 118.4052 | 0.50354 | 118.1488 | 123.3307 | -123.5001 | -0.41656 | 117.7917 | 123.0606 | 117.6132 | 121.5179
1761.5 | 123.4222 | -120.1538 | 3.0624 | -0.050049 | 0.0039799 | 0.1206 | 0.00024352 | 0.00019874 | 0.0017794 | -0.0011663 | 0.004242 | 0.14089 | 0.004471 | -0.0044412 | -0.0049476 | -0.0029438 | 0.0020187 | -2.4078 | -2.1469 | -120.4559 | -2.449 | -2.2659 | -119.9387 | -2.3026 | 1.506 | 3.1494 | 2.6413 | 2.9526 | 2.9984 | 2.8885 | 2.948 | -0.30212 | -5.2094 | -5.5115 | 117.8879 | 117.8513 | 0.21515 | 118.1534 | 0.51727 | 122.7951 | 0.086975 | -0.10986 | 123.1522 | 123.1018 | 123.0423 | 0.3067 | 0.24719 | 118.19 | 118.0069 | 0.35706 | 0.31128 | 118.309 | 0.50812 | 118.0069 | 123.3032 | -123.5184 | -0.42114 | 117.7048 | 123.1064 | 117.746 | 121.6599
1762.4844 | 123.2712 | -120.1126 | 3.1906 | -0.050049 | 0.0029117 | 0.12466 | 0.0019525 | 0.0027621 | 0.0013522 | -0.0015935 | -0.11172 | 0.13982 | 0.0059664 | -0.0038004 | -0.0038794 | -0.0010212 | -0.0020401 | -2.4124 | -2.0874 | -120.52 | -2.5223 | -2.3666 | -120.0485 | -2.4307 | 1.3596 | 3.186 | 2.5772 | 2.9388 | 2.8793 | 2.8107 | 2.9205 | -0.40741 | -5.278 | -5.7129 | 117.746 | 117.6819 | 0.064087 | 118.0893 | 0.4715 | 122.6898 | -0.004578 | -0.25177 | 122.9919 | 123.0331 | 122.9233 | 0.34332 | 0.23346 | 118.1534 | 117.9977 | 0.30212 | 0.36163 | 118.4326 | 0.60883 | 118.0252 | 123.2986 | -123.7106 | -0.6134 | 117.5903 | 123.0515 | 117.7002 | 121.4722
1763.5469 | 123.2803 | -120.2911 | 3.0167 | -0.0042723 | 0.0026981 | 0.12039 | 0.0034479 | 0.00083954 | 0.00092498 | -0.0028753 | -0.14529 | 0.14366 | 0.0055392 | 0.0015402 | -0.004093 | -0.0018756 | 0.00030966 | -2.4994 | -2.1286 | -120.5521 | -2.6001 | -2.4948 | -119.8196 | -2.3804 | 1.2909 | 3.1769 | 2.4857 | 2.742 | 2.7191 | 2.6001 | 2.6917 | -0.26093 | -5.1453 | -5.6168 | 117.7963 | 117.9108 | 0.4715 | 118.1717 | 0.73242 | 122.7768 | 0.16022 | -0.27466 | 123.0103 | 122.9828 | 122.8912 | 0.20599 | 0.11444 | 118.0573 | 117.952 | 0.23346 | 0.25635 | 118.4235 | 0.69122 | 118.1625 | 123.468 | -123.5687 | -0.53101 | 117.691 | 123.0331 | 117.7917 | 121.582
1764.4844 | 123.3078 | -120.2637 | 3.0579 | -0.042419 | 0.0048343 | 0.12381 | 0.0034479 | -0.0021513 | 0.0013522 | 0.00096987 | -0.13309 | 0.14067 | 0.0021212 | 0.001113 | -0.0055884 | -0.00080758 | 0.0022323 | -2.5864 | -2.2018 | -120.5658 | -2.6093 | -2.4582 | -120.3598 | -2.5085 | 1.4008 | 3.1677 | 2.5177 | 2.8198 | 2.742 | 2.655 | 2.7512 | -0.30212 | -5.2597 | -5.6671 | 117.8055 | 117.7551 | -0.09613 | 118.0573 | 0.20599 | 122.7814 | 0.10986 | -0.23804 | 123.0057 | 123.0148 | 122.9187 | 0.23346 | 0.13733 | 118.1076 | 117.9565 | 0.2243 | 0.30212 | 118.364 | 0.65002 | 118.0618 | 123.4314 | -123.6237 | -0.54016 | 117.6544 | 123.0835 | 117.6773 | 121.6644
1765.4844 | 123.2895 | -120.2545 | 3.0212 | -0.080566 | 0.0037661 | 0.12188 | 0.0057977 | 0.0021213 | 0.00071138 | -0.00073913 | -0.11783 | 0.14366 | 0.0036166 | 0.00047219 | -0.0025976 | -0.0014484 | 0.00095066 | -2.4719 | -2.1606 | -120.5612 | -2.6047 | -2.4307 | -120.2408 | -2.504 | 1.2589 | 3.0853 | 2.504 | 2.7649 | 2.7283 | 2.6093 | 2.7283 | -0.3067 | -5.1819 | -5.6259 | 117.8238 | 117.7506 | 0.013733 | 118.0573 | 0.32043 | 122.7585 | 0.064087 | -0.25635 | 122.9828 | 122.9828 | 122.8638 | 0.2243 | 0.10529 | 118.1305 | 117.9565 | 0.2243 | 0.26093 | 118.4006 | 0.58136 | 118.0939 | 123.3398 | -123.5825 | -0.51727 | 117.6498 | 123.0194 | 117.7826 | 121.5134
1766.5625 | 123.3536 | -120.1721 | 3.1036 | -0.088196 | 0.0046207 | 0.12146 | 0.0025933 | -0.0021513 | 0.00092498 | -0.00095273 | -0.0049134 | 0.1411 | 0.0048984 | -0.0029458 | -0.0019568 | -0.0018756 | -0.00054474 | -2.5726 | -2.2614 | -120.4514 | -2.6413 | -2.4994 | -119.7235 | -2.5269 | 1.3092 | 3.1403 | 2.5681 | 2.8976 | 2.8839 | 2.7878 | 2.8656 | -0.27924 | -5.365 | -5.7449 | 117.6727 | 117.6453 | 0.44861 | 117.9245 | 0.72784 | 122.7402 | 0.036621 | -0.20599 | 123.056 | 123.0377 | 122.9599 | 0.29755 | 0.21973 | 117.952 | 117.8101 | 0.31586 | 0.32959 | 118.19 | 0.5722 | 117.9108 | 123.3124 | -123.555 | -0.53558 | 117.5308 | 123.0698 | 117.5995 | 121.4813
1767.4844 | 123.3582 | -119.9387 | 3.3142 | -0.065308 | 0.0022709 | 0.12274 | 0.0057977 | 0.0034029 | 0.00092498 | 0.00054267 | -0.087311 | 0.14217 | 0.0038302 | 0.0019674 | -0.0043066 | -0.00038018 | -0.00097194 | -2.449 | -2.1561 | -120.2179 | -2.5314 | -2.3804 | -119.8242 | -2.417 | 1.3779 | 3.3691 | 2.5589 | 3.2364 | 2.8748 | 2.7786 | 2.8748 | -0.27924 | -5.4703 | -5.8456 | 117.5583 | 117.5217 | 0.11444 | 117.8009 | 0.39368 | 122.4976 | 0.054932 | -0.07782 | 122.8134 | 122.8134 | 122.7173 | 0.31586 | 0.21973 | 117.8375 | 117.6865 | 0.31586 | 0.67749 | 118.0618 | 0.81024 | 117.7826 | 123.3078 | -123.5321 | -0.75531 | 117.4072 | 123.175 | 117.4896 | 121.3165
1768.4844 | 123.262 | -120.2637 | 3.0624 | -0.027161 | 0.0037661 | 0.12359 | 0.0047295 | 0.0027621 | 0.0011386 | -0.0018073 | -0.11783 | 0.13832 | 0.0038302 | 0.004531 | -0.0034522 | -0.00016658 | -0.00011754 | -2.6184 | -2.2842 | -120.5658 | -2.742 | -2.6093 | -120.2316 | -2.6459 | 1.2405 | 3.1082 | 2.4261 | 2.742 | 2.6367 | 2.5269 | 2.6642 | -0.30212 | -5.3467 | -5.8044 | 117.6544 | 117.6178 | 0.032044 | 117.9199 | 0.33417 | 122.6898 | 0.045776 | -0.32043 | 122.9004 | 122.9279 | 122.7905 | 0.23804 | 0.10071 | 117.9565 | 117.8238 | 0.21057 | 0.31586 | 118.2816 | 0.68207 | 117.9794 | 123.3719 | -123.6282 | -0.63629 | 117.5217 | 123.0057 | 117.6453 | 121.5042
1769.5469 | 123.2986 | -120.1859 | 3.1403 | 0.049133 | 0.0039799 | 0.12188 | 0.0036615 | 0.0021213 | -0.00057042 | -0.0054389 | -0.047638 | 0.1426 | 0.0059664 | -0.0078592 | -0.0047338 | -0.0037982 | -0.0026809 | -2.6596 | -2.2568 | -120.4285 | -2.7328 | -2.5864 | -119.9066 | -2.6001 | 1.3412 | 3.2043 | 2.5955 | 2.8519 | 2.8381 | 2.71 | 2.8244 | -0.24262 | -5.397 | -5.8731 | 117.5995 | 117.5858 | 0.27924 | 117.8284 | 0.52185 | 122.7814 | 0.064087 | -0.28839 | 123.024 | 123.0103 | 122.8958 | 0.22888 | 0.11444 | 117.8421 | 117.6956 | 0.24261 | 0.25635 | 118.1717 | 0.60883 | 117.9291 | 123.3902 | -123.5687 | -0.54474 | 117.453 | 123.0377 | 117.5262 | 121.5271
1770.4844 | 123.2574 | -119.9524 | 3.3096 | -0.050049 | 0.0026981 | 0.12338 | 0.0036615 | -0.0025785 | 0.0028476 | 0.0016107 | -0.081207 | 0.14131 | 0.005112 | 0.00047219 | -0.003025 | -0.00059378 | -0.0028945 | -3.5889 | -2.3026 | -120.3552 | -2.7695 | -2.5955 | -120.1263 | -2.655 | 1.3 | 3.2776 | 2.5269 | 3.0441 | 2.8656 | 2.7557 | 2.8885 | -0.40283 | -5.6122 | -6.0791 | 117.3569 | 117.2974 | -0.17395 | 117.7002 | 0.22888 | 122.4792 | -0.032043 | -0.2655 | 122.818 | 122.8409 | 122.7081 | 0.36163 | 0.22888 | 117.7597 | 117.5858 | 0.33875 | 0.51727 | 118.0527 | 0.75073 | 117.6498 | 123.23 | -123.6649 | -0.78278 | 117.1829 | 122.9965 | 116.3635 | 121.2524
1771.4844 | 123.2758 | -119.8242 | 3.5248 | -0.027161 | 0.0018435 | 0.11932 | 0.0019525 | -0.0038603 | 0.00049778 | -0.0020209 | -0.056793 | 0.13982 | 0.0059664 | -0.0097818 | -0.002384 | -0.0027302 | 0.0065049 | -2.6321 | -2.2339 | -120.1859 | -2.6825 | -2.5269 | -119.9295 | -2.5406 | 1.3458 | 3.5065 | 2.5543 | 3.2639 | 2.8702 | 2.7786 | 2.8381 | -0.36163 | -5.7587 | -6.2073 | 117.2974 | 117.2836 | -0.10528 | 117.6453 | 0.25635 | 122.3785 | -0.01831 | -0.26092 | 122.6944 | 122.6624 | 122.6028 | 0.28381 | 0.2243 | 117.659 | 117.5034 | 0.31586 | 0.70953 | 117.952 | 0.95215 | 117.5903 | 123.3307 | -123.7106 | -0.97046 | 117.1417 | 123.0881 | 117.1921 | 121.17
1772.4844 | 123.3124 | -119.8883 | 3.3875 | -0.03479 | 0.00077547 | 0.11975 | 0.0032343 | 0.0029757 | -0.00099762 | -0.0020209 | -0.093414 | 0.14025 | 0.0053256 | 0.0034628 | -0.003025 | -0.0018756 | 0.0011643 | -2.4445 | -2.1149 | -120.1401 | -2.5406 | -2.4033 | -119.989 | -2.4673 | 1.3779 | 3.4332 | 2.623 | 3.1769 | 2.8427 | 2.7374 | 2.8519 | -0.25177 | -5.5023 | -5.928 | 117.485 | 117.421 | -0.10071 | 117.6727 | 0.15106 | 122.5113 | 0.045777 | -0.21057 | 122.731 | 122.7402 | 122.6257 | 0.22888 | 0.11444 | 117.7368 | 117.5995 | 0.21973 | 0.55389 | 118.0252 | 0.81024 | 117.7734 | 123.3215 | -123.5275 | -0.76446 | 117.3477 | 123.0652 | 117.4438 | 121.2662
1773.5469 | 123.2849 | -120.1813 | 3.1219 | -0.042419 | 0.0061161 | 0.12274 | 0.0036615 | 0.00083954 | 0.0028476 | -0.0015935 | -0.11172 | 0.14089 | 0.0031894 | -0.0016642 | -0.002384 | -0.0023028 | 0.0022323 | -2.5177 | -2.1469 | -120.4468 | -2.5909 | -2.4353 | -120.1813 | -2.504 | 1.236 | 3.1906 | 2.4536 | 2.8473 | 2.6733 | 2.5864 | 2.7145 | -0.2655 | -5.2689 | -5.7129 | 117.746 | 117.6773 | 0 | 117.9428 | 0.2655 | 122.6349 | 0.068665 | -0.27466 | 122.8546 | 122.8958 | 122.7676 | 0.26093 | 0.13275 | 118.0115 | 117.8558 | 0.21973 | 0.39368 | 118.2999 | 0.737 | 118.0344 | 123.3719 | -123.5687 | -0.66834 | 117.5903 | 123.0286 | 117.6636 | 121.4172
1774.4844 | 123.3261 | -119.957 | 3.3005 | -0.011902 | 0.0044071 | 0.12124 | 0.0030207 | -0.00044226 | 0.0028476 | -0.0028753 | -0.081207 | 0.14409 | 0.0038302 | -0.003373 | -0.0021704 | -0.0020892 | 0.0030869 | -3.1128 | -2.2888 | -120.2774 | -2.7512 | -2.6093 | -116.1301 | -2.6321 | 1.2863 | 3.3783 | 2.6367 | 3.0624 | 2.8748 | 2.6459 | 2.7603 | -0.32044 | -5.5893 | -6.0516 | 117.3477 | 117.3248 | 3.8269 | 117.6453 | 4.1473 | 122.5937 | 0.07782 | -0.23804 | 122.8317 | 122.7173 | 122.6028 | 0.1236 | 0.009155 | 117.6682 | 117.5262 | 0.23804 | 0.42572 | 117.9886 | 0.74158 | 117.6682 | 123.3353 | -123.5779 | -0.66376 | 117.2058 | 123.0194 | 116.8442 | 121.2433
1775.5469 | 123.3398 | -120.1309 | 3.1265 | -0.042419 | 0.0050479 | 0.12274 | 0.0034479 | 0.0036165 | 7.0582e-05 | -0.0013799 | -0.10257 | 0.14217 | 0.003403 | -0.0014504 | -0.002384 | -0.0040118 | 0.00030966 | -2.6779 | -2.092 | -120.433 | -2.5269 | -2.3758 | -120.1675 | -2.4124 | 1.2772 | 3.2135 | 2.536 | 2.9343 | 2.8244 | 2.7237 | 2.8427 | -0.30212 | -5.2185 | -5.6534 | 117.7551 | 117.7185 | -0.036622 | 118.0206 | 0.2655 | 122.6669 | 0.086975 | -0.19226 | 122.9553 | 122.9736 | 122.8546 | 0.3067 | 0.18768 | 118.0573 | 117.9062 | 0.28839 | 0.39825 | 118.3411 | 0.67749 | 118.0389 | 123.3444 | -123.5596 | -0.59052 | 117.6041 | 123.0652 | 117.453 | 121.4081
1776.4844 | 123.2941 | -120.0989 | 3.2089 | -0.065308 | 0.0054751 | 0.12124 | 0.0060113 | 0.0023349 | 0.0032748 | -0.00052553 | -0.11783 | 0.14025 | 0.0038302 | -0.0052958 | -0.0019568 | -0.001662 | -0.0011855 | -3.0762 | -2.2842 | -120.433 | -2.7695 | -2.6505 | -120.2866 | -2.6459 | 1.1993 | 3.2547 | 2.4994 | 2.9205 | 2.7328 | 2.623 | 2.7557 | -0.33417 | -5.4932 | -5.9784 | 117.4484 | 117.453 | -0.18768 | 117.7872 | 0.14648 | 122.5983 | 0.045777 | -0.28839 | 122.8317 | 122.8546 | 122.7219 | 0.25635 | 0.1236 | 117.7826 | 117.6636 | 0.23346 | 0.42114 | 118.1488 | 0.75531 | 117.8146 | 123.3536 | -123.642 | -0.70953 | 117.3294 | 123.0194 | 117.0227 | 121.2982
1777.4844 | 123.468 | -118.4921 | 4.6326 | -0.03479 | 0.0044071 | 0.1206 | 0.0032343 | -0.00065586 | 0.0024204 | -0.0015935 | -0.069 | 0.14131 | 0.0038302 | 0.00068579 | -0.004093 | -0.001662 | -0.0031081 | -8.3588 | -1.4694 | -118.895 | -1.8768 | -1.712 | -118.4097 | -1.7532 | 2.1469 | 4.7379 | 4.1382 | 4.5273 | 4.4724 | 4.3671 | 4.5136 | -0.40283 | -6.102 | -6.5094 | 116.7801 | 116.7389 | 0.082397 | 117.1417 | 0.48523 | 122.6303 | 0.10529 | -0.10529 | 122.9645 | 123.0057 | 122.8592 | 0.37537 | 0.22888 | 117.1829 | 117.0181 | 0.33417 | 0.3891 | 117.4255 | 0.59967 | 117.0227 | 123.23 | -123.5275 | -0.49438 | 116.6153 | 123.0194 | 110.1334 | 120.639
1778.5469 | 123.4955 | -87.1811 | 4.7562 | -0.03479 | 0.0059025 | 0.022123 | -0.0046699 | -0.019668 | 0.13722 | -0.0075751 | 0.068329 | 0.19173 | 0.0023348 | -0.0046548 | -0.0036658 | -0.0020892 | -0.0011855 | 0.62714 | -2.0599 | -53.8376 | 1.9821 | -0.3067 | -128.1921 | -1.6937 | 2.2202 | 4.8431 | 5.6213 | 4.6692 | 4.6097 | 4.4495 | 4.5364 | 33.3435 | -6.8161 | -2.774 | 86.8744 | 85.4874 | -41.011 | 52.1439 | -74.3546 | 92.8024 | 0.086975 | -0.086976 | 91.7908 | 91.7175 | 91.6306 | -1.0849 | -1.1719 | 53.5309 | 55.8197 | -1.0117 | -0.95215 | 51.7776 | -0.7782 | 85.1212 | 92.0242 | -58.5938 | 0.86517 | 89.1632 | 91.8503 | 87.8082 | 89.4012
1779.4844 | 123.3032 | -119.1147 | 4.1885 | -0.072937 | 0.0035525 | 0.12082 | 0.0030207 | -0.0017239 | 0.00071138 | -0.00095273 | -0.072052 | 0.14089 | 0.0046848 | 0.0058126 | -0.0025976 | -0.0018756 | -0.0011855 | -1.9547 | -1.5976 | -119.4077 | -2.0554 | -1.9318 | -119.1559 | -2.0599 | 1.8631 | 4.2572 | 3.685 | 3.9688 | 3.8956 | 3.8406 | 3.9505 | -0.29297 | -5.7861 | -6.2439 | 117.1829 | 117.0547 | -0.041199 | 117.3477 | 0.25177 | 122.7997 | 0.068664 | -0.21973 | 123.0103 | 123.0652 | 122.9553 | 0.2655 | 0.15564 | 117.4759 | 117.3523 | 0.21057 | 0.28381 | 117.8101 | 0.5722 | 117.5171 | 123.3719 | -123.5962 | -0.50354 | 117.0593 | 123.0835 | 117.16 | 120.9778
1780.4844 | 123.262 | -118.8629 | 4.454 | -0.0042723 | 0.0048343 | 0.1221 | 0.0047295 | 0.00083954 | 0.00071138 | -0.00031193 | -0.099518 | 0.14067 | 0.0029758 | -0.003373 | -0.0021704 | -0.0020892 | -0.0026809 | -2.0599 | -1.7303 | -119.1559 | -2.1835 | -2.0416 | -118.8492 | -2.092 | 1.9272 | 4.5181 | 3.9276 | 4.1885 | 4.1611 | 4.0512 | 4.1931 | -0.29297 | -6.1844 | -6.6376 | 116.8213 | 116.7709 | 0.013733 | 117.0639 | 0.3067 | 122.7905 | 0.064086 | -0.2655 | 123.024 | 123.056 | 122.9141 | 0.2655 | 0.1236 | 117.1143 | 116.9724 | 0.23346 | 0.26093 | 117.4255 | 0.59051 | 117.1326 | 123.381 | -123.6099 | -0.52643 | 116.6794 | 123.0515 | 116.803 | 120.7901
1781.5469 | 123.2758 | -118.8995 | 4.3945 | -0.03479 | 0.0041935 | 0.11975 | 0.0032343 | 0.0019077 | -0.00099762 | -0.0011663 | -0.10867 | 0.13875 | 0.0025484 | 0.00025839 | -0.003025 | -0.00059378 | -0.0018265 | -2.0462 | -1.6937 | -119.0689 | -2.179 | -2.0233 | -118.8675 | -2.0645 | 1.918 | 4.5547 | 3.9734 | 4.1748 | 4.1153 | 4.0146 | 4.1656 | -0.16937 | -6.0883 | -6.5735 | 116.8762 | 116.835 | 0.032043 | 117.0044 | 0.20142 | 122.8729 | 0.16022 | -0.21973 | 123.0148 | 123.0652 | 122.9141 | 0.19226 | 0.041198 | 117.0456 | 116.89 | 0.14191 | 0.20142 | 117.3752 | 0.58136 | 117.2058 | 123.4543 | -123.4634 | -0.42114 | 116.7206 | 123.0743 | 116.8533 | 120.8176
1782.4844 | 123.3353 | -118.5013 | 4.7699 | -0.042419 | 0.00077547 | 0.11996 | 0.0047295 | 0.00041234 | 0.0034884 | -0.00031193 | -0.096466 | 0.1379 | 0.0057528 | 4.4788e-05 | -0.0032386 | -0.00080758 | 0.0024461 | -1.9501 | -1.5884 | -118.7897 | -2.0554 | -1.9043 | -118.4601 | -1.9272 | 2.1378 | 4.8386 | 4.2526 | 4.5731 | 4.5731 | 4.4495 | 4.5776 | -0.28839 | -6.3583 | -6.8253 | 116.597 | 116.5741 | 0.041199 | 116.8625 | 0.32959 | 122.7539 | 0.068665 | -0.19684 | 123.0743 | 123.0789 | 122.9507 | 0.32501 | 0.19684 | 116.8854 | 116.7343 | 0.32043 | 0.32043 | 117.2012 | 0.58594 | 116.9128 | 123.3398 | -123.5596 | -0.51727 | 116.4459 | 123.0743 | 116.5512 | 120.639
1783.4844 | 123.3673 | -118.3914 | 4.8065 | -0.14923 | 0.0048343 | 0.11953 | 0.0028069 | 0.0014803 | 0.0028476 | 0.0018243 | -0.038483 | 0.14067 | 0.0046848 | 0.0070944 | -0.004093 | -0.0027302 | -0.00075834 | -1.9043 | -1.68 | -118.6295 | -1.9867 | -1.8082 | -118.4143 | -1.886 | 2.298 | 4.8798 | 4.3854 | 4.7653 | 4.6692 | 4.6463 | 4.7653 | -0.23804 | -6.4865 | -6.7932 | 116.5833 | 116.5054 | -0.022889 | 116.7435 | 0.21515 | 122.7768 | 0.073242 | -0.041199 | 123.0606 | 123.1567 | 123.0377 | 0.37994 | 0.26093 | 116.8213 | 116.6428 | 0.28381 | 0.37994 | 116.9495 | 0.49439 | 116.7114 | 123.2712 | -123.436 | -0.42114 | 116.4047 | 123.1567 | 116.4871 | 120.6894
1784.4844 | 123.262 | -118.3868 | 4.9072 | -0.057678 | 0.0048343 | 0.12146 | 0.0045159 | 0.0038303 | 0.0024204 | -0.0039435 | -0.090363 | 0.14067 | 0.0059664 | -0.0014504 | -0.0032386 | -0.00016658 | 0.0013779 | -1.886 | -1.5289 | -118.7027 | -2.005 | -1.8906 | -118.428 | -1.8768 | 2.1286 | 4.9622 | 4.3533 | 4.6326 | 4.5959 | 4.5181 | 4.6783 | -0.31586 | -6.4362 | -6.9122 | 116.4963 | 116.51 | -0.041199 | 116.8259 | 0.27466 | 122.7402 | 0.054931 | -0.27466 | 122.9828 | 123.0652 | 122.905 | 0.32501 | 0.16479 | 116.8121 | 116.6977 | 0.24261 | 0.27923 | 117.1738 | 0.60882 | 116.8579 | 123.349 | -123.6099 | -0.55389 | 116.3818 | 123.0194 | 116.5009 | 120.5154
1785.5469 | 123.262 | -118.3777 | 4.9484 | -0.042419 | 0.0054751 | 0.12146 | 0.0040887 | 0.0021213 | 7.0582e-05 | 0.0018243 | -0.10562 | 0.13854 | 0.0036166 | 0.0017538 | -0.0043066 | -0.0023028 | 0.00073706 | -1.9226 | -1.5884 | -118.6707 | -2.0554 | -1.8906 | -118.3365 | -1.9455 | 2.1835 | 4.9988 | 4.4174 | 4.6967 | 4.6875 | 4.5914 | 4.6783 | -0.29297 | -6.5369 | -7.0038 | 116.4871 | 116.4322 | 0.041199 | 116.7252 | 0.33417 | 122.7951 | 0.050354 | -0.25177 | 123.0652 | 123.056 | 122.9691 | 0.26093 | 0.17395 | 116.7801 | 116.6153 | 0.27008 | 0.27924 | 117.0822 | 0.58136 | 116.7892 | 123.3765 | -123.6191 | -0.53101 | 116.3223 | 123.0743 | 116.4551 | 120.5612
1786.4844 | 123.2803 | -118.7393 | 4.541 | -0.0042723 | 0.0039799 | 0.12188 | 0.0032343 | 0.0010531 | 0.0047702 | -0.00095273 | -0.10257 | 0.14195 | 0.0027622 | 0.002822 | -0.0028112 | -0.0018756 | 9.6064e-05 | -1.9089 | -1.6067 | -119.0048 | -2.037 | -1.886 | -118.6111 | -1.9501 | 2.0004 | 4.5959 | 4.0146 | 4.2709 | 4.2801 | 4.1931 | 4.3259 | -0.2655 | -6.1478 | -6.5781 | 116.8533 | 116.7892 | 0.12817 | 117.0547 | 0.39368 | 122.7539 | 0.054931 | -0.27008 | 123.0194 | 123.0652 | 122.9324 | 0.31128 | 0.17853 | 117.1188 | 116.9678 | 0.2655 | 0.25635 | 117.3981 | 0.58136 | 117.1326 | 123.3353 | -123.5458 | -0.52643 | 116.7023 | 123.0103 | 116.8304 | 120.7397
1787.4844 | 123.4039 | -118.6066 | 4.5959 | -0.080566 | 0.0035525 | 0.12103 | 0.0043023 | 0.0014803 | 0.00071138 | -0.0041571 | -0.065949 | 0.14067 | 0.003403 | -0.00059601 | -0.0032386 | -0.0010212 | 0.0011643 | -1.8631 | -1.6525 | -118.9545 | -1.9638 | -1.7761 | -118.5287 | -1.8631 | 2.1378 | 4.6509 | 4.129 | 4.4815 | 4.509 | 4.4312 | 4.5502 | -0.3479 | -6.2485 | -6.5598 | 116.8304 | 116.7435 | 0.077819 | 117.0914 | 0.42572 | 122.7356 | 0.054932 | -0.11444 | 123.1155 | 123.1567 | 123.0377 | 0.42114 | 0.30212 | 117.1783 | 116.9907 | 0.37994 | 0.35248 | 117.3019 | 0.52185 | 116.954 | 123.2574 | -123.5504 | -0.46692 | 116.6428 | 123.0881 | 116.7435 | 120.7443
1788.4844 | 123.2666 | -118.6981 | 4.5914 | -0.050049 | 0.0016299 | 0.11825 | 0.0045159 | 0.0014803 | 7.0582e-05 | -0.0020209 | -0.093414 | 0.14003 | 0.0040438 | 0.00389 | -0.0047338 | -0.0046528 | 9.6064e-05 | -1.9501 | -1.5839 | -119.0369 | -2.0599 | -1.9226 | -118.7347 | -1.9409 | 1.9272 | 4.6234 | 4.0329 | 4.39 | 4.2114 | 4.2664 | 4.3716 | -0.33875 | -6.1752 | -6.6513 | 116.7755 | 116.7572 | -0.036621 | 117.0959 | 0.30212 | 122.731 | 0.032043 | -0.20142 | 122.9095 | 123.0698 | 122.9645 | 0.33874 | 0.23346 | 117.1143 | 116.9769 | 0.17853 | 0.35706 | 117.453 | 0.59051 | 117.1143 | 123.3215 | -123.6282 | -0.55847 | 116.6382 | 123.0881 | 116.748 | 120.6253
1789.5469 | 123.2986 | -118.5608 | 4.7516 | -0.057678 | 0.0048343 | 0.1206 | 0.0013117 | -0.00022866 | -0.00078402 | -0.0015935 | -0.087311 | 0.13918 | 0.0040438 | -0.002305 | -0.0019568 | -0.0037982 | 0.00052346 | -1.9958 | -1.6983 | -118.8858 | -2.1194 | -1.9455 | -119.8975 | -2.0004 | 2.1835 | 4.7424 | 4.184 | 4.6005 | 4.5273 | 4.4449 | 4.5273 | -0.32501 | -6.4499 | -6.871 | 116.6153 | 116.5604 | -1.3367 | 116.8854 | -1.0117 | 122.7448 | -0.009155 | -0.15106 | 123.0881 | 123.0881 | 123.0057 | 0.34332 | 0.26093 | 116.9403 | 116.7664 | 0.34332 | 0.41657 | 117.1875 | 0.55847 | 116.8625 | 123.3032 | -123.6374 | -0.56763 | 116.4413 | 123.1613 | 116.5649 | 120.7443
1790.4844 | 123.3124 | -118.8675 | 4.3625 | 0.010986 | 0.0048343 | 0.12082 | 0.0036615 | 0.0014803 | -0.0012112 | 0.00011527 | -0.099518 | 0.14025 | 0.0031894 | -0.0016642 | -0.0025976 | -0.00059378 | 0.0018051 | -2.1286 | -1.7395 | -119.165 | -2.1881 | -2.0782 | -118.8263 | -2.092 | 1.8219 | 4.4678 | 3.9047 | 4.1748 | 4.1748 | 4.0604 | 4.1931 | -0.29755 | -6.102 | -6.5506 | 116.7892 | 116.7755 | 0.041199 | 117.0731 | 0.33874 | 122.7722 | 0.10529 | -0.18768 | 123.0423 | 123.0606 | 122.9279 | 0.28839 | 0.15564 | 117.0868 | 116.9769 | 0.27008 | 0.27008 | 117.4255 | 0.56305 | 117.128 | 123.3353 | -123.5275 | -0.45776 | 116.6794 | 123.0423 | 116.7389 | 120.6894
1791.4844 | 123.3765 | -118.8492 | 4.39 | -0.0042723 | 0.0014163 | 0.12295 | 0.0028069 | 0.0034029 | 0.0015658 | -0.00052553 | -0.059845 | 0.13854 | 0.0010532 | 0.0017538 | -0.0028112 | -0.0020892 | 0.00030966 | -2.1927 | -1.8631 | -119.1467 | -2.2568 | -2.1011 | -118.515 | -2.1469 | 1.8951 | 4.4861 | 3.9368 | 4.2664 | 4.303 | 4.1382 | 4.2938 | -0.29755 | -6.2531 | -6.6467 | 116.748 | 116.7023 | 0.33417 | 116.9998 | 0.63171 | 122.7859 | 0.09613 | -0.1236 | 123.1522 | 123.143 | 122.9874 | 0.35705 | 0.20142 | 117.0456 | 116.89 | 0.36621 | 0.32959 | 117.2836 | 0.54932 | 116.9861 | 123.3353 | -123.5367 | -0.45319 | 116.5924 | 123.1155 | 116.6565 | 120.7443
1792.5469 | 123.3398 | -118.6798 | 4.6097 | -0.057678 | 0.0033389 | 0.12146 | 0.0045159 | 0.0012667 | 0.00071138 | 0.00032907 | -0.081207 | 0.13875 | 0.0031894 | 0.0047446 | -0.0036658 | -0.0018756 | -0.00075834 | -2.179 | -1.767 | -118.9636 | -2.1606 | -1.9913 | -118.8858 | -2.0645 | 1.9638 | 4.6463 | 4.1061 | 4.3991 | 4.4037 | 4.3121 | 4.422 | -0.28381 | -6.3766 | -6.7703 | 116.6885 | 116.6153 | -0.20599 | 116.8991 | 0.07782 | 122.7859 | 0.036621 | -0.21057 | 123.0835 | 123.1018 | 122.9919 | 0.31586 | 0.20599 | 116.9724 | 116.803 | 0.29755 | 0.29297 | 117.1967 | 0.54016 | 116.9128 | 123.3261 | -123.5733 | -0.50354 | 116.5192 | 123.0789 | 116.5009 | 120.6436
1793.4844 | 123.349 | -118.4738 | 4.7653 | -0.03479 | 0.0050479 | 0.11911 | 0.0057977 | 0.0029757 | -0.0020658 | -0.00031193 | -0.087311 | 0.14089 | 0.0038302 | 0.001113 | -0.003025 | -0.00016658 | -0.00054474 | -2.2293 | -1.8814 | -118.808 | -2.3209 | -2.1698 | -118.5791 | -2.2018 | 1.8539 | 4.8523 | 4.2847 | 4.6051 | 4.6005 | 4.5044 | 4.6326 | -0.33417 | -6.6467 | -7.0862 | 116.304 | 116.272 | -0.10529 | 116.6061 | 0.22888 | 122.7585 | 0.086975 | -0.16022 | 123.0743 | 123.1064 | 122.9782 | 0.3479 | 0.21973 | 116.6382 | 116.4871 | 0.31586 | 0.32043 | 116.9266 | 0.56763 | 116.5924 | 123.3261 | -123.5733 | -0.48065 | 116.153 | 123.0789 | 116.2445 | 120.3278
1794.4844 | 123.2666 | -118.4784 | 4.7928 | -0.03479 | 0.0035525 | 0.12039 | 0.0043023 | -0.0015103 | -0.00035682 | 0.0026789 | -0.12088 | 0.13832 | 0.0029758 | 0.0015402 | -0.002384 | -0.00080758 | -0.0018265 | -2.1011 | -1.7578 | -118.8354 | -2.243 | -2.092 | -118.3228 | -2.1194 | 1.7258 | 4.8752 | 4.2618 | 4.5136 | 4.4861 | 4.3762 | 4.5136 | -0.35706 | -6.5506 | -7.0358 | 116.3864 | 116.3589 | 0.15564 | 116.716 | 0.51269 | 122.7402 | 0.082397 | -0.27924 | 122.9645 | 122.9919 | 122.8546 | 0.25177 | 0.11444 | 116.7435 | 116.5924 | 0.2243 | 0.25177 | 117.0776 | 0.6134 | 116.7206 | 123.3536 | -123.6282 | -0.53101 | 116.2354 | 122.9919 | 116.3773 | 120.2042
1795.5469 | 123.2803 | -118.5242 | 4.747 | -0.0042723 | 0.0035525 | 0.11975 | 0.0043023 | 0.0029757 | 0.0015658 | -0.0026617 | -0.14224 | 0.14003 | 0.003403 | 0.00047219 | -0.0011022 | -0.0027302 | -0.0016129 | -2.0966 | -1.7532 | -118.8538 | -2.1973 | -2.0554 | -118.4143 | -2.1103 | 1.8906 | 4.8157 | 4.1885 | 4.5136 | 4.509 | 4.3854 | 4.5273 | -0.32959 | -6.5002 | -6.9443 | 116.4688 | 116.4139 | 0.10986 | 116.7435 | 0.43945 | 122.7127 | 0.068665 | -0.23346 | 123.0331 | 123.0515 | 122.9095 | 0.33874 | 0.19684 | 116.7984 | 116.6565 | 0.32043 | 0.32501 | 117.1005 | 0.62714 | 116.7709 | 123.3398 | -123.6008 | -0.55847 | 116.3269 | 123.0377 | 116.4276 | 120.4147
1796.4844 | 123.2803 | -118.364 | 4.9118 | 0.010986 | 0.0056889 | 0.12146 | 0.0032343 | 0.0023349 | 0.0019932 | 0.0020379 | -0.090363 | 0.14003 | 0.0027622 | -0.002305 | -0.0032386 | -0.0023028 | 0.0028733 | -2.2247 | -1.8448 | -118.7073 | -2.3209 | -2.1881 | -118.4738 | -2.2247 | 1.6708 | 4.9805 | 4.3671 | 4.66 | 4.6234 | 4.5044 | 4.6463 | -0.34332 | -6.7566 | -7.2327 | 116.1758 | 116.1392 | -0.10986 | 116.4825 | 0.23346 | 122.731 | 0.068665 | -0.25177 | 122.9874 | 123.0103 | 122.8683 | 0.27924 | 0.13733 | 116.5192 | 116.3864 | 0.25635 | 0.29297 | 116.8625 | 0.6134 | 116.5192 | 123.3444 | -123.6191 | -0.54474 | 116.0431 | 123.024 | 116.1392 | 120.0348
1797.5469 | 123.2483 | -118.3823 | 4.9576 | -0.03479 | 0.0041935 | 0.11953 | 0.0043023 | 0.0014803 | 0.0022068 | -0.0030889 | -0.075104 | 0.13832 | 0.0027622 | 0.00025839 | -0.003025 | -0.00080758 | 0.00052346 | -2.2842 | -1.9318 | -118.689 | -2.4078 | -2.243 | -118.8812 | -2.3026 | 1.6022 | 4.953 | 4.3625 | 4.6692 | 4.5959 | 4.5227 | 4.66 | -0.3067 | -6.8893 | -7.3654 | 116.1392 | 116.0797 | -0.49896 | 116.3864 | -0.19226 | 122.7448 | -0.004578 | -0.28839 | 122.9782 | 123.0423 | 122.905 | 0.29755 | 0.16022 | 116.4459 | 116.2811 | 0.23346 | 0.3067 | 116.7572 | 0.59051 | 116.4505 | 123.3353 | -123.6465 | -0.59509 | 115.9744 | 123.0515 | 116.098 | 119.9844
1798.4844 | 123.2758 | -118.3228 | 4.9805 | -0.050049 | 0.0037661 | 0.12082 | 0.0028069 | -1.486e-05 | 0.00028418 | 0.00032907 | -0.12088 | 0.13854 | 0.0042574 | 0.00089939 | -0.003025 | -0.00038018 | 0.0022323 | -2.2614 | -1.9272 | -118.6569 | -2.3575 | -2.2339 | -118.6203 | -2.2659 | 1.6663 | 5.0446 | 4.3808 | 4.7241 | 4.66 | 4.541 | 4.7012 | -0.33417 | -6.9077 | -7.338 | 116.0889 | 116.0568 | -0.29755 | 116.391 | 0.036621 | 122.7036 | 0.064087 | -0.25635 | 122.9828 | 123.024 | 122.8638 | 0.32043 | 0.16022 | 116.423 | 116.2994 | 0.27924 | 0.34332 | 116.7297 | 0.66376 | 116.3956 | 123.3673 | -123.6374 | -0.59967 | 115.9653 | 123.0469 | 116.0614 | 119.989
1799.4844 | 123.3078 | -118.396 | 4.8981 | -0.065308 | 0.0039799 | 0.11889 | 0.0043023 | -0.0017239 | -0.00035682 | -0.0020209 | 0.062225 | 0.13854 | 0.0046848 | -0.0031594 | -0.0015296 | -0.0035846 | -0.0020401 | -2.3346 | -1.9821 | -118.6707 | -2.4582 | -2.3071 | -113.4201 | -2.3804 | 1.4008 | 4.9805 | 4.335 | 4.6738 | 4.5822 | 4.5319 | 4.6463 | -0.27466 | -6.8802 | -7.3563 | 116.0889 | 116.0156 | 4.9759 | 116.2903 | 5.2505 | 122.731 | 0.082398 | -0.2243 | 122.9782 | 123.0423 | 122.9279 | 0.31128 | 0.19684 | 116.3635 | 116.2125 | 0.24719 | 0.33874 | 116.6885 | 0.64545 | 116.4139 | 123.3765 | -123.5687 | -0.56305 | 115.9378 | 123.0698 | 116.0614 | 119.7968
1800.5469 | 122.4655 | -44.3253 | 78.0899 | -0.011902 | 0.0033389 | 0.04199 | 0.00024352 | -1.486e-05 | 0.0019932 | -0.0035163 | -0.020172 | 0.0060905 | 0.0027622 | 0.045974 | -0.003025 | -0.0029438 | 0.0011643 | -1.7166 | -1.387 | -45.3278 | -1.8402 | -1.712 | -45.2499 | -1.7212 | 4.0237 | 78.1677 | 1.9958 | 78.1036 | 2.3575 | 2.1606 | 2.2659 | -1.0025 | -79.4769 | -79.9301 | 42.6132 | 42.6041 | -0.92468 | 43.6066 | 0.07782 | 46.3211 | 0.07782 | 0.013733 | 46.6827 | 46.5912 | 46.4859 | 0.27008 | 0.1648 | 43.6157 | 43.4875 | 0.36163 | 76.1078 | 43.9407 | 76.1719 | 42.9382 | 122.493 | -123.4177 | -76.0941 | 42.485 | 122.4289 | 42.6086 | 48.349
1801.4844 | 123.5367 | -118.4235 | 4.6555 | -0.080566 | 0.0014163 | 0.1206 | 0.0047295 | 0.00083954 | -0.00078402 | -0.00031193 | -0.035431 | 0.13939 | 0.0029758 | -0.003373 | -0.0028112 | -0.0012348 | -0.00033114 | -2.9709 | -2.623 | -118.6981 | -2.9938 | -2.9205 | -118.7943 | -2.9663 | 1.3962 | 4.6188 | 4.1519 | 4.5868 | 4.3808 | 4.2801 | 4.3991 | -0.27466 | -7.2784 | -7.6492 | 115.5029 | 115.4572 | -0.37079 | 115.7318 | -0.09613 | 122.5754 | -0.036622 | -0.068665 | 122.8043 | 122.8226 | 122.7036 | 0.24719 | 0.12817 | 115.7776 | 115.7043 | 0.22888 | 0.43487 | 116.0751 | 0.46692 | 115.8005 | 123.0423 | -123.3536 | -0.50354 | 115.4297 | 123.0103 | 115.4526 | 119.8196
1802.4844 | 101.1978 | -43.2404 | 63.5742 | -0.24841 | 0.02406 | 0.11313 | 0.065826 | 0.036087 | 0.054331 | 0.047967 | -0.30093 | -0.0028817 | -0.0053556 | 0.039138 | -0.011143 | -0.010421 | -0.013149 | 0.09613 | 0.09613 | -17.157 | 0.091553 | 0.10071 | -23.6618 | 0.082397 | 0.09613 | 51.947 | 1.8173 | 67.424 | 1.4694 | 0.11902 | 0.07782 | 26.0834 | -63.4781 | -63.4827 | 43.3411 | 43.3228 | 19.5786 | 17.2394 | -6.5048 | 45.0577 | -11.6272 | 3.8498 | 44.7098 | 43.3182 | 43.3594 | -1.7395 | -1.6983 | 17.2577 | 17.2485 | -0.3479 | 65.6067 | 17.2531 | 50.1297 | 43.3365 | 95.1874 | -80.7312 | -61.7569 | 43.3319 | 110.6644 | 43.3365 | 43.3365
1803.4844 | 122.8409 | -43.7942 | 78.3829 | -0.46204 | 0.0033389 | 0.042631 | 0.0030207 | -0.0017239 | 0.0013522 | -0.0030889 | -0.0049134 | 0.0041679 | 0.0023348 | 0.038924 | -0.0025976 | -0.0014484 | 9.6064e-05 | -1.3962 | -1.1215 | -43.9453 | -1.442 | -1.387 | -43.5013 | -1.4832 | 3.7765 | 78.4378 | 1.8723 | 79.2847 | 2.2293 | 2.0737 | 2.2247 | -0.15106 | -79.5044 | -79.8248 | 42.4072 | 42.3111 | 0.29297 | 42.4622 | 0.44403 | 45.6665 | 0.054931 | 0.90179 | 46.0236 | 46.019 | 45.8679 | 0.35248 | 0.20142 | 42.5583 | 42.5034 | 0.35706 | 77.4124 | 42.8238 | 76.5656 | 42.6727 | 122.2321 | -122.3282 | -76.5106 | 42.3523 | 123.0789 | 42.3981 | 47.5708
1804.5469 | 94.1299 | -44.1925 | 69.9875 | -0.27893 | 0.0037661 | 0.043272 | 0.0040887 | -0.0015103 | 0.0039158 | -0.0013799 | 0.068329 | 0.0028861 | 0.0046848 | 0.041701 | -0.001316 | -0.003371 | 0.0030869 | -1.1902 | -0.76446 | -42.9474 | -1.355 | -1.3367 | -44.3207 | -1.3824 | 3.5294 | 78.8864 | 1.8127 | 78.1036 | 1.767 | 1.5518 | 1.6388 | 1.2451 | -70.752 | -71.3425 | 42.8558 | 42.8101 | -0.12817 | 41.5649 | -1.3733 | 46.0052 | 8.8989 | 8.1162 | 45.9595 | 45.8313 | 45.7443 | -0.17395 | -0.26092 | 41.6107 | 41.5924 | -0.045776 | 76.2909 | 42.1829 | 77.0737 | 43.428 | 123.0789 | -112.9349 | -68.1747 | 42.8375 | 122.2961 | 43.0023 | 47.7219
1805.4844 | 123.4772 | -118.7347 | 4.3991 | 0.026245 | 0.0026981 | 0.12231 | 0.0021661 | 0.0010531 | 0.0015658 | -9.8328e-05 | -0.038483 | 0.13811 | 0.0053256 | -0.0025186 | -0.002384 | -0.0031574 | 0.0011643 | -2.1469 | -1.8127 | -119.1742 | -2.4445 | -2.4307 | -119.0323 | -2.4765 | 1.2726 | 4.4678 | 3.9413 | 4.2755 | 4.1061 | 3.9185 | 4.01 | -0.43945 | -6.2119 | -6.8436 | 116.304 | 116.2582 | -0.29755 | 116.6977 | 0.14191 | 122.6761 | 0.068664 | -0.1236 | 122.8409 | 122.7448 | 122.6532 | 0.068665 | -0.022888 | 116.7435 | 116.7297 | 0.16479 | 0.33417 | 117.3615 | 0.52643 | 116.922 | 123.2025 | -123.5733 | -0.45776 | 116.2903 | 123.0103 | 116.5878 | 120.0073
1806.4844 | 123.3673 | -118.8309 | 4.4495 | -0.011902 | 0.0020573 | 0.11249 | 0.0013117 | -0.01625 | -0.00527 | -0.010993 | -0.11783 | 0.14665 | -0.00621 | -0.014909 | -0.020756 | -0.01747 | -0.01144 | -2.2705 | -1.7761 | -119.1101 | -2.6917 | 0.091553 | -101.6876 | -2.4994 | 1.0117 | 4.4403 | 4.0283 | 4.2206 | 4.0192 | 3.9368 | 4.0192 | -0.27923 | -6.2256 | -7.1411 | 118.9224 | 116.3315 | 17.1432 | 116.6107 | 17.4225 | 122.8592 | -0.009155 | -0.22888 | 122.85 | 122.85 | 122.7676 | -0.009155 | -0.091552 | 119.2017 | 116.4185 | -0.009155 | 0.19226 | 117.334 | 0.41199 | 117.0547 | 123.2712 | -123.5596 | -0.42114 | 116.1392 | 123.0515 | 116.5604 | 119.8425
1807.4844 | 123.381 | -118.7851 | 4.5319 | -0.065308 | 0.0026981 | 0.11697 | 0.0057977 | -0.00086946 | 0.0019932 | -0.0047979 | -0.27347 | 0.13127 | 0.0055392 | -0.0035868 | -0.0002478 | -0.00016658 | 0.0039413 | -2.1423 | -1.7853 | -118.9636 | -2.3804 | -2.4673 | -111.3556 | -2.6093 | 1.1398 | 4.6005 | 3.9642 | 4.2801 | 4.3259 | 3.9276 | 3.891 | -0.17853 | -6.3171 | -6.9122 | 116.3177 | 116.1758 | 7.4295 | 116.3544 | 7.608 | 122.7493 | 0.068665 | -0.25177 | 123.111 | 122.6761 | 122.7127 | -0.073242 | -0.036621 | 116.4963 | 116.5833 | 0.36163 | 0.31586 | 117.1783 | 0.63629 | 116.9998 | 123.3856 | -123.4955 | -0.56763 | 116.4047 | 123.0652 | 116.6428 | 119.9249
1808.4844 | 123.4039 | -118.8766 | 4.3762 | -0.080566 | 0.0035525 | 0.12146 | 0.0049433 | 0.0034029 | 0.0028476 | -0.00073913 | -0.072052 | 0.13982 | 0.0021212 | -0.003373 | -0.0019568 | -0.0014484 | -0.0018265 | -2.2339 | -1.8906 | -119.0231 | -2.33 | -2.3392 | -118.7164 | -2.3392 | 1.0803 | 4.4678 | 3.9368 | 4.2206 | 4.2023 | 4.1016 | 4.0878 | -0.14648 | -6.2668 | -6.7062 | 116.5375 | 116.5375 | 0.16022 | 116.684 | 0.3067 | 122.8134 | 0.091552 | -0.15564 | 123.0789 | 122.9645 | 122.9782 | 0.15106 | 0.16479 | 116.684 | 116.6931 | 0.2655 | 0.28381 | 117.1326 | 0.53101 | 116.9861 | 123.3444 | -123.3994 | -0.43945 | 116.5466 | 123.0972 | 116.6428 | 119.957
1809.5469 | 123.3582 | -118.9316 | 4.3945 | -0.0042723 | 0.0052615 | 0.12188 | 0.0053705 | -0.0023649 | 0.002634 | -0.0086431 | -0.12393 | 0.1317 | -0.0042874 | -0.011277 | -0.020756 | -0.006148 | -0.016994 | -2.3621 | -2.092 | -118.9087 | -2.5726 | -2.6276 | -100.8865 | -2.8519 | 1.0483 | 4.3808 | 3.8315 | 4.184 | 4.184 | 3.891 | 3.9139 | 0.022889 | -6.4865 | -6.9672 | 116.304 | 116.0797 | 18.045 | 116.0568 | 18.0222 | 122.7631 | -0.013733 | -0.21057 | 123.1155 | 122.8455 | 122.8226 | 0.082397 | 0.059509 | 116.2811 | 116.3361 | 0.35248 | 0.35248 | 116.8167 | 0.54932 | 116.8396 | 123.3124 | -123.3032 | -0.56305 | 116.3589 | 123.1155 | 116.5695 | 119.9799
1810.4844 | 123.3536 | -118.9682 | 4.3167 | -0.080566 | 0.0033389 | 0.1174 | 0.0028069 | 0.0012667 | 0.0037022 | 0.00032907 | -0.087311 | 0.13896 | 0.0038302 | 0.0032492 | -0.0032386 | -0.0010212 | -0.0024673 | -2.4765 | -2.124 | -118.9957 | -2.6047 | -2.449 | -118.5883 | -2.5177 | 1.0208 | 4.4037 | 3.8681 | 4.1473 | 4.129 | 4.0329 | 4.0924 | -0.027466 | -6.4407 | -6.9214 | 116.5192 | 116.4505 | 0.37994 | 116.478 | 0.40741 | 122.8363 | 0.086976 | -0.16937 | 123.0972 | 123.0606 | 123.0011 | 0.2243 | 0.1648 | 116.5466 | 116.391 | 0.26092 | 0.27924 | 116.8716 | 0.53558 | 116.8442 | 123.3719 | -123.3124 | -0.44861 | 116.3635 | 123.1155 | 116.4917 | 119.989
1811.5469 | 123.2803 | -119.0002 | 4.3213 | -0.050049 | 0.0044071 | 0.1221 | 0.0047295 | 0.0023349 | -0.0012112 | -0.0067205 | -0.38028 | 0.12615 | 0.003403 | -0.0014504 | -0.0064428 | -0.014693 | -0.0050307 | -2.4216 | -2.0645 | -118.9133 | -2.5131 | -2.4811 | -116.1163 | -2.6962 | 0.8606 | 4.39 | 3.8315 | 4.0833 | 4.0604 | 3.9597 | 3.9185 | 0.086975 | -6.3858 | -6.8344 | 116.5192 | 116.304 | 2.8839 | 116.217 | 2.7969 | 122.8317 | 0.068665 | -0.23804 | 123.0606 | 122.9187 | 122.9599 | 0.086975 | 0.12817 | 116.4322 | 116.4001 | 0.22888 | 0.25177 | 116.8488 | 0.55847 | 116.9357 | 123.3902 | -123.2346 | -0.48981 | 116.4871 | 123.0835 | 116.5787 | 119.8608
1812.4844 | 123.2986 | -118.959 | 4.3671 | -0.065308 | 0.0031253 | 0.12103 | 0.0043023 | -1.486e-05 | 0.00049778 | 0.0020379 | -0.20633 | 0.13768 | 0.0025484 | -0.007432 | -0.0017432 | -0.0014484 | -0.0033219 | -2.3117 | -1.9363 | -118.959 | -2.4033 | -2.2934 | -118.6386 | -2.3666 | 1.0254 | 4.4312 | 3.8498 | 4.1107 | 4.0924 | 3.9963 | 4.0512 | 0 | -6.3034 | -6.7703 | 116.6656 | 116.5924 | 0.32043 | 116.5924 | 0.32043 | 122.8088 | 0.064087 | -0.25635 | 123.0515 | 123.0103 | 122.9553 | 0.20142 | 0.14649 | 116.6656 | 116.5558 | 0.24261 | 0.26093 | 117.0227 | 0.58136 | 117.0227 | 123.3902 | -123.3261 | -0.51727 | 116.5558 | 123.0698 | 116.6473 | 119.9844
1813.4844 | 123.3902 | -118.8721 | 4.3808 | -0.065308 | 0.0054751 | 0.12146 | 0.0021661 | 0.00019874 | 0.0011386 | -0.0015935 | -0.065949 | 0.13982 | 0.0029758 | -0.00016881 | -0.0032386 | -0.0012348 | 0.0026597 | -2.2888 | -1.9867 | -119.1742 | -2.3621 | -2.211 | -118.6066 | -2.2614 | 1.2177 | 4.4495 | 3.9185 | 4.2709 | 4.2755 | 4.1885 | 4.3213 | -0.30212 | -6.3675 | -6.7429 | 116.6611 | 116.6107 | 0.2655 | 116.9128 | 0.56763 | 122.7905 | 0.068665 | -0.10986 | 123.1476 | 123.1934 | 123.0606 | 0.40283 | 0.27008 | 116.9632 | 116.8121 | 0.35706 | 0.35248 | 117.1875 | 0.53101 | 116.8854 | 123.3215 | -123.555 | -0.46234 | 116.51 | 123.143 | 116.5833 | 120.0897
1814.4844 | 123.2895 | -118.9636 | 4.3808 | -0.11108 | 0.0035525 | 0.12018 | 0.0064385 | -0.00044226 | 0.0015658 | -0.00073913 | -0.21854 | 0.13491 | 0.0040438 | -0.0014504 | 0.0025292 | -0.0042254 | -0.0016129 | -2.3117 | -1.9775 | -119.2612 | -2.4307 | -2.3163 | -118.5104 | -2.3529 | 1.0529 | 4.4128 | 3.8406 | 4.1199 | 4.0924 | 3.978 | 4.1428 | -0.29755 | -6.3583 | -6.8115 | 116.6473 | 116.6107 | 0.45319 | 116.9083 | 0.75073 | 122.8043 | 0.032044 | -0.26093 | 123.056 | 123.1064 | 122.9416 | 0.30212 | 0.13733 | 116.9449 | 116.8304 | 0.25177 | 0.27924 | 117.2836 | 0.57221 | 116.9861 | 123.3765 | -123.642 | -0.54016 | 116.5329 | 123.0835 | 116.6519 | 120.0165
1815.5469 | 123.317 | -118.9362 | 4.3625 | 0.018616 | 0.0041935 | 0.11868 | 0.0015253 | -0.00044226 | -0.001852 | -0.0022345 | -0.29788 | 0.12956 | 0.0021212 | -0.011064 | -0.0079382 | -0.017684 | -0.010158 | -2.1378 | -2.0691 | -119.0048 | -2.4765 | -2.2934 | -118.4143 | -2.3804 | 1.1124 | 4.454 | 3.8956 | 4.1565 | 4.1199 | 4.0329 | 4.097 | -0.068665 | -6.4316 | -6.839 | 116.6428 | 116.5558 | 0.52185 | 116.6245 | 0.59052 | 122.8317 | 0.091553 | -0.20599 | 123.056 | 123.0331 | 122.9691 | 0.20142 | 0.13733 | 116.7114 | 116.5283 | 0.2243 | 0.26093 | 116.9357 | 0.55847 | 116.8671 | 123.3902 | -123.3673 | -0.46692 | 116.4597 | 123.0927 | 116.7984 | 120.0485
1816.4844 | 123.2941 | -118.8675 | 4.4449 | -0.080566 | 0.0033389 | 0.11953 | 0.0038751 | -0.00065586 | 0.0011386 | -0.0045843 | -0.096466 | 0.13854 | 0.004471 | 0.001113 | -0.0019568 | -0.00038018 | 0.0015915 | -2.4719 | -2.1286 | -119.1101 | -2.5406 | -2.5818 | -118.5242 | -2.2568 | 0.97961 | 4.509 | 3.8635 | 4.184 | 4.1199 | 4.0146 | 4.1473 | -0.24261 | -6.5735 | -6.9855 | 116.2857 | 116.6107 | 0.34332 | 116.8533 | 0.58594 | 122.731 | 0.064087 | -0.26093 | 122.9874 | 123.0148 | 122.8821 | 0.28381 | 0.15106 | 116.5283 | 116.5695 | 0.25635 | 0.32043 | 116.9815 | 0.64545 | 116.7389 | 123.3765 | -123.555 | -0.58136 | 116.3269 | 123.0515 | 116.3956 | 119.8471
1817.5469 | 123.3353 | -118.8171 | 4.454 | -0.48492 | 0.00013467 | 0.12124 | 0.0053705 | 0.0031893 | -0.00099762 | -0.0035163 | -0.16055 | 0.13832 | 0.005112 | -0.0082864 | -0.003025 | -0.0046528 | -0.0016129 | -2.4811 | -2.1378 | -119.1834 | -2.6184 | -2.4536 | -119.0414 | -2.5223 | 0.97046 | 4.5136 | 3.8727 | 4.1931 | 4.1336 | 4.01 | 4.0375 | -0.36621 | -6.5918 | -7.0724 | 116.3635 | 116.2949 | -0.2243 | 116.6611 | 0.14191 | 122.6898 | 0.059509 | -0.26093 | 122.9507 | 122.8546 | 122.8271 | 0.16479 | 0.13733 | 116.7297 | 116.5649 | 0.26093 | 0.32043 | 117.0456 | 0.64087 | 116.6794 | 123.3307 | -123.6374 | -0.58136 | 116.1987 | 123.0103 | 116.3361 | 119.7876
1818.4844 | 123.349 | -118.7714 | 4.4632 | -0.042419 | 0.0033389 | 0.1221 | 0.0040887 | 0.0014803 | 0.0024204 | 0.0018243 | -0.11783 | 0.13683 | 0.0048984 | -0.0046548 | -0.0028112 | 0.001756 | 0.0020187 | -2.4719 | -2.1194 | -119.1559 | -2.6001 | -2.4445 | -118.8583 | -2.4765 | 1.0895 | 4.5456 | 3.9093 | 4.2114 | 4.2389 | 4.0054 | 4.0787 | -0.38452 | -6.5826 | -7.0633 | 116.3269 | 116.2949 | -0.086975 | 116.6794 | 0.29755 | 122.6807 | 0.082397 | -0.25177 | 123.0103 | 122.85 | 122.7768 | 0.16937 | 0.09613 | 116.7114 | 116.5558 | 0.32959 | 0.30212 | 117.0364 | 0.63629 | 116.6519 | 123.317 | -123.6191 | -0.55389 | 116.1713 | 122.9828 | 116.2994 | 119.8608
1819.4844 | 123.4406 | -118.7988 | 4.4312 | -0.027161 | 0.0039799 | 0.1206 | 0.0025933 | -0.00022866 | 0.0045566 | -0.0028753 | -0.053741 | 0.13768 | 0.0046848 | -0.00080961 | -0.004093 | -0.0035846 | 0.0013779 | -2.4307 | -2.1378 | -119.0918 | -2.4948 | -2.3163 | -118.7805 | -2.3758 | 1.1032 | 4.4861 | 3.9276 | 4.3121 | 4.2664 | 4.1794 | 4.3213 | -0.29297 | -6.5689 | -6.926 | 116.4825 | 116.423 | 0.01831 | 116.716 | 0.31128 | 122.7264 | 0.054932 | -0.11902 | 123.0652 | 123.1201 | 122.9782 | 0.39368 | 0.25177 | 116.7755 | 116.597 | 0.33875 | 0.38452 | 116.954 | 0.55847 | 116.6611 | 123.2849 | -123.5229 | -0.50354 | 116.304 | 123.111 | 116.3681 | 119.902
1820.5469 | 123.2895 | -118.9957 | 4.3259 | 0.0033567 | 0.0050479 | 0.11932 | 0.0038751 | 0.0023349 | 0.0015658 | 0.0018243 | -0.11783 | 0.13747 | 0.0048984 | -0.012559 | -0.0049476 | -0.0099934 | -0.00033114 | -2.5085 | -2.1744 | -119.3115 | -2.6367 | -2.4994 | -118.5333 | -2.5223 | 0.90637 | 4.3671 | 3.7216 | 4.0375 | 3.9505 | 3.8635 | 3.9093 | -0.31586 | -6.5002 | -6.9626 | 116.4963 | 116.4734 | 0.46234 | 116.7892 | 0.7782 | 122.7173 | 0.041198 | -0.28839 | 122.9462 | 122.905 | 122.8592 | 0.18768 | 0.14191 | 116.8121 | 116.6748 | 0.22888 | 0.31586 | 117.1371 | 0.64545 | 116.8213 | 123.3627 | -123.6374 | -0.60425 | 116.3589 | 123.0331 | 116.4871 | 119.902
1821.4844 | 123.436 | -118.7439 | 4.4174 | -0.080566 | 0.0046207 | 0.12082 | 0.0028069 | 0.0010531 | 7.0582e-05 | -0.00095273 | -0.075104 | 0.13768 | 0.0055392 | 0.0019674 | -0.004093 | -0.0035846 | -0.00011754 | -2.2385 | -2.0325 | -119.0598 | -2.3163 | -2.1378 | -118.6981 | -2.2293 | 1.1398 | 4.5227 | 3.9505 | 4.3945 | 4.2206 | 4.2297 | 4.3259 | -0.31586 | -6.4499 | -6.7337 | 116.6061 | 116.5146 | 0.045776 | 116.8304 | 0.36163 | 122.6944 | 0.10529 | -0.022888 | 122.9645 | 123.0698 | 122.9736 | 0.37537 | 0.27924 | 116.922 | 116.7435 | 0.27008 | 0.44403 | 117.0273 | 0.57221 | 116.7114 | 123.2666 | -123.4772 | -0.46692 | 116.4276 | 123.1384 | 116.5054 | 119.8837
1822.5469 | 123.3078 | -118.7714 | 4.5273 | -0.080566 | 0.0033389 | 0.11953 | 0.0055841 | 0.0010531 | 0.0024204 | -9.8328e-05 | -0.13919 | 0.1396 | 0.005112 | 0.0041038 | -0.0025976 | -0.0065754 | -0.0013991 | -2.298 | -1.9592 | -119.1376 | -2.4261 | -2.298 | -118.8034 | -2.3209 | 0.86517 | 4.5731 | 3.9459 | 4.3716 | 4.0924 | 4.1336 | 4.2664 | -0.36621 | -6.4865 | -6.9534 | 116.4734 | 116.4505 | -0.032044 | 116.8167 | 0.33417 | 122.7173 | 0.045776 | -0.15564 | 122.8638 | 123.0377 | 122.905 | 0.32043 | 0.18768 | 116.8396 | 116.7114 | 0.14648 | 0.42572 | 117.1783 | 0.62714 | 116.8121 | 123.3444 | -123.6649 | -0.58136 | 116.3452 | 123.143 | 116.4734 | 119.6365
1823.4844 | 123.3765 | -118.7393 | 4.5136 | -0.072937 | 0.0041935 | 0.11953 | 0.0015253 | 0.00019874 | 0.00049778 | -0.0020209 | -0.035431 | 0.1364 | 0.003403 | -0.0097818 | -0.0045202 | -0.0037982 | -0.0020401 | -2.2888 | -1.9958 | -119.0231 | -2.3529 | -2.1835 | -118.8904 | -2.2293 | 0.97961 | 4.5547 | 4.01 | 4.335 | 4.3121 | 4.2389 | 4.3533 | -0.28381 | -6.5094 | -6.8665 | 116.5558 | 116.51 | -0.15106 | 116.7938 | 0.13275 | 122.7493 | 0.041199 | -0.17853 | 123.0515 | 123.0927 | 122.9782 | 0.34332 | 0.22888 | 116.8396 | 116.6702 | 0.30212 | 0.32501 | 117.0273 | 0.54474 | 116.7435 | 123.2941 | -123.5367 | -0.50354 | 116.3864 | 123.0743 | 116.4505 | 119.7189
1824.5469 | 123.2986 | -118.7897 | 4.5456 | 0.018616 | 0.0039799 | 0.11911 | 0.0028069 | 0.0014803 | 0.00092498 | -0.0013799 | -0.065949 | 0.14025 | 0.0038302 | -0.0076456 | -0.0025976 | -0.00059378 | 0.00095066 | -2.3666 | -2.0233 | -119.101 | -2.4078 | -2.0782 | -118.2404 | -2.4445 | 0.90637 | 4.628 | 4.0009 | 4.2709 | 4.2435 | 4.129 | 4.2572 | -0.31128 | -6.5689 | -6.9534 | 116.7114 | 116.3452 | 0.54932 | 116.6565 | 0.8606 | 122.7905 | 0.082398 | -0.27466 | 123.0331 | 123.0469 | 122.9187 | 0.25635 | 0.12817 | 117.0227 | 116.6931 | 0.24261 | 0.27008 | 117.0776 | 0.62714 | 116.7664 | 123.4177 | -123.6465 | -0.54474 | 116.3818 | 123.0606 | 116.423 | 119.696
1825.4844 | 123.4222 | -118.8995 | 4.2984 | -0.11108 | 0.0046207 | 0.12082 | 0.0049433 | 0.0010531 | -0.0020658 | -0.00052553 | -0.10562 | 0.13811 | 0.0014804 | -0.0027322 | -0.0036658 | -0.0014484 | -0.0011855 | -2.5406 | -2.3209 | -119.2337 | -2.6505 | -2.4673 | -117.2974 | -2.5497 | 1.03 | 4.3671 | 3.8223 | 4.2068 | 4.1565 | 4.0878 | 4.1977 | -0.33417 | -6.6193 | -6.9489 | 116.4322 | 116.3498 | 1.6022 | 116.684 | 1.9363 | 122.7219 | 0.068664 | -0.091553 | 123.056 | 123.0972 | 122.9874 | 0.37537 | 0.2655 | 116.7664 | 116.5833 | 0.33417 | 0.38452 | 116.9128 | 0.54474 | 116.5787 | 123.2666 | -123.5321 | -0.47607 | 116.2491 | 123.1064 | 116.3589 | 119.9295
1826.4844 | 123.3032 | -118.895 | 4.3808 | -0.095825 | -0.0094785 | 0.1174 | 0.0057977 | -0.0010831 | 0.0037022 | -0.0020209 | -0.14529 | 0.13896 | 0.004471 | -0.007432 | 0.0012476 | -0.00038018 | 0.0024461 | -2.5726 | -2.2476 | -119.2612 | -2.6917 | -2.5635 | -118.959 | -2.6047 | 0.84228 | 4.4266 | 3.8177 | 4.129 | 4.0604 | 3.978 | 4.1016 | -0.36621 | -6.6284 | -7.0724 | 116.3315 | 116.2903 | -0.064087 | 116.6565 | 0.30212 | 122.7127 | 0.045777 | -0.25177 | 122.9553 | 122.9965 | 122.8729 | 0.28381 | 0.16022 | 116.6977 | 116.5695 | 0.24261 | 0.31128 | 117.0135 | 0.60883 | 116.6473 | 123.3215 | -123.642 | -0.56305 | 116.2033 | 123.024 | 116.3223 | 119.7372
1827.4844 | 123.3673 | -119.0598 | 4.1702 | -0.10345 | 0.0048343 | 0.11975 | 0.0038751 | 0.00019874 | 0.0039158 | -0.0013799 | -0.11172 | 0.13939 | 0.0048984 | -0.0010232 | -0.0028112 | -0.0029438 | -0.00033114 | -2.3621 | -2.0096 | -119.4168 | -2.4582 | -2.3071 | -119.3939 | -2.3346 | 0.84686 | 4.2343 | 3.6804 | 3.9963 | 3.9688 | 3.8727 | 4.0009 | -0.35706 | -6.1798 | -6.6284 | 116.7526 | 116.7252 | -0.33417 | 117.0822 | 0.022888 | 122.7402 | 0.064087 | -0.17395 | 123.0286 | 123.0606 | 122.9324 | 0.32043 | 0.19226 | 117.1097 | 116.9586 | 0.28839 | 0.31586 | 117.4072 | 0.55389 | 117.0502 | 123.2941 | -123.587 | -0.48981 | 116.6016 | 123.056 | 116.6977 | 119.9066
1828.4844 | 123.3582 | -119.1376 | 4.1931 | -0.03479 | 0.0050479 | 0.12018 | 0.0045159 | 0.00083954 | 0.00071138 | -0.00095273 | -0.13004 | 0.13896 | 0.0055392 | 4.4788e-05 | -3.4196e-05 | 0.00068782 | 0.0013779 | -2.3071 | -1.9592 | -119.4763 | -2.4307 | -2.3117 | -119.0369 | -2.3071 | 0.81482 | 4.2297 | 3.6301 | 3.9963 | 3.9597 | 3.7949 | 3.9322 | -0.33875 | -6.1523 | -6.6238 | 116.8259 | 116.8304 | 0.10071 | 117.1692 | 0.43945 | 122.7676 | 0.036621 | -0.19684 | 123.0972 | 123.0698 | 122.9324 | 0.30212 | 0.1648 | 117.1646 | 117.0456 | 0.32959 | 0.36621 | 117.5171 | 0.59967 | 117.1783 | 123.3673 | -123.6694 | -0.56305 | 116.7068 | 123.1339 | 116.8304 | 119.9524
1829.4844 | 123.4451 | -118.7988 | 4.3854 | -0.095825 | 0.0056889 | 0.11825 | 0.0032343 | -0.00044226 | 0.002634 | 0.00075627 | -0.069 | 0.14025 | 0.0042574 | 0.0021812 | -0.003025 | -0.0020892 | 0.0026597 | -2.1561 | -1.9409 | -119.1284 | -2.2247 | -2.0554 | -118.7027 | -2.1286 | 0.81482 | 4.4403 | 3.9505 | 4.2892 | 4.2847 | 4.2114 | 4.335 | -0.32959 | -6.3263 | -6.6101 | 116.7435 | 116.6702 | 0.09613 | 116.9998 | 0.42572 | 122.7493 | 0.054932 | -0.09613 | 123.0835 | 123.1338 | 123.0103 | 0.38452 | 0.26093 | 117.0731 | 116.9037 | 0.33417 | 0.33875 | 117.1875 | 0.48981 | 116.8579 | 123.2391 | -123.5138 | -0.43488 | 116.5741 | 123.0881 | 116.6428 | 119.6136
1830.4844 | 123.381 | -118.8263 | 4.454 | -0.03479 | 0.0048343 | 0.11868 | 0.0032343 | 0.0014803 | 0.00092498 | -0.0020209 | -0.10867 | 0.14003 | 0.0042574 | -0.0031594 | -0.0038794 | -0.0014484 | 0.0022323 | -2.2202 | -1.8997 | -119.1376 | -2.3438 | -2.2156 | -118.8309 | -2.2385 | 0.88806 | 4.5319 | 3.978 | 4.2664 | 4.2343 | 4.1428 | 4.2801 | -0.31128 | -6.3538 | -6.7978 | 116.6107 | 116.5878 | -0.004578 | 116.8991 | 0.3067 | 122.8043 | 0.077819 | -0.18768 | 123.0606 | 123.1064 | 122.9691 | 0.30212 | 0.1648 | 116.922 | 116.7938 | 0.25635 | 0.28839 | 117.2379 | 0.55389 | 116.9266 | 123.3582 | -123.5916 | -0.47608 | 116.4825 | 123.0927 | 116.6061 | 119.7144
1831.4844 | 123.4772 | -118.8263 | 4.3579 | -0.11108 | 0.0046207 | 0.11996 | 0.0053705 | 0.0021213 | 0.00092498 | 0.00096987 | -0.059845 | 0.1411 | 0.0036166 | -0.0018778 | -0.0025976 | -0.0027302 | -0.0011855 | -2.1332 | -1.9226 | -119.1467 | -2.2339 | -2.0691 | -118.7393 | -2.124 | 1.0208 | 4.4632 | 3.9688 | 4.2984 | 4.3808 | 4.2114 | 4.303 | -0.32043 | -6.2805 | -6.5918 | 116.7572 | 116.7023 | 0.086975 | 117.0227 | 0.40741 | 122.7951 | 0.10529 | -0.059509 | 123.2071 | 123.1293 | 123.0377 | 0.33417 | 0.24262 | 117.0776 | 116.9128 | 0.41199 | 0.32959 | 117.2241 | 0.49438 | 116.9037 | 123.2895 | -123.5046 | -0.3891 | 116.5924 | 123.1247 | 116.6931 | 119.8471
1832.4844 | 123.4451 | -118.7531 | 4.4678 | -0.042419 | 0.0048343 | 0.11911 | 0.0040887 | 0.0021213 | 0.0022068 | -0.0037299 | -0.10257 | 0.13832 | 0.0019076 | -0.00059601 | -0.0043066 | -0.0029438 | -0.00075834 | -2.2385 | -1.9409 | -119.101 | -2.3117 | -2.1515 | -118.19 | -2.2064 | 0.95215 | 4.5319 | 4.0192 | 4.3854 | 4.3716 | 4.2664 | 4.4037 | -0.3479 | -6.4087 | -6.7795 | 116.6016 | 116.5466 | 0.56305 | 116.8945 | 0.91095 | 122.7722 | 0.064087 | -0.082397 | 123.1247 | 123.1567 | 123.0194 | 0.38452 | 0.24719 | 116.9495 | 116.7892 | 0.35248 | 0.36621 | 117.16 | 0.51269 | 116.8121 | 123.2849 | -123.5687 | -0.44861 | 116.4413 | 123.1384 | 116.5146 | 119.7052
1833.5469 | 123.3398 | -118.8263 | 4.4769 | -0.027161 | 0.00013467 | 0.11953 | 0.0053705 | 0.0027621 | 0.0013522 | 0.00075627 | -0.13309 | 0.1379 | 0.0057528 | -0.0061502 | -0.0036658 | -0.010421 | 0.00052346 | -2.298 | -1.9592 | -119.1055 | -2.4261 | -2.2751 | -118.7759 | -2.3346 | 0.90179 | 4.5364 | 3.9871 | 4.2618 | 4.2297 | 4.129 | 4.2572 | -0.27924 | -6.4362 | -6.9031 | 116.5512 | 116.4917 | 0.050354 | 116.7709 | 0.32959 | 122.8134 | 0.059509 | -0.21515 | 123.056 | 123.0835 | 122.9553 | 0.27008 | 0.14191 | 116.8304 | 116.6794 | 0.24261 | 0.27466 | 117.1463 | 0.54932 | 116.8671 | 123.3627 | -123.5825 | -0.48981 | 116.4001 | 123.0881 | 116.5283 | 119.7281
1834.4844 | 123.3398 | -118.7805 | 4.4769 | -0.057678 | 0.0069705 | 0.12295 | 0.0040887 | 0.0016939 | -0.0014248 | 0.00011527 | -0.10867 | 0.1396 | 0.0046848 | -0.0012368 | -0.0019568 | -0.001662 | -0.0037491 | -2.5406 | -2.1332 | -119.1147 | -2.5818 | -2.4582 | -118.6981 | -2.4628 | 0.81482 | 4.5364 | 3.978 | 4.2572 | 4.216 | 4.1153 | 4.2526 | -0.33417 | -6.6101 | -7.0587 | 116.3223 | 116.3177 | 0.082398 | 116.6519 | 0.41656 | 122.7585 | 0.059509 | -0.21973 | 122.9965 | 123.0331 | 122.8958 | 0.27466 | 0.13733 | 116.6565 | 116.5329 | 0.23804 | 0.27924 | 116.9815 | 0.55847 | 116.6473 | 123.317 | -123.5916 | -0.49896 | 116.1987 | 123.0377 | 116.2399 | 119.5953
1835.4844 | 123.3856 | -118.7668 | 4.4403 | -0.14923 | 0.0054751 | 0.11761 | 0.0028069 | -0.0021513 | 0.0032748 | -0.00052553 | -0.041534 | 0.13896 | 0.0046848 | 0.001113 | -0.0045202 | -0.0025164 | -0.0043899 | -2.2705 | -2.0645 | -119.101 | -2.3483 | -2.1652 | -118.6798 | -2.243 | 0.99335 | 4.5136 | 4.0237 | 4.3442 | 4.3716 | 4.2664 | 4.3854 | -0.33417 | -6.5048 | -6.7886 | 116.6016 | 116.5237 | 0.086975 | 116.8579 | 0.42114 | 122.7905 | 0.073242 | -0.096131 | 123.1384 | 123.1522 | 123.0331 | 0.36163 | 0.24261 | 116.9357 | 116.7526 | 0.3479 | 0.32043 | 117.0364 | 0.48981 | 116.7023 | 123.2803 | -123.5413 | -0.41657 | 116.4185 | 123.111 | 116.4963 | 119.7601
1836.5469 | 123.1567 | -118.6798 | 4.5639 | -0.15686 | 0.0029117 | 0.12018 | 0.0060113 | 0.0016939 | 0.0034884 | 0.0018243 | -0.12393 | 0.13939 | 0.0036166 | -0.0018778 | -0.0049476 | -0.0010212 | 0.00052346 | -2.3575 | -2.0096 | -119.0552 | -2.4719 | -2.33 | -118.7485 | -2.3621 | 0.78278 | 4.6371 | 4.0604 | 4.3304 | 4.3076 | 4.2068 | 4.5639 | -0.37537 | -6.5735 | -7.0358 | 116.3498 | 116.3177 | -0.068664 | 116.6931 | 0.3067 | 122.7402 | 0.073242 | -0.23346 | 122.9874 | 123.2437 | 122.8867 | 0.50354 | 0.14648 | 116.7252 | 116.5833 | 0.24719 | 0.27008 | 117.0456 | 0.57678 | 116.6702 | 123.317 | -123.6191 | -0.50354 | 116.2079 | 123.0103 | 116.3223 | 119.4626
1837.4844 | 123.4085 | -118.6478 | 4.5776 | -0.011902 | 0.0033389 | 0.12124 | 0.0034479 | -0.0010831 | 0.00028418 | 0.00075627 | -0.047638 | 0.13725 | 0.0074618 | 0.0021812 | -0.0045202 | -0.0046528 | 0.0024461 | -2.33 | -2.1057 | -118.9865 | -2.3849 | -2.211 | -118.5837 | -2.2751 | 0.95215 | 4.6097 | 4.1199 | 4.4769 | 4.4678 | 4.3991 | 4.4952 | -0.33874 | -6.6834 | -6.9626 | 116.4368 | 116.3727 | 0.064087 | 116.7114 | 0.40283 | 122.7676 | 0.032043 | -0.10071 | 123.1155 | 123.143 | 123.0469 | 0.37537 | 0.27924 | 116.7755 | 116.6016 | 0.3479 | 0.35706 | 116.8808 | 0.48981 | 116.5421 | 123.2574 | -123.5641 | -0.45776 | 116.2628 | 123.1247 | 116.3177 | 119.5999
1838.4844 | 123.3627 | -118.808 | 4.4037 | -0.050049 | 0.0041935 | 0.11953 | 0.0040887 | -1.486e-05 | 0.0028476 | -0.00031193 | -0.11478 | 0.13939 | 0.0029758 | 0.00389 | -0.003025 | -0.00059378 | -0.0018265 | -2.6047 | -2.2888 | -119.1742 | -2.6688 | -2.5406 | -119.2429 | -2.5726 | 0.88348 | 4.4769 | 3.9505 | 4.2847 | 4.2938 | 4.2114 | 4.335 | -0.36621 | -6.6925 | -7.0724 | 116.2674 | 116.2354 | -0.43488 | 116.6016 | -0.068665 | 122.7585 | 0.073242 | -0.11902 | 123.1018 | 123.143 | 123.0194 | 0.38452 | 0.26093 | 116.6336 | 116.5054 | 0.34332 | 0.33417 | 116.8854 | 0.52643 | 116.5192 | 123.2849 | -123.5779 | -0.45319 | 116.1392 | 123.0927 | 116.2033 | 119.6915
1839.4844 | 123.3856 | -118.5745 | 4.6555 | -0.17975 | 0.0041935 | 0.11932 | 0.0043023 | -0.0027921 | 0.0015658 | -0.0035163 | -0.047638 | 0.13725 | 0.0042574 | 0.0043174 | -0.0043066 | -0.0020892 | 0.0013779 | -2.4673 | -2.2568 | -118.9453 | -2.5543 | -2.3621 | -118.0893 | -2.4536 | 0.98419 | 4.6555 | 4.1611 | 4.5227 | 4.5547 | 4.4861 | 4.5959 | -0.37079 | -6.9122 | -7.2098 | 116.2125 | 116.1209 | 0.48523 | 116.4917 | 0.85602 | 122.7356 | 0 | -0.13275 | 123.1293 | 123.1705 | 123.0606 | 0.43487 | 0.32501 | 116.5833 | 116.391 | 0.39368 | 0.36163 | 116.6885 | 0.49439 | 116.3177 | 123.23 | -123.6008 | -0.49439 | 116.0202 | 123.0972 | 116.1072 | 119.5587
1840.5469 | 123.2803 | -118.721 | 4.5639 | -0.401 | -0.00071993 | 0.11889 | 0.0034479 | 0.0016939 | -0.00035682 | -0.0022345 | -0.14529 | 0.14089 | 0.0023348 | -0.0029458 | -3.4196e-05 | -0.0020892 | -0.00011754 | -2.1744 | -1.8539 | -119.0506 | -2.3026 | -2.1515 | -118.5333 | -2.2064 | 0.84686 | 4.6234 | 4.0741 | 4.3304 | 4.3213 | 4.2252 | 4.3442 | -0.32959 | -6.4178 | -6.8665 | 116.5695 | 116.5146 | 0.18768 | 116.8442 | 0.51727 | 122.7951 | 0.059509 | -0.23346 | 123.0423 | 123.0652 | 122.9462 | 0.27008 | 0.15106 | 116.8991 | 116.748 | 0.24719 | 0.25635 | 117.1967 | 0.54932 | 116.8671 | 123.3444 | -123.6145 | -0.48981 | 116.4185 | 123.0515 | 116.5466 | 119.5679
1841.4844 | 123.4909 | -116.2582 | 5.2277 | -0.56122 | -0.0302 | 0.067411 | -0.0093695 | 0.0010531 | 0.060953 | -0.0041571 | -0.19412 | 0.1866 | 0.005112 | -0.002305 | -0.0068702 | -0.0020892 | -0.0013991 | -0.21057 | -2.211 | -95.2469 | -0.55847 | -1.6067 | -102.7267 | -2.1057 | 1.2909 | 5.2094 | 7.3608 | 5.1956 | 5.159 | 5.1178 | 5.3421 | 21.0114 | -7.4387 | -5.7861 | 114.6515 | 114.1525 | 13.5315 | 93.1412 | -7.4799 | 123.6191 | -0.01831 | -0.032043 | 121.4172 | 121.6003 | 121.376 | -2.0187 | -2.243 | 93.6401 | 94.6884 | -2.2018 | -2.1652 | 93.0359 | -2.1515 | 114.0472 | 121.4676 | -100.4745 | 2.1332 | 115.6998 | 121.4539 | 116.0477 | 117.5491
1842.5 | 123.3765 | -118.6661 | 4.5776 | -0.042419 | 0.0026981 | 0.11868 | 0.0030207 | -0.0047147 | 0.0034884 | -0.0018073 | -0.056793 | 0.13939 | 0.0029758 | -0.0059366 | -0.0017432 | -0.0023028 | -0.0013991 | -2.1927 | -1.973 | -119.0048 | -2.2842 | -2.1057 | -114.1617 | -2.1698 | 1.0712 | 4.6371 | 4.1153 | 4.3854 | 4.4495 | 4.3488 | 4.4266 | -0.33875 | -6.5506 | -6.8619 | 116.5604 | 116.4963 | 4.5044 | 116.835 | 4.8431 | 122.7814 | 0.059509 | -0.19226 | 123.1155 | 123.0927 | 123.0148 | 0.31128 | 0.23346 | 116.8991 | 116.7206 | 0.33417 | 0.27008 | 117.0319 | 0.52185 | 116.6931 | 123.3032 | -123.5825 | -0.46234 | 116.3818 | 123.0515 | 116.4734 | 119.7372
1843.4844 | 123.3994 | -118.6798 | 4.5731 | -0.072937 | 0.0048343 | 0.12018 | 0.0025933 | -0.0015103 | -0.00099762 | -0.0011663 | -0.032379 | 0.1379 | 0.0025484 | -0.0020914 | -0.0047338 | -0.0040118 | 0.0030869 | -2.0874 | -1.7944 | -118.9636 | -2.1698 | -2.005 | -118.4647 | -2.0279 | 0.99335 | 4.6234 | 4.1107 | 4.4174 | 4.454 | 4.3488 | 4.4403 | -0.28381 | -6.3675 | -6.7429 | 116.6748 | 116.6519 | 0.21515 | 116.9357 | 0.49896 | 122.7905 | 0.050354 | -0.15564 | 123.1339 | 123.1201 | 123.0286 | 0.32959 | 0.23804 | 116.9586 | 116.7938 | 0.34332 | 0.3067 | 117.1692 | 0.51269 | 116.8854 | 123.3032 | -123.5367 | -0.46234 | 116.51 | 123.0972 | 116.5924 | 119.6732
1844.5469 | 123.2986 | -118.7027 | 4.5868 | -0.0042723 | 0.0059025 | 0.11889 | 0.0053705 | 0.0040439 | 0.00071138 | 0.0016107 | -0.1514 | 0.13896 | 0.00618 | -0.0014504 | -0.0025976 | -0.00080758 | -0.00075834 | -2.2842 | -1.9501 | -119.0048 | -2.4216 | -2.3026 | -118.6935 | -2.3346 | 0.85144 | 4.6463 | 4.0833 | 4.3579 | 4.3304 | 4.2435 | 4.3854 | -0.30212 | -6.5369 | -7.0084 | 116.4001 | 116.3681 | 0.009156 | 116.6702 | 0.31128 | 122.7859 | 0.059509 | -0.22888 | 123.0331 | 123.0881 | 122.9462 | 0.30212 | 0.16022 | 116.7023 | 116.5833 | 0.24719 | 0.27466 | 117.0547 | 0.56305 | 116.7526 | 123.349 | -123.5916 | -0.50354 | 116.2811 | 123.0606 | 116.4185 | 119.5541
1845.4844 | 123.3719 | -118.6386 | 4.5822 | -0.080566 | 0.0020573 | 0.11847 | 0.0023797 | -0.0012967 | 0.002634 | -0.0015935 | -0.047638 | 0.13854 | 0.0046848 | -0.0016642 | -0.0036658 | -0.0048664 | 0.0022323 | -2.1378 | -1.886 | -118.9682 | -2.2018 | -2.0279 | -117.897 | -2.0966 | 0.97504 | 4.6234 | 4.1382 | 4.454 | 4.4449 | 4.3716 | 4.4861 | -0.32959 | -6.4682 | -6.7841 | 116.6107 | 116.5421 | 0.74158 | 116.8716 | 1.0712 | 122.7768 | 0.041199 | -0.12817 | 123.0835 | 123.1247 | 123.0103 | 0.3479 | 0.23346 | 116.9403 | 116.7664 | 0.3067 | 0.31586 | 117.0822 | 0.48523 | 116.7526 | 123.262 | -123.5504 | -0.44403 | 116.4368 | 123.0927 | 116.5009 | 119.6136
1846.4844 | 123.3673 | -118.6295 | 4.5731 | -0.065308 | 0.0020573 | 0.12039 | 0.0019525 | -0.0010831 | 0.0013522 | -0.0039435 | -0.069 | 0.13768 | 0.0036166 | -0.0048684 | -0.002384 | -0.0046528 | -0.00097194 | -2.3758 | -2.1469 | -118.959 | -2.449 | -2.2797 | -118.602 | -2.3392 | 1.0162 | 4.6234 | 4.1336 | 4.454 | 4.4632 | 4.3854 | 4.4769 | -0.32959 | -6.72 | -7.0221 | 116.3498 | 116.2903 | 0.027466 | 116.6199 | 0.35706 | 122.7631 | 0.050354 | -0.11902 | 123.0927 | 123.1064 | 123.0148 | 0.34332 | 0.25177 | 116.6794 | 116.51 | 0.32959 | 0.32043 | 116.8121 | 0.48981 | 116.4825 | 123.2529 | -123.5321 | -0.43945 | 116.1804 | 123.0835 | 116.2537 | 119.6457
1847.5625 | 123.3673 | -118.634 | 4.6005 | -0.042419 | 0.0037661 | 0.11932 | 0.0034479 | -0.00086946 | -0.001852 | -0.00073913 | -0.05069 | 0.13725 | 0.0053256 | -0.0046548 | -0.0019568 | -0.0027302 | 0.0022323 | -2.5864 | -2.2842 | -118.9178 | -2.6413 | -2.4994 | -118.4326 | -2.536 | 0.95215 | 4.7104 | 4.1794 | 4.4769 | 4.509 | 4.422 | 4.5136 | -0.28381 | -6.8848 | -7.2418 | 116.1346 | 116.098 | 0.20142 | 116.3818 | 0.48523 | 122.8134 | 0.10986 | -0.1236 | 123.143 | 123.1476 | 123.056 | 0.33417 | 0.24261 | 116.4185 | 116.2766 | 0.32959 | 0.29755 | 116.6336 | 0.53101 | 116.3498 | 123.3444 | -123.5184 | -0.42114 | 115.9927 | 123.111 | 116.0477 | 119.5862
1848.4844 | 123.4497 | -118.6981 | 4.4815 | -0.042419 | 0.0046207 | 0.12082 | 0.0049433 | 0.00041234 | 0.0011386 | -0.0047979 | -0.096466 | 0.1379 | 0.0040438 | 0.001113 | -0.0028112 | -0.0025164 | 9.6064e-05 | -2.4673 | -2.2156 | -119.0506 | -2.5314 | -2.3895 | -118.5287 | -2.4719 | 1.0162 | 4.5502 | 4.0558 | 4.4083 | 4.39 | 4.3213 | 4.4586 | -0.35248 | -6.6971 | -7.0129 | 116.3086 | 116.2262 | 0.16937 | 116.5787 | 0.52185 | 122.7539 | 0.068665 | -0.073242 | 123.0881 | 123.1567 | 123.0194 | 0.40283 | 0.2655 | 116.6611 | 116.5192 | 0.33417 | 0.35248 | 116.835 | 0.49438 | 116.4825 | 123.2483 | -123.5321 | -0.42572 | 116.1667 | 123.1064 | 116.2308 | 119.7144
1849.4844 | 123.3765 | -118.6569 | 4.5822 | -0.0042723 | 0.0022709 | 0.12274 | 0.0032343 | 0.0016939 | -0.0014248 | -0.0018073 | -0.044586 | 0.13875 | 0.003403 | -0.003373 | -0.0015296 | -0.0031574 | -0.0018265 | -2.5864 | -2.3026 | -118.9545 | -2.655 | -2.5177 | -118.3548 | -2.5497 | 0.92468 | 4.6509 | 4.1336 | 4.4266 | 4.4586 | 4.3533 | 4.454 | -0.29755 | -6.8848 | -7.2372 | 116.1392 | 116.1072 | 0.30212 | 116.4047 | 0.59967 | 122.7905 | 0.068665 | -0.15564 | 123.1155 | 123.111 | 123.0103 | 0.32043 | 0.21973 | 116.4368 | 116.2994 | 0.32501 | 0.29297 | 116.6519 | 0.51727 | 116.3544 | 123.3078 | -123.5367 | -0.44861 | 116.0019 | 123.0835 | 116.0706 | 119.5816
1850.4844 | 123.4222 | -118.6157 | 4.5593 | -0.065308 | 0.0041935 | 0.11719 | 0.0038751 | 0.00062594 | 0.00049778 | -0.0015935 | -0.12393 | 0.1364 | 0.0031894 | 0.004531 | -0.0049476 | -0.0023028 | 0.00030966 | -2.4033 | -2.1744 | -118.9407 | -2.4765 | -2.3117 | -118.5242 | -2.3804 | 1.0025 | 4.6371 | 4.1428 | 4.5456 | 4.4357 | 4.4128 | 4.5227 | -0.32501 | -6.7337 | -7.0358 | 116.304 | 116.2354 | 0.091553 | 116.5604 | 0.41657 | 122.7585 | 0.07782 | -0.013733 | 123.0515 | 123.1384 | 123.0286 | 0.37994 | 0.27008 | 116.629 | 116.4642 | 0.29297 | 0.40283 | 116.7664 | 0.49439 | 116.4413 | 123.2529 | -123.5001 | -0.41657 | 116.1392 | 123.1613 | 116.2125 | 119.6182
1851.4844 | 123.3627 | -118.6844 | 4.5502 | -0.057678 | 0.0044071 | 0.11847 | 0.0025933 | -0.0010831 | -0.00057042 | -0.0020209 | -0.053741 | 0.13704 | 0.0029758 | 4.4788e-05 | -0.0028112 | -0.0040118 | 0.0026597 | -2.5269 | -2.2247 | -118.9957 | -2.5909 | -2.4261 | -118.5699 | -2.4994 | 0.92926 | 4.6371 | 4.1199 | 4.4174 | 4.4312 | 4.3533 | 4.4449 | -0.31128 | -6.7749 | -7.1411 | 116.2582 | 116.185 | 0.11444 | 116.4963 | 0.42572 | 122.8043 | 0.086975 | -0.13275 | 123.1155 | 123.1293 | 123.0377 | 0.32501 | 0.23346 | 116.5695 | 116.4047 | 0.31128 | 0.29755 | 116.7709 | 0.51727 | 116.4597 | 123.3215 | -123.5458 | -0.4303 | 116.0934 | 123.1018 | 116.1575 | 119.6136
1852.4844 | 123.4177 | -118.5333 | 4.7058 | -0.019531 | 0.0054751 | 0.11889 | 0.0028069 | -0.00044226 | -0.00078402 | 0.00075627 | -0.038483 | 0.13875 | 0.0040438 | -0.0029458 | -0.0045202 | -0.0025164 | -0.0011855 | -2.5497 | -2.3117 | -118.8171 | -2.6047 | -2.4353 | -118.1808 | -2.4857 | 1.181 | 4.7516 | 4.2709 | 4.6097 | 4.6463 | 4.5776 | 4.6371 | -0.28381 | -7.0175 | -7.3105 | 116.098 | 116.0477 | 0.35248 | 116.3315 | 0.63629 | 122.8043 | 0.045776 | -0.096131 | 123.1796 | 123.1705 | 123.111 | 0.36621 | 0.3067 | 116.3818 | 116.2125 | 0.37537 | 0.33875 | 116.5054 | 0.48065 | 116.2216 | 123.2849 | -123.5229 | -0.43488 | 115.9287 | 123.143 | 115.9836 | 119.7144
1853.5469 | 123.3215 | -118.5059 | 4.7607 | -0.057678 | 0.0033389 | 0.11825 | 0.0028069 | 0.0014803 | 0.0024204 | -0.0028753 | -0.14835 | 0.13768 | 0.0029758 | 0.00025839 | -0.0032386 | -0.0010212 | -0.0026809 | -2.4582 | -2.124 | -118.8629 | -2.5726 | -2.4582 | -118.4784 | -2.4902 | 0.93384 | 4.8386 | 4.2526 | 4.5639 | 4.5456 | 4.4495 | 4.5868 | -0.35706 | -6.8848 | -7.3334 | 116.0477 | 116.0156 | 0.027465 | 116.3727 | 0.38452 | 122.7585 | 0.07782 | -0.19684 | 123.0515 | 123.0927 | 122.9553 | 0.33417 | 0.19684 | 116.4047 | 116.2903 | 0.29297 | 0.31128 | 116.7389 | 0.58594 | 116.3818 | 123.3444 | -123.6237 | -0.50812 | 115.9332 | 123.0698 | 116.0477 | 119.4397
1854.4844 | 123.3902 | -118.5425 | 4.6967 | -0.03479 | 0.0018435 | 0.11889 | 0.0030207 | 0.0021213 | 0.0015658 | 0.00075627 | -0.11783 | 0.1396 | 0.0012668 | -0.00038241 | -0.0011022 | -0.00059378 | 9.6064e-05 | -2.4353 | -2.1103 | -118.8766 | -2.5177 | -2.3849 | -118.2129 | -2.4353 | 0.99792 | 4.7653 | 4.2252 | 4.5914 | 4.5822 | 4.4952 | 4.6051 | -0.33417 | -6.8069 | -7.2144 | 116.1575 | 116.1072 | 0.32959 | 116.4413 | 0.66376 | 122.7676 | 0.068665 | -0.10528 | 123.1247 | 123.1476 | 123.0377 | 0.37994 | 0.27008 | 116.4917 | 116.3589 | 0.35705 | 0.36621 | 116.7664 | 0.54016 | 116.4322 | 123.3078 | -123.5733 | -0.4715 | 116.0248 | 123.1338 | 116.1072 | 119.5404
1855.5469 | 123.3536 | -118.5013 | 4.7882 | -0.080566 | 0.0037661 | 0.11825 | 0.0036615 | -0.0034329 | -0.0016384 | 0.00096987 | -0.12088 | 0.1411 | 0.0055392 | 0.0015402 | -0.0043066 | -0.0037982 | -0.0018265 | -2.4673 | -2.1469 | -118.8126 | -2.5726 | -2.4353 | -118.4509 | -2.4719 | 1.0025 | 4.8294 | 4.2618 | 4.5639 | 4.5868 | 4.4769 | 4.5776 | -0.31128 | -6.9351 | -7.3608 | 116.066 | 116.0294 | 0.050354 | 116.3406 | 0.36163 | 122.7631 | 0.041199 | -0.2243 | 123.0881 | 123.0789 | 122.9782 | 0.31586 | 0.21515 | 116.3773 | 116.2399 | 0.32501 | 0.30212 | 116.6656 | 0.56763 | 116.3544 | 123.3307 | -123.6008 | -0.52643 | 115.9287 | 123.0652 | 116.0339 | 119.5038
1856.4844 | 123.3902 | -118.5013 | 4.7333 | -0.065308 | 0.0050479 | 0.12082 | 0.0032343 | 0.0027621 | 0.0019932 | -0.0013799 | -0.056793 | 0.13854 | 0.003403 | -0.0035868 | -0.000675 | -0.0046528 | 0.0024461 | -2.3483 | -2.092 | -118.8446 | -2.3987 | -2.2339 | -118.3685 | -2.3026 | 1.0666 | 4.7745 | 4.2801 | 4.5914 | 4.6051 | 4.541 | 4.6326 | -0.34332 | -6.8253 | -7.132 | 116.2674 | 116.1987 | 0.13275 | 116.5421 | 0.47607 | 122.7814 | 0.041199 | -0.14191 | 123.1064 | 123.1339 | 123.0423 | 0.35248 | 0.26093 | 116.6107 | 116.4459 | 0.32501 | 0.31128 | 116.7526 | 0.49438 | 116.4093 | 123.2758 | -123.5779 | -0.45319 | 116.1026 | 123.0927 | 116.153 | 119.5679
1857.5625 | 123.3353 | -118.4784 | 4.7974 | -0.027161 | 0.0037661 | 0.12103 | 0.0040887 | -1.486e-05 | -0.00078402 | -0.00031193 | -0.062897 | 0.1379 | 0.0038302 | -0.00016881 | -0.002384 | 4.7018e-05 | 0.0026597 | -2.3346 | -2.1011 | -118.7805 | -2.4124 | -2.2385 | -118.4143 | -2.3209 | 1.1444 | 4.834 | 4.3304 | 4.6326 | 4.6692 | 4.5914 | 4.66 | -0.30212 | -6.8985 | -7.2098 | 116.2399 | 116.1575 | 0.064087 | 116.4597 | 0.36621 | 122.8088 | 0.036621 | -0.16479 | 123.1476 | 123.1384 | 123.0698 | 0.32959 | 0.26093 | 116.5421 | 116.3681 | 0.33875 | 0.30212 | 116.6794 | 0.50354 | 116.3773 | 123.3124 | -123.5779 | -0.46692 | 116.066 | 123.111 | 116.1438 | 119.6228
1858.4844 | 123.3948 | -118.4372 | 4.8065 | -0.057678 | 0.0026981 | 0.1174 | 0.0045159 | -0.00044226 | 0.0024204 | -9.8328e-05 | -0.062897 | 0.13704 | 0.0036166 | -0.0027322 | -0.0011022 | -0.0014484 | 0.0043687 | -2.2476 | -1.9592 | -118.7256 | -2.3026 | -2.1606 | -120.9869 | -2.1973 | 1.0574 | 4.8523 | 4.3579 | 4.6417 | 4.6738 | 4.6051 | 4.7058 | -0.28839 | -6.7657 | -7.1091 | 116.2766 | 116.2399 | -2.5497 | 116.5283 | -2.2614 | 122.7951 | 0.045776 | -0.16479 | 123.111 | 123.143 | 123.0423 | 0.3479 | 0.24719 | 116.5649 | 116.423 | 0.31586 | 0.28381 | 116.7664 | 0.49438 | 116.478 | 123.2895 | -123.5321 | -0.44861 | 116.1346 | 123.0789 | 116.1896 | 119.4946
1859.5469 | 123.4314 | -118.4418 | 4.7928 | -0.080566 | 0.0022709 | 0.11868 | 0.0030207 | 0.00019874 | -0.00078402 | 0.0011835 | -0.10257 | 0.13811 | 0.0031894 | 0.0030356 | -0.0032386 | 4.7018e-05 | 0.00030966 | -2.3941 | -2.179 | -118.7485 | -2.4536 | -2.298 | -118.1854 | -2.3712 | 1.1673 | 4.8798 | 4.3625 | 4.715 | 4.7195 | 4.6326 | 4.7424 | -0.3067 | -6.9717 | -7.2464 | 116.1438 | 116.0706 | 0.25635 | 116.3773 | 0.56305 | 122.8043 | 0.086975 | -0.07782 | 123.1613 | 123.1842 | 123.0743 | 0.37994 | 0.27008 | 116.4505 | 116.2949 | 0.35705 | 0.35248 | 116.5695 | 0.51727 | 116.2628 | 123.3215 | -123.5413 | -0.4303 | 115.9882 | 123.1567 | 116.0477 | 119.6091
1860.4844 | 123.3582 | -118.3868 | 4.834 | -0.072937 | 0.0037661 | 0.11804 | 0.0036615 | -0.0010831 | -0.0012112 | -0.00031193 | -0.093414 | 0.14046 | 0.0021212 | 0.001113 | -0.0021704 | -0.0010212 | 0.00073706 | -2.5223 | -2.2751 | -118.7073 | -2.5772 | -2.4078 | -118.3182 | -2.4765 | 1.0803 | 4.8981 | 4.3854 | 4.715 | 4.7058 | 4.6417 | 4.7379 | -0.32043 | -7.1091 | -7.4112 | 115.979 | 115.9103 | 0.068665 | 116.2308 | 0.3891 | 122.7722 | 0.064087 | -0.11902 | 123.0927 | 123.1247 | 123.0286 | 0.35248 | 0.25635 | 116.2994 | 116.1301 | 0.32043 | 0.32959 | 116.4322 | 0.51269 | 116.1118 | 123.2849 | -123.5413 | -0.44861 | 115.8096 | 123.1018 | 115.8646 | 119.4672
1861.4844 | 123.3673 | -118.3319 | 4.9118 | -0.057678 | 0.0044071 | 0.11932 | 0.0049433 | 0.00041234 | -0.00057042 | -0.00052553 | -0.084259 | 0.13683 | 0.0021212 | -0.0031594 | -0.0017432 | 0.00026062 | 0.00030966 | -2.2293 | -1.9775 | -118.6203 | -2.2797 | -2.1011 | -117.7734 | -2.1744 | 1.2543 | 4.9667 | 4.4724 | 4.8019 | 4.8019 | 4.7241 | 4.834 | -0.28839 | -6.8893 | -7.1915 | 116.2308 | 116.1575 | 0.55847 | 116.4459 | 0.84686 | 122.8043 | 0.054932 | -0.10986 | 123.1338 | 123.1659 | 123.056 | 0.36163 | 0.25177 | 116.5192 | 116.3406 | 0.32959 | 0.32959 | 116.6428 | 0.49439 | 116.3544 | 123.2986 | -123.5321 | -0.43945 | 116.0522 | 123.1338 | 116.1026 | 119.5862
1862.5625 | 123.3994 | -118.2449 | 4.9667 | 0.1712 | 0.0035525 | 0.11932 | 0.0034479 | 0.0016939 | 0.0028476 | -0.0020209 | -0.044586 | 0.13725 | 0.0031894 | -0.0020914 | -0.003025 | -0.0010212 | -0.0011855 | -2.4216 | -2.0874 | -118.6432 | -2.4033 | -2.2705 | -118.0756 | -2.2705 | 1.0941 | 5.0354 | 4.4952 | 4.8386 | 4.8706 | 4.7791 | 4.8843 | -0.39825 | -7.0541 | -7.37 | 115.9744 | 115.9744 | 0.16937 | 116.3727 | 0.56763 | 122.7402 | 0.068664 | -0.12817 | 123.1155 | 123.1293 | 123.024 | 0.3891 | 0.28381 | 116.3727 | 116.2399 | 0.37537 | 0.34332 | 116.5558 | 0.54016 | 116.1575 | 123.2803 | -123.6099 | -0.4715 | 115.8417 | 123.0835 | 115.8234 | 119.339
1863.4844 | 123.3765 | -118.222 | 5.0079 | -0.019531 | 0.0035525 | 0.11676 | 0.00024352 | -0.0036465 | 7.0582e-05 | -0.00031193 | -0.099518 | 0.13683 | 0.005112 | -0.0025186 | -0.0047338 | -0.0025164 | -0.00054474 | -2.3346 | -2.0508 | -118.5379 | -2.3895 | -2.3209 | -118.0573 | -2.4033 | 1.062 | 4.985 | 4.5227 | 4.8798 | 4.921 | 4.8157 | 4.921 | -0.31586 | -7.0587 | -7.3975 | 115.9012 | 115.8188 | 0.1648 | 116.1346 | 0.48065 | 122.7448 | -0.022889 | -0.12817 | 123.143 | 123.143 | 123.0377 | 0.39825 | 0.29297 | 116.217 | 116.1484 | 0.39825 | 0.35706 | 116.4871 | 0.46234 | 116.1713 | 123.2071 | -123.5458 | -0.48523 | 115.8325 | 123.1018 | 115.8875 | 119.2841
1864.5469 | 123.3353 | -118.1305 | 5.1819 | 0.0033567 | 0.0048343 | 0.11932 | 0.0047295 | 0.0021213 | 0.00028418 | 0.00075627 | -0.17886 | 0.13896 | 0.0031894 | 0.002822 | -0.0019568 | -0.006148 | 0.0043687 | -2.1881 | -1.9135 | -118.5059 | -2.2934 | -2.1423 | -118.1763 | -2.2156 | 1.1169 | 5.191 | 4.6097 | 5.1041 | 4.953 | 4.9347 | 4.9942 | -0.37537 | -7.0953 | -7.4753 | 115.9882 | 115.9149 | -0.045777 | 116.2903 | 0.32959 | 122.7402 | 0.009155 | -0.07782 | 123.0835 | 123.1247 | 123.0652 | 0.38452 | 0.32501 | 116.3635 | 116.2125 | 0.34332 | 0.49439 | 116.5924 | 0.58136 | 116.217 | 123.3215 | -123.6877 | -0.57221 | 115.8371 | 123.2346 | 115.9424 | 119.2474
1865.4844 | 123.3856 | -118.1763 | 5.0674 | -0.042419 | 0.0041935 | 0.11889 | 0.0010981 | -0.00022866 | 0.00028418 | -0.0026617 | -0.075104 | 0.13875 | 0.003403 | 0.00047219 | -0.002384 | -0.0018756 | -0.0026809 | -2.2339 | -1.9226 | -118.4555 | -2.2842 | -2.1286 | -118.0984 | -2.298 | 1.1032 | 5.0812 | 4.5868 | 4.9484 | 4.9622 | 4.8614 | 4.9667 | -0.27923 | -6.9901 | -7.3517 | 116.0477 | 115.8783 | 0.07782 | 116.1575 | 0.35706 | 122.7631 | 0.013733 | -0.11902 | 123.1384 | 123.143 | 123.0377 | 0.37994 | 0.27466 | 116.3269 | 116.1713 | 0.37537 | 0.36163 | 116.5329 | 0.49439 | 116.2537 | 123.2574 | -123.5229 | -0.48065 | 115.892 | 123.1247 | 115.9424 | 119.2795
1866.4844 | 123.3582 | -118.2266 | 4.9942 | -0.072937 | 0.0044071 | 0.11932 | 0.0053705 | -0.00022866 | 0.0017794 | -0.0039435 | -0.099518 | 0.13811 | 0.0048984 | -0.0016642 | -0.0021704 | -0.0010212 | -0.00033114 | -2.1606 | -1.9226 | -118.5425 | -2.1973 | -2.0462 | -118.1168 | -2.124 | 1.1581 | 5.0446 | 4.5547 | 4.8843 | 4.8935 | 4.7974 | 4.9118 | -0.31586 | -6.9168 | -7.1915 | 116.1804 | 116.1026 | 0.10986 | 116.4185 | 0.42572 | 122.7814 | 0.050354 | -0.10986 | 123.1201 | 123.1384 | 123.024 | 0.35705 | 0.24261 | 116.4963 | 116.3452 | 0.33874 | 0.32959 | 116.6199 | 0.48981 | 116.304 | 123.2712 | -123.5367 | -0.43945 | 116.0294 | 123.111 | 116.066 | 119.3848
1867.4844 | 123.3765 | -118.2404 | 4.9988 | -0.11108 | 0.00013467 | 0.11761 | 0.0025933 | -0.0023649 | 0.00049778 | -9.8328e-05 | -0.081207 | 0.1364 | 0.0053256 | 0.001113 | -0.0028112 | -0.0040118 | 0.0033005 | -2.2568 | -1.9592 | -118.5425 | -2.3117 | -2.1652 | -118.158 | -2.3438 | 1.0529 | 4.9896 | 4.5136 | 4.8706 | 4.8981 | 4.7928 | 4.8798 | -0.30212 | -6.958 | -7.3105 | 116.0751 | 115.8966 | 0.082397 | 116.1987 | 0.38452 | 122.7539 | -0.009155 | -0.12817 | 123.1384 | 123.1201 | 123.0331 | 0.36621 | 0.27924 | 116.3773 | 116.2308 | 0.38452 | 0.35705 | 116.5833 | 0.47607 | 116.2811 | 123.23 | -123.5413 | -0.48523 | 115.9286 | 123.111 | 115.9836 | 119.2932
1868.5469 | 123.3627 | -97.6685 | 5.3467 | -0.31708 | 0.0029117 | 0.044126 | -0.016846 | -0.022018 | 0.10496 | -0.0022345 | 0.2728 | 0.17314 | -1.4954e-05 | -0.00038241 | -0.004093 | -0.0012348 | -0.0048171 | -0.80566 | -2.3621 | -61.3358 | -0.45776 | -1.506 | -142.3874 | -2.0645 | 1.0895 | 5.5344 | 4.9347 | 5.2826 | 5.246 | 5.1819 | 5.1498 | 36.3327 | -7.7087 | -5.8044 | 96.1624 | 95.6039 | -44.7189 | 59.2712 | -81.0516 | 102.6031 | 0.18768 | -0.064087 | 102.9144 | 102.8183 | 102.8503 | 0.21515 | 0.24719 | 59.8297 | 60.878 | 0.31128 | 0.3479 | 58.9737 | 0.59967 | 95.3064 | 103.2028 | -66.6824 | -0.41199 | 97.2107 | 102.9511 | 96.8628 | 98.7579
1869.4844 | 123.3627 | -118.3914 | 4.8157 | -0.080566 | 0.0059025 | 0.11996 | 0.0043023 | 0.00041234 | 0.00049778 | -0.0041571 | -0.084259 | 0.13683 | 0.0048984 | -0.0065774 | -0.0019568 | -0.0029438 | 0.0024461 | -2.1881 | -1.8997 | -118.721 | -2.2385 | -2.1469 | -118.9407 | -2.2522 | 0.93384 | 4.7974 | 4.3167 | 4.6829 | 4.7104 | 4.5959 | 4.6967 | -0.32959 | -6.7154 | -7.0541 | 116.2445 | 116.1392 | -0.54932 | 116.4688 | -0.21973 | 122.7081 | -0.018311 | -0.13275 | 123.1018 | 123.0881 | 122.9874 | 0.37994 | 0.27924 | 116.5741 | 116.4825 | 0.39368 | 0.36621 | 116.8213 | 0.48065 | 116.4917 | 123.1888 | -123.5367 | -0.49896 | 116.153 | 123.0743 | 116.2033 | 119.3253
1870.5469 | 123.4085 | -118.5516 | 4.6555 | -0.042419 | 0.0052615 | 0.12039 | 0.0030207 | 0.00041234 | 0.0022068 | -0.00031193 | -0.12698 | 0.13768 | 0.00041225 | 0.0015402 | -0.003025 | -0.0012348 | 0.0041551 | -2.1561 | -1.8997 | -118.9041 | -2.1927 | -2.0599 | -118.6935 | -2.1103 | 1.0574 | 4.6967 | 4.2114 | 4.5776 | 4.5914 | 4.4815 | 4.6005 | -0.35248 | -6.5552 | -6.8481 | 116.4917 | 116.4413 | -0.14191 | 116.7938 | 0.21057 | 122.7631 | 0.041198 | -0.07782 | 123.143 | 123.1522 | 123.0331 | 0.3891 | 0.27008 | 116.8442 | 116.7114 | 0.37994 | 0.36621 | 117.0044 | 0.48523 | 116.6519 | 123.2483 | -123.5596 | -0.44403 | 116.3589 | 123.1293 | 116.3956 | 119.6091
1871.4844 | 123.3856 | -118.4875 | 4.7516 | -0.042419 | 0.0029117 | 0.11783 | 0.0040887 | -0.00065586 | 0.00071138 | -0.0026617 | -0.05069 | 0.13982 | 0.0036166 | -0.004014 | -0.0062292 | -0.0012348 | 0.0011643 | -2.0828 | -1.8631 | -118.7759 | -2.1332 | -1.9409 | -117.8375 | -2.0187 | 1.0941 | 4.8157 | 4.3167 | 4.66 | 4.6967 | 4.6326 | 4.7058 | -0.28839 | -6.6147 | -6.8848 | 116.5466 | 116.4688 | 0.65002 | 116.7572 | 0.93842 | 122.8043 | 0.064087 | -0.091553 | 123.1842 | 123.1934 | 123.1201 | 0.3891 | 0.31586 | 116.835 | 116.6428 | 0.37994 | 0.34332 | 116.9128 | 0.49896 | 116.6245 | 123.3032 | -123.5275 | -0.43488 | 116.3544 | 123.1476 | 116.4047 | 119.5816
1872.5469 | 123.262 | -118.515 | 4.8065 | -0.072937 | 0.0061161 | 0.11953 | 0.0045159 | 0.0034029 | 0.0017794 | -0.0028753 | -0.18802 | 0.13875 | 0.0066074 | 0.0032492 | -0.0036658 | 0.0023968 | 0.0011643 | -2.1881 | -1.8631 | -118.84 | -2.3026 | -2.1698 | -118.0756 | -2.211 | 0.8194 | 4.8752 | 4.2892 | 4.5547 | 4.5593 | 4.4403 | 4.5639 | -0.32501 | -6.6696 | -7.1091 | 116.3452 | 116.304 | 0.43945 | 116.629 | 0.76447 | 122.8043 | 0.068664 | -0.25177 | 123.0743 | 123.0789 | 122.9553 | 0.27466 | 0.15106 | 116.6702 | 116.5375 | 0.27008 | 0.2655 | 116.9769 | 0.58594 | 116.6519 | 123.3902 | -123.6465 | -0.51727 | 116.2125 | 123.0698 | 116.3269 | 119.3344
1873.4844 | 123.3994 | -118.515 | 4.7516 | -0.057678 | 0.0044071 | 0.11783 | 0.0023797 | -1.486e-05 | 0.00028418 | -0.0028753 | -0.029327 | 0.13854 | 0.0029758 | -0.0020914 | -0.001316 | -0.0014484 | -0.0043899 | -2.1515 | -1.8814 | -118.8171 | -2.1927 | -2.0233 | -118.19 | -2.0737 | 1.0437 | 4.7928 | 4.2709 | 4.6371 | 4.66 | 4.5868 | 4.6555 | -0.30212 | -6.633 | -6.9443 | 116.4917 | 116.4413 | 0.32501 | 116.7435 | 0.62714 | 122.7859 | 0.041199 | -0.11444 | 123.175 | 123.1705 | 123.1018 | 0.38452 | 0.31586 | 116.7938 | 116.6245 | 0.3891 | 0.36621 | 116.9357 | 0.52185 | 116.6336 | 123.3078 | -123.5687 | -0.48065 | 116.3223 | 123.1522 | 116.3635 | 119.5587
1874.4844 | 123.349 | -118.5287 | 4.7012 | -0.080566 | 0.0022709 | 0.1221 | 0.0032343 | 0.0014803 | 0.00049778 | -0.00052553 | -0.075104 | 0.13896 | 0.0021212 | 0.00047219 | -0.0021704 | -0.00038018 | 0.00073706 | -2.1378 | -1.9089 | -118.8492 | -2.179 | -2.0142 | -118.3456 | -2.092 | 1.1124 | 4.7516 | 4.216 | 4.6051 | 4.5639 | 4.4815 | 4.5959 | -0.32043 | -6.6101 | -6.8802 | 116.5146 | 116.4368 | 0.18311 | 116.7572 | 0.50354 | 122.7448 | 0.050354 | -0.09613 | 123.0927 | 123.1247 | 123.0103 | 0.37994 | 0.2655 | 116.835 | 116.6702 | 0.3479 | 0.3891 | 116.9403 | 0.53558 | 116.6199 | 123.2803 | -123.5504 | -0.48523 | 116.3498 | 123.1339 | 116.391 | 119.6411
1875.5469 | 123.2895 | -118.5974 | 4.6875 | -0.0042723 | 0.0054751 | 0.11804 | 0.0064385 | -0.0012967 | 0.0015658 | -0.00095273 | -0.1575 | 0.13896 | 0.0029758 | -0.0018778 | -0.0032386 | -0.0087116 | 9.6064e-05 | -2.1835 | -1.8585 | -118.8583 | -2.2751 | -2.1332 | -118.6523 | -2.1973 | 0.91095 | 4.7516 | 4.1931 | 4.5044 | 4.4312 | 4.3579 | 4.4861 | -0.26093 | -6.546 | -6.9626 | 116.4642 | 116.4001 | -0.054932 | 116.6611 | 0.20599 | 122.7905 | 0.064087 | -0.18311 | 123.0286 | 123.0835 | 122.9553 | 0.29297 | 0.1648 | 116.7252 | 116.5833 | 0.23804 | 0.31128 | 116.9998 | 0.55847 | 116.7389 | 123.349 | -123.5458 | -0.49439 | 116.3223 | 123.1018 | 116.4139 | 119.5084
1876.4844 | 123.3856 | -118.4967 | 4.7241 | -0.027161 | 0.0037661 | 0.11825 | 0.0010981 | -0.00022866 | -0.00014322 | 0.0016107 | -0.032379 | 0.1379 | 0.0042574 | -0.005082 | -0.002384 | -0.0029438 | 0.0011643 | -2.1927 | -1.9135 | -118.8309 | -2.2293 | -2.0645 | -118.6066 | -2.1011 | 1.0162 | 4.7928 | 4.2709 | 4.6188 | 4.6463 | 4.5639 | 4.6371 | -0.33417 | -6.6376 | -6.9534 | 116.4322 | 116.3956 | -0.10986 | 116.7297 | 0.22431 | 122.7676 | 0.068665 | -0.10529 | 123.143 | 123.1338 | 123.0606 | 0.36621 | 0.29297 | 116.7664 | 116.6016 | 0.37537 | 0.3479 | 116.9174 | 0.52185 | 116.5833 | 123.2895 | -123.555 | -0.45319 | 116.2674 | 123.1155 | 116.304 | 119.5129
1877.4844 | 123.4039 | -118.5883 | 4.6188 | -0.088196 | 0.0039799 | 0.11996 | 0.0030207 | -0.0032193 | 0.0028476 | -0.0015935 | -0.041534 | 0.14003 | 0.0048984 | -0.0038004 | -0.0028112 | -0.001662 | -0.0018265 | -2.2018 | -1.9592 | -118.8766 | -2.2339 | -2.0416 | -118.0298 | -2.1149 | 1.0483 | 4.6738 | 4.1519 | 4.5136 | 4.541 | 4.4724 | 4.541 | -0.28839 | -6.5781 | -6.8527 | 116.5466 | 116.4734 | 0.55847 | 116.7618 | 0.84686 | 122.7402 | 0.054932 | -0.10528 | 123.1293 | 123.1293 | 123.0606 | 0.3891 | 0.32043 | 116.835 | 116.6428 | 0.3891 | 0.36163 | 116.9174 | 0.52185 | 116.629 | 123.262 | -123.4955 | -0.46692 | 116.3544 | 123.1018 | 116.3864 | 119.6365
1878.4844 | 123.3719 | -118.6249 | 4.628 | -0.019531 | 0.0033389 | 0.11953 | 0.0060113 | 0.0012667 | 0.0013522 | 0.00032907 | -0.011017 | 0.14025 | 0.0042574 | 0.001113 | -0.0036658 | -0.0012348 | 0.00052346 | -7.0175 | -2.0554 | -118.9362 | -2.4033 | -2.2705 | -118.4555 | -2.2797 | 0.82855 | 4.6417 | 4.129 | 4.4769 | 4.4952 | 4.3945 | 4.4907 | -0.31128 | -6.6833 | -7.0312 | 116.3544 | 116.3452 | 0.16937 | 116.6565 | 0.48065 | 122.7539 | 0.013733 | -0.15106 | 123.1201 | 123.1155 | 123.0194 | 0.36163 | 0.2655 | 116.6656 | 116.5329 | 0.36621 | 0.3479 | 116.8808 | 0.5127 | 116.5695 | 123.2666 | -123.5641 | -0.49896 | 116.2216 | 123.1018 | 111.6074 | 119.4534
1879.4844 | 123.4314 | -118.3044 | 4.8752 | -0.065308 | 0.0026981 | 0.11996 | 0.0030207 | -0.0023649 | 0.00071138 | 0.00032907 | -0.029327 | 0.13704 | 0.0038302 | -0.0063638 | -0.0017432 | -0.0029438 | -0.0022537 | -3.9413 | -1.9958 | -118.6615 | -2.2797 | -2.0966 | -118.1946 | -2.1698 | 1.0117 | 4.9393 | 4.3121 | 4.7928 | 4.6646 | 4.6005 | 4.6692 | -0.35706 | -6.871 | -7.1548 | 116.2079 | 116.1346 | 0.10986 | 116.4917 | 0.46692 | 122.6166 | 0.064087 | -0.082397 | 122.9691 | 122.9736 | 122.905 | 0.35705 | 0.28839 | 116.5649 | 116.3818 | 0.35248 | 0.48065 | 116.6656 | 0.62714 | 116.3086 | 123.2437 | -123.5367 | -0.56305 | 116.0248 | 123.0972 | 114.3631 | 119.3161
1880.5469 | 123.1018 | -21.2402 | 101.1749 | -0.24078 | 0.0031253 | 0.017637 | 0.0043023 | -0.0017239 | 0.04664 | -0.00052553 | 0.010345 | 0.0020315 | 0.0019076 | 0.053451 | -0.0019568 | -0.0029438 | 0.0020187 | -1.4511 | -1.1261 | -21.0892 | -1.442 | -1.2589 | -13.5132 | -1.3412 | 4.2664 | 101.5549 | 2.3849 | 101.9943 | 2.7878 | 2.655 | 2.7557 | 0.15106 | -102.301 | -102.6169 | 19.9814 | 19.899 | 7.7271 | 19.7479 | 7.576 | 23.6252 | 0.37994 | 0.8194 | 24.028 | 23.996 | 23.8953 | 0.37079 | 0.27008 | 19.8303 | 19.6472 | 0.40283 | 99.6094 | 19.9631 | 99.1699 | 20.1141 | 122.7951 | -122.2641 | -98.79 | 19.7983 | 123.2346 | 19.7891 | 25.5066
1881.4844 | 122.8226 | -20.2103 | 102.6123 | -0.019531 | 0.0022709 | 0.015714 | 0.00088432 | -1.486e-05 | 0.048563 | 0.00075627 | 0.010345 | 0.00053628 | 0.0014804 | 0.054519 | -0.0025976 | -0.0029438 | 0.00030966 | -1.3824 | -1.0803 | -20.2423 | -1.3824 | -1.2589 | -12.1765 | -1.5152 | 3.4698 | 102.3056 | 2.5269 | 102.8778 | 2.98 | 2.829 | 2.8976 | -0.032044 | -103.6926 | -103.9948 | 18.9514 | 18.6951 | 8.0338 | 18.7271 | 8.0658 | 22.7371 | -0.3067 | 0.2655 | 23.1903 | 23.1079 | 23.0392 | 0.37079 | 0.30212 | 18.9835 | 18.8599 | 0.45319 | 100.351 | 19.162 | 99.7787 | 19.1299 | 122.5159 | -122.8546 | -100.0855 | 18.8278 | 123.0881 | 18.8278 | 23.6801
1882.4844 | 123.1476 | -19.9402 | 102.507 | -0.050049 | 0.0022709 | 0.012296 | 0.0036615 | -0.0019377 | 0.049204 | -0.0028753 | 0.05307 | 0.0018179 | 0.0025484 | 0.054946 | -0.003025 | -0.0012348 | -0.0011855 | -1.4008 | -1.1032 | -19.8578 | -1.4465 | -1.2543 | -11.824 | -1.3412 | 3.2684 | 102.8915 | 2.6184 | 103.2944 | 3.0121 | 2.9205 | 2.9892 | 0.082398 | -103.6102 | -103.9536 | 18.6859 | 18.5989 | 8.1162 | 18.5165 | 8.0338 | 22.5586 | 0.38452 | 0.78735 | 22.9523 | 22.9294 | 22.8607 | 0.37079 | 0.30212 | 18.6035 | 18.4113 | 0.39368 | 100.676 | 18.7546 | 100.2731 | 18.837 | 122.8317 | -122.3648 | -99.8886 | 18.4937 | 123.2346 | 18.5394 | 23.2086
1883.5469 | 122.7127 | -22.3022 | 101.9165 | -0.019531 | -7.913e-05 | 0.013792 | 0.0023797 | -0.00044226 | 0.044077 | 0.00075627 | 0.071381 | 0.0018179 | 0.0023348 | 0.054092 | 0.0012476 | -0.0044392 | -0.0022537 | -1.6479 | -1.1032 | -22.5586 | -1.5244 | -1.3092 | -11.5036 | -1.3184 | 0.73242 | 102.4292 | 0.67749 | 103.7842 | 3.0533 | 2.2018 | 3.186 | -0.25635 | -103.0197 | -103.4409 | 20.993 | 20.9839 | 10.7986 | 21.2402 | 11.055 | 22.9797 | 0.51269 | 1.8677 | 25.3555 | 25.4883 | 24.5041 | 2.5085 | 1.5244 | 21.2494 | 21.0342 | 2.3758 | 103.1067 | 21.4554 | 101.7517 | 21.199 | 124.7314 | -124.4751 | -101.239 | 20.7779 | 126.0864 | 20.6543 | 23.0347
1884.4844 | 122.7859 | -19.1986 | 103.4134 | 0.0033567 | 0.00056187 | 0.013151 | 0.0040887 | -0.0012967 | 0.049204 | -0.0039435 | -0.029327 | 0.0026725 | 0.0014804 | 0.051742 | -0.0028112 | -0.0029438 | 0.0024461 | -1.3962 | -1.1444 | -19.2307 | -1.4282 | -1.3779 | -10.8215 | -1.4832 | 3.1311 | 103.4592 | 2.6276 | 103.8849 | 3.1036 | 2.9617 | 3.0441 | -0.032044 | -104.5578 | -104.8416 | 17.8207 | 17.7155 | 8.3771 | 17.7475 | 8.4091 | 21.8262 | 0.045776 | 0.4715 | 22.3022 | 22.2427 | 22.1603 | 0.41657 | 0.33417 | 17.8528 | 17.8024 | 0.47608 | 101.2573 | 18.0862 | 100.8316 | 18.0542 | 122.6578 | -122.644 | -100.7858 | 17.7704 | 123.0835 | 17.8024 | 22.3297
1885.5469 | 123.143 | -19.1116 | 103.2166 | -0.072937 | 0.0012027 | 0.013792 | 0.0019525 | -0.0053555 | 0.047281 | -0.0018073 | 0.065277 | 0.00032248 | 0.003403 | 0.051101 | -0.0028112 | -0.0035846 | 0.0030869 | -1.355 | -1.0757 | -19.0659 | -1.3962 | -1.2222 | -10.7437 | -1.2451 | 3.067 | 103.7292 | 2.6733 | 104.1595 | 3.1403 | 3.0304 | 3.0624 | 0.045776 | -104.2923 | -104.6127 | 17.8894 | 17.8665 | 8.3679 | 17.8207 | 8.3221 | 21.785 | 0.51269 | 0.94299 | 22.2519 | 22.1741 | 22.142 | 0.3891 | 0.35706 | 17.8436 | 17.6697 | 0.46692 | 101.4862 | 17.9901 | 101.0559 | 18.0359 | 122.8409 | -122.2824 | -100.5432 | 17.7155 | 123.2712 | 17.7567 | 22.1787
1886.4844 | 101.7105 | -18.4753 | 104.1229 | -0.65277 | 0.00077547 | 0.012937 | 0.0036615 | 0.00083954 | 0.047495 | 0.00032907 | 0.083588 | 0.0020315 | 0.0036166 | 0.053023 | -0.0028112 | -0.0020892 | 0.0018051 | -1.4603 | -1.1536 | -18.631 | -1.4145 | -1.2268 | -10.5011 | -1.268 | 2.6093 | 104.1504 | 4.5914 | 104.6219 | 3.0991 | 3.0579 | 3.4698 | -0.15564 | -105.2765 | -105.5374 | 17.2485 | 17.2073 | 7.9742 | 17.363 | 8.1299 | 23.0667 | 0.027466 | 0.49896 | 21.5744 | 21.9452 | 21.5332 | -1.1215 | -1.5335 | 17.4042 | 17.2165 | -1.4923 | 100.0305 | 17.4774 | 99.559 | 17.3218 | 122.6257 | -122.7539 | -99.5316 | 17.0609 | 123.0972 | 17.0151 | 21.0846
1887.4844 | 123.4726 | -118.808 | 4.4083 | -0.065308 | 0.0022709 | 0.11889 | 0.0030207 | -0.0012967 | 0.0039158 | -0.0033025 | -0.17276 | 0.13704 | 0.00062585 | -0.0072184 | -0.0021704 | -0.003371 | 0.0022323 | -7.2327 | -1.8723 | -119.1147 | -2.1835 | -2.0233 | -117.2333 | -2.0554 | 1.1032 | 4.4312 | 3.9322 | 4.2709 | 4.3167 | 4.2023 | 4.3076 | -0.3067 | -6.2805 | -6.5918 | 116.7847 | 116.7526 | 1.5747 | 117.0593 | 1.8814 | 122.7402 | 0.022888 | -0.13733 | 123.1247 | 123.1155 | 123.0103 | 0.37537 | 0.27008 | 117.0914 | 116.9312 | 0.38452 | 0.33874 | 117.2424 | 0.49896 | 116.9357 | 123.2391 | -123.5229 | -0.47607 | 116.6244 | 123.0789 | 111.5753 | 119.9112
1888.5469 | 123.4451 | -118.8858 | 4.3167 | -0.03479 | 0.0031253 | 0.11911 | 0.0045159 | 0.0021213 | -0.00014322 | -0.0039435 | -0.10562 | 0.14131 | 0.0057528 | -0.0070046 | -0.0021704 | -0.0031574 | -0.0011855 | -5.571 | -1.9043 | -119.2291 | -2.2247 | -2.0508 | -119.9753 | -2.124 | 0.9201 | 4.3854 | 3.8864 | 4.2206 | 4.2206 | 4.1519 | 4.2801 | -0.34332 | -6.221 | -6.5414 | 116.835 | 116.7618 | -1.0895 | 117.1051 | -0.74616 | 122.7722 | 0.068665 | -0.09613 | 123.1064 | 123.1659 | 123.0377 | 0.39368 | 0.2655 | 117.1783 | 117.0044 | 0.33417 | 0.33417 | 117.3248 | 0.49896 | 116.9815 | 123.2712 | -123.5458 | -0.4303 | 116.6611 | 123.1064 | 113.3148 | 119.8059
1889.4844 | 123.4543 | -118.5333 | 4.6921 | 0.010986 | 0.0014163 | 0.11975 | 0.0021661 | -0.00086946 | 0.0022068 | -0.0013799 | 0.12936 | 0.14046 | 0.006821 | -0.0025186 | -0.0032386 | -0.0042254 | -0.0020401 | -7.7087 | -1.6525 | -118.8446 | -1.9363 | -1.7395 | -118.2999 | -1.8494 | 0.65002 | 4.7516 | 4.2252 | 4.5731 | 4.5868 | 4.5273 | 4.6143 | -0.31128 | -6.3446 | -6.6284 | 116.7938 | 116.684 | 0.23346 | 116.9952 | 0.54474 | 122.7585 | 0.059509 | -0.11902 | 123.1201 | 123.1476 | 123.0606 | 0.3891 | 0.30212 | 117.1051 | 116.9083 | 0.36163 | 0.3479 | 117.1921 | 0.52643 | 116.8808 | 123.2849 | -123.5367 | -0.46692 | 116.597 | 123.1064 | 110.8246 | 119.1833
1890.5469 | 123.4131 | -118.5104 | 4.7516 | -0.072937 | 0.0024845 | 0.12039 | 0.0064385 | -0.0023649 | -0.00057042 | -0.0013799 | -0.11478 | 0.13725 | 0.0042574 | -0.005723 | -0.0032386 | -0.00080758 | -0.0035355 | -1.9409 | -1.6479 | -118.8538 | -1.9867 | -1.8768 | -121.4081 | -1.9913 | 0.60883 | 4.7379 | 4.2297 | 4.5959 | 4.5959 | 4.5364 | 4.6143 | -0.34332 | -6.3995 | -6.7383 | 116.6336 | 116.5192 | -2.8976 | 116.8625 | -2.5543 | 122.7402 | -0.013733 | -0.15564 | 123.1064 | 123.1247 | 123.0469 | 0.38452 | 0.3067 | 116.9769 | 116.8671 | 0.36621 | 0.36621 | 117.2058 | 0.50812 | 116.8625 | 123.2483 | -123.6053 | -0.52185 | 116.5237 | 123.1064 | 116.5695 | 119.1193
1891.4844 | 123.3444 | -118.428 | 4.8477 | -0.027161 | 0.0039799 | 0.11825 | 0.0034479 | 0.0031893 | 7.0582e-05 | -0.00073913 | -0.038483 | 0.13704 | 0.0036166 | -0.00038241 | -0.0036658 | -0.0012348 | 0.00052346 | -11.9339 | -2.0645 | -118.7622 | -2.536 | -2.3575 | -118.3411 | -2.3849 | 0.60883 | 4.8981 | 4.2343 | 4.5639 | 4.5364 | 4.454 | 4.5319 | -0.33417 | -6.9122 | -7.3837 | 116.0706 | 116.0431 | 0.086976 | 116.3773 | 0.42114 | 122.6624 | 0.050354 | -0.28381 | 122.9645 | 122.9599 | 122.8821 | 0.29755 | 0.21973 | 116.4047 | 116.2262 | 0.30212 | 0.32959 | 116.6977 | 0.66376 | 116.3635 | 123.3261 | -123.6099 | -0.6134 | 115.892 | 122.9919 | 106.4941 | 119.0369
1892.4844 | 122.7127 | -21.6751 | 100.6622 | -0.12634 | 0.00077547 | 0.018278 | 0.0034479 | -0.0023649 | 0.043009 | 0.00011527 | -0.0018616 | 0.0020315 | 0.00041225 | 0.051314 | -0.0032386 | -0.0023028 | -0.0033219 | -2.0416 | -1.506 | -21.7575 | -1.8036 | -1.6159 | -14.1449 | -1.6617 | 2.3026 | 101.3855 | 2.4307 | 101.5915 | 2.8931 | 2.7603 | 2.829 | -0.082397 | -102.1683 | -102.4658 | 20.0592 | 20.0134 | 7.5302 | 20.0958 | 7.6126 | 24.1058 | 0.72327 | 0.92926 | 24.5682 | 24.5041 | 24.4354 | 0.39825 | 0.32959 | 20.1416 | 19.9539 | 0.46234 | 99.1608 | 20.2515 | 98.9548 | 20.1691 | 123.0606 | -122.4197 | -98.2315 | 19.8715 | 123.2666 | 19.6335 | 23.9777
1893.5469 | 122.5662 | -20.9656 | 101.1566 | -0.057678 | -7.913e-05 | 0.015501 | 0.0010981 | -0.0055691 | 0.043222 | -0.00031193 | 0.043915 | 0.00053628 | 0.0042574 | 0.050246 | -0.0021704 | -0.0014484 | 0.00052346 | -1.8677 | -1.1307 | -20.5124 | -1.4511 | -1.3 | -12.3459 | -1.3046 | 1.8723 | 102.9831 | 2.4811 | 102.9922 | 2.948 | 2.8244 | 0.36163 | 0.45319 | -102.2873 | -102.6077 | 19.6655 | 19.6609 | 8.6197 | 19.2078 | 8.1665 | 23.4467 | 1.8265 | 1.8356 | 23.9136 | 21.3272 | 23.79 | -2.1194 | 0.34332 | 19.2123 | 19.0613 | 0.46692 | 100.5112 | 19.3817 | 100.502 | 19.8349 | 123.9487 | -121.669 | -98.6755 | 19.5145 | 123.9578 | 19.0979 | 22.8378
1894.4844 | 122.8912 | -19.9493 | 102.8229 | -0.057678 | 0.0029117 | 0.015501 | 0.0021661 | -0.0015103 | 0.047495 | -0.0028753 | 0.074432 | 0.0022453 | 0.0059664 | 0.047896 | -0.002384 | -0.0025164 | 0.00095066 | -1.7899 | -1.149 | -20.1416 | -1.4374 | -1.2543 | -11.8515 | -1.3092 | 1.4832 | 103.3447 | 2.4948 | 103.3768 | 2.9388 | 2.8244 | 2.8839 | -0.19226 | -103.9719 | -104.2603 | 18.6951 | 18.6401 | 8.0978 | 18.8324 | 8.2901 | 22.4442 | 0.52185 | 0.55389 | 22.8882 | 22.8333 | 22.7737 | 0.3891 | 0.32959 | 18.8873 | 18.7042 | 0.44403 | 100.882 | 18.9926 | 100.8499 | 18.8004 | 123.2941 | -122.9645 | -100.3281 | 18.512 | 123.3261 | 18.1595 | 21.4325
1895.5469 | 122.8638 | -19.4916 | 103.3218 | -0.17975 | 0.0014163 | 0.015714 | 0.0023797 | 0.0010531 | 0.046854 | -0.0013799 | 0.025604 | 0.0030997 | 0.0029758 | 0.052383 | -0.0017432 | -0.0025164 | -0.0011855 | -1.6479 | -1.4694 | -12.204 | -1.3412 | -1.2589 | -11.4075 | -1.4145 | 1.4328 | 101.532 | 2.6642 | 103.7338 | 2.9617 | 2.7969 | 2.8976 | 7.2876 | -104.7913 | -104.6631 | 18.2327 | 18.0771 | 8.0841 | 10.7895 | 0.79651 | 22.1558 | -1.7899 | 0.41199 | 22.4533 | 22.3892 | 22.2885 | 0.23346 | 0.13275 | 10.9451 | 10.8627 | 0.29755 | 101.0696 | 10.7346 | 98.8678 | 18.0222 | 121.0236 | -115.5258 | -100.6577 | 18.1503 | 123.2254 | 17.8436 | 20.9244
1896.4844 | 123.4772 | -118.3594 | 4.834 | 0.0033567 | 0.0020573 | 0.11996 | 0.0038751 | -0.0025785 | 0.0019932 | -0.0043707 | -0.01712 | 0.13982 | 0.003403 | -0.0014504 | -0.0028112 | -0.0044392 | 0.0013779 | -13.9206 | -1.7349 | -118.6844 | -2.0416 | -1.8539 | -117.9749 | -1.8906 | 0.56763 | 4.9118 | 4.3671 | 4.7012 | 4.7241 | 4.6738 | 4.7333 | -0.32501 | -6.5689 | -6.8756 | 116.5054 | 116.4688 | 0.38452 | 116.7938 | 0.70953 | 122.7264 | 0.07782 | -0.13275 | 123.0835 | 123.0927 | 123.0331 | 0.36621 | 0.3067 | 116.8304 | 116.6428 | 0.35706 | 0.33417 | 116.9495 | 0.54474 | 116.6245 | 123.2712 | -123.5184 | -0.46692 | 116.3177 | 123.0606 | 104.4388 | 118.927
1897.4844 | 123.3673 | -118.4372 | 4.8706 | 0.033875 | 0.0026981 | 0.11889 | 0.0036615 | -0.00022866 | -0.00035682 | -0.0015935 | -0.069 | 0.13896 | 0.003403 | -0.0059366 | -0.0038794 | -0.001662 | -0.0026809 | -9.7458 | -1.5472 | -118.7439 | -1.9547 | -1.7899 | -118.8171 | -1.8311 | 0.72327 | 4.9301 | 4.335 | 4.6097 | 4.6234 | 4.5364 | 4.6097 | -0.3067 | -6.4178 | -6.8253 | 116.6473 | 116.6061 | -0.37994 | 116.9128 | -0.073243 | 122.7722 | 0.05951 | -0.26093 | 123.0606 | 123.0469 | 122.9736 | 0.27466 | 0.20142 | 116.954 | 116.7892 | 0.28839 | 0.27466 | 117.1967 | 0.59509 | 116.89 | 123.3673 | -123.6145 | -0.53558 | 116.4825 | 123.0469 | 108.6914 | 119.1605
1898.5469 | 123.4726 | -118.2587 | 4.9347 | -0.042419 | 0.0026981 | 0.11996 | 0.0049433 | -0.0025785 | 0.0024204 | -0.0013799 | -0.029327 | 0.13811 | 0.0031894 | -0.005723 | -0.0015296 | -0.0042254 | -0.0028945 | -15.0101 | -1.8082 | -118.6249 | -2.1194 | -1.9638 | -118.1122 | -1.973 | 0.96588 | 5.0171 | 4.454 | 4.8248 | 4.8294 | 4.7653 | 4.8477 | -0.36621 | -6.7429 | -7.0541 | 116.2949 | 116.2857 | 0.14648 | 116.6519 | 0.51269 | 122.7127 | 0.082398 | -0.10986 | 123.0881 | 123.1064 | 123.024 | 0.39368 | 0.31128 | 116.6611 | 116.5054 | 0.37537 | 0.37079 | 116.8167 | 0.56305 | 116.4505 | 123.2758 | -123.5596 | -0.48065 | 116.1392 | 123.0835 | 103.2486 | 119.2245
1899.4844 | 123.4451 | -118.2037 | 5.04 | -0.40863 | 0.00034827 | 0.11825 | 0.0055841 | 0.0023349 | -0.0027066 | -9.8328e-05 | -0.13004 | 0.13725 | 0.0059664 | 0.0034628 | -0.0038794 | -0.001662 | 0.0015915 | -4.2526 | -1.3733 | -118.5883 | -1.8402 | -1.7166 | -117.9062 | -1.7303 | 0.81024 | 5.127 | 4.4449 | 4.8065 | 4.7058 | 4.5547 | 4.5959 | -0.38452 | -6.4133 | -6.8802 | 116.4871 | 116.4734 | 0.29755 | 116.8579 | 0.68207 | 122.6486 | 0.086975 | -0.23346 | 122.9095 | 122.7997 | 122.7585 | 0.15106 | 0.10986 | 116.8716 | 116.748 | 0.26093 | 0.36163 | 117.215 | 0.68207 | 116.8304 | 123.3307 | -123.6282 | -0.59509 | 116.3635 | 123.0103 | 113.9511 | 119.014
1900.4844 | 123.555 | -118.1625 | 4.9713 | -0.042419 | 0.0031253 | 0.11847 | 0.0043023 | -0.00065586 | -0.00057042 | -0.0015935 | -0.014069 | 0.13747 | 0.0038302 | -0.0046548 | -0.004093 | -0.0029438 | -0.0026809 | -5.3192 | -1.5839 | -118.5425 | -1.8677 | -1.6983 | -118.6981 | -1.7624 | 0.94299 | 5.0583 | 4.5181 | 4.9072 | 4.8843 | 4.8431 | 4.9072 | -0.37994 | -6.5552 | -6.839 | 116.4642 | 116.4001 | -0.53558 | 116.7801 | -0.15564 | 122.6807 | 0.086976 | -0.064086 | 123.0469 | 123.0698 | 123.0057 | 0.3891 | 0.32501 | 116.8442 | 116.6748 | 0.36621 | 0.3891 | 116.9586 | 0.54016 | 116.5787 | 123.2208 | -123.5138 | -0.45319 | 116.2949 | 123.0698 | 112.8433 | 119.1055
1901.5469 | 123.4589 | -118.158 | 5.0812 | 0.010986 | 0.0048343 | 0.11889 | 0.0057977 | 0.00041234 | 0.0028476 | -0.0028753 | -0.044586 | 0.13832 | 0.0027622 | -0.00016881 | -0.0015296 | -0.0012348 | 0.0033005 | -2.2659 | -1.7303 | -118.4463 | -2.0599 | -1.8997 | -117.7139 | -1.9501 | 0.86517 | 5.1407 | 4.5868 | 4.9713 | 4.8843 | 4.8248 | 4.9301 | -0.28839 | -6.8115 | -7.1411 | 116.2582 | 116.2079 | 0.44403 | 116.4963 | 0.73242 | 122.7448 | 0.059509 | -0.10986 | 123.0423 | 123.0881 | 122.9828 | 0.34332 | 0.23804 | 116.5466 | 116.3864 | 0.29755 | 0.38452 | 116.716 | 0.55389 | 116.4276 | 123.2986 | -123.5275 | -0.49439 | 116.098 | 123.1293 | 115.892 | 119.0231
1902.4844 | 123.4772 | -118.1396 | 5.0583 | -0.019531 | 0.0056889 | 0.11847 | 0.0023797 | -0.00086946 | -0.00014322 | -0.0043707 | -0.023224 | 0.13811 | 0.0012668 | -0.0059366 | -0.0019568 | -0.0027302 | 0.0011643 | -12.561 | -2.1469 | -118.4647 | -2.4765 | -2.2934 | -117.3386 | -2.33 | 0.97046 | 5.1315 | 4.5502 | 4.9896 | 4.9347 | 4.8752 | 4.9576 | -0.32501 | -7.2052 | -7.5348 | 115.8463 | 115.8096 | 0.80109 | 116.1346 | 1.1261 | 122.6898 | 0.073242 | -0.068665 | 123.0743 | 123.0972 | 123.0148 | 0.40741 | 0.32501 | 116.1713 | 115.9882 | 0.38452 | 0.43945 | 116.3177 | 0.58136 | 115.9927 | 123.2712 | -123.523 | -0.50812 | 115.6631 | 123.1293 | 105.5786 | 119.1101
1903.4844 | 123.468 | -44.4901 | 78.6575 | -0.0042723 | 0.0024845 | 0.042631 | 0.0025933 | -0.00065586 | 0.0039158 | -0.00095273 | 0.0072936 | 0.0028861 | 0.004471 | 0.040633 | -0.0025976 | -0.0023028 | 0.00052346 | -1.5518 | -1.1993 | -44.5999 | -1.4603 | -1.3184 | -44.9249 | -1.3596 | 2.4857 | 78.6072 | 2.0645 | 78.7308 | 2.5131 | 2.3666 | 2.4399 | -0.10986 | -79.8569 | -80.1178 | 43.1717 | 43.1305 | -0.43488 | 43.2404 | -0.32501 | 46.5546 | -0.050354 | 0.073242 | 47.0032 | 46.9299 | 46.8567 | 0.37537 | 0.30212 | 43.2816 | 43.1396 | 0.44861 | 76.6663 | 43.4006 | 76.5427 | 43.2907 | 123.0972 | -123.2574 | -76.593 | 43.0298 | 123.2208 | 42.9382 | 46.9757
1904.5469 | 123.468 | -44.5862 | 78.5202 | 0.010986 | 0.0024845 | 0.04199 | 0.0060113 | 0.0021213 | 0.00092498 | -0.0024481 | 0.010345 | 0.0016043 | 0.0057528 | 0.038497 | -0.0015296 | -0.003371 | 0.0015915 | -2.298 | -1.3458 | -44.9524 | -1.7853 | -1.6296 | -45.3781 | -1.6479 | 1.7899 | 78.5706 | 2.0142 | 78.6163 | 2.4445 | 2.2934 | 2.3849 | -0.36621 | -79.866 | -80.3055 | 42.9565 | 42.9382 | -0.79193 | 43.3044 | -0.42572 | 46.6003 | 0.050354 | 0.09613 | 47.0306 | 46.9711 | 46.8796 | 0.37079 | 0.27924 | 43.3228 | 43.1671 | 0.4303 | 76.6022 | 43.6066 | 76.5564 | 43.2404 | 123.1567 | -123.4726 | -76.506 | 42.8009 | 123.2025 | 42.2882 | 46.376
1905.4844 | 122.6898 | -43.9911 | 79.2755 | 0.056763 | 0.0054751 | 0.040067 | 0.0057977 | 0.0021213 | 0.0045566 | -0.00031193 | -0.023224 | 0.0035269 | 0.0036166 | 0.032943 | -0.0028112 | -0.0025164 | -0.0013991 | -2.005 | -1.5381 | -44.22 | -1.9775 | -1.8356 | -43.7988 | -1.8356 | 1.973 | 79.3304 | 2.0599 | 79.2297 | 2.3849 | 2.2339 | 2.1606 | -0.22888 | -80.8136 | -81.2531 | 42.1555 | 42.1555 | 0.19226 | 42.3843 | 0.42114 | 46.051 | 0.054931 | -0.045777 | 46.376 | 46.1517 | 46.225 | 0.10071 | 0.17395 | 42.3843 | 42.2424 | 0.32501 | 77.1698 | 42.6819 | 77.2705 | 42.453 | 123.3215 | -123.4955 | -77.2156 | 42.0136 | 123.2208 | 41.9861 | 45.9641
1906.4844 | 122.7127 | -43.6569 | 79.5593 | 0.010986 | 0.00034827 | 0.040494 | 0.0040887 | -1.486e-05 | 0.0037022 | -0.0026617 | -0.026276 | 0.0024589 | 0.0036166 | 0.041915 | -0.0028112 | -0.0012348 | 0.00095066 | -1.6205 | -1.2405 | -43.895 | -1.6891 | -1.5472 | -43.4326 | -1.5564 | 1.5472 | 79.66 | 2.1194 | 79.5593 | 2.4536 | 2.3026 | 2.298 | -0.23804 | -80.7999 | -81.2485 | 42.1097 | 42.1005 | 0.2243 | 42.3386 | 0.46234 | 45.7764 | 0.10071 | 0 | 46.1105 | 45.9549 | 45.9595 | 0.17853 | 0.1831 | 42.3477 | 42.2058 | 0.33417 | 77.4399 | 42.6544 | 77.5406 | 42.4164 | 123.317 | -123.4543 | -77.4399 | 41.9678 | 123.2162 | 42.0364 | 45.2042
1907.5469 | 123.4085 | -44.5175 | 78.6621 | -0.080566 | 0.00077547 | 0.041776 | 0.0021661 | -0.0036465 | 0.0034884 | -0.0015935 | 0.025604 | 0.0024589 | 0.0046848 | 0.033584 | -0.0036658 | -0.0035846 | 0.00030966 | -1.7807 | -1.2726 | -44.8242 | -1.5747 | -1.442 | -44.5816 | -1.4557 | 1.7487 | 78.6942 | 2.1515 | 78.7491 | 2.5726 | 2.4445 | 2.5177 | -0.3067 | -79.9347 | -80.2368 | 43.0756 | 43.0618 | -0.064087 | 43.3685 | 0.24262 | 46.669 | 0.032044 | 0.086975 | 47.0901 | 47.0352 | 46.962 | 0.36621 | 0.29297 | 43.3823 | 43.2495 | 0.42114 | 76.5976 | 43.5516 | 76.5427 | 43.2449 | 123.2117 | -123.4863 | -76.5106 | 42.9428 | 123.2666 | 42.7368 | 46.2662
1908.4844 | 123.1064 | -14.8682 | 107.547 | -0.042419 | 0.0016299 | 0.010374 | 0.0045159 | -0.0032193 | 0.057749 | -0.0033025 | 0.043915 | 0.00074988 | 0.0029758 | 0.056441 | -0.0019568 | -0.0040118 | -0.0016129 | -2.2522 | -1.9272 | -14.9826 | -2.2247 | -2.0599 | -4.9255 | -2.0828 | 2.2339 | 108.3893 | 2.9434 | 108.4717 | 3.4332 | 3.3005 | 3.36 | -0.11444 | -109.4742 | -109.7717 | 12.8082 | 12.7853 | 9.9426 | 12.8998 | 10.0571 | 17.8116 | 0.84228 | 0.92468 | 18.3014 | 18.2281 | 18.1686 | 0.41656 | 0.35706 | 12.9227 | 12.7579 | 0.48981 | 105.5283 | 13.0554 | 105.4459 | 12.941 | 123.2574 | -122.5296 | -104.6036 | 12.6434 | 123.3398 | 12.616 | 17.1021
1909.4844 | 121.1884 | -15.3168 | 107.8445 | -0.057678 | 0.0035525 | 0.0090917 | -0.00018368 | 0.0027621 | 0.056681 | -9.8328e-05 | 0.040863 | 0.0028861 | 0.003403 | 0.0558 | -0.0019568 | -0.001662 | -0.00033114 | -2.7054 | -2.4536 | -15.4312 | -2.7649 | -2.5864 | -5.6717 | -2.6413 | 1.68 | 107.5745 | 2.9572 | 107.8079 | 3.4058 | 3.3096 | 3.3234 | -0.11444 | -110.2982 | -110.6094 | 12.7304 | 12.6755 | 9.6451 | 12.7899 | 9.7595 | 18.2739 | -0.27008 | -0.036621 | 18.7225 | 18.6401 | 18.6264 | 0.36621 | 0.35248 | 12.8448 | 12.6663 | 0.44861 | 104.8508 | 12.9776 | 104.6173 | 12.8632 | 122.8912 | -123.2758 | -104.8874 | 12.5519 | 123.1247 | 12.6114 | 16.9968
1910.5469 | 123.1155 | -15.4266 | 107.135 | -0.13397 | 0.00098907 | 0.010587 | 0.0019525 | -0.0023649 | 0.056253 | -0.0013799 | 0.025604 | 0.0020315 | 0.0025484 | 0.051955 | -0.0021704 | -0.0029438 | 0.0015915 | -2.6321 | -2.3209 | -15.2481 | -2.6779 | -2.4994 | -5.6488 | -2.5269 | 1.7303 | 107.5012 | 2.9526 | 107.84 | 3.36 | 3.2547 | 3.3279 | 0.17853 | -109.4559 | -109.8129 | 12.9272 | 12.8998 | 9.7778 | 12.7213 | 9.5993 | 18.3792 | 0.36621 | 0.70496 | 18.7866 | 18.7546 | 18.6813 | 0.37537 | 0.30212 | 12.7487 | 12.5702 | 0.40741 | 104.8874 | 12.9272 | 104.5486 | 13.1058 | 122.9279 | -122.3831 | -104.1824 | 12.7487 | 123.2666 | 12.7945 | 17.157
1911.4844 | 105.0522 | -15.2939 | 87.9181 | -0.24841 | 0.0016299 | 0.0080237 | -0.0036017 | -0.0030057 | 0.054972 | 0.0024653 | -0.20328 | 0.0011771 | -0.0032194 | 0.057937 | -0.002384 | -0.0014484 | -0.0069533 | -2.5635 | -1.9272 | -15.033 | -2.7924 | -2.504 | -3.5568 | -2.5406 | 1.2405 | 103.9581 | 2.9526 | 102.3239 | 3.4241 | 3.4378 | 3.3325 | 0.26093 | -89.8453 | -90.7104 | 12.7899 | 12.7533 | 11.7371 | 12.4924 | 11.4761 | 18.2465 | 16.04 | 14.4058 | 18.718 | 18.6264 | 18.7317 | 0.37994 | 0.48523 | 12.529 | 12.2406 | 0.4715 | 99.3713 | 13.1058 | 101.0056 | 13.3667 | 119.252 | -102.9511 | -84.9655 | 12.5015 | 117.6178 | 12.7304 | 16.5344
1912.4844 | 122.7676 | -15.0513 | 107.3547 | -0.057678 | 0.0012027 | 0.010374 | 0.0010981 | -0.0049283 | 0.055399 | 0.00054267 | 0.13242 | 0.0013907 | 0.0036166 | 0.051528 | -0.0025976 | -0.0027302 | 0.0033005 | -2.6001 | -2.3438 | -15.1749 | -2.6138 | -2.4765 | -5.7999 | -2.7283 | 1.3 | 107.2678 | 3.0167 | 108.0734 | 3.4836 | 3.3096 | 3.3691 | -0.1236 | -109.6985 | -109.9686 | 12.5748 | 12.323 | 9.2514 | 12.4466 | 9.375 | 18.0679 | -0.086975 | 0.71869 | 18.5349 | 18.4204 | 18.3609 | 0.35248 | 0.29297 | 12.6984 | 12.561 | 0.46692 | 105.0568 | 12.8311 | 104.2511 | 12.7075 | 122.319 | -122.5296 | -104.3381 | 12.4374 | 123.1247 | 12.4512 | 16.3513
1913.5469 | 123.5458 | -44.7098 | 78.3463 | 0.0033567 | 0.0012027 | 0.042417 | 0.0032343 | -0.00044226 | -0.0014248 | -0.0043707 | 0.050018 | 0.0013907 | 0.004471 | 0.042769 | -0.0015296 | -0.001662 | -0.00097194 | -1.5244 | -1.2405 | -45.0806 | -1.5656 | -1.3916 | -44.9432 | -1.387 | 1.1719 | 78.4149 | 2.3346 | 78.4836 | 2.7786 | 2.6642 | 2.7374 | -0.37079 | -79.5868 | -79.9118 | 43.3182 | 43.3228 | -0.23346 | 43.6935 | 0.13733 | 47.0444 | 0.068665 | 0.13733 | 47.4884 | 47.4472 | 47.374 | 0.40283 | 0.32959 | 43.689 | 43.515 | 0.44403 | 76.149 | 43.84 | 76.0803 | 43.4692 | 123.1247 | -123.4268 | -76.0117 | 43.1442 | 123.1934 | 43.1854 | 45.8817
1914.4844 | 123.4451 | -44.1925 | 78.9276 | -0.080566 | 0.0016299 | 0.041563 | 0.0043023 | -0.0040739 | 0.0028476 | -9.8328e-05 | 0.074432 | 0.0039541 | 0.0025484 | 0.040206 | -0.0043066 | -0.0063618 | 0.0026597 | -1.5152 | -1.2817 | -44.4672 | -1.5839 | -1.3916 | -44.5724 | -1.4648 | 1.2405 | 78.6942 | 2.4033 | 79.0741 | 2.6459 | 2.7145 | 2.742 | -0.27466 | -80.2094 | -80.5115 | 42.8009 | 42.7277 | -0.37994 | 43.0023 | -0.10529 | 46.5958 | -0.23346 | 0.14648 | 46.8384 | 46.9345 | 46.907 | 0.33875 | 0.31128 | 43.0756 | 42.8833 | 0.24262 | 76.6708 | 43.1854 | 76.2909 | 42.9108 | 122.8867 | -123.3948 | -76.5244 | 42.6086 | 123.2666 | 42.6773 | 45.433
1915.4844 | 123.3673 | -44.7601 | 78.5156 | -0.40863 | 0.00034827 | 0.042631 | 0.0060113 | -0.0012967 | -0.0012112 | -0.0015935 | -0.020172 | 0.0018179 | 0.0036166 | 0.039138 | -0.0017432 | -0.0020892 | 0.0035141 | -1.5427 | -1.1993 | -45.0394 | -1.6617 | -1.5198 | -44.751 | -1.5106 | 1.149 | 78.5431 | 2.298 | 78.4653 | 2.6459 | 2.2293 | 2.2568 | -0.27924 | -79.715 | -80.1773 | 43.2404 | 43.2495 | 0.009155 | 43.5287 | 0.28839 | 47.0581 | 0.027466 | -0.050354 | 47.406 | 47.0169 | 46.9894 | -0.041199 | -0.068665 | 43.5196 | 43.3777 | 0.3479 | 76.1673 | 43.84 | 76.2451 | 43.5608 | 123.3032 | -123.555 | -76.2177 | 43.0984 | 123.2254 | 43.2175 | 45.9091
1916.5469 | 123.4589 | -44.7968 | 78.3737 | -0.042419 | -0.00050633 | 0.040708 | 0.0028069 | -0.0032193 | 0.0015658 | -0.0033025 | 0.059174 | 0.0022453 | 0.0040438 | 0.039779 | -0.0047338 | -0.0031574 | 0.0026597 | -1.6525 | -1.3687 | -45.1218 | -1.68 | -1.5244 | -45.0302 | -1.5289 | 1.3 | 78.4378 | 2.3117 | 78.4836 | 2.7374 | 2.6093 | 2.6505 | -0.32501 | -79.7424 | -80.0537 | 43.2724 | 43.2678 | -0.23346 | 43.5928 | 0.091553 | 47.1085 | 0.064087 | 0.10986 | 47.5342 | 47.4472 | 47.406 | 0.33874 | 0.29755 | 43.5974 | 43.4418 | 0.42572 | 76.1719 | 43.7531 | 76.1261 | 43.428 | 123.2346 | -123.4955 | -76.062 | 43.1168 | 123.2803 | 43.1442 | 46.0968
1917.4844 | 123.3673 | -45.0989 | 78.1494 | -0.019531 | 0.0014163 | 0.043699 | 0.0047295 | 0.0012667 | 0.00071138 | -0.0026617 | 0.019501 | 0.0026725 | 0.0019076 | 0.038924 | -0.0032386 | -0.0025164 | 0.00073706 | -1.8539 | -1.6022 | -45.2774 | -1.9318 | -1.767 | -45.1172 | -1.8082 | 1.1353 | 78.2318 | 2.2934 | 78.1906 | 2.655 | 2.4811 | 2.5131 | -0.17853 | -79.7516 | -80.0812 | 43.3319 | 43.2907 | -0.01831 | 43.4692 | 0.16022 | 47.3923 | 0.082398 | 0.041199 | 47.7539 | 47.612 | 47.58 | 0.21973 | 0.18768 | 43.5104 | 43.3456 | 0.36163 | 75.8972 | 43.6752 | 75.9384 | 43.4967 | 123.3307 | -123.4268 | -75.856 | 43.1671 | 123.2895 | 43.2449 | 46.2341
1918.5469 | 123.381 | -45.0302 | 78.2089 | -0.65277 | -0.0020017 | 0.040281 | 0.0028069 | -0.0017239 | 0.0019932 | 0.00096987 | -0.11783 | 0.0022453 | 0.0048984 | 0.044265 | -0.0021704 | -0.0014484 | 0.0024461 | -1.8402 | -1.5015 | -45.282 | -1.9272 | -1.7944 | -45.1447 | -1.8219 | 1.355 | 78.3005 | 2.2385 | 78.2684 | 2.5818 | 2.4353 | 2.449 | -0.25177 | -79.7104 | -80.1361 | 43.2358 | 43.2083 | -0.11444 | 43.4601 | 0.13733 | 47.2687 | 0.091553 | 0.05951 | 47.612 | 47.4792 | 47.4655 | 0.21057 | 0.19684 | 43.4875 | 43.3548 | 0.34332 | 76.03 | 43.7805 | 76.062 | 43.5287 | 123.3307 | -123.4909 | -75.9705 | 43.103 | 123.2986 | 43.19 | 46.3852
1919.4844 | 122.9736 | -44.9478 | 78.2867 | -0.065308 | 0.0024845 | 0.041563 | 0.0062249 | 0.00083954 | 0.00071138 | -0.0030889 | -0.032379 | 0.0060905 | 0.0040438 | 0.040633 | -0.0008886 | 0.00068782 | -0.00097194 | -1.6891 | -1.3412 | -45.2316 | -1.712 | -1.3779 | -45.076 | -1.7349 | 1.2039 | 78.4058 | 2.1332 | 78.2822 | 2.4261 | 2.2614 | 2.1652 | -0.28381 | -79.628 | -79.9988 | 43.5699 | 43.2129 | -0.12817 | 43.4967 | 0.15564 | 47.081 | 0.11902 | -0.004577 | 47.374 | 47.113 | 47.2092 | 0.032043 | 0.12817 | 43.8538 | 43.5196 | 0.29297 | 76.149 | 43.8904 | 76.2726 | 43.6066 | 123.3536 | -123.5184 | -76.1536 | 43.2358 | 123.23 | 43.2587 | 46.1517
1920.4844 | 123.468 | -44.989 | 78.2089 | -0.03479 | 0.0029117 | 0.042844 | 0.0040887 | -0.0015103 | 0.0037022 | -0.0030889 | 0.05307 | 0.00096348 | 0.003403 | 0.044692 | -0.000675 | -0.003371 | -0.00033114 | -1.6113 | -1.3733 | -45.2545 | -1.6754 | -1.474 | -45.1218 | -1.5472 | 1.2085 | 78.2822 | 2.0782 | 78.2547 | 2.6184 | 2.1011 | 2.2614 | -0.2655 | -79.5822 | -79.8843 | 43.515 | 43.4418 | -0.13275 | 43.7073 | 0.13275 | 47.0673 | 0.073243 | 0.045777 | 47.6074 | 47.2504 | 47.0901 | 0.18311 | 0.022888 | 43.7805 | 43.5791 | 0.54016 | 76.1765 | 43.8812 | 76.2039 | 43.6157 | 123.2712 | -123.4634 | -76.1307 | 43.3136 | 123.2437 | 43.3777 | 46.1975
1921.4844 | 122.6166 | -44.9615 | 78.3188 | -0.042419 | 0.0037661 | 0.042631 | 0.0036615 | 0.00041234 | -0.00035682 | -0.0033025 | -0.014069 | 0.0016043 | 0.0046848 | 0.036788 | -0.003025 | -0.0046528 | 0.0026597 | -1.6067 | -1.3367 | -45.1721 | -1.7258 | -1.5427 | -45.1904 | -1.5884 | 0.97961 | 78.3737 | 2.2659 | 78.2776 | 2.6001 | 2.449 | 2.536 | -0.21057 | -79.6555 | -80.0446 | 43.4189 | 43.3731 | -0.22888 | 43.5837 | -0.018311 | 47.2275 | 0.054931 | -0.041199 | 47.5616 | 47.4976 | 47.4106 | 0.27008 | 0.18311 | 43.6295 | 43.4464 | 0.33417 | 76.0117 | 43.8354 | 76.1078 | 43.6249 | 123.3353 | -123.4909 | -76.0529 | 43.2358 | 123.2391 | 43.3548 | 45.9412
1922.4844 | 123.4543 | -44.8654 | 78.3188 | -0.03479 | 0.0016299 | 0.041563 | 0.0021661 | 0.00019874 | 0.00071138 | -0.0024481 | 0.028656 | 0.00096348 | 0.0055392 | 0.03807 | -0.0034522 | -0.0027302 | -0.00097194 | -1.5472 | -1.2772 | -45.1401 | -1.5564 | -1.4145 | -45.0851 | -1.442 | 1.181 | 78.3875 | 2.2293 | 78.4241 | 2.6779 | 2.536 | 2.6047 | -0.27466 | -79.5959 | -79.8752 | 43.4509 | 43.4235 | -0.21973 | 43.6981 | 0.054932 | 47.0947 | 0.068664 | 0.10528 | 47.5433 | 47.4701 | 47.4014 | 0.37537 | 0.3067 | 43.7256 | 43.5837 | 0.44861 | 76.1948 | 43.8629 | 76.1581 | 43.5883 | 123.2529 | -123.4589 | -76.0895 | 43.309 | 123.2895 | 43.3182 | 46.0464
1923.5469 | 123.3948 | -44.8013 | 78.392 | -0.027161 | 0.0026981 | 0.040922 | 0.0030207 | -0.0017239 | 0.00049778 | -0.0022345 | 0.043915 | 0.0028861 | 0.004471 | 0.03807 | -0.0051612 | -0.0040118 | -0.00011754 | -1.4603 | -1.2177 | -45.0714 | -1.4923 | -1.3321 | -44.989 | -1.355 | 1.0345 | 78.4698 | 2.3117 | 78.5019 | 2.7374 | 2.6001 | 2.6733 | -0.27008 | -79.6097 | -79.8843 | 43.4692 | 43.4464 | -0.18768 | 43.7164 | 0.082397 | 47.113 | 0.07782 | 0.10986 | 47.5388 | 47.4747 | 47.4014 | 0.36163 | 0.28839 | 43.7393 | 43.5791 | 0.42572 | 76.1902 | 43.8538 | 76.1581 | 43.5837 | 123.2712 | -123.4634 | -76.0803 | 43.309 | 123.3032 | 43.3411 | 45.8359
1924.4844 | 123.0652 | -44.7647 | 78.4241 | 0.010986 | 0.0026981 | 0.043272 | 0.0040887 | -0.00022866 | 0.0013522 | -0.0071477 | 0.062225 | 0.0016043 | 0.001694 | 0.040633 | -0.0055884 | -0.0042254 | -0.0018265 | -1.4603 | -1.2039 | -45.0073 | -1.561 | -1.2131 | -45.1813 | -1.474 | 0.96588 | 78.4927 | 2.3438 | 78.5339 | 2.7832 | 2.6413 | 2.7191 | -0.24261 | -79.628 | -79.985 | 43.5516 | 43.2907 | -0.41656 | 43.5333 | -0.17395 | 47.1085 | 0.068665 | 0.10986 | 47.5479 | 47.4838 | 47.406 | 0.37537 | 0.29755 | 43.7942 | 43.4463 | 0.43945 | 76.1902 | 43.8034 | 76.149 | 43.5608 | 123.2574 | -123.4314 | -76.0803 | 43.2037 | 123.2986 | 43.3044 | 45.7306
1925.4844 | 122.6303 | -44.6457 | 78.4515 | -0.16449 | 0.00077547 | 0.041563 | 0.0066523 | -0.00022866 | 0.00028418 | -0.0011663 | -0.020172 | 0.00074988 | 0.0029758 | 0.042983 | -0.0025976 | 0.00026062 | -0.0022537 | -1.5335 | -1.2039 | -45.0943 | -1.6251 | -1.474 | -45.0943 | -1.5198 | 0.89722 | 78.5156 | 2.33 | 78.3783 | 2.6825 | 2.5314 | 2.6093 | -0.44861 | -79.6555 | -80.0766 | 43.1717 | 43.1259 | -0.44861 | 43.5745 | 0 | 46.9757 | 0.064087 | -0.073242 | 47.3282 | 47.2549 | 47.1771 | 0.27924 | 0.20142 | 43.6203 | 43.4692 | 0.35248 | 76.0483 | 43.8904 | 76.1856 | 43.4418 | 123.1613 | -123.5458 | -76.1215 | 43.0206 | 123.024 | 43.1122 | 45.5429
1926.5469 | 123.4131 | -44.8013 | 78.3966 | -0.019531 | 0.0026981 | 0.043912 | 0.0032343 | 0.00019874 | 0.00071138 | -0.0015935 | 0.028656 | 0.0033133 | 0.0048984 | 0.038497 | -0.002384 | -0.0018756 | 0.0011643 | -1.5427 | -1.2451 | -45.0623 | -1.5884 | -1.4511 | -45.0485 | -1.4786 | 0.77362 | 78.4012 | 2.3621 | 78.4607 | 2.7924 | 2.6688 | 2.7374 | -0.26093 | -79.6417 | -79.985 | 43.3502 | 43.3228 | -0.24719 | 43.5837 | 0.013733 | 47.1634 | 0.004578 | 0.064087 | 47.5937 | 47.5388 | 47.4701 | 0.37537 | 0.3067 | 43.6111 | 43.4738 | 0.4303 | 76.0986 | 43.8171 | 76.0391 | 43.5562 | 123.2025 | -123.4589 | -76.0345 | 43.2129 | 123.262 | 43.2587 | 45.575
1927.4844 | 122.9324 | -44.7052 | 78.4653 | -0.072937 | 0.0033389 | 0.042203 | 0.0028069 | -0.0010831 | 0.00049778 | -0.00073913 | -0.0079652 | 0.0028861 | 0.0059664 | 0.04042 | -0.0008886 | -0.00059378 | -0.00075834 | -1.4694 | -1.1765 | -45.0073 | -1.5701 | -1.4282 | -45.0485 | -1.4557 | 0.87433 | 78.5797 | 2.3987 | 78.4378 | 2.7512 | 2.6184 | 2.6825 | -0.30212 | -79.6417 | -80.0354 | 43.277 | 43.2495 | -0.34332 | 43.5516 | -0.041199 | 47.1039 | 0.11444 | -0.027466 | 47.4564 | 47.3877 | 47.3236 | 0.28381 | 0.21973 | 43.5791 | 43.4372 | 0.35248 | 76.0391 | 43.8309 | 76.181 | 43.5287 | 123.2849 | -123.4726 | -76.0666 | 43.1351 | 123.143 | 43.2358 | 45.5795
1928.5469 | 123.3994 | -44.9615 | 78.2776 | -0.0042723 | 0.0020573 | 0.042203 | 0.0045159 | -0.00065586 | -0.00099762 | -0.0011663 | 0.0072936 | 0.0016043 | 0.0027622 | 0.043624 | -0.0036658 | -0.001662 | -0.0024673 | -1.7578 | -1.4923 | -45.1263 | -1.8219 | -1.6617 | -45.1218 | -1.7029 | 1.0254 | 78.3783 | 2.4445 | 78.3051 | 2.6917 | 2.6093 | 2.7466 | -0.16479 | -79.7699 | -80.0995 | 43.2999 | 43.2587 | -0.16022 | 43.4235 | 0.004578 | 47.406 | 0.10071 | 0.027466 | 47.6532 | 47.7081 | 47.5708 | 0.30212 | 0.16479 | 43.4647 | 43.3044 | 0.24719 | 75.8606 | 43.634 | 75.9338 | 43.4692 | 123.3398 | -123.4039 | -75.8331 | 43.1396 | 123.2666 | 43.2037 | 45.9869
1929.4844 | 123.2986 | -44.6594 | 78.5339 | -0.17212 | 0.0039799 | 0.041349 | 0.0043023 | -0.0027921 | 0.00049778 | -0.0045843 | 0.034759 | 0.00074988 | 0.0029758 | 0.040206 | -0.0036658 | -0.0027302 | -0.0026809 | -1.4236 | -1.2131 | -44.9661 | -1.4694 | -1.3092 | -44.8837 | -1.3962 | 1.1581 | 78.6072 | 2.4582 | 78.6118 | 2.8793 | 2.7603 | 2.8198 | -0.3067 | -79.747 | -80.0034 | 43.3502 | 43.2632 | -0.2243 | 43.5699 | 0.082397 | 47.1176 | 0.073242 | 0.077819 | 47.5388 | 47.4792 | 47.4197 | 0.36163 | 0.30212 | 43.6569 | 43.4967 | 0.42114 | 76.1536 | 43.7531 | 76.149 | 43.4464 | 123.2666 | -123.5001 | -76.0757 | 43.19 | 123.2712 | 43.2358 | 45.8176
1930.5469 | 123.4406 | -44.632 | 78.5339 | -0.12634 | 0.0033389 | 0.04199 | 0.0032343 | 0.00019874 | -0.00014322 | -0.0037299 | -0.029327 | 0.0026725 | 0.0021212 | 0.034652 | -0.0028112 | 0.00047422 | 0.0024461 | -1.8951 | -1.1993 | -44.9249 | -1.4328 | -1.2863 | -44.9936 | -1.4053 | 1.2497 | 78.5797 | 2.4445 | 78.6392 | 2.8564 | 2.7512 | 2.8473 | -0.29297 | -79.7333 | -79.9667 | 43.3456 | 43.2266 | -0.36163 | 43.5196 | -0.068664 | 47.0764 | 0.045776 | 0.10529 | 47.4884 | 47.4792 | 47.3831 | 0.40283 | 0.3067 | 43.6386 | 43.4921 | 0.41199 | 76.1948 | 43.7256 | 76.1353 | 43.4326 | 123.2117 | -123.4589 | -76.0895 | 43.1992 | 123.2712 | 42.7368 | 45.8817
1931.4844 | 123.0011 | -44.7922 | 78.447 | -0.2179 | 0.0029117 | 0.041776 | 0.0049433 | -0.00065586 | 0.00028418 | -0.0030889 | -0.05069 | 0.00074988 | 0.003403 | 0.046401 | -0.0025976 | -0.0020892 | -0.00011754 | -2.2797 | -1.3229 | -45.0943 | -1.7578 | -1.6067 | -45.076 | -1.6479 | 0.98877 | 78.5477 | 2.3895 | 78.4103 | 2.7328 | 2.5818 | 2.6642 | -0.30212 | -79.7699 | -80.2048 | 43.1854 | 43.1442 | -0.28381 | 43.4464 | 0.01831 | 47.1817 | 0.10071 | -0.036621 | 47.525 | 47.4564 | 47.374 | 0.27466 | 0.19226 | 43.4875 | 43.3365 | 0.34332 | 76.0208 | 43.7714 | 76.1581 | 43.4692 | 123.3398 | -123.5413 | -76.0574 | 43.0344 | 123.2025 | 42.5125 | 45.7809
1932.4844 | 123.4406 | -44.751 | 78.4561 | -0.042419 | 0.0022709 | 0.041349 | 0.0025933 | 0.00041234 | 0.0015658 | -0.0013799 | 0.019501 | 0.0026725 | 0.0012668 | 0.043624 | -0.0028112 | -0.0023028 | 0.0020187 | -1.5839 | -1.3596 | -45.0577 | -1.6296 | -1.4648 | -44.9661 | -1.4191 | 0.94757 | 78.5019 | 2.4628 | 78.5248 | 2.9205 | 2.7924 | 2.8473 | -0.3067 | -79.8157 | -80.0858 | 43.2861 | 43.3319 | -0.21515 | 43.6386 | 0.091553 | 47.2137 | 0.045776 | 0.068664 | 47.6715 | 47.5983 | 47.5433 | 0.38452 | 0.32959 | 43.5928 | 43.428 | 0.45776 | 76.062 | 43.6981 | 76.0391 | 43.3914 | 123.2529 | -123.5138 | -75.9933 | 43.1213 | 123.2758 | 43.1671 | 45.6985
1933.5 | 122.7631 | -44.5221 | 78.4744 | -0.24841 | 0.023847 | 0.032804 | -0.0027473 | 0.034165 | -0.014669 | 0.050103 | -0.27957 | 0.013567 | -0.0072782 | 0.033156 | -0.005802 | -0.010421 | 0.00073706 | -2.3804 | -1.3641 | -45.0897 | -1.7715 | -1.6434 | -45.1447 | -1.7075 | 1.0208 | 78.5385 | 2.504 | 78.3463 | 2.8152 | 2.6688 | 2.7969 | -0.56763 | -79.8386 | -80.246 | 42.8787 | 42.8146 | -0.62256 | 43.3823 | -0.054931 | 47.0261 | 0.064087 | -0.12817 | 47.3373 | 47.319 | 47.1909 | 0.29297 | 0.1648 | 43.4464 | 43.3182 | 0.31128 | 75.8423 | 43.7256 | 76.0345 | 43.158 | 123.0606 | -123.5641 | -75.9705 | 42.7505 | 122.8683 | 42.1417 | 45.5429
1934.4844 | 123.4177 | -44.7464 | 78.4378 | -0.027161 | 0.00056187 | 0.043912 | 0.0025933 | -0.0038603 | 0.0017794 | -0.0028753 | -0.0018616 | 0.0020315 | 0.001694 | 0.04042 | -0.0085792 | -0.00508 | -0.0016129 | -1.6159 | -1.3824 | -45.0119 | -1.6617 | -1.4694 | -44.9341 | -1.5518 | 1.3138 | 78.5339 | 2.5681 | 78.5797 | 2.829 | 2.8793 | 2.9846 | -0.2655 | -79.8203 | -80.0995 | 43.277 | 43.1946 | -0.18768 | 43.4601 | 0.07782 | 47.3145 | 0.096131 | 0.14191 | 47.5754 | 47.731 | 47.6257 | 0.41656 | 0.31128 | 43.5425 | 43.3502 | 0.26092 | 76.0117 | 43.6295 | 75.9659 | 43.364 | 123.2803 | -123.4497 | -75.8698 | 43.0847 | 123.3261 | 43.1305 | 46.0602
1935.4844 | 122.7539 | -44.8196 | 78.4744 | -0.065308 | 0.0018435 | 0.041563 | 0.0040887 | 0.0046847 | 0.0015658 | 0.00032907 | -0.032379 | 0.0024589 | 0.0029758 | 0.037429 | -0.0021704 | -0.0020892 | -0.0020401 | -1.6983 | -1.4053 | -45.0714 | -1.8036 | -1.6479 | -45.0256 | -1.712 | 1.0117 | 78.5385 | 2.655 | 78.4424 | 3.0258 | 2.8519 | 2.916 | -0.25177 | -79.8798 | -80.278 | 43.1717 | 43.1076 | -0.20599 | 43.3594 | 0.045776 | 47.4747 | 0.064087 | -0.032043 | 47.8455 | 47.7356 | 47.6715 | 0.26093 | 0.19684 | 43.4235 | 43.2678 | 0.37079 | 75.7874 | 43.6661 | 75.8835 | 43.4143 | 123.3582 | -123.5458 | -75.8194 | 43.0161 | 123.262 | 43.1213 | 45.8313
1936.5469 | 123.1018 | -46.225 | 77.2888 | -0.26367 | 0.0039799 | 0.043699 | 0.0023797 | -0.0015103 | 0.0024204 | -0.00095273 | -0.035431 | 0.0011771 | 0.0012668 | 0.040206 | -0.0011022 | -0.0014484 | 0.0024461 | -4.0146 | -2.1103 | -45.4605 | -2.3941 | -2.2018 | -45.3827 | -2.2842 | 1.4786 | 78.1265 | 2.3483 | 73.5214 | 3.1128 | 4.9896 | 4.2114 | 0.76447 | -79.3991 | -79.6829 | 44.0231 | 43.9407 | 0.84229 | 43.1763 | 0.07782 | 48.5733 | 0.83771 | -3.7674 | 49.3378 | 50.4364 | 51.2146 | 1.8631 | 2.6413 | 43.2587 | 43.0664 | 0.76446 | 71.1731 | 43.3502 | 75.7782 | 44.1147 | 124.3515 | -122.7493 | -74.9405 | 43.8309 | 119.7464 | 42.2104 | 47.7036
1937.4844 | 123.1155 | -44.6457 | 78.5614 | -0.042419 | 0.0014163 | 0.038358 | 0.0034479 | 0.0016939 | 0.00071138 | -0.00031193 | 0.010345 | 0.0018179 | 0.0038302 | 0.033584 | -0.0019568 | -0.0027302 | -0.00011754 | -3.891 | -1.355 | -44.9432 | -1.6388 | -1.4374 | -44.8517 | -1.5289 | 1.1353 | 78.6392 | 2.6871 | 78.6392 | 3.1219 | 2.9984 | 3.0579 | -0.29755 | -79.9164 | -80.2002 | 43.2083 | 43.1168 | -0.20599 | 43.4143 | 0.091552 | 47.3328 | 0.07782 | 0.07782 | 47.7676 | 47.7036 | 47.644 | 0.37079 | 0.31128 | 43.5059 | 43.3044 | 0.43488 | 75.9521 | 43.5883 | 75.9521 | 43.2907 | 123.2849 | -123.5046 | -75.8743 | 43.0069 | 123.2849 | 40.7547 | 45.7809
1938.5625 | 119.3939 | -44.1605 | 78.4149 | -0.46204 | -0.014178 | 0.033872 | 0.0025933 | -0.011337 | -0.0063382 | -0.01142 | -0.23685 | -0.010359 | -0.0098416 | 0.037429 | -0.0034522 | -0.013411 | -0.00054474 | -3.978 | -1.3 | -44.9707 | -1.6891 | -1.5427 | -44.9707 | -1.561 | 1.2131 | 78.6392 | 2.6413 | 78.3005 | 3.0121 | 2.8656 | 2.9617 | -0.81024 | -79.715 | -80.1041 | 42.6178 | 42.5995 | -0.81024 | 43.4097 | 0 | 46.8018 | 0.2243 | -0.11444 | 47.1725 | 47.1222 | 47.0261 | 0.32043 | 0.2243 | 43.428 | 43.2816 | 0.37079 | 75.6592 | 43.6707 | 75.9979 | 42.8604 | 122.7997 | -123.3856 | -75.7736 | 42.4713 | 122.4609 | 40.1825 | 45.3735
1939.4844 | 122.6715 | -44.4214 | 78.5202 | -0.16449 | 0.0029117 | 0.041349 | 0.0045159 | 0.00019874 | -0.00078402 | -0.0011663 | -0.084259 | 0.0024589 | 0.004471 | 0.035934 | -0.0008886 | -0.0031574 | -0.0011855 | -11.38 | -1.3596 | -45.0485 | -1.7578 | -1.6525 | -45.0531 | -1.6708 | 1.0986 | 78.5889 | 2.5955 | 78.4653 | 2.9434 | 2.7878 | 2.8656 | -0.62714 | -79.8798 | -80.278 | 42.7689 | 42.7506 | -0.63171 | 43.3777 | -0.004578 | 47.0169 | 0.068664 | -0.054932 | 47.3648 | 47.287 | 47.2092 | 0.27008 | 0.19226 | 43.396 | 43.2907 | 0.3479 | 75.8698 | 43.689 | 75.9933 | 43.0618 | 123.0103 | -123.5687 | -75.9247 | 42.6636 | 122.8867 | 33.0414 | 45.52
1940.4844 | 123.436 | -44.6594 | 78.5294 | -0.0042723 | 0.0022709 | 0.043485 | 0.0023797 | 0.00019874 | 7.0582e-05 | -0.0011663 | 0.028656 | 0.0045951 | 0.0029758 | 0.036788 | -0.0021704 | -0.003371 | 0.0035141 | -10.8032 | -1.1902 | -44.9295 | -1.4694 | -1.2863 | -44.8013 | -1.3504 | 1.3412 | 78.6163 | 2.3666 | 78.6621 | 2.774 | 2.655 | 2.7786 | -0.27008 | -79.7195 | -79.9988 | 43.3731 | 43.309 | -0.14191 | 43.5791 | 0.12817 | 47.0261 | 0.086975 | 0.13275 | 47.4335 | 47.438 | 47.3145 | 0.41199 | 0.28839 | 43.6432 | 43.4601 | 0.40741 | 76.2955 | 43.7393 | 76.2497 | 43.4692 | 123.2758 | -123.4589 | -76.1627 | 43.19 | 123.3215 | 33.8562 | 46.0007
1941.5469 | 123.2162 | -28.4088 | 94.6243 | -0.10345 | 0.0031253 | 0.022977 | 0.0047295 | -0.0015103 | 0.033609 | -0.0026617 | -0.044586 | 0.0030997 | 0.003403 | 0.047256 | -0.0019568 | -0.0044392 | -0.00075834 | -6.9489 | -2.9343 | -28.7018 | -3.2135 | -3.0396 | -23.1033 | -3.1036 | 1.6022 | 94.8807 | 3.1036 | 94.9173 | 3.5431 | 3.3966 | 3.511 | -0.29297 | -97.5586 | -97.8378 | 25.3693 | 25.3052 | 5.3055 | 25.5981 | 5.5984 | 31.5125 | 0.25635 | 0.29297 | 31.9519 | 31.9199 | 31.8054 | 0.40741 | 0.29297 | 25.6622 | 25.4883 | 0.43945 | 91.8137 | 25.7675 | 91.777 | 25.4745 | 123.2895 | -123.3261 | -91.5207 | 25.1953 | 123.3261 | 21.46 | 30.011
1942.4844 | 123.1705 | -25.1312 | 97.4213 | -0.03479 | 0.0037661 | 0.021482 | 0.0043023 | -0.0012967 | 0.032328 | -0.0030889 | 0.010345 | 0.00032248 | 0.003403 | 0.054092 | -0.0015296 | -0.0035846 | 0.0011643 | -5.4886 | -1.4053 | -25.383 | -1.6525 | -1.474 | -18.9194 | -1.561 | 1.886 | 98.1583 | 2.9709 | 98.172 | 3.4515 | 3.2913 | 3.36 | -0.25177 | -98.8266 | -99.0738 | 23.6572 | 23.5703 | 6.2119 | 23.822 | 6.4636 | 28.1021 | 0.737 | 0.75073 | 28.5828 | 28.4912 | 28.4225 | 0.3891 | 0.32043 | 23.909 | 23.7305 | 0.48065 | 95.2011 | 23.9777 | 95.1874 | 23.7259 | 123.2895 | -122.8043 | -94.4504 | 23.4787 | 123.3032 | 19.6426 | 27.0172
1943.5 | 122.7081 | -23.8129 | 98.2224 | -0.58411 | -0.0015743 | 0.019987 | 0.0021661 | -0.00044226 | 0.039377 | 0.0022517 | -0.062897 | 0.0052359 | 0.0031894 | 0.058791 | -0.0011022 | -0.0029438 | 0.0035141 | -5.3604 | -1.5564 | -24.0692 | -1.973 | -1.8448 | -17.8894 | -1.8723 | 1.7532 | 98.8403 | 3.0899 | 98.8083 | 3.7125 | 3.5385 | 3.5797 | -0.25635 | -99.7787 | -100.1953 | 21.9681 | 21.9406 | 5.9235 | 22.197 | 6.1798 | 26.9028 | 0.61798 | 0.58594 | 27.5253 | 27.3926 | 27.3514 | 0.48981 | 0.44861 | 22.2244 | 22.0963 | 0.62256 | 95.7184 | 22.5128 | 95.7504 | 22.2565 | 122.6532 | -122.2916 | -95.1324 | 21.8399 | 122.6212 | 18.4525 | 25.5661
1944.4844 | 123.5779 | -118.0115 | 5.2094 | -0.072937 | 0.0041935 | 0.12188 | 0.0049433 | -0.0021513 | 0.002634 | -0.0013799 | -0.032379 | 0.13875 | 0.0040438 | -0.0029458 | -0.001316 | -0.003371 | 0.0041551 | -26.9348 | -2.3026 | -118.364 | -2.6321 | -2.417 | -117.9565 | -2.4673 | 0.52185 | 5.2643 | 4.7333 | 5.0812 | 5.1178 | 5.0629 | 5.1315 | -0.35248 | -7.5119 | -7.8415 | 115.5945 | 115.5441 | 0.054932 | 115.8966 | 0.40741 | 122.7448 | 0.054931 | -0.12817 | 123.1293 | 123.143 | 123.0743 | 0.39825 | 0.32959 | 115.947 | 115.7318 | 0.38452 | 0.3479 | 116.0614 | 0.53101 | 115.7089 | 123.2758 | -123.5733 | -0.47607 | 115.3793 | 123.0927 | 91.0767 | 118.5333
1945.5625 | 123.3994 | -118.0023 | 5.3375 | 0.026245 | 0.0048343 | 0.12124 | 0.0045159 | 0.0014803 | 0.0022068 | -0.0045843 | -0.084259 | 0.13939 | 0.0038302 | -0.0025186 | -0.002384 | -0.0046528 | 0.0013779 | -27.0584 | -2.1652 | -118.3136 | -2.6093 | -2.4582 | -117.8284 | -2.4765 | 0.45319 | 5.4153 | 4.8019 | 5.0674 | 5.072 | 5.0125 | 5.127 | -0.31128 | -7.5027 | -7.9468 | 115.5441 | 115.5258 | 0.17395 | 115.8371 | 0.48523 | 122.8043 | 0.07782 | -0.27008 | 123.0743 | 123.1293 | 123.0148 | 0.32501 | 0.21057 | 115.8554 | 115.7043 | 0.27008 | 0.2655 | 116.1484 | 0.6134 | 115.8371 | 123.4177 | -123.6511 | -0.53558 | 115.3931 | 123.0698 | 90.9439 | 118.4555
1946.4844 | 123.4451 | -118.0435 | 5.2551 | -0.0042723 | 0.0063297 | 0.11975 | 0.0038751 | 0.0029757 | 0.002634 | -0.0047979 | -0.029327 | 0.13854 | 0.0019076 | -0.0089272 | -0.0019568 | -0.0029438 | 0.0026597 | -26.8295 | -2.1286 | -118.3228 | -2.4261 | -2.2522 | -117.8238 | -2.3026 | 0.62256 | 5.3101 | 4.7836 | 5.0995 | 5.1086 | 5.0583 | 5.1407 | -0.27924 | -7.3837 | -7.6813 | 115.7913 | 115.741 | 0.21973 | 116.0202 | 0.49896 | 122.8271 | 0.054932 | -0.15564 | 123.1522 | 123.1842 | 123.1018 | 0.35706 | 0.27466 | 116.0706 | 115.8966 | 0.32501 | 0.31586 | 116.1942 | 0.52643 | 115.9149 | 123.3536 | -123.5779 | -0.4715 | 115.6174 | 123.143 | 91.214 | 118.6661
1947.4844 | 123.381 | -118.2312 | 5.1178 | -0.050049 | 0.0048343 | 0.12231 | 0.0051569 | -0.00086946 | 0.0011386 | -0.0026617 | -0.078156 | 0.13875 | 0.0040438 | 0.00068579 | -0.0032386 | -0.0037982 | -0.00054474 | -28.125 | -2.2247 | -118.4875 | -2.6138 | -2.4445 | -121.6919 | -2.4719 | 0.59509 | 5.191 | 4.6143 | 4.9026 | 4.866 | 4.8248 | 4.9164 | -0.25635 | -7.3425 | -7.7316 | 115.7867 | 115.7593 | -3.4607 | 116.0156 | -3.2043 | 122.8455 | 0.073242 | -0.21515 | 123.0972 | 123.1476 | 123.056 | 0.30212 | 0.21057 | 116.0431 | 115.8737 | 0.25177 | 0.28839 | 116.2628 | 0.57678 | 116.0065 | 123.4222 | -123.6053 | -0.50354 | 115.6174 | 123.1338 | 90.1062 | 118.8263
1948.5625 | 123.4085 | -118.3136 | 5.04 | -0.072937 | 0.0050479 | 0.12188 | 0.0057977 | -0.0038603 | -0.00035682 | -0.0030889 | -0.14529 | 0.13597 | 0.0012668 | -0.0065774 | -0.0064428 | -0.015334 | -0.0016129 | -28.5324 | -2.3438 | -118.6249 | -2.742 | -2.5772 | -118.3136 | -2.6459 | 0.57678 | 5.1453 | 4.5593 | 4.834 | 4.8111 | 4.7195 | 4.8203 | -0.31128 | -7.3837 | -7.782 | 115.7364 | 115.6677 | 0 | 115.979 | 0.31128 | 122.8729 | 0.10529 | -0.20599 | 123.1247 | 123.1338 | 123.0331 | 0.26092 | 0.16022 | 116.0477 | 115.8829 | 0.25177 | 0.27466 | 116.2811 | 0.58594 | 115.9698 | 123.4589 | -123.6649 | -0.48065 | 115.5716 | 123.1476 | 89.7812 | 118.8904
1949.4844 | 123.4406 | -118.4647 | 4.834 | -0.0042723 | 0.0052615 | 0.12146 | 0.0032343 | -0.00086946 | 0.00092498 | -9.8328e-05 | -0.020172 | 0.13918 | 0.0029758 | -0.00016881 | -0.0015296 | -0.0025164 | 0.0030869 | -21.0159 | -1.8539 | -118.7531 | -2.1881 | -2.005 | -126.8509 | -2.0599 | 0.50812 | 4.9072 | 4.3625 | 4.6371 | 4.6417 | 4.5868 | 4.6509 | -0.28839 | -6.6879 | -7.0221 | 116.4597 | 116.4047 | -8.3862 | 116.6931 | -8.0978 | 122.8271 | 0.073243 | -0.19684 | 123.1064 | 123.1155 | 123.0515 | 0.28839 | 0.2243 | 116.748 | 116.5649 | 0.27924 | 0.27466 | 116.8991 | 0.54474 | 116.6107 | 123.3719 | -123.587 | -0.4715 | 116.2766 | 123.1018 | 97.4487 | 118.9728
1950.5469 | 123.4543 | -118.3594 | 4.8889 | -0.065308 | 0.0046207 | 0.1221 | 0.0047295 | -0.0017239 | 0.00071138 | -0.0024481 | -0.059845 | 0.13875 | 0.005112 | -0.0065774 | -0.0028112 | -0.001662 | 0.00052346 | -24.4583 | -2.1332 | -118.6981 | -2.4307 | -2.2568 | -118.3228 | -2.3071 | 0.60425 | 4.953 | 4.4312 | 4.7882 | 4.7607 | 4.6875 | 4.8065 | -0.33875 | -7.0221 | -7.3196 | 116.1026 | 116.0522 | 0.036621 | 116.391 | 0.37537 | 122.7905 | 0.064087 | -0.10071 | 123.1201 | 123.1659 | 123.0469 | 0.37537 | 0.25635 | 116.4413 | 116.2674 | 0.32959 | 0.35706 | 116.5649 | 0.52185 | 116.2262 | 123.3124 | -123.587 | -0.45776 | 115.9287 | 123.1476 | 93.9011 | 118.9636
1951.4844 | 123.3719 | -118.4601 | 4.8981 | -0.0042723 | 0.0033389 | 0.12082 | 0.0038751 | -0.0010831 | 0.002634 | -0.0018073 | -0.078156 | 0.1396 | 0.004471 | -0.0012368 | -0.0019568 | -0.0027302 | 0.0041551 | -24.9756 | -2.2476 | -118.7485 | -2.6505 | -2.5131 | -118.3823 | -2.5269 | 0.45776 | 4.9759 | 4.3625 | 4.628 | 4.6509 | 4.5685 | 4.6509 | -0.28839 | -7.1457 | -7.5485 | 115.947 | 115.9332 | 0.07782 | 116.2216 | 0.36621 | 122.8226 | 0.07782 | -0.27008 | 123.111 | 123.111 | 123.0286 | 0.28839 | 0.20599 | 116.2354 | 116.098 | 0.28839 | 0.2655 | 116.5009 | 0.6134 | 116.2125 | 123.436 | -123.6465 | -0.53558 | 115.8096 | 123.0881 | 93.4845 | 118.9178
1952.4844 | 123.4818 | -118.5287 | 4.7745 | -0.019531 | 0.0029117 | 0.12082 | 0.0040887 | -0.0036465 | 0.0022068 | -0.0058661 | -0.026276 | 0.13896 | 0.0038302 | -0.01085 | -0.0004614 | -0.0029438 | -0.0011855 | -27.4979 | -2.3941 | -118.7988 | -2.6733 | -2.4857 | -118.3365 | -2.5635 | 0.6134 | 4.8294 | 4.2755 | 4.6509 | 4.6646 | 4.5914 | 4.6692 | -0.27008 | -7.1686 | -7.4478 | 116.0431 | 115.9653 | 0.19226 | 116.2354 | 0.46234 | 122.8043 | 0.054932 | -0.1236 | 123.1934 | 123.1979 | 123.1201 | 0.39368 | 0.31586 | 116.3132 | 116.1255 | 0.3891 | 0.37537 | 116.4047 | 0.55389 | 116.1346 | 123.3582 | -123.5733 | -0.49896 | 115.8554 | 123.1796 | 91.0309 | 119.1422
1953.5625 | 123.3856 | -119.0598 | 4.248 | -0.042419 | -0.01076 | 0.10544 | 0.0055841 | 0.00083954 | 0.0022068 | -9.8328e-05 | -0.14529 | 0.13725 | 0.0025484 | -0.002305 | -0.0017432 | -0.001662 | 0.0033005 | -21.8628 | -3.7125 | -119.4031 | -4.1885 | -4.0649 | -120.6573 | -4.1199 | 0.35706 | 4.3259 | 3.7079 | 3.9917 | 3.9551 | 3.8498 | 3.9642 | -0.34332 | -7.9605 | -8.4366 | 114.9948 | 114.9399 | -1.5976 | 115.2832 | -1.2543 | 122.7676 | 0.07782 | -0.25635 | 123.0148 | 123.024 | 122.9095 | 0.25635 | 0.14191 | 115.3381 | 115.2145 | 0.24719 | 0.28381 | 115.6906 | 0.61798 | 115.3473 | 123.3856 | -123.6511 | -0.54016 | 114.8712 | 123.0515 | 97.197 | 119.4168
1954.4844 | 123.436 | -118.7531 | 4.5456 | -0.050049 | 0.0033389 | 0.11889 | 0.0038751 | -0.0045011 | 0.00028418 | -0.0030889 | -0.053741 | 0.13811 | 0.0014804 | -0.0055094 | -0.0021704 | -0.0037982 | -0.0011855 | -21.3867 | -1.9409 | -119.0506 | -2.2797 | -2.0599 | -118.4967 | -2.1332 | 0.53101 | 4.6097 | 4.0283 | 4.4083 | 4.3854 | 4.3167 | 4.39 | -0.29755 | -6.4865 | -6.8253 | 116.6931 | 116.6199 | 0.25635 | 116.9174 | 0.55389 | 122.7814 | 0.064087 | -0.13733 | 123.1384 | 123.143 | 123.0698 | 0.36163 | 0.28839 | 116.9907 | 116.7709 | 0.35706 | 0.37994 | 117.1097 | 0.58136 | 116.8121 | 123.3627 | -123.5962 | -0.51727 | 116.4734 | 123.1613 | 97.3663 | 119.2841
1955.4844 | 122.644 | -45.8725 | 77.3987 | -0.019531 | 0.0037661 | 0.042631 | 0.0021661 | -0.0036465 | 0.00049778 | -0.0020209 | -0.053741 | 0.0041679 | 0.0027622 | 0.038497 | -0.0025976 | -0.0018756 | -0.00033114 | -11.7371 | -2.6596 | -45.694 | -3.0991 | -2.9709 | -46.1838 | -2.9846 | 1.7212 | 77.4353 | 1.7761 | 77.33 | 2.1194 | 1.9638 | 2.0462 | 0.17853 | -80.0583 | -80.4977 | 42.9016 | 42.8879 | -0.31128 | 42.7094 | -0.48981 | 47.6486 | 0.036621 | -0.068665 | 47.9919 | 47.9187 | 47.8363 | 0.27008 | 0.18768 | 42.7231 | 42.5949 | 0.34332 | 75.5539 | 43.0344 | 75.6592 | 43.2129 | 123.3078 | -123.0927 | -75.6226 | 42.7734 | 123.2025 | 34.1354 | 47.5937
1956.4844 | 123.4818 | -117.8696 | 5.3421 | -0.0042723 | 0.0065433 | 0.11911 | 0.0034479 | -0.0027921 | 0.0049838 | 0.00032907 | -0.041534 | 0.13725 | 0.004471 | -0.0014504 | -0.002384 | -0.0029438 | -0.00033114 | -12.4008 | -3.1723 | -118.2404 | -3.5339 | -3.3691 | -118.3914 | -3.4378 | 0.48065 | 5.397 | 4.7699 | 5.127 | 5.0629 | 5.0125 | 5.0949 | -0.37079 | -8.5144 | -8.876 | 114.5004 | 114.4318 | -0.52185 | 114.8026 | -0.15106 | 122.6395 | 0.054932 | -0.21515 | 122.9324 | 122.9645 | 122.8821 | 0.32501 | 0.24261 | 114.8712 | 114.7064 | 0.29297 | 0.35706 | 115.0681 | 0.62714 | 114.6973 | 123.2666 | -123.5825 | -0.5722 | 114.3356 | 122.9965 | 105.4688 | 118.3502
1957.5469 | 123.5367 | -118.4738 | 4.7287 | -0.042419 | 0.0033389 | 0.12018 | 0.0028069 | -0.0021513 | 7.0582e-05 | -9.8328e-05 | -0.093414 | 0.13747 | 0.0053256 | 0.0023948 | -0.0025976 | -0.00016658 | 0.0011643 | -12.7075 | -2.6505 | -118.8492 | -2.9663 | -2.829 | -118.4372 | -2.8702 | 0.49439 | 4.7974 | 4.216 | 4.66 | 4.5456 | 4.4724 | 4.5914 | -0.37537 | -7.3792 | -7.695 | 115.6448 | 115.6036 | 0.036621 | 115.979 | 0.41199 | 122.6898 | 0.068664 | -0.068665 | 123.0194 | 123.0652 | 122.9462 | 0.37537 | 0.25635 | 116.0202 | 115.8829 | 0.32959 | 0.44403 | 116.1987 | 0.58136 | 115.8234 | 123.2712 | -123.5779 | -0.5127 | 115.5075 | 123.1338 | 105.7663 | 118.9682
1958.4844 | 123.4131 | -44.783 | 78.4287 | 0.041504 | 0.0044071 | 0.039854 | -0.0031745 | -0.0047147 | 0.0034884 | -9.8328e-05 | 0.0011902 | 0.0020315 | 0.00062585 | 0.037429 | -0.0034522 | -0.001662 | 0.0011643 | -5.4703 | -1.8814 | -45.0577 | -2.3575 | -2.1103 | -44.6869 | -2.1744 | 1.8219 | 78.4653 | 1.9958 | 78.5385 | 2.4628 | 2.3346 | 2.3712 | -0.27466 | -80.3101 | -80.7861 | 42.6727 | 42.6086 | 0.09613 | 42.8833 | 0.37079 | 46.7789 | 0.036621 | 0.10986 | 47.2458 | 47.1542 | 47.1176 | 0.37537 | 0.33875 | 42.9474 | 42.7002 | 0.46692 | 76.5427 | 43.1763 | 76.4694 | 42.9016 | 123.2483 | -123.4863 | -76.4328 | 42.4255 | 123.3215 | 39.3127 | 46.6049
1959.4844 | 115.6036 | -45.2728 | 78.0029 | 0.010986 | 0.0050479 | 0.039213 | 0.0028069 | -0.00065586 | 0.0013522 | -0.0050115 | -0.081207 | -0.00074552 | 0.0010532 | 0.038497 | -0.0047338 | -0.011916 | -0.0033219 | -11.7645 | -2.0737 | -45.5429 | -2.4719 | -2.3346 | -45.4376 | -2.3804 | 1.3962 | 78.0716 | 2.1515 | 78.0487 | 2.536 | 2.3666 | 2.504 | -0.27008 | -80.0766 | -80.4749 | 42.9382 | 42.8925 | -0.16479 | 43.1625 | 0.10529 | 47.4243 | 0.068664 | 0.045776 | 47.8088 | 47.7768 | 47.6395 | 0.35248 | 0.21515 | 43.2083 | 43.071 | 0.38452 | 75.8972 | 43.4692 | 75.9201 | 43.1992 | 123.3444 | -123.5458 | -75.8514 | 42.8009 | 123.3215 | 33.5083 | 46.669
1960.5469 | 122.9507 | -45.076 | 78.1723 | -0.057678 | 0.0037661 | 0.042203 | 0.0053705 | -0.00044226 | 0.0019932 | 0.00075627 | -0.11783 | 0.0041679 | 0.00618 | 0.041915 | -0.002384 | -0.003371 | -0.0052445 | -11.6821 | -2.1378 | -45.3323 | -2.5864 | -2.4353 | -45.3003 | -2.4765 | 1.3092 | 78.2501 | 2.1423 | 78.2227 | 2.5269 | 2.3666 | 2.4902 | -0.25635 | -80.3101 | -80.7587 | 42.6407 | 42.5995 | -0.2243 | 42.8558 | 0.032043 | 47.2183 | 0.07782 | 0.050354 | 47.6028 | 47.5662 | 47.4426 | 0.3479 | 0.2243 | 42.897 | 42.746 | 0.38452 | 76.0803 | 43.1946 | 76.1078 | 42.9382 | 123.3261 | -123.5046 | -76.03 | 42.4896 | 123.2986 | 33.3939 | 46.3852
1961.4844 | 122.8271 | -44.9066 | 78.3417 | -0.011902 | 0.0041935 | 0.039854 | 0.0036615 | -0.0038603 | 0.00092498 | 0.0018243 | -0.047638 | 0.0024589 | 0.0048984 | 0.038497 | -0.0045202 | -0.0025164 | -0.0011855 | -9.8511 | -1.9226 | -45.1538 | -2.3804 | -2.2202 | -45.0485 | -2.2614 | 1.4282 | 78.4332 | 2.1835 | 78.3234 | 2.5543 | 2.3849 | 2.4902 | -0.24719 | -80.2643 | -80.722 | 42.6865 | 42.6453 | -0.14191 | 42.8925 | 0.10529 | 47.0901 | 0.091553 | -0.018311 | 47.4609 | 47.3969 | 47.2916 | 0.3067 | 0.20142 | 42.9337 | 42.7734 | 0.37079 | 76.1398 | 43.2312 | 76.2497 | 42.984 | 123.3398 | -123.4955 | -76.1581 | 42.5262 | 123.23 | 35.0555 | 46.3348
1962.5469 | 123.4589 | -44.664 | 78.4927 | 0.026245 | 0.0016299 | 0.04199 | 0.0017389 | -0.0021513 | 0.00092498 | -0.0033025 | 0.022552 | 0.0026725 | 0.006821 | 0.038711 | -0.0021704 | -0.0042254 | -0.0037491 | -11.7737 | -1.7166 | -44.9432 | -2.0233 | -1.8631 | -44.7601 | -1.9089 | 1.4923 | 78.5934 | 2.2797 | 78.6301 | 2.7237 | 2.5589 | 2.623 | -0.27924 | -80.2094 | -80.5161 | 42.8009 | 42.7551 | -0.096131 | 43.0344 | 0.18311 | 46.9437 | 0.10071 | 0.13733 | 47.3877 | 47.287 | 47.2229 | 0.34332 | 0.27924 | 43.0801 | 42.9199 | 0.44403 | 76.3504 | 43.2266 | 76.3138 | 42.9474 | 123.2574 | -123.436 | -76.2131 | 42.6407 | 123.2941 | 32.8903 | 46.1563
1963.4844 | 122.6578 | -44.9341 | 78.3554 | -0.042419 | 0.0014163 | 0.041135 | 0.0034479 | -0.0027921 | 0.00071138 | -9.8328e-05 | -0.023224 | 0.0054495 | 0.0019076 | 0.037002 | -0.0034522 | -0.0031574 | -0.0013991 | -11.879 | -1.8677 | -45.1675 | -2.3026 | -2.1423 | -45.1035 | -2.1881 | 1.1353 | 78.4332 | 2.1103 | 78.2867 | 2.4628 | 2.3071 | 2.3849 | -0.23346 | -80.2231 | -80.658 | 42.7917 | 42.746 | -0.16937 | 42.9794 | 0.064087 | 47.0444 | 0.07782 | -0.068665 | 47.3969 | 47.319 | 47.2412 | 0.27466 | 0.19684 | 43.0252 | 42.865 | 0.35248 | 76.1765 | 43.2999 | 76.3229 | 43.0664 | 123.3673 | -123.5229 | -76.2451 | 42.6315 | 123.2208 | 33.0551 | 46.0693
1964.4844 | 123.1247 | -44.9936 | 78.2913 | -0.042419 | 0.0037661 | 0.042631 | 0.0023797 | 0.0016939 | 0.00071138 | -0.00095273 | -0.020172 | 0.0026725 | 0.0023348 | 0.041701 | -0.0021704 | -0.0010212 | 0.00073706 | -12.0712 | -2.0554 | -45.2271 | -2.4261 | -2.2476 | -45.1355 | -2.3117 | 1.0803 | 78.3325 | 2.2385 | 78.2501 | 2.6001 | 2.4948 | 2.5589 | -0.23346 | -80.3467 | -80.7175 | 42.746 | 42.6819 | -0.14191 | 42.9153 | 0.091553 | 47.2321 | 0.041199 | -0.041199 | 47.5937 | 47.5525 | 47.4884 | 0.32043 | 0.25635 | 42.9794 | 42.8009 | 0.36163 | 76.0117 | 43.1717 | 76.0941 | 42.9382 | 123.3261 | -123.5184 | -76.0529 | 42.5674 | 123.2437 | 32.9224 | 46.0739
1965.5469 | 123.6465 | -44.9844 | 78.035 | -0.027161 | 0.0022709 | 0.040708 | 0.0036615 | -0.0012967 | 0.00028418 | -0.00073913 | -0.0049134 | 0.0033133 | 0.0036166 | 0.040847 | -0.0036658 | -0.0040118 | 0.0018051 | -12.0575 | -1.8951 | -45.1401 | -2.1835 | -2.0096 | -44.8242 | -2.0599 | 1.1627 | 78.4698 | 2.2797 | 78.511 | 2.7237 | 2.6001 | 2.6596 | -0.15564 | -79.9301 | -80.2185 | 42.9749 | 42.9245 | 0.16022 | 43.0801 | 0.31586 | 47.2641 | 0.43488 | 0.47607 | 47.7081 | 47.644 | 47.5845 | 0.37994 | 0.32043 | 43.1305 | 42.9565 | 0.44403 | 76.2314 | 43.2449 | 76.1902 | 43.0893 | 123.4543 | -123.175 | -75.7553 | 42.8009 | 123.4955 | 32.9269 | 46.1472
1966.4844 | 122.8088 | -45.0943 | 78.1906 | 0.041504 | 0.0037661 | 0.040922 | 0.0025933 | -1.486e-05 | 0.00071138 | 0.0024653 | -0.059845 | 0.0037405 | 0.003403 | 0.036147 | -0.0019568 | -0.0048664 | 9.6064e-05 | -11.9568 | -1.973 | -45.3049 | -2.3392 | -2.1835 | -45.2362 | -2.2339 | 0.88348 | 78.2593 | 2.2247 | 78.1403 | 2.5818 | 2.4353 | 2.4857 | -0.21057 | -80.1636 | -80.5298 | 42.9108 | 42.8604 | -0.14191 | 43.071 | 0.068665 | 47.319 | 0.068664 | -0.050354 | 47.6761 | 47.58 | 47.5296 | 0.26093 | 0.21057 | 43.1213 | 42.9657 | 0.35706 | 75.9155 | 43.3319 | 76.0345 | 43.1213 | 123.3536 | -123.4955 | -75.9659 | 42.7551 | 123.2346 | 33.1375 | 45.9778
1967.4844 | 122.5159 | -44.7098 | 78.1311 | -0.17212 | -0.0096921 | 0.03729 | 0.0064385 | -0.014541 | -0.001852 | -0.014411 | -0.10867 | -0.0020273 | -0.0059964 | 0.047042 | -3.4196e-05 | -0.0097796 | 9.6064e-05 | -12.3367 | -2.0874 | -45.4056 | -2.4261 | -2.298 | -45.3415 | -2.3575 | 1.181 | 78.2364 | 2.2156 | 78.1174 | 2.6184 | 2.449 | 2.5406 | -0.6958 | -80.2185 | -80.5573 | 42.4118 | 42.3523 | -0.63171 | 43.0481 | 0.064087 | 46.9254 | 0.10529 | -0.013733 | 47.3282 | 47.2504 | 47.1588 | 0.32501 | 0.23346 | 43.1076 | 42.9794 | 0.40283 | 75.9018 | 43.3182 | 76.0208 | 42.6224 | 122.9462 | -123.5367 | -75.9155 | 42.2836 | 122.8271 | 32.373 | 45.8908
1968.5469 | 123.468 | -45.0851 | 78.0945 | -0.088196 | 0.0020573 | 0.040281 | 0.0023797 | 0.0025485 | 7.0582e-05 | -0.0028753 | 0.0011902 | 0.0020315 | 0.0040438 | 0.042556 | -0.0019568 | -0.0029438 | -0.0018265 | -12.0483 | -2.0325 | -45.3323 | -2.298 | -2.1332 | -45.2225 | -2.1881 | 1.1856 | 78.1723 | 2.1011 | 78.2318 | 2.5543 | 2.4216 | 2.4719 | -0.24719 | -80.127 | -80.3925 | 42.952 | 42.897 | -0.13733 | 43.1442 | 0.10986 | 47.1863 | 0.07782 | 0.13733 | 47.6395 | 47.5571 | 47.5067 | 0.37079 | 0.32043 | 43.1992 | 43.0344 | 0.45319 | 76.1307 | 43.2999 | 76.0712 | 43.0527 | 123.2574 | -123.4268 | -75.9933 | 42.7872 | 123.317 | 33.0368 | 46.2708
1969.4844 | 123.111 | -45.0623 | 78.1448 | 0.018616 | 0.0037661 | 0.042631 | 0.0043023 | 0.0029757 | 0.0015658 | -0.00052553 | -0.090363 | 0.0022453 | 0.0038302 | 0.038711 | -0.002384 | -0.0012348 | -0.0028945 | -12.1445 | -2.005 | -45.401 | -2.4719 | -2.33 | -45.3278 | -2.3666 | 1.0574 | 78.2272 | 2.0554 | 78.1403 | 2.4261 | 2.2842 | 2.3666 | -0.33875 | -80.1498 | -80.6168 | 42.7322 | 42.6956 | -0.2655 | 43.0344 | 0.073242 | 47.1176 | 0.082398 | -0.004577 | 47.4884 | 47.4289 | 47.3465 | 0.31128 | 0.22888 | 43.071 | 42.9291 | 0.37079 | 76.0849 | 43.396 | 76.1719 | 43.0573 | 123.2895 | -123.5458 | -76.0895 | 42.5903 | 123.2025 | 32.9178 | 46.1197
1970.4844 | 123.4222 | -118.4738 | 4.747 | -0.057678 | 0.0046207 | 0.11932 | 0.0064385 | 0.00041234 | 0.0019932 | -0.0030889 | -0.075104 | 0.14153 | 0.003403 | -0.002305 | -0.0028112 | -0.0020892 | -0.0020401 | -16.9647 | -2.5131 | -118.8675 | -2.9388 | -2.7924 | -118.3777 | -2.8152 | 0.33875 | 4.8386 | 4.2709 | 4.4952 | 4.5547 | 4.4769 | 4.5456 | -0.39368 | -7.2601 | -7.6859 | 115.6815 | 115.6586 | 0.09613 | 116.0522 | 0.48981 | 122.7448 | 0.091553 | -0.25177 | 123.0286 | 123.0194 | 122.9507 | 0.27466 | 0.20599 | 116.0751 | 115.9286 | 0.28381 | 0.2243 | 116.3544 | 0.56763 | 115.9607 | 123.3124 | -123.6145 | -0.47607 | 115.535 | 122.9691 | 101.5091 | 118.8126
1971.5469 | 123.436 | -118.6111 | 4.6829 | -0.03479 | 0.0037661 | 0.12103 | 0.0051569 | 0.00062594 | -0.00078402 | -0.00052553 | -0.05069 | 0.14003 | 0.0046848 | -0.00016881 | -0.002384 | -0.0029438 | 0.0033005 | -11.2198 | -2.5314 | -118.9453 | -2.9984 | -2.8473 | -119.1742 | -2.8839 | 0.26093 | 4.7653 | 4.1748 | 4.4357 | 4.4357 | 4.3762 | 4.454 | -0.33417 | -7.2144 | -7.6813 | 115.7639 | 115.7272 | -0.56305 | 116.0614 | -0.22888 | 122.7859 | 0.082398 | -0.24719 | 123.0469 | 123.0652 | 122.9874 | 0.27924 | 0.20142 | 116.098 | 115.947 | 0.26093 | 0.26093 | 116.4139 | 0.59051 | 116.0797 | 123.3765 | -123.6282 | -0.50812 | 115.6128 | 123.0469 | 107.3914 | 118.8721
1972.4844 | 123.4497 | -118.6752 | 4.6463 | -0.027161 | 0.0024845 | 0.1221 | 0.0060113 | 0.0021213 | 0.0011386 | -0.0018073 | -0.11172 | 0.1411 | 0.0040438 | 0.0041038 | -0.002384 | -0.00059378 | 0.0015915 | -11.087 | -2.536 | -118.9819 | -2.9892 | -2.8519 | -118.5425 | -2.8885 | 0.32044 | 4.7379 | 4.1656 | 4.4586 | 4.4449 | 4.3808 | 4.4861 | -0.3067 | -7.1823 | -7.6355 | 115.8234 | 115.7867 | 0.13275 | 116.0934 | 0.43945 | 122.8409 | 0.091553 | -0.18768 | 123.1201 | 123.1613 | 123.056 | 0.32043 | 0.21515 | 116.1301 | 115.9927 | 0.27924 | 0.29297 | 116.4459 | 0.5722 | 116.1392 | 123.4131 | -123.6282 | -0.48065 | 115.686 | 123.1338 | 107.5882 | 118.9957
1973.5469 | 123.3856 | -118.689 | 4.6738 | 0.0033567 | 0.0037661 | 0.1206 | 0.0049433 | 0.0025485 | -0.00014322 | -0.0018073 | -0.041534 | 0.1411 | 0.0040438 | 0.00025839 | -0.0045202 | -0.0035846 | -0.00075834 | -11.5402 | -2.4765 | -118.9865 | -2.9251 | -2.7649 | -118.6203 | -2.7924 | 0.31586 | 4.7516 | 4.1473 | 4.4266 | 4.4266 | 4.3625 | 4.4449 | -0.29755 | -7.1503 | -7.5989 | 115.9241 | 115.8966 | 0.068665 | 116.1942 | 0.36621 | 122.8363 | 0.07782 | -0.24719 | 123.1155 | 123.1338 | 123.0515 | 0.29755 | 0.21515 | 116.2216 | 116.0614 | 0.27924 | 0.27924 | 116.51 | 0.60425 | 116.2125 | 123.4406 | -123.6603 | -0.52643 | 115.7639 | 123.1155 | 107.1487 | 119.0048
1974.4844 | 123.4085 | -118.6295 | 4.7195 | -0.019531 | 0.0026981 | 0.12103 | 0.0049433 | 0.0046847 | 0.0013522 | 0.00054267 | -0.096466 | 0.14217 | 0.0046848 | 0.00068579 | -0.0036658 | -0.001662 | 0.0013779 | -3.978 | -2.3895 | -118.9453 | -2.8564 | -2.7054 | -118.5516 | -2.7374 | 0.41199 | 4.8065 | 4.2206 | 4.509 | 4.509 | 4.4174 | 4.5227 | -0.31586 | -7.1091 | -7.576 | 115.9241 | 115.892 | 0.07782 | 116.2079 | 0.39368 | 122.85 | 0.086976 | -0.21057 | 123.1384 | 123.1522 | 123.0469 | 0.30212 | 0.19684 | 116.2399 | 116.0889 | 0.28839 | 0.28839 | 116.5558 | 0.58594 | 116.2399 | 123.436 | -123.6649 | -0.49896 | 115.773 | 123.1384 | 114.6515 | 119.0414
1975.5469 | 123.3994 | -118.4555 | 4.8889 | 0.026245 | 0.0033389 | 0.1206 | 0.0028069 | 0.00041234 | -0.00014322 | 0.0011835 | -0.041534 | 0.13832 | 0.0031894 | -0.0059366 | -0.0015296 | -0.0020892 | -0.00097194 | -2.9251 | -2.4857 | -118.7027 | -2.8152 | -2.6505 | -118.1992 | -2.7008 | 0.41657 | 4.921 | 4.3945 | 4.66 | 4.6829 | 4.6234 | 4.7012 | -0.24719 | -7.3746 | -7.7042 | 115.8051 | 115.7547 | 0.25635 | 116.0019 | 0.50354 | 122.85 | 0.032043 | -0.22888 | 123.1384 | 123.1567 | 123.0789 | 0.3067 | 0.22888 | 116.0522 | 115.8875 | 0.28839 | 0.2655 | 116.217 | 0.52643 | 115.9698 | 123.3765 | -123.5916 | -0.49439 | 115.6403 | 123.1155 | 115.5304 | 118.8721
1976.4844 | 123.3856 | -118.4601 | 4.8843 | -0.050049 | 0.0037661 | 0.11719 | 0.0034479 | 0.0016939 | -0.00099762 | -0.00095273 | -0.099518 | 0.13683 | 0.004471 | -0.003373 | -0.0025976 | -0.0025164 | -0.0020401 | -9.169 | -2.4445 | -118.7622 | -2.8976 | -2.7649 | -118.2587 | -2.7832 | 0.33875 | 4.9576 | 4.3671 | 4.6692 | 4.6875 | 4.6097 | 4.6967 | -0.30212 | -7.3288 | -7.782 | 115.6952 | 115.6769 | 0.20142 | 115.979 | 0.50354 | 122.8271 | 0.073243 | -0.21515 | 123.1476 | 123.1567 | 123.0698 | 0.32959 | 0.24261 | 115.9973 | 115.8646 | 0.32043 | 0.30212 | 116.3177 | 0.59052 | 116.0156 | 123.4177 | -123.6465 | -0.51727 | 115.5624 | 123.1293 | 109.2911 | 118.7988
1977.4844 | 123.3582 | -118.4601 | 4.8706 | -0.019531 | 0.0016299 | 0.1206 | 0.0053705 | 0.0034029 | 7.0582e-05 | -0.0015935 | -0.087311 | 0.13854 | 0.0031894 | 0.0019674 | -0.004093 | 0.00026062 | -0.0020401 | -6.2027 | -2.3895 | -118.7302 | -2.8336 | -2.6962 | -118.6752 | -2.7283 | 0.34332 | 4.9713 | 4.3808 | 4.66 | 4.6921 | 4.5959 | 4.7104 | -0.27008 | -7.2601 | -7.7042 | 115.7639 | 115.7318 | -0.21515 | 116.0019 | 0.054932 | 122.8409 | 0.10071 | -0.21057 | 123.1522 | 123.1705 | 123.056 | 0.32959 | 0.21515 | 116.0339 | 115.8966 | 0.31128 | 0.27924 | 116.3406 | 0.59051 | 116.0706 | 123.4314 | -123.6008 | -0.48981 | 115.6265 | 123.1201 | 112.2574 | 118.8034
1978.5469 | 123.4131 | -118.3182 | 4.9759 | -0.042419 | 0.0033389 | 0.12188 | 0.0025933 | 0.0021213 | -0.00078402 | -0.0015935 | -0.0018616 | 0.13747 | 0.0027622 | -0.0025186 | -0.0015296 | -0.0031574 | -0.0013991 | -3.9047 | -2.4673 | -118.6295 | -2.7969 | -2.6138 | -118.3456 | -2.6688 | 0.45319 | 5.0171 | 4.3716 | 4.7882 | 4.7104 | 4.6371 | 4.7058 | -0.31128 | -7.4432 | -7.7728 | 115.7043 | 115.6494 | -0.027466 | 115.9607 | 0.28381 | 122.6898 | 0.041199 | -0.18768 | 123.0286 | 123.024 | 122.9553 | 0.33417 | 0.2655 | 116.0156 | 115.8325 | 0.33875 | 0.41657 | 116.1621 | 0.64545 | 115.8508 | 123.3353 | -123.6053 | -0.60425 | 115.5212 | 123.1064 | 114.4135 | 118.7714
1979.4844 | 118.7897 | -43.3594 | 79.8615 | -0.23315 | -0.012469 | 0.032804 | 0.0034479 | 0.0025485 | 0.006052 | -0.0024481 | -0.10257 | 0.0041679 | 0.0012668 | 0.047469 | 0.0006066 | -0.011916 | -0.00097194 | -2.8427 | -1.4099 | -43.5333 | -1.7899 | -1.6251 | -43.1992 | -1.6846 | 1.5015 | 79.9484 | 2.2476 | 79.8523 | 2.6138 | 2.4445 | 2.5635 | -0.17395 | -81.2714 | -81.6513 | 41.7343 | 41.6748 | 0.16022 | 41.8488 | 0.33417 | 45.607 | 0.086975 | -0.009155 | 45.9732 | 45.9229 | 45.8038 | 0.31586 | 0.19684 | 41.9083 | 41.7435 | 0.36621 | 77.6047 | 42.1234 | 77.7008 | 41.9495 | 123.3078 | -123.3948 | -77.6138 | 41.5695 | 123.2117 | 40.5167 | 44.8608
1980.4844 | 118.5608 | -42.1097 | 80.9143 | -0.011902 | 0.0050479 | 0.038358 | 0.0057977 | 0.0014803 | 0.0056248 | -0.0013799 | -0.065949 | 0.0030997 | 0.0029758 | 0.047042 | -0.0034522 | -0.00016658 | 0.0039413 | -2.6642 | -1.387 | -42.627 | -1.7944 | -1.6388 | -41.629 | -1.68 | 1.3916 | 80.9692 | 2.0874 | 80.9326 | 2.4902 | 2.298 | 2.4078 | -0.51727 | -82.3013 | -82.7087 | 40.4709 | 40.4297 | 0.48065 | 40.947 | 0.99793 | 44.1971 | 0.054931 | 0.01831 | 44.5999 | 44.5175 | 44.4077 | 0.32043 | 0.21057 | 40.9882 | 40.8325 | 0.40283 | 78.8452 | 41.2399 | 78.8818 | 40.7227 | 123.0789 | -123.5413 | -78.8269 | 40.3152 | 123.0423 | 39.4455 | 43.5013
1981.5469 | 123.5184 | -118.1213 | 5.0583 | 0.010986 | 0.0031253 | 0.12381 | 0.0040887 | -0.0019377 | 0.0013522 | -0.0020209 | -0.01712 | 0.1379 | 0.0025484 | -0.0097818 | -0.002384 | -0.0037982 | 0.00030966 | -7.8094 | -2.005 | -118.5425 | -2.3117 | -2.1286 | -118.0618 | -2.1835 | 0.42114 | 5.1498 | 4.5868 | 4.9393 | 4.9484 | 4.8843 | 4.9622 | -0.42114 | -7.0633 | -7.37 | 115.9927 | 115.9378 | 0.059509 | 116.3589 | 0.48065 | 122.7081 | 0.091552 | -0.11902 | 123.0698 | 123.0835 | 123.0057 | 0.37537 | 0.29755 | 116.4139 | 116.2308 | 0.36163 | 0.35248 | 116.5375 | 0.56305 | 116.1163 | 123.2712 | -123.6008 | -0.4715 | 115.8096 | 123.0606 | 110.3119 | 118.5425
1982.4844 | 123.4543 | -118.3868 | 4.8706 | 0.033875 | 0.0039799 | 0.1221 | 0.0043023 | 0.0046847 | 0.00071138 | -0.00031193 | -0.099518 | 0.14153 | 0.0021212 | 0.0023948 | -0.0021704 | 0.00090142 | 0.0011643 | -7.0404 | -1.9226 | -118.7531 | -2.3438 | -2.1881 | -118.2587 | -2.2385 | 0.42114 | 4.9438 | 4.3671 | 4.7012 | 4.6738 | 4.5959 | 4.7058 | -0.36621 | -6.7932 | -7.2144 | 116.1987 | 116.1484 | 0.12817 | 116.5146 | 0.49438 | 122.7539 | 0.073243 | -0.16937 | 123.0606 | 123.0927 | 122.9828 | 0.33875 | 0.22888 | 116.5649 | 116.4093 | 0.3067 | 0.33417 | 116.8304 | 0.57678 | 116.4642 | 123.3307 | -123.6237 | -0.50354 | 116.0431 | 123.0881 | 111.3464 | 118.808
1983.5469 | 123.3994 | -118.5745 | 4.7791 | 0.0033567 | 0.0033389 | 0.12018 | 0.0047295 | 0.0010531 | -0.00035682 | -0.0026617 | -0.081207 | 0.13875 | 0.0048984 | 0.0017538 | -0.0045202 | -0.0012348 | -0.00033114 | -9.0546 | -2.1698 | -118.8354 | -2.6505 | -2.4994 | -118.4189 | -2.5406 | 0.37079 | 4.8386 | 4.2664 | 4.541 | 4.5273 | 4.454 | 4.5776 | -0.26093 | -6.9489 | -7.4295 | 116.0751 | 116.0339 | 0.15564 | 116.2949 | 0.41656 | 122.8409 | 0.059509 | -0.23804 | 123.1018 | 123.1522 | 123.0286 | 0.31128 | 0.18768 | 116.3361 | 116.185 | 0.26093 | 0.27466 | 116.6656 | 0.5722 | 116.4047 | 123.4131 | -123.6145 | -0.5127 | 115.9241 | 123.1155 | 109.52 | 118.9453
1984.4844 | 123.3353 | -118.5242 | 4.834 | -0.042419 | 0.00098907 | 0.11953 | 0.0032343 | 0.0031893 | 0.0015658 | -0.0033025 | -0.041534 | 0.13939 | 0.0019076 | 0.0064536 | -0.0036658 | -0.00016658 | 0.0022323 | -11.7737 | -2.4445 | -118.7851 | -2.916 | -2.7603 | -118.158 | -2.7786 | 0.36621 | 4.9164 | 4.3213 | 4.5776 | 4.6051 | 4.5273 | 4.6097 | -0.26093 | -7.2784 | -7.7499 | 115.7639 | 115.7455 | 0.36621 | 116.0065 | 0.62714 | 122.8455 | 0.082398 | -0.25635 | 123.1293 | 123.1338 | 123.0515 | 0.28839 | 0.20599 | 116.0248 | 115.8691 | 0.28381 | 0.25635 | 116.3406 | 0.59509 | 116.0797 | 123.4406 | -123.6191 | -0.51269 | 115.6082 | 123.1018 | 106.7505 | 118.8904
1985.4844 | 123.3719 | -118.4097 | 4.8843 | -0.03479 | 0.0041935 | 0.12103 | 0.0049433 | 0.0021213 | 0.0011386 | 0.0011835 | -0.099518 | 0.13918 | 0.0038302 | -0.004014 | -0.0043066 | -0.0025164 | 9.6064e-05 | -10.7254 | -2.3895 | -118.7897 | -2.8107 | -2.6505 | -118.3823 | -2.71 | 0.44403 | 4.9072 | 4.3488 | 4.6555 | 4.6326 | 4.7012 | 4.7653 | -0.37994 | -7.2739 | -7.695 | 115.7593 | 115.6998 | 0.027466 | 116.0797 | 0.40741 | 122.7585 | 0.022889 | -0.22888 | 123.0423 | 123.175 | 123.111 | 0.41657 | 0.35248 | 116.1392 | 115.979 | 0.28381 | 0.3067 | 116.4001 | 0.55847 | 116.0202 | 123.317 | -123.674 | -0.53558 | 115.5991 | 123.0652 | 107.6843 | 118.8538
1986.5469 | 123.381 | -118.4647 | 4.8798 | -0.03479 | 0.0039799 | 0.11975 | 0.0028069 | -0.00022866 | 0.00049778 | -9.8328e-05 | -0.041534 | 0.14089 | 0.0029758 | -0.0027322 | -0.0004614 | -0.0040118 | 0.00052346 | -10.5789 | -2.3849 | -118.7347 | -2.774 | -2.6138 | -118.396 | -2.655 | 0.36621 | 4.9484 | 4.3762 | 4.628 | 4.6646 | 4.5868 | 4.6646 | -0.27008 | -7.2647 | -7.6538 | 115.8508 | 115.8096 | 0.068665 | 116.0797 | 0.33875 | 122.8409 | 0.068664 | -0.25177 | 123.1293 | 123.1293 | 123.0515 | 0.28839 | 0.21057 | 116.1209 | 115.9607 | 0.28839 | 0.25177 | 116.3498 | 0.5722 | 116.0797 | 123.4131 | -123.6145 | -0.50354 | 115.6906 | 123.0927 | 107.8857 | 118.8309
1987.4844 | 123.3398 | -118.4601 | 4.8981 | -0.072937 | 0.0039799 | 0.12039 | 0.0066523 | 0.0053255 | 0.00071138 | -0.0011663 | -0.1514 | 0.13854 | 0.0036166 | 0.0013266 | -0.0032386 | -0.0010212 | 0.0022323 | -8.1482 | -2.4353 | -118.7622 | -2.9022 | -2.7603 | -118.4463 | -2.8061 | 0.27008 | 4.9622 | 4.3716 | 4.6463 | 4.6234 | 4.5181 | 4.6646 | -0.30212 | -7.3334 | -7.8003 | 115.6998 | 115.654 | 0.013733 | 115.9561 | 0.31586 | 122.8317 | 0.064087 | -0.25177 | 123.0835 | 123.1247 | 122.9782 | 0.29297 | 0.14648 | 116.0019 | 115.86 | 0.25177 | 0.27466 | 116.3269 | 0.59051 | 116.0248 | 123.4222 | -123.6603 | -0.52643 | 115.5579 | 123.1064 | 110.3119 | 118.7302
1988.4844 | 123.3444 | -118.3365 | 5.0171 | -0.0042723 | 0.0050479 | 0.11996 | 0.0064385 | 0.00062594 | 0.002634 | -0.0028753 | -0.099518 | 0.13875 | 0.0019076 | 0.00068579 | -0.0021704 | 0.00090142 | 0.0052231 | -6.3309 | -2.5497 | -118.5974 | -3.0029 | -2.8427 | -119.22 | -2.916 | 0.36621 | 5.0858 | 4.4357 | 4.7928 | 4.6829 | 4.5914 | 4.7058 | -0.26093 | -7.5668 | -8.02 | 115.4938 | 115.4205 | -0.88348 | 115.6815 | -0.62256 | 122.7722 | 0.068664 | -0.2243 | 123.0194 | 123.0423 | 122.9279 | 0.27008 | 0.15564 | 115.7547 | 115.5945 | 0.24719 | 0.35706 | 116.0477 | 0.65002 | 115.7867 | 123.4222 | -123.6145 | -0.58136 | 115.3336 | 123.1293 | 112.0056 | 118.7027
1989.4844 | 123.3582 | -118.364 | 4.9667 | -0.0042723 | 0.0037661 | 0.11932 | 0.0025933 | 0.0019077 | -0.00035682 | 0.0024653 | -0.11172 | 0.13875 | 0.0023348 | -0.0027322 | -0.0021704 | -0.001662 | -0.0016129 | -7.8781 | -2.6184 | -118.6432 | -3.0853 | -2.9388 | -118.3777 | -3.0029 | 0.4303 | 5.0354 | 4.4449 | 4.7241 | 4.6921 | 4.6188 | 4.7379 | -0.27923 | -7.5851 | -8.0521 | 115.4251 | 115.361 | -0.013733 | 115.6403 | 0.2655 | 122.8088 | 0.068664 | -0.24261 | 123.056 | 123.1018 | 122.9828 | 0.29297 | 0.17395 | 115.7043 | 115.5579 | 0.24719 | 0.27924 | 116.0248 | 0.59051 | 115.7455 | 123.3994 | -123.6099 | -0.52185 | 115.2786 | 123.0881 | 110.4858 | 118.7943
1990.4844 | 123.3673 | -118.3777 | 4.9255 | 0.018616 | 0.0035525 | 0.12167 | 0.0034479 | -1.486e-05 | 0.0028476 | -9.8328e-05 | -0.075104 | 0.13854 | 0.0046848 | 0.0015402 | -0.0011022 | -0.0012348 | 0.0037277 | -7.9147 | -2.742 | -118.6935 | -3.1769 | -3.0029 | -118.2449 | -3.0396 | 0.3891 | 4.9988 | 4.4037 | 4.7333 | 4.7195 | 4.6417 | 4.747 | -0.31586 | -7.6675 | -8.1024 | 115.3748 | 115.3381 | 0.13275 | 115.654 | 0.44861 | 122.7814 | 0.073242 | -0.19226 | 123.0972 | 123.1247 | 123.0194 | 0.34332 | 0.23804 | 115.6906 | 115.5167 | 0.31586 | 0.32959 | 115.9515 | 0.59509 | 115.6357 | 123.3765 | -123.6191 | -0.52185 | 115.2008 | 123.111 | 110.463 | 118.7668
1991.5469 | 123.3261 | -118.4189 | 4.9301 | 0.033875 | 0.0033389 | 0.11975 | 0.0038751 | -0.0010831 | 0.00092498 | -0.0022345 | 0.0011902 | 0.13683 | 0.0036166 | -0.0010232 | -0.0036658 | -0.0014484 | 0.00052346 | -12.7487 | -2.7832 | -118.6752 | -3.1952 | -2.9938 | -118.3777 | -3.0624 | 0.46234 | 4.9942 | 4.3808 | 4.6646 | 4.6692 | 4.5639 | 4.6234 | -0.25635 | -7.7133 | -8.1253 | 115.4251 | 115.3564 | 0.041198 | 115.6128 | 0.29755 | 122.7997 | 0.064087 | -0.2655 | 123.0881 | 123.0423 | 122.9828 | 0.24261 | 0.18311 | 115.6815 | 115.48 | 0.28839 | 0.28381 | 115.892 | 0.6134 | 115.6357 | 123.4131 | -123.6053 | -0.54932 | 115.2237 | 123.0835 | 105.6702 | 118.8812
1992.4844 | 123.3536 | -118.3365 | 4.9667 | -0.050049 | 0.0056889 | 0.11654 | 0.0023797 | 0.0016939 | -0.00035682 | 0.00075627 | -0.069 | 0.13725 | 0.0040438 | -0.0035868 | -0.0004614 | -0.0025164 | -0.0018265 | -13.4628 | -2.7466 | -118.6615 | -3.1769 | -3.0258 | -118.3044 | -3.0533 | 0.48981 | 5.0217 | 4.3762 | 4.7516 | 4.6875 | 4.6143 | 4.715 | -0.32501 | -7.7133 | -8.1436 | 115.3107 | 115.2832 | 0.032044 | 115.6082 | 0.35706 | 122.7127 | 0.054931 | -0.21515 | 123.024 | 123.0515 | 122.9507 | 0.33875 | 0.23804 | 115.6357 | 115.4846 | 0.31128 | 0.37537 | 115.9149 | 0.64545 | 115.5899 | 123.3582 | -123.6282 | -0.59051 | 115.1596 | 123.0881 | 104.8737 | 118.8263
1993.4844 | 122.9187 | -44.3527 | 78.6484 | -0.37811 | -0.0077695 | 0.03964 | 0.0051569 | 0.00041234 | 0.0019932 | 0.0022517 | -0.084259 | 0.0016043 | 0.0025484 | 0.046401 | -0.0028112 | -0.0018756 | 9.6064e-05 | -11.3251 | -1.6205 | -44.545 | -2.0782 | -1.9409 | -44.8059 | -1.9775 | 1.4191 | 78.6484 | 2.1698 | 78.566 | 2.4811 | 2.3483 | 2.4673 | -0.19226 | -80.2689 | -80.7266 | 42.4118 | 42.3752 | -0.45319 | 42.5674 | -0.26093 | 46.5225 | 0 | -0.082397 | 46.8338 | 46.8201 | 46.7011 | 0.29755 | 0.17853 | 42.6041 | 42.4667 | 0.31128 | 76.3962 | 42.9245 | 76.4786 | 42.7322 | 123.0011 | -123.1934 | -76.4786 | 42.2745 | 122.9187 | 33.0276 | 45.7718
1994.5469 | 123.4406 | -118.3365 | 4.8889 | -0.011902 | 0.0029117 | 0.11847 | 0.0034479 | -0.00086946 | -0.00078402 | -0.0024481 | -0.011017 | 0.13854 | 0.0046848 | -0.0025186 | -0.0028112 | -0.0025164 | -0.0011855 | -26.8341 | -2.4078 | -118.6981 | -2.7878 | -2.6276 | -118.3365 | -2.6733 | 0.36621 | 4.9576 | 4.3442 | 4.6371 | 4.6371 | 4.5364 | 4.6051 | -0.36163 | -7.2968 | -7.6767 | 115.7089 | 115.6631 | 0 | 116.0248 | 0.36163 | 122.6807 | 0.068665 | -0.25177 | 122.9736 | 122.9416 | 122.8729 | 0.26093 | 0.19226 | 116.0706 | 115.9103 | 0.29297 | 0.29297 | 116.2903 | 0.6134 | 115.9287 | 123.2941 | -123.587 | -0.54474 | 115.5487 | 122.9736 | 91.5024 | 118.7027
1995.4844 | 123.4497 | -118.4692 | 4.747 | -0.072937 | 0.0031253 | 0.11953 | 0.0015253 | 0.0019077 | 0.00028418 | -0.00095273 | -0.090363 | 0.1396 | 0.003403 | 0.00389 | -0.0025976 | -0.0020892 | -0.0037491 | -16.6122 | -2.504 | -118.8583 | -2.9572 | -2.8061 | -118.7714 | -2.8427 | 0.32501 | 4.8523 | 4.2664 | 4.5822 | 4.5593 | 4.4678 | 4.6051 | -0.3891 | -7.251 | -7.7042 | 115.6631 | 115.6265 | -0.30212 | 116.0156 | 0.086975 | 122.7356 | 0.10529 | -0.1648 | 123.0286 | 123.0743 | 122.937 | 0.33875 | 0.20142 | 116.0522 | 115.9012 | 0.29297 | 0.31586 | 116.3544 | 0.58594 | 115.9653 | 123.3215 | -123.6053 | -0.48065 | 115.5121 | 123.0515 | 101.857 | 118.7943
1996.5469 | 123.3948 | -118.5471 | 4.7653 | -0.0042723 | 0.0035525 | 0.1206 | 0.0047295 | -0.0019377 | -0.00057042 | 0.00054267 | -0.065949 | 0.14067 | 0.0040438 | -0.0010232 | -0.0036658 | -0.00038018 | -0.0011855 | -18.8004 | -2.5726 | -118.8217 | -3.0579 | -2.9022 | -118.3868 | -2.9251 | 0.31586 | 4.834 | 4.2618 | 4.5502 | 4.5364 | 4.4769 | 4.5685 | -0.27466 | -7.338 | -7.8232 | 115.6448 | 115.6219 | 0.16022 | 115.8966 | 0.43487 | 122.8088 | 0.068664 | -0.21515 | 123.0835 | 123.1155 | 123.024 | 0.3067 | 0.21515 | 115.9195 | 115.7639 | 0.27466 | 0.28839 | 116.2491 | 0.5722 | 115.9744 | 123.381 | -123.587 | -0.50354 | 115.4892 | 123.0972 | 99.7467 | 118.8629
1997.4844 | 123.2162 | -118.5471 | 4.7745 | -0.011902 | 0.0048343 | 0.11975 | 0.0045159 | 0.0023349 | -0.00035682 | -0.00031193 | -0.11783 | 0.1379 | 0.0083164 | 4.4788e-05 | -0.0036658 | -0.0023028 | 9.6064e-05 | -19.8898 | -2.6413 | -118.8629 | -3.1174 | -2.9984 | -118.4647 | -3.0029 | 0.27466 | 4.8477 | 4.2664 | 4.5547 | 4.5044 | 4.4357 | 4.5639 | -0.31586 | -7.4158 | -7.8918 | 115.5487 | 115.5441 | 0.082397 | 115.86 | 0.39825 | 122.8134 | 0.073242 | -0.21973 | 123.0515 | 123.111 | 122.9828 | 0.29755 | 0.16937 | 115.8646 | 115.7455 | 0.23804 | 0.28839 | 116.2216 | 0.58136 | 115.9058 | 123.3948 | -123.6374 | -0.50812 | 115.4297 | 123.1018 | 98.6572 | 118.8217
1998.4844 | 123.4131 | -118.5516 | 4.7882 | -0.03479 | 0.0016299 | 0.11996 | 0.0049433 | 0.00019874 | 0.00049778 | 0.00096987 | -0.062897 | 0.13661 | 0.0019076 | 0.00068579 | -0.004093 | -0.0023028 | 0.0011643 | -24.9847 | -2.6505 | -118.8171 | -3.0945 | -2.9663 | -118.3914 | -2.9892 | 0.33417 | 4.8614 | 4.2938 | 4.5731 | 4.5868 | 4.4998 | 4.6051 | -0.2655 | -7.4387 | -7.8827 | 115.5853 | 115.5624 | 0.16022 | 115.8279 | 0.42572 | 122.8455 | 0.073242 | -0.21515 | 123.1384 | 123.1567 | 123.0515 | 0.31128 | 0.20599 | 115.8508 | 115.7227 | 0.29297 | 0.27924 | 116.1667 | 0.56763 | 115.9012 | 123.4131 | -123.6053 | -0.49439 | 115.4572 | 123.1247 | 93.5669 | 118.8858
1999.5469 | 123.3398 | -118.5242 | 4.8019 | -0.03479 | 0.0054751 | 0.12018 | 0.0043023 | 0.0038303 | -0.00035682 | 0.00054267 | -0.090363 | 0.13747 | 0.0031894 | -0.0018778 | -0.0034522 | -0.00059378 | -0.0018265 | -11.6913 | -2.6276 | -118.7439 | -3.0396 | -2.8839 | -118.4509 | -2.9572 | 0.49439 | 4.866 | 4.3488 | 4.6005 | 4.5959 | 4.5044 | 4.6326 | -0.21973 | -7.4295 | -7.8415 | 115.6403 | 115.567 | 0.073242 | 115.7867 | 0.29297 | 122.8729 | 0.064087 | -0.20142 | 123.1201 | 123.1567 | 123.0286 | 0.28381 | 0.15564 | 115.86 | 115.7043 | 0.24719 | 0.25177 | 116.1163 | 0.51727 | 115.8966 | 123.3902 | -123.5458 | -0.45319 | 115.4846 | 123.1247 | 106.8329 | 119.0186
2000.4844 | 123.317 | -118.428 | 4.8706 | 0.018616 | 0.0050479 | 0.11932 | 0.0047295 | 0.0012667 | -0.00099762 | 0.0018243 | -0.096466 | 0.13854 | 0.0042574 | -0.0025186 | -0.0025976 | -0.0031574 | 0.0037277 | -9.6039 | -2.5589 | -118.7439 | -2.9892 | -2.8427 | -118.6615 | -2.9205 | 0.43945 | 4.9576 | 4.3579 | 4.6555 | 4.5959 | 4.5227 | 4.6417 | -0.31586 | -7.4295 | -7.8598 | 115.5853 | 115.5075 | -0.23346 | 115.8234 | 0.082397 | 122.7859 | 0.086976 | -0.21515 | 123.024 | 123.0698 | 122.9507 | 0.28381 | 0.16479 | 115.9012 | 115.7547 | 0.23804 | 0.29755 | 116.185 | 0.59967 | 115.8691 | 123.3856 | -123.6145 | -0.51269 | 115.4388 | 123.0835 | 108.8242 | 118.8675
2001.5469 | 123.3765 | -118.4601 | 4.8569 | -0.03479 | 0.0035525 | 0.12018 | 0.0049433 | 0.00062594 | 0.00092498 | -0.0022345 | -0.090363 | 0.13939 | 0.004471 | 0.00068579 | -0.002384 | -0.0012348 | -0.00097194 | -9.3475 | -2.5681 | -118.7759 | -3.0075 | -2.8519 | -118.3777 | -2.8748 | 0.50812 | 4.9301 | 4.335 | 4.6875 | 4.6234 | 4.5502 | 4.66 | -0.31586 | -7.4249 | -7.8644 | 115.6082 | 115.5853 | 0.082397 | 115.9012 | 0.39825 | 122.7951 | 0.073242 | -0.16937 | 123.0835 | 123.1201 | 123.0103 | 0.32501 | 0.21515 | 115.9241 | 115.7684 | 0.28839 | 0.35248 | 116.2079 | 0.59509 | 115.892 | 123.3902 | -123.6328 | -0.52185 | 115.4526 | 123.1476 | 109.1125 | 118.9682
2002.4844 | 123.3261 | -118.3914 | 4.9118 | 0.049133 | 0.0024845 | 0.12082 | 0.0038751 | 0.0025485 | 0.0015658 | -0.0015935 | -0.093414 | 0.13896 | 0.0036166 | -0.002305 | -0.0032386 | -0.0012348 | 9.6064e-05 | -10.3867 | -2.5772 | -118.6523 | -3.0121 | -2.8656 | -118.3548 | -2.9251 | 0.48523 | 4.9759 | 4.3716 | 4.6967 | 4.6097 | 4.541 | 4.66 | -0.26093 | -7.489 | -7.9239 | 115.5258 | 115.4663 | 0.036621 | 115.7272 | 0.29755 | 122.7631 | 0.064087 | -0.21515 | 123.0011 | 123.0515 | 122.9324 | 0.28839 | 0.16937 | 115.7867 | 115.6403 | 0.23804 | 0.32501 | 116.0751 | 0.60425 | 115.8142 | 123.3673 | -123.5641 | -0.54016 | 115.3793 | 123.0881 | 108.0048 | 118.8766
2003.4844 | 123.3124 | -118.3502 | 4.9713 | -0.057678 | 0.0052615 | 0.11804 | 0.0060113 | -0.00044226 | 0.0017794 | 0.00054267 | -0.099518 | 0.1364 | 0.0027622 | -0.0044412 | -0.002384 | 0.00068782 | 0.0030869 | -10.2219 | -2.6413 | -118.6203 | -3.1128 | -2.9343 | -118.3136 | -3.0167 | 0.41657 | 5.0308 | 4.3671 | 4.7287 | 4.6051 | 4.541 | 4.6738 | -0.27008 | -7.6126 | -8.0841 | 115.416 | 115.3336 | 0.036621 | 115.6036 | 0.3067 | 122.7173 | 0.05951 | -0.24261 | 122.9553 | 123.024 | 122.8912 | 0.3067 | 0.17395 | 115.686 | 115.5075 | 0.23804 | 0.36163 | 115.979 | 0.66376 | 115.7089 | 123.381 | -123.5916 | -0.60425 | 115.2374 | 123.0789 | 108.1284 | 118.7668
2004.5469 | 122.9645 | -44.7556 | 78.1952 | -0.042419 | -0.00029273 | 0.041563 | 0.0028069 | -0.00065586 | -0.00057042 | -0.0015935 | -0.026276 | 0.0011771 | 0.005112 | 0.04042 | -0.0019568 | -0.0018756 | -0.00033114 | -6.0562 | -2.2293 | -44.8288 | -2.6596 | -2.5314 | -45.1172 | -2.5452 | 2.1469 | 78.2364 | 1.9684 | 78.1906 | 2.3483 | 2.1881 | 2.2614 | -0.073242 | -80.4245 | -80.8548 | 42.2241 | 42.2104 | -0.36163 | 42.2836 | -0.28839 | 46.7239 | 0.041199 | -0.004577 | 47.1039 | 47.0169 | 46.9437 | 0.29297 | 0.21973 | 42.2974 | 42.1692 | 0.37994 | 76.2222 | 42.5995 | 76.268 | 42.5262 | 122.9919 | -123.024 | -76.2268 | 42.0959 | 122.9462 | 38.6993 | 46.9025
2005.4844 | 120.4514 | -43.9774 | 78.8498 | -0.057678 | 0.0016299 | 0.039854 | 0.0032343 | 0.00041234 | -0.0012112 | -0.00052553 | -0.078156 | 0.0028861 | 0.0042574 | 0.045547 | -0.0011022 | -0.0027302 | -0.0011855 | -3.8727 | -1.7807 | -44.2017 | -2.1652 | -2.0004 | -44.339 | -2.0508 | 1.2222 | 78.9093 | 2.037 | 78.8086 | 2.4399 | 2.3254 | 2.3987 | -0.2243 | -80.6305 | -81.015 | 41.9769 | 41.9266 | -0.36163 | 42.1509 | -0.13733 | 46.0144 | 0.05951 | -0.041198 | 46.4172 | 46.376 | 46.3028 | 0.36163 | 0.28839 | 42.2012 | 42.0364 | 0.40283 | 76.7715 | 42.421 | 76.8723 | 42.1967 | 122.8867 | -123.0515 | -76.8127 | 41.8121 | 122.7859 | 40.1047 | 45.1996
2006.4844 | 119.0414 | -44.4122 | 78.4607 | -0.027161 | 0.0061161 | 0.043485 | 0.0036615 | 0.00041234 | 0.00049778 | 0.0026789 | -0.059845 | 0.0022453 | 0.0046848 | 0.04341 | -0.0045202 | -0.001662 | 0.0018051 | -2.6642 | -1.4648 | -44.7693 | -1.8768 | -1.6983 | -44.9524 | -1.767 | 3.0396 | 78.4927 | 2.2751 | 78.241 | 2.5726 | 2.4216 | 2.4902 | -0.35706 | -79.9255 | -80.3375 | 42.7139 | 42.6453 | -0.54016 | 43.0023 | -0.18311 | 46.6873 | 0.032044 | -0.21973 | 46.9849 | 46.9025 | 46.8338 | 0.21515 | 0.14649 | 43.071 | 42.8925 | 0.29755 | 75.9659 | 43.3044 | 76.2177 | 42.9474 | 122.905 | -123.23 | -76.1856 | 42.5354 | 122.6532 | 41.748 | 47.4518
2007.4844 | 122.8821 | -44.5633 | 78.5477 | -0.027161 | 0.0046207 | 0.042417 | 0.0034479 | -0.0021513 | 0.0019932 | -0.0050115 | -0.023224 | 0.0030997 | 0.005112 | 0.037429 | -0.0032386 | -0.00080758 | 0.0013779 | -3.0991 | -1.1719 | -44.8242 | -1.6479 | -1.474 | -44.8975 | -1.5335 | 1.0666 | 78.6713 | 2.2156 | 78.5614 | 2.5681 | 2.3987 | 2.5085 | -0.26093 | -79.7195 | -80.1956 | 43.0893 | 43.0298 | -0.33417 | 43.2907 | -0.073242 | 46.7789 | 0.1236 | 0.013733 | 47.1313 | 47.0718 | 46.962 | 0.29297 | 0.18311 | 43.3502 | 43.1763 | 0.35248 | 76.3458 | 43.6523 | 76.4557 | 43.3914 | 123.2346 | -123.3719 | -76.3321 | 42.9153 | 123.1247 | 41.4642 | 45.6299
2008.5469 | 123.317 | -45.076 | 78.0853 | -0.027161 | 0.0050479 | 0.043272 | 0.0023797 | 0.0019077 | -0.0012112 | -0.0035163 | 0.074432 | 0.00096348 | -0.0025784 | 0.040633 | -0.004093 | -0.0031574 | -0.0028945 | -3.891 | -1.9501 | -45.3552 | -2.2476 | -2.0554 | -45.1538 | -2.124 | 1.181 | 78.1677 | 2.2018 | 78.154 | 2.6596 | 2.5726 | 2.6093 | -0.27924 | -80.0354 | -80.3329 | 43.0206 | 42.952 | -0.07782 | 43.2312 | 0.20142 | 47.2778 | 0.082398 | 0.068665 | 47.7356 | 47.6852 | 47.6486 | 0.40741 | 0.37079 | 43.2999 | 43.1076 | 0.45776 | 75.9521 | 43.4052 | 75.9659 | 43.1259 | 123.2437 | -123.4406 | -75.8835 | 42.8284 | 123.23 | 41.185 | 46.257
2009.4844 | 123.2162 | -44.6091 | 78.0991 | -0.011902 | 0.0029117 | 0.040281 | 0.0060113 | -0.010696 | -0.0020658 | -0.0041571 | -0.065949 | 0.0035269 | -0.00044215 | 0.044051 | -0.002384 | -0.001662 | 0.0015915 | -4.5776 | -2.005 | -45.4193 | -2.4353 | -2.2888 | -45.3278 | -2.3438 | 1.1124 | 78.1403 | 2.2888 | 78.0441 | 2.6093 | 2.3712 | 2.5314 | -0.81024 | -80.1041 | -80.5344 | 42.3203 | 42.2653 | -0.71869 | 43.0756 | 0.091553 | 46.8979 | 0.041199 | -0.054932 | 47.2183 | 47.1405 | 46.9803 | 0.24261 | 0.082398 | 43.1305 | 42.984 | 0.32043 | 75.7553 | 43.4143 | 75.8514 | 42.6041 | 122.7493 | -123.5184 | -75.8102 | 42.1738 | 122.6532 | 40.0314 | 45.7214
2010.5469 | 123.4543 | -118.0161 | 5.2002 | -0.027161 | 0.0041935 | 0.12039 | 0.0036615 | -0.0019377 | 0.00028418 | -0.0011663 | 0.019501 | 0.13597 | 0.004471 | -0.003373 | -0.0028112 | -0.0040118 | 0.0039413 | -5.3467 | -2.7695 | -118.3914 | -3.1403 | -2.9572 | -118.0344 | -3.0121 | 0.40741 | 5.2551 | 4.6692 | 4.9301 | 4.9805 | 4.8981 | 4.9713 | -0.37537 | -7.9697 | -8.3405 | 115.0589 | 115.004 | -0.018311 | 115.3793 | 0.35706 | 122.6852 | 0.054932 | -0.27008 | 122.9965 | 122.9874 | 122.9141 | 0.30212 | 0.22888 | 115.4343 | 115.2512 | 0.31128 | 0.26093 | 115.6219 | 0.58594 | 115.2466 | 123.2712 | -123.5916 | -0.53101 | 114.8758 | 122.9462 | 112.6694 | 118.4235
2011.4844 | 119.2886 | -45.6665 | 77.6001 | -0.24078 | 0.0024845 | 0.043699 | 0.0043023 | -0.01326 | -0.00014322 | -0.0028753 | -0.084259 | 0.0026725 | 0.001694 | 0.040847 | -0.0021704 | -0.0018756 | 0.00095066 | -2.9755 | -1.9272 | -45.8496 | -2.3849 | -2.2476 | -45.845 | -2.3071 | 0.89722 | 77.742 | 1.6113 | 77.5772 | 1.9272 | 1.767 | 1.8631 | -0.1831 | -79.5273 | -79.985 | 43.4189 | 43.3594 | -0.17853 | 43.5425 | 0.004577 | 47.2778 | 0.14191 | -0.022889 | 47.5937 | 47.5296 | 47.4335 | 0.25177 | 0.15564 | 43.602 | 43.4647 | 0.31586 | 75.9659 | 43.9224 | 76.1307 | 43.7393 | 123.4085 | -123.4497 | -75.9888 | 43.2816 | 123.2437 | 42.691 | 46.5637
2012.4844 | 123.4772 | -117.3019 | 5.928 | 0.026245 | 0.0065433 | 0.11719 | 0.0045159 | -0.0012967 | 0.0013522 | -0.0020209 | -0.035431 | 0.13619 | 0.0046848 | -0.0031594 | -0.0021704 | -0.003371 | -0.00011754 | -5.3009 | -2.6871 | -117.7322 | -3.1448 | -2.9984 | -120.9366 | -3.0167 | 0.28381 | 5.9601 | 5.3284 | 5.8044 | 5.722 | 5.4153 | 5.5984 | -0.4303 | -8.6151 | -9.0729 | 114.3036 | 114.2853 | -3.6346 | 114.7156 | -3.2043 | 122.6303 | 0.032043 | -0.1236 | 123.024 | 122.9004 | 122.7173 | 0.27008 | 0.086975 | 114.7339 | 114.5874 | 0.39368 | 0.47607 | 115.0452 | 0.63171 | 114.6149 | 123.262 | -123.6603 | -0.59967 | 114.1571 | 123.1064 | 112.001 | 117.5858
2013.5469 | 123.4177 | -118.0481 | 5.2322 | -0.027161 | 0.0054751 | 0.11911 | 0.0043023 | 0.0012667 | -0.00099762 | -0.0020209 | -0.035431 | 0.13704 | 0.0031894 | 0.00025839 | -0.0038794 | -0.0040118 | -0.0028945 | -6.4774 | -2.8107 | -118.3777 | -3.2181 | -3.0579 | -117.9886 | -3.0945 | 0.3891 | 5.2963 | 4.7287 | 4.9896 | 4.9896 | 4.9393 | 5.0308 | -0.32959 | -8.0429 | -8.4503 | 114.9902 | 114.9536 | 0.05951 | 115.2832 | 0.3891 | 122.7768 | 0.064087 | -0.24261 | 123.0377 | 123.0789 | 122.9874 | 0.30212 | 0.21057 | 115.3198 | 115.1596 | 0.26093 | 0.26093 | 115.567 | 0.56763 | 115.2374 | 123.3444 | -123.6099 | -0.50354 | 114.83 | 123.0377 | 111.5707 | 118.4372
2014.4844 | 123.4222 | -118.158 | 5.1224 | -0.042419 | 0.0022709 | 0.11761 | 0.0066523 | 0.0021213 | -0.0022794 | 0.0024653 | -0.065949 | 0.13811 | 0.0055392 | -0.0016642 | -0.001316 | -0.0025164 | -0.0020401 | -8.1024 | -2.7512 | -118.5059 | -3.2043 | -3.0808 | -118.0664 | -3.0945 | 0.36163 | 5.2094 | 4.6051 | 4.9118 | 4.8889 | 4.8477 | 4.9576 | -0.3479 | -7.8735 | -8.3267 | 115.0772 | 115.0635 | 0.091553 | 115.4114 | 0.43945 | 122.7631 | 0.086976 | -0.21057 | 123.0469 | 123.1155 | 123.0057 | 0.35248 | 0.24261 | 115.4251 | 115.3015 | 0.28381 | 0.3067 | 115.7547 | 0.60425 | 115.4068 | 123.3673 | -123.6282 | -0.51727 | 114.9536 | 123.0698 | 110.0555 | 118.5196
2015.5469 | 123.3673 | -118.2724 | 5.0583 | -0.0042723 | 0.0016299 | 0.11953 | 0.0017389 | -0.0023649 | -0.0014248 | 0.00032907 | -0.035431 | 0.1364 | 0.0042574 | -0.0025186 | -0.0021704 | -0.0035846 | 0.0013779 | -5.3101 | -2.71 | -118.5928 | -3.1815 | -3.0075 | -118.2175 | -3.0624 | 0.41657 | 5.127 | 4.541 | 4.8248 | 4.7058 | 4.7516 | 4.8477 | -0.32043 | -7.7683 | -8.2397 | 115.2649 | 115.21 | 0.054932 | 115.5304 | 0.37537 | 122.8134 | 0.068664 | -0.23346 | 122.9782 | 123.1201 | 123.024 | 0.3067 | 0.21057 | 115.5853 | 115.4114 | 0.16479 | 0.28381 | 115.8829 | 0.58594 | 115.5624 | 123.3994 | -123.6511 | -0.51727 | 115.0909 | 123.0972 | 112.9623 | 118.689
2016.4844 | 123.3673 | -118.2632 | 5.0812 | -0.065308 | 0.0035525 | 0.11633 | 0.0036615 | 0.0029757 | -0.0029202 | -0.00095273 | -0.062897 | 0.13896 | 0.004471 | 0.0026084 | -0.0019568 | -0.0044392 | 0.0022323 | -5.5344 | -2.5681 | -118.5562 | -3.0579 | -2.916 | -118.1671 | -2.9434 | 0.3891 | 5.1086 | 4.541 | 4.834 | 4.6783 | 4.747 | 4.8569 | -0.29297 | -7.6492 | -8.139 | 115.3473 | 115.3198 | 0.096131 | 115.6128 | 0.3891 | 122.8043 | 0.027466 | -0.24719 | 122.9416 | 123.1201 | 123.0103 | 0.31586 | 0.20599 | 115.6403 | 115.4984 | 0.13733 | 0.29297 | 115.9882 | 0.56763 | 115.6952 | 123.3719 | -123.6374 | -0.54016 | 115.2054 | 123.0972 | 112.7289 | 118.6523
2017.5469 | 123.3627 | -118.3319 | 4.9942 | 0.0033567 | 0.0029117 | 0.11911 | 0.0034479 | 0.0021213 | -0.0016384 | -0.0028753 | -0.035431 | 0.13832 | 0.0053256 | -0.0012368 | -0.0038794 | -0.0029438 | -0.00033114 | -5.7861 | -2.5497 | -118.5837 | -2.9205 | -2.7328 | -118.1763 | -2.7969 | 0.50812 | 5.072 | 4.509 | 4.7928 | 4.6188 | 4.7104 | 4.834 | -0.25177 | -7.5439 | -7.9147 | 115.5991 | 115.535 | 0.15564 | 115.7867 | 0.40741 | 122.8409 | 0.077819 | -0.20142 | 122.9507 | 123.1659 | 123.0423 | 0.32501 | 0.20142 | 115.8508 | 115.6631 | 0.10986 | 0.28381 | 116.0339 | 0.56305 | 115.7822 | 123.4039 | -123.5779 | -0.48523 | 115.4114 | 123.1247 | 112.5458 | 118.84
2018.4844 | 123.349 | -118.8492 | 4.5319 | -0.019531 | 0.0026981 | 0.11847 | 0.0038751 | -0.00065586 | -0.00014322 | -0.0018073 | -0.0079652 | 0.13811 | 0.0029758 | 0.00089939 | -0.0021704 | -0.0018756 | 0.0054367 | -4.9438 | -2.5223 | -119.101 | -2.9251 | -2.7649 | -118.7347 | -2.8244 | 0.39368 | 4.5776 | 4.0009 | 4.2572 | 4.1245 | 4.2068 | 4.2938 | -0.25177 | -7.0541 | -7.457 | 116.0843 | 116.0248 | 0.11444 | 116.2766 | 0.36621 | 122.85 | 0.045777 | -0.27466 | 122.9736 | 123.143 | 123.056 | 0.29297 | 0.20599 | 116.3361 | 116.1758 | 0.1236 | 0.25635 | 116.5787 | 0.57678 | 116.3269 | 123.4268 | -123.6328 | -0.53101 | 115.9241 | 123.1064 | 113.9053 | 119.2429
2019.5469 | 123.3856 | -119.0186 | 4.3442 | -0.0042723 | 0.0039799 | 0.1221 | 0.0070795 | 0.0029757 | 0.0024204 | 0.00075627 | -0.081207 | 0.13811 | 0.0012668 | 0.0013266 | -0.003025 | -0.0023028 | 9.6064e-05 | -4.9805 | -2.5314 | -119.2978 | -2.98 | -2.861 | -118.959 | -2.8931 | 0.36621 | 4.4128 | 3.8315 | 4.1107 | 3.9825 | 4.0283 | 4.1473 | -0.27924 | -6.8756 | -7.3242 | 116.1575 | 116.1255 | 0.05951 | 116.4047 | 0.33875 | 122.85 | 0.068665 | -0.23346 | 123.0011 | 123.1659 | 123.0469 | 0.31586 | 0.19684 | 116.4368 | 116.3177 | 0.15106 | 0.27924 | 116.7664 | 0.58136 | 116.4871 | 123.4314 | -123.642 | -0.5127 | 116.0385 | 123.1293 | 114.0381 | 119.3848
2020.4844 | 123.3856 | -118.9728 | 4.3442 | 0.041504 | 0.0048343 | 0.12082 | 0.0053705 | 0.0019077 | 7.0582e-05 | -0.0026617 | -0.087311 | 0.13704 | 0.0042574 | -0.0029458 | -0.0025976 | -0.0014484 | -0.00011754 | -4.4861 | -2.5864 | -119.3115 | -3.0396 | -2.8702 | -118.7485 | -2.9022 | 0.37537 | 4.4357 | 3.8544 | 4.1748 | 4.1611 | 4.0741 | 4.1656 | -0.33874 | -6.9305 | -7.3837 | 116.1026 | 116.0706 | 0.2243 | 116.4093 | 0.56305 | 122.8271 | 0.091553 | -0.16937 | 123.1339 | 123.1384 | 123.0469 | 0.31128 | 0.21973 | 116.4413 | 116.272 | 0.3067 | 0.32044 | 116.7252 | 0.58136 | 116.3864 | 123.4085 | -123.6557 | -0.48981 | 115.9332 | 123.1476 | 114.4867 | 119.3481
2021.5469 | 123.3582 | -119.0826 | 4.2206 | -0.042419 | 0.0016299 | 0.12167 | 0.0034479 | -0.00086946 | 0.004343 | -0.0015935 | -0.026276 | 0.13875 | 0.0029758 | 0.00047219 | -0.0034522 | -0.00059378 | -0.00033114 | -5.8044 | -2.6779 | -119.3619 | -3.0258 | -2.8336 | -119.0643 | -2.8976 | 0.43488 | 4.2801 | 3.7308 | 4.0009 | 4.0375 | 3.9459 | 4.0237 | -0.27923 | -6.8985 | -7.2464 | 116.2491 | 116.185 | 0.018311 | 116.4642 | 0.29755 | 122.8134 | 0.059509 | -0.21973 | 123.1201 | 123.1064 | 123.0286 | 0.29297 | 0.21515 | 116.5283 | 116.3361 | 0.3067 | 0.27008 | 116.684 | 0.54932 | 116.4047 | 123.3627 | -123.5825 | -0.48981 | 116.0568 | 123.0835 | 113.2782 | 119.5175
2022.4844 | 123.349 | -118.5287 | 4.7791 | -0.042419 | 0.0037661 | 0.12103 | 0.0047295 | 0.0014803 | 0.00071138 | -0.0013799 | -0.10257 | 0.13747 | 0.0027622 | -0.0012368 | -0.0034522 | -0.0018756 | 0.0013779 | -6.2622 | -2.6733 | -118.8858 | -3.0716 | -2.9205 | -118.5379 | -2.9755 | 0.53101 | 4.866 | 4.2847 | 4.5685 | 4.5959 | 4.4998 | 4.6051 | -0.35706 | -7.4524 | -7.8506 | 115.6082 | 115.5533 | -0.009155 | 115.9103 | 0.3479 | 122.8134 | 0.086975 | -0.21057 | 123.1247 | 123.1339 | 123.0286 | 0.32043 | 0.21515 | 115.9653 | 115.8142 | 0.31128 | 0.28381 | 116.2125 | 0.58136 | 115.8554 | 123.3948 | -123.6649 | -0.49439 | 115.4572 | 123.0972 | 112.2665 | 119.0598
2023.5469 | 123.4589 | -118.7119 | 4.5868 | -0.0042723 | 0.0020573 | 0.11975 | 0.0043023 | -0.00086946 | 0.0011386 | 0.0011835 | 0.0072936 | 0.13747 | 0.0029758 | -0.00080961 | -0.0036658 | -0.0025164 | 0.0022323 | -5.9601 | -2.71 | -119.046 | -3.0029 | -2.8427 | -118.9545 | -2.8931 | 0.71869 | 4.3945 | 3.9734 | 4.4861 | 4.5227 | 4.454 | 4.4907 | -0.33417 | -7.2968 | -7.5897 | 115.8691 | 115.8188 | -0.24262 | 116.153 | 0.091553 | 122.6852 | -0.19226 | -0.10071 | 123.2346 | 123.2025 | 123.1659 | 0.51727 | 0.48065 | 116.2033 | 116.0431 | 0.54932 | 0.51269 | 116.3361 | 0.42114 | 116.0019 | 123.1064 | -123.6328 | -0.6134 | 115.7089 | 123.1979 | 112.7518 | 119.4305
2024.5 | 123.3719 | -119.133 | 4.1611 | -0.065308 | 0.0056889 | 0.1206 | 0.0053705 | 0.0044711 | 0.00071138 | -9.8328e-05 | -0.12088 | 0.13982 | 0.005112 | 0.001113 | -0.0034522 | -0.0014484 | 9.6064e-05 | -4.9896 | -2.6779 | -119.4351 | -3.1357 | -2.9984 | -119.1193 | -3.0441 | 0.40741 | 4.216 | 3.685 | 3.9688 | 3.9871 | 3.8864 | 4.0054 | -0.30212 | -6.839 | -7.2968 | 116.1346 | 116.0889 | 0.013733 | 116.391 | 0.31586 | 122.818 | 0.054931 | -0.19226 | 123.1201 | 123.1384 | 123.0194 | 0.32043 | 0.20142 | 116.4368 | 116.2994 | 0.30212 | 0.28381 | 116.7572 | 0.531 | 116.4551 | 123.349 | -123.5962 | -0.47607 | 115.9973 | 123.1018 | 114.1434 | 119.5404
2025.4844 | 123.3444 | -118.7073 | 4.628 | 0.018616 | 0.00098907 | 0.12082 | 0.0051569 | -1.486e-05 | 0.004343 | 0.00075627 | -0.075104 | 0.13854 | 0.0023348 | 0.0013266 | -0.0028112 | 0.00068782 | -0.0018265 | -5.6168 | -2.6413 | -119.0094 | -3.0945 | -2.9205 | -118.7073 | -2.9663 | 0.38452 | 4.7104 | 4.129 | 4.3716 | 4.2343 | 4.3213 | 4.4083 | -0.30212 | -7.2693 | -7.7225 | 115.7867 | 115.741 | 0 | 116.0431 | 0.30212 | 122.8363 | 0.082397 | -0.25635 | 122.9416 | 123.1155 | 123.0286 | 0.27924 | 0.19226 | 116.0889 | 115.9149 | 0.10529 | 0.24261 | 116.3681 | 0.58136 | 116.066 | 123.4177 | -123.6374 | -0.49896 | 115.6128 | 123.0789 | 113.0905 | 119.0918
2026.5469 | 123.4268 | -118.5928 | 4.6829 | 0.0033567 | 0.0039799 | 0.11911 | 0.0028069 | -0.00065586 | 0.0019932 | -0.0028753 | -0.011017 | 0.13619 | 0.0023348 | -0.0012368 | -0.0008886 | -0.001662 | 0.0018051 | -8.139 | -2.5909 | -118.9087 | -2.9251 | -2.742 | -118.4692 | -2.8015 | 0.52643 | 4.7195 | 4.216 | 4.5502 | 4.4128 | 4.5273 | 4.6097 | -0.31586 | -7.2739 | -7.608 | 115.8508 | 115.7913 | 0.1236 | 116.1072 | 0.43945 | 122.8088 | 0.036621 | -0.13275 | 123.0057 | 123.2025 | 123.1201 | 0.39368 | 0.31128 | 116.1667 | 115.9836 | 0.19684 | 0.33417 | 116.3177 | 0.50354 | 116.0019 | 123.3124 | -123.5916 | -0.46692 | 115.6677 | 123.143 | 110.4538 | 119.1193
2027.4844 | 123.3398 | -118.6249 | 4.6875 | 0.026245 | 0.0044071 | 0.11804 | 0.0053705 | 0.0021213 | 0.00071138 | -0.00095273 | -0.11172 | 0.13896 | 0.004471 | -0.004014 | -0.002384 | -0.00016658 | 0.00073706 | -4.4632 | -2.4902 | -118.9362 | -2.8885 | -2.7237 | -118.5837 | -2.8061 | 0.5127 | 4.7516 | 4.2068 | 4.4998 | 4.3259 | 4.4037 | 4.5273 | -0.31128 | -7.1777 | -7.576 | 115.9012 | 115.8188 | 0.041199 | 116.1301 | 0.35248 | 122.8317 | 0.064087 | -0.18768 | 122.9507 | 123.1522 | 123.0286 | 0.32043 | 0.19684 | 116.2125 | 116.0477 | 0.11902 | 0.29297 | 116.4459 | 0.54474 | 116.1346 | 123.3765 | -123.6237 | -0.48065 | 115.7364 | 123.1247 | 114.1617 | 119.1376
2028.5469 | 123.3902 | -118.5516 | 4.7333 | -0.080566 | 0.0052615 | 0.11932 | 0.0032343 | -0.0017239 | 7.0582e-05 | -0.0013799 | -0.035431 | 0.13982 | 0.0046848 | -0.00059601 | -0.0034522 | -0.0023028 | -0.00075834 | -4.2847 | -2.4857 | -118.8492 | -2.8427 | -2.6733 | -118.4235 | -2.7191 | 0.49896 | 4.7791 | 4.2664 | 4.5639 | 4.39 | 4.5181 | 4.6005 | -0.29755 | -7.2189 | -7.576 | 115.8783 | 115.8325 | 0.12817 | 116.1301 | 0.42572 | 122.818 | 0.045777 | -0.16937 | 122.9416 | 123.1522 | 123.0698 | 0.33417 | 0.25177 | 116.1758 | 116.0065 | 0.1236 | 0.29755 | 116.3635 | 0.5127 | 116.066 | 123.3307 | -123.5825 | -0.46692 | 115.7089 | 123.1155 | 114.267 | 119.0506
2029.5 | 123.3948 | -118.5608 | 4.6875 | -0.065308 | 0.0052615 | 0.12124 | 0.0025933 | 0.00041234 | 0.0019932 | 0.00032907 | -0.062897 | 0.13939 | 0.003403 | -0.0020914 | -0.004093 | -0.0012348 | 0.0033005 | -7.6126 | -2.536 | -118.9453 | -2.8152 | -2.6459 | -118.4372 | -2.7328 | 0.53558 | 4.7287 | 4.2023 | 4.5639 | 4.4037 | 4.4998 | 4.6051 | -0.38452 | -7.2235 | -7.5027 | 115.9149 | 115.8279 | 0.1236 | 116.2125 | 0.50812 | 122.7631 | 0.041199 | -0.1236 | 122.9645 | 123.1659 | 123.0606 | 0.40283 | 0.29755 | 116.2994 | 116.1301 | 0.20142 | 0.36163 | 116.4093 | 0.52643 | 116.0248 | 123.2895 | -123.6328 | -0.48523 | 115.7455 | 123.1247 | 110.9482 | 119.0964
2030.4844 | 123.3261 | -118.5608 | 4.7562 | -0.011902 | 0.0031253 | 0.11889 | 0.0049433 | -0.0019377 | 0.0017794 | 0.0016107 | -0.093414 | 0.13747 | 0.0038302 | -0.00016881 | -0.0032386 | -0.00080758 | 0.00030966 | -5.5756 | -2.5223 | -118.8492 | -2.9984 | -2.8839 | -118.4555 | -2.8976 | 0.40283 | 4.834 | 4.2709 | 4.5273 | 4.3808 | 4.4724 | 4.5685 | -0.28839 | -7.2784 | -7.7545 | 115.6769 | 115.6631 | 0.10529 | 115.9515 | 0.39368 | 122.8317 | 0.077819 | -0.22888 | 122.9416 | 123.1293 | 123.0331 | 0.29755 | 0.20142 | 115.9653 | 115.8508 | 0.10986 | 0.25635 | 116.3269 | 0.56305 | 116.0385 | 123.3948 | -123.6053 | -0.48523 | 115.5624 | 123.0881 | 112.9852 | 118.9636
2031.5469 | 123.2986 | -118.4509 | 4.9301 | -0.080566 | 0.0029117 | 0.11932 | 0.0045159 | -0.0015103 | -0.0012112 | 0.00032907 | -0.056793 | 0.13747 | 0.0036166 | -0.00080961 | -0.002384 | -0.0025164 | 9.6064e-05 | -6.5094 | -2.7191 | -118.7347 | -3.186 | -3.0258 | -118.1122 | -3.0441 | 0.46234 | 4.953 | 4.3213 | 4.6738 | 4.834 | 4.5136 | 4.541 | -0.28381 | -7.6492 | -8.1161 | 115.4251 | 115.4068 | 0.33875 | 115.6906 | 0.62256 | 122.7722 | 0.022888 | -0.25635 | 123.2849 | 122.9919 | 122.9645 | 0.21973 | 0.19226 | 115.7089 | 115.5487 | 0.51269 | 0.35248 | 116.0156 | 0.63171 | 115.7318 | 123.4039 | -123.6649 | -0.60883 | 115.2649 | 123.1247 | 111.9415 | 118.9133
2032.4844 | 123.3536 | -118.2358 | 5.0125 | -0.072937 | 0.0056889 | 0.11804 | 0.0025933 | 0.0019077 | -0.00078402 | -0.0018073 | -0.05069 | 0.13533 | 0.004471 | 0.00025839 | -0.002384 | -0.0031574 | 0.00030966 | -5.9555 | -2.8152 | -118.5608 | -3.1586 | -2.9892 | -118.2266 | -3.0487 | 0.50812 | 5.0674 | 4.4998 | 4.8065 | 4.7333 | 4.7287 | 4.7974 | -0.32501 | -7.8278 | -8.1711 | 115.2466 | 115.1871 | 0.009155 | 115.5121 | 0.33417 | 122.7356 | 0.054932 | -0.20599 | 122.9691 | 123.0331 | 122.9645 | 0.29755 | 0.22888 | 115.5716 | 115.4022 | 0.23346 | 0.3067 | 115.7455 | 0.56763 | 115.4205 | 123.3032 | -123.5733 | -0.51269 | 115.0772 | 123.0423 | 112.2803 | 118.7439
2033.4844 | 123.349 | -118.3456 | 4.9301 | 0.0033567 | 0.00056187 | 0.11889 | 0.0060113 | 0.0027621 | -0.00099762 | -0.0035163 | -0.096466 | 0.13811 | 0.0027622 | -0.0031594 | -0.0038794 | -0.00016658 | -0.0016129 | -5.6442 | -2.8107 | -118.6661 | -3.2639 | -3.1403 | -118.2907 | -3.1677 | 0.59052 | 5.0034 | 4.3625 | 4.7287 | 4.6234 | 4.5914 | 4.6875 | -0.32044 | -7.7408 | -8.194 | 115.2054 | 115.1779 | 0.054932 | 115.4984 | 0.37537 | 122.7081 | 0.073242 | -0.20142 | 122.9691 | 123.0331 | 122.937 | 0.32501 | 0.22888 | 115.5258 | 115.4022 | 0.26093 | 0.36621 | 115.8554 | 0.64087 | 115.535 | 123.349 | -123.5962 | -0.56763 | 115.0818 | 123.0743 | 112.7014 | 118.9362
2034.5469 | 123.3582 | -118.4006 | 4.8935 | -0.0042723 | 0.0041935 | 0.12103 | 0.0066523 | 0.0036165 | -0.00078402 | 0.00032907 | -0.10867 | 0.1379 | 0.004471 | 0.0030356 | -0.003025 | -0.0020892 | 0.0043687 | -4.9988 | -2.8152 | -118.6981 | -3.2227 | -2.8519 | -118.3136 | -3.0075 | 0.57678 | 5.0125 | 4.3716 | 4.6783 | 4.5776 | 4.5181 | 4.6463 | -0.29755 | -7.7087 | -8.1161 | 115.5487 | 115.3931 | 0.086975 | 115.6906 | 0.38452 | 122.7722 | 0.11902 | -0.21515 | 122.9782 | 123.0469 | 122.9187 | 0.27466 | 0.14648 | 115.8463 | 115.4755 | 0.20599 | 0.3067 | 115.8829 | 0.64087 | 115.5853 | 123.4131 | -123.5916 | -0.52185 | 115.1779 | 123.0789 | 113.4018 | 118.9774
2035.4844 | 123.3398 | -118.4555 | 4.8294 | -0.011902 | 0.0031253 | 0.1206 | 0.0055841 | 0.0055393 | 0.00028418 | 0.0018243 | -0.12698 | 0.13725 | 0.001694 | -0.00059601 | -0.0049476 | -0.0031574 | -0.0018265 | -8.963 | -2.7924 | -118.7988 | -3.2135 | -3.0441 | -118.3914 | -3.1082 | 0.71869 | 4.9026 | 4.3121 | 4.6234 | 4.6143 | 4.4952 | 4.6326 | -0.34332 | -7.6218 | -8.0429 | 115.4114 | 115.3473 | 0.064087 | 115.6906 | 0.40741 | 122.7676 | 0.073242 | -0.20599 | 123.0698 | 123.0881 | 122.9507 | 0.32043 | 0.1831 | 115.7547 | 115.5853 | 0.30212 | 0.31128 | 116.0065 | 0.59051 | 115.6631 | 123.3582 | -123.6282 | -0.51727 | 115.242 | 123.0789 | 109.4925 | 119.1742
2036.5469 | 123.3627 | -118.4784 | 4.7882 | -0.072937 | 0.0029117 | 0.1206 | 0.0032343 | 0.0021213 | 0.00092498 | -0.0041571 | -0.023224 | 0.13939 | 0.0036166 | -0.0052958 | -0.0008886 | -0.0025164 | 0.00073706 | -7.1274 | -2.7557 | -118.7668 | -3.1219 | -2.9572 | -118.4509 | -2.9938 | 0.41657 | 4.8431 | 4.3167 | 4.6234 | 4.5914 | 4.5547 | 4.6783 | -0.28839 | -7.5439 | -7.9102 | 115.5212 | 115.4846 | 0.027466 | 115.773 | 0.31586 | 122.7951 | 0.054932 | -0.16479 | 123.0698 | 123.1567 | 123.0331 | 0.36163 | 0.23804 | 115.8096 | 115.6448 | 0.27466 | 0.3067 | 116.011 | 0.52643 | 115.7227 | 123.3215 | -123.555 | -0.4715 | 115.3564 | 123.1018 | 111.351 | 118.895
2037.4844 | 123.2849 | -118.3502 | 4.9301 | -0.03479 | 0.0046207 | 0.11825 | 0.0066523 | -0.0034329 | -0.00057042 | 0.0013971 | -0.13614 | 0.1396 | 0.0025484 | 0.0021812 | -0.0045202 | -0.0020892 | -0.0018265 | -5.127 | -2.7145 | -118.7439 | -3.1219 | -2.9572 | -118.3182 | -3.035 | 0.43945 | 4.9118 | 4.3488 | 4.6463 | 4.5731 | 4.7928 | 4.8111 | -0.39368 | -7.6447 | -8.0521 | 115.3931 | 115.3152 | 0.032044 | 115.7089 | 0.42572 | 122.699 | -0.018311 | -0.28381 | 122.9233 | 123.1613 | 123.143 | 0.46234 | 0.44403 | 115.7867 | 115.6219 | 0.2243 | 0.29755 | 116.0294 | 0.56305 | 115.6357 | 123.262 | -123.674 | -0.58136 | 115.2283 | 122.9965 | 113.2233 | 118.7897
2038.5469 | 123.3032 | -118.4418 | 4.8706 | -0.011902 | 0.0048343 | 0.11996 | 0.0025933 | -0.0015103 | 0.0024204 | -0.0018073 | -0.038483 | 0.13768 | 0.003403 | 0.004531 | -0.0036658 | -0.0020892 | 9.6064e-05 | -6.5781 | -2.6642 | -118.6844 | -3.0579 | -2.8885 | -118.2175 | -2.9434 | 0.42114 | 4.9576 | 4.3854 | 4.6188 | 4.6463 | 4.5868 | 4.6783 | -0.24262 | -7.5348 | -7.9285 | 115.5533 | 115.4984 | 0.2243 | 115.741 | 0.46692 | 122.8271 | 0.086976 | -0.25177 | 123.0881 | 123.1201 | 123.0286 | 0.29297 | 0.20142 | 115.7959 | 115.6265 | 0.26093 | 0.23346 | 116.0202 | 0.57221 | 115.7776 | 123.3994 | -123.555 | -0.48523 | 115.3839 | 123.0606 | 111.8637 | 118.8629
2039.4844 | 123.3261 | -118.4097 | 4.9118 | -0.050049 | 0.0035525 | 0.12018 | 0.0040887 | 0.0019077 | 0.0015658 | -0.00095273 | -0.10257 | 0.13576 | 0.0048984 | 0.0026084 | -0.0021704 | -0.0018756 | -0.0039627 | -5.5069 | -2.7603 | -118.7393 | -3.1586 | -3.0029 | -118.3136 | -3.0762 | 0.55389 | 4.953 | 4.3854 | 4.7058 | 4.6417 | 4.6143 | 4.7379 | -0.32959 | -7.6721 | -8.0704 | 115.4068 | 115.3336 | 0.09613 | 115.6631 | 0.42572 | 122.7951 | 0.041199 | -0.20599 | 123.0515 | 123.1476 | 123.024 | 0.35248 | 0.22888 | 115.7364 | 115.5807 | 0.25635 | 0.32043 | 115.979 | 0.56763 | 115.6494 | 123.3627 | -123.6511 | -0.52643 | 115.2512 | 123.1155 | 112.9028 | 118.9636
2040.4844 | 123.3032 | -118.4189 | 4.9164 | 0.010986 | 0.0024845 | 0.1174 | 0.0032343 | -0.0034329 | 0.00049778 | -9.8328e-05 | -0.12393 | 0.13747 | 0.001694 | -0.004014 | -0.002384 | -0.0014484 | -0.00075834 | -6.221 | -2.7695 | -118.7347 | -3.2318 | -3.0899 | -118.103 | -2.9205 | 0.46234 | 5.0262 | 4.422 | 4.6417 | 4.6875 | 4.5868 | 4.6875 | -0.31586 | -7.6859 | -8.1482 | 115.329 | 115.4984 | 0.31586 | 115.8142 | 0.63171 | 122.8409 | 0.10986 | -0.27466 | 123.1064 | 123.1064 | 123.0057 | 0.2655 | 0.16479 | 115.6448 | 115.5029 | 0.2655 | 0.21973 | 115.9653 | 0.60425 | 115.6494 | 123.4451 | -123.6511 | -0.49438 | 115.1871 | 123.0606 | 112.1979 | 118.8812
2041.5469 | 123.3261 | -118.4647 | 4.8248 | -0.011902 | 0.0031253 | 0.11953 | 0.0047295 | -0.00044226 | 0.0049838 | -0.0015935 | -0.11172 | 0.13619 | 0.0025484 | -0.003373 | -0.002384 | -0.0012348 | 0.0026597 | -5.0995 | -2.7878 | -118.7531 | -3.1357 | -2.9709 | -118.3319 | -3.0945 | 0.43945 | 4.9438 | 4.39 | 4.6097 | 4.6005 | 4.541 | 4.6692 | -0.28839 | -7.6126 | -7.9605 | 115.4938 | 115.3702 | 0.13275 | 115.6586 | 0.42114 | 122.8546 | 0.11902 | -0.21515 | 123.0652 | 123.1339 | 123.0057 | 0.27923 | 0.15106 | 115.7822 | 115.6174 | 0.21057 | 0.21973 | 115.9653 | 0.55389 | 115.6769 | 123.4085 | -123.5779 | -0.43487 | 115.329 | 123.0743 | 113.3652 | 118.9041
2042.4844 | 123.3627 | -118.5242 | 4.7882 | 0.0033567 | 0.0041935 | 0.11975 | 0.0045159 | -1.486e-05 | 0.00092498 | -0.0024481 | -0.065949 | 0.1379 | 0.0046848 | -0.0038004 | -0.0028112 | -0.001662 | 0.0013779 | -6.7017 | -2.7832 | -118.8217 | -3.2501 | -3.1036 | -118.5059 | -3.1311 | 0.35248 | 4.8706 | 4.2755 | 4.5319 | 4.5639 | 4.4952 | 4.6005 | -0.29755 | -7.5714 | -8.0383 | 115.4205 | 115.3931 | 0.018311 | 115.6906 | 0.31586 | 122.7997 | 0.082397 | -0.25635 | 123.0881 | 123.1247 | 123.0194 | 0.32501 | 0.21973 | 115.7181 | 115.5716 | 0.28839 | 0.25635 | 116.0385 | 0.59509 | 115.741 | 123.3948 | -123.6099 | -0.51269 | 115.274 | 123.056 | 111.8225 | 118.8766
2043.5469 | 123.3673 | -118.2175 | 5.0812 | -0.03479 | 0.0052615 | 0.11975 | 0.0030207 | 0.00062594 | 0.0019932 | 0.00096987 | -0.0049134 | 0.13576 | 0.0046848 | -0.0012368 | -0.002384 | -0.0023028 | 0.0039413 | -5.3513 | -2.9343 | -118.4921 | -3.2455 | -3.0853 | -118.1122 | -3.1494 | 0.54932 | 5.1178 | 4.5731 | 4.866 | 4.8386 | 4.8477 | 4.921 | -0.27466 | -8.0154 | -8.3267 | 115.1321 | 115.0681 | 0.10528 | 115.3427 | 0.37994 | 122.7905 | 0.036621 | -0.21515 | 123.056 | 123.1384 | 123.0652 | 0.3479 | 0.27466 | 115.4068 | 115.2466 | 0.2655 | 0.29297 | 115.5579 | 0.54474 | 115.2832 | 123.3353 | -123.5733 | -0.50812 | 114.9719 | 123.0835 | 112.8662 | 118.7668
2044.4844 | 123.349 | -118.0298 | 5.2597 | 0.010986 | 0.0031253 | 0.11697 | 0.0060113 | -0.00022866 | 0.00049778 | -0.0020209 | -0.11783 | 0.13768 | 0.003403 | -0.0018778 | -0.0021704 | -0.00059378 | -0.0024673 | -5.777 | -2.8427 | -118.364 | -3.2318 | -3.0899 | -118.0023 | -3.1265 | 0.45776 | 5.3055 | 4.6692 | 5.04 | 4.9942 | 4.921 | 5.04 | -0.33417 | -8.1024 | -8.4915 | 114.9399 | 114.9033 | 0.027466 | 115.2374 | 0.36163 | 122.699 | 0.045776 | -0.21973 | 123.024 | 123.0698 | 122.9507 | 0.37079 | 0.25177 | 115.274 | 115.1321 | 0.32501 | 0.37079 | 115.5212 | 0.63629 | 115.1871 | 123.3353 | -123.6237 | -0.59052 | 114.798 | 123.0698 | 112.2528 | 118.4875
2045.5469 | 123.3994 | -45.5063 | 77.623 | -0.03479 | 0.0014163 | 0.045194 | 0.0023797 | -0.00022866 | 0.0019932 | 0.0011835 | 0.010345 | 0.0039541 | 0.0036166 | 0.038711 | -0.0028112 | -0.0029438 | 0.0018051 | -8.4915 | -1.5518 | -46.1975 | -1.8631 | -1.6983 | -45.8267 | -1.7258 | 1.9775 | 77.6413 | 2.0096 | 77.6459 | 2.4719 | 2.3392 | 2.4124 | -0.69122 | -79.1748 | -79.4861 | 43.808 | 43.7805 | -0.32043 | 44.4717 | 0.37079 | 47.5159 | 0.01831 | 0.022888 | 47.9782 | 47.9187 | 47.8455 | 0.40283 | 0.32959 | 44.4992 | 44.3344 | 0.46234 | 75.6363 | 44.6457 | 75.6317 | 43.9545 | 123.1476 | -123.8205 | -75.6134 | 43.6432 | 123.1522 | 37.0148 | 47.4838
2046.4844 | 122.937 | -44.6411 | 78.5202 | -0.042419 | 0.0039799 | 0.043699 | 0.0017389 | -0.0023649 | 7.0582e-05 | -0.0039435 | -0.020172 | 0.0033133 | 0.0053256 | 0.038711 | -0.0032386 | -0.001662 | -0.00054474 | -9.5856 | -1.0666 | -44.957 | -1.3962 | -1.2314 | -45.1263 | -1.2863 | 1.6525 | 78.6575 | 2.3804 | 78.5568 | 2.7603 | 2.5955 | 2.655 | -0.31586 | -79.5868 | -79.9164 | 43.4097 | 43.3548 | -0.48523 | 43.6707 | -0.16937 | 47.0215 | 0.13733 | 0.036621 | 47.4014 | 47.2961 | 47.2366 | 0.27466 | 0.21515 | 43.7256 | 43.5608 | 0.37994 | 76.1765 | 43.8904 | 76.2772 | 43.5745 | 123.2986 | -123.4772 | -76.1398 | 43.2449 | 123.1979 | 35.0555 | 46.2936
2047.4844 | 123.436 | -117.6682 | 5.4977 | 0.041504 | 0.00098907 | 0.12231 | 0.0049433 | -0.00086946 | -0.0012112 | -0.00031193 | -0.099518 | 0.13832 | 0.0031894 | 0.007308 | -0.0025976 | -0.0012348 | -0.0031081 | -7.5531 | -2.1835 | -118.1808 | -2.5772 | -2.4078 | -116.5695 | -2.4902 | 0.39825 | 5.5023 | 4.8935 | 5.2505 | 5.1819 | 5.2872 | 5.278 | -0.51269 | -7.6813 | -8.075 | 115.2603 | 115.1779 | 1.0986 | 115.6906 | 1.6113 | 122.5616 | 0.004577 | -0.24719 | 122.85 | 122.9462 | 122.9553 | 0.38452 | 0.39368 | 115.773 | 115.6036 | 0.28839 | 0.35706 | 115.9973 | 0.60883 | 115.4846 | 123.1705 | -123.6786 | -0.60425 | 115.0909 | 122.9187 | 110.1151 | 118.0664
2048.4844 | 119.0689 | -45.2866 | 78.0075 | 0.08728 | 0.0048343 | 0.043272 | 0.0057977 | 0.0012667 | -0.0022794 | 0.00096987 | -0.038483 | 0.0054495 | 0.0038302 | 0.036361 | -0.002384 | -0.0018756 | -0.0016129 | -5.3558 | -1.1215 | -45.4559 | -1.5747 | -1.4374 | -45.4926 | -1.4557 | 1.3275 | 78.0807 | 1.9958 | 77.9938 | 2.3621 | 2.2018 | 2.3117 | -0.16937 | -79.129 | -79.5822 | 43.8492 | 43.8309 | -0.20599 | 44.0002 | -0.036621 | 47.2824 | 0.073243 | -0.013733 | 47.6486 | 47.5983 | 47.4884 | 0.31586 | 0.20599 | 44.0186 | 43.8812 | 0.36621 | 75.9979 | 44.3344 | 76.0849 | 44.165 | 123.3673 | -123.4634 | -76.0117 | 43.7119 | 123.2803 | 39.9307 | 46.6141
2049.5469 | 122.5571 | -44.545 | 78.7857 | 0.0033567 | 0.0018435 | 0.043058 | 0.0038751 | 0.0036165 | 0.0015658 | -0.0011663 | -0.020172 | 0.0050223 | 0.0040438 | 0.036361 | -0.0017432 | -0.0031574 | 0.00030966 | -1.506 | -1.0757 | -44.6823 | -1.5198 | -1.3687 | -44.664 | -1.3916 | 1.3641 | 78.9047 | 3.8315 | 78.6575 | 4.2389 | 4.1565 | 4.2343 | -0.13733 | -79.8615 | -80.3055 | 43.1763 | 43.1534 | -0.11902 | 43.2907 | 0.018311 | 48.3765 | 0.11902 | -0.12817 | 48.7839 | 48.7793 | 48.7015 | 0.40283 | 0.32501 | 43.3136 | 43.1625 | 0.40741 | 74.8261 | 43.6066 | 75.0732 | 43.4692 | 123.4497 | -123.468 | -74.9542 | 43.0252 | 123.2025 | 43.0389 | 45.9091
2050.4844 | 123.4406 | -117.9337 | 5.2505 | 0.0033567 | 0.0012027 | 0.11911 | 0.0053705 | 0.0025485 | 0.0022068 | 0.00075627 | -0.075104 | 0.13747 | 0.0029758 | 0.0064536 | -0.0017432 | -0.0029438 | -0.0035355 | -3.3005 | -2.8748 | -118.3731 | -3.3417 | -3.186 | -118.0481 | -3.2318 | 0.49896 | 5.3146 | 4.6234 | 5.0491 | 4.921 | 4.8477 | 4.9667 | -0.43945 | -8.1253 | -8.5922 | 114.7476 | 114.7018 | -0.11444 | 115.1413 | 0.32501 | 122.5571 | 0.064087 | -0.20142 | 122.8546 | 122.9004 | 122.7814 | 0.34332 | 0.2243 | 115.1871 | 115.0314 | 0.29755 | 0.42572 | 115.4984 | 0.69122 | 115.0589 | 123.2483 | -123.6237 | -0.62714 | 114.592 | 122.9828 | 114.6332 | 118.4326
2051.5469 | 123.3994 | -118.0023 | 5.2597 | 0.026245 | 0.0026981 | 0.11975 | 0.0062249 | 0.00019874 | -0.00057042 | -0.00095273 | -0.065949 | 0.13939 | 0.001694 | -0.00016881 | -0.0032386 | -0.0012348 | -0.0018265 | -2.1973 | -1.8677 | -118.2953 | -2.3254 | -2.2018 | -117.8741 | -2.2247 | 0.54016 | 5.3558 | 4.6829 | 5.0583 | 4.9255 | 4.8569 | 4.9576 | -0.29297 | -7.1274 | -7.5851 | 115.8005 | 115.7776 | 0.12817 | 116.0706 | 0.42114 | 122.6852 | 0.09613 | -0.20142 | 122.9279 | 122.9599 | 122.8592 | 0.27466 | 0.17395 | 116.0934 | 115.9698 | 0.24262 | 0.37537 | 116.4276 | 0.67291 | 116.1346 | 123.3582 | -123.555 | -0.57678 | 115.6769 | 123.0606 | 115.8051 | 118.5425
2052.4844 | 123.4177 | -117.6224 | 5.603 | 0.056763 | -0.00029273 | 0.11825 | 0.0030207 | 0.00019874 | 0.00092498 | -0.0022345 | -0.075104 | 0.13747 | 0.0027622 | -0.0010232 | -0.0043066 | -0.0029438 | 0.00095066 | -3.479 | -2.9846 | -117.9565 | -3.4744 | -3.3234 | -117.5812 | -3.3463 | 0.75073 | 5.7266 | 5.0583 | 5.3833 | 5.3146 | 5.2597 | 5.3741 | -0.33417 | -8.5876 | -9.0775 | 114.299 | 114.2761 | 0.041198 | 114.6103 | 0.37537 | 122.6807 | 0.1236 | -0.21973 | 122.937 | 122.9965 | 122.8821 | 0.31586 | 0.20142 | 114.6332 | 114.4821 | 0.25635 | 0.32501 | 114.9719 | 0.66833 | 114.6378 | 123.349 | -123.5596 | -0.54474 | 114.1479 | 123.0057 | 114.1434 | 118.3731
2053.5469 | 123.3902 | -118.1625 | 5.1086 | -0.019531 | 0.0035525 | 0.11761 | 0.0025933 | 0.0021213 | -0.0014248 | -0.0045843 | -0.087311 | 0.13832 | 0.0048984 | -0.0025186 | -0.0017432 | -0.0014484 | 9.6064e-05 | -6.5964 | -2.9709 | -118.4921 | -3.3783 | -3.4241 | -118.0069 | -3.3096 | 0.48523 | 5.2231 | 4.6234 | 4.8981 | 4.8752 | 4.7928 | 4.9164 | -0.32959 | -8.0795 | -8.4869 | 114.7385 | 114.8529 | 0.15564 | 115.1825 | 0.48523 | 122.7859 | 0.11444 | -0.21057 | 123.0377 | 123.0789 | 122.9553 | 0.29297 | 0.16937 | 115.0681 | 115.1138 | 0.25177 | 0.27466 | 115.5212 | 0.59967 | 115.1917 | 123.3856 | -123.6008 | -0.48523 | 114.7842 | 123.0606 | 111.5662 | 118.6478
2054.4844 | 123.4085 | -118.158 | 5.159 | -0.027161 | 0.0031253 | 0.11719 | 0.0045159 | 0.0038303 | 0.0024204 | -9.8328e-05 | -0.10562 | 0.13747 | 0.004471 | -0.0012368 | -0.005802 | -0.0010212 | -0.0028945 | -3.5431 | -2.9892 | -118.4692 | -3.4287 | -3.2547 | -117.8146 | -3.3051 | 0.58136 | 5.2139 | 4.6326 | 4.9759 | 4.9255 | 4.8706 | 4.9896 | -0.31128 | -8.1482 | -8.5876 | 114.9033 | 114.8529 | 0.34332 | 115.1642 | 0.6546 | 122.7905 | 0.054931 | -0.18311 | 123.0835 | 123.1476 | 123.0286 | 0.35706 | 0.23804 | 115.2145 | 115.0406 | 0.29297 | 0.34332 | 115.48 | 0.58136 | 115.1688 | 123.3719 | -123.6282 | -0.52643 | 114.7293 | 123.1339 | 114.6149 | 118.7393
2055.5469 | 123.3582 | -118.1946 | 5.1453 | -0.065308 | 0.0031253 | 0.11996 | 0.0055841 | 0.0021213 | 0.0011386 | -0.00073913 | -0.11478 | 0.13982 | 0.0025484 | -0.00016881 | -0.0028112 | 4.7018e-05 | -0.00033114 | -3.6346 | -3.0579 | -118.4738 | -3.511 | -3.3554 | -118.0389 | -3.4424 | 0.55847 | 5.2048 | 4.6326 | 4.9393 | 4.8935 | 4.8019 | 4.9393 | -0.27924 | -8.2031 | -8.6563 | 114.8392 | 114.7522 | 0.15564 | 115.0314 | 0.43488 | 122.8271 | 0.059509 | -0.20599 | 123.0881 | 123.1338 | 122.9965 | 0.3067 | 0.16937 | 115.1184 | 114.9628 | 0.26093 | 0.3067 | 115.416 | 0.57221 | 115.1367 | 123.3994 | -123.6191 | -0.5127 | 114.6835 | 123.1338 | 114.5599 | 118.7531
2056.4844 | 123.3719 | -118.5745 | 4.7607 | 0.12543 | 0.0026981 | 0.11932 | 0.0057977 | -0.0012967 | 0.00028418 | 0.00054267 | -0.059845 | 0.13811 | 0.0055392 | 0.0013266 | -0.0019568 | -0.0018756 | 9.6064e-05 | -5.2643 | -3.4241 | -118.8034 | -3.9551 | -3.7903 | -118.4372 | -3.8086 | 0.52185 | 4.834 | 4.2664 | 4.5319 | 4.5227 | 4.4266 | 4.5593 | -0.22888 | -8.1848 | -8.7158 | 114.7842 | 114.7659 | 0.13733 | 114.9948 | 0.36621 | 122.8409 | 0.073242 | -0.22888 | 123.0972 | 123.1338 | 123.0011 | 0.29297 | 0.16022 | 115.0131 | 114.8483 | 0.25635 | 0.2655 | 115.3793 | 0.56763 | 115.1505 | 123.4085 | -123.5641 | -0.49438 | 114.6194 | 123.1064 | 113.3102 | 119.0964
2057.4844 | 123.3765 | -118.5425 | 4.7653 | -0.03479 | 0.0022709 | 0.11911 | 0.0062249 | 0.0016939 | -0.0014248 | -9.8328e-05 | -0.087311 | 0.13832 | 0.0029758 | 0.00047219 | -0.0002478 | -0.0018756 | 0.00095066 | -4.8203 | -2.3483 | -118.8538 | -2.742 | -2.5772 | -118.4738 | -2.6367 | 0.57678 | 4.834 | 4.2709 | 4.6097 | 4.5685 | 4.4769 | 4.5822 | -0.31128 | -7.1136 | -7.5073 | 115.9653 | 115.9058 | 0.068664 | 116.217 | 0.37994 | 122.8134 | 0.068664 | -0.15564 | 123.111 | 123.1247 | 123.0194 | 0.31128 | 0.20599 | 116.2766 | 116.1118 | 0.29755 | 0.33875 | 116.5054 | 0.56305 | 116.1942 | 123.3765 | -123.6191 | -0.49439 | 115.8005 | 123.1522 | 113.7222 | 119.1193
2058.4844 | 123.3444 | -118.5654 | 4.7699 | -0.027161 | 0.0050479 | 0.11847 | 0.0047295 | -0.0034329 | 0.0022068 | -0.0022345 | -0.044586 | 0.13725 | 0.0063938 | -0.0035868 | -0.003025 | -0.0014484 | 0.0013779 | -5.4291 | -2.3483 | -118.8492 | -2.6184 | -2.5635 | -118.6615 | -2.6596 | 0.48065 | 4.8706 | 4.2755 | 4.5364 | 4.5319 | 4.4357 | 4.541 | -0.28381 | -7.1182 | -7.3883 | 116.0019 | 115.9058 | -0.09613 | 116.1896 | 0.18768 | 122.8409 | 0.10071 | -0.23346 | 123.0972 | 123.1064 | 123.0011 | 0.2655 | 0.16022 | 116.2857 | 116.2308 | 0.25635 | 0.26093 | 116.5009 | 0.59509 | 116.217 | 123.436 | -123.6191 | -0.49438 | 115.947 | 123.1018 | 113.1363 | 119.046
2059.5469 | 123.3536 | -118.5745 | 4.7562 | -0.0042723 | 0.0029117 | 0.11825 | 0.0047295 | 0.0021213 | 0.0019932 | -0.0026617 | -0.062897 | 0.13832 | 0.001694 | -0.0014504 | -0.003025 | -0.0025164 | -0.00097194 | -5.7953 | -2.33 | -118.7897 | -2.8015 | -2.6367 | -118.3685 | -2.6733 | 0.50354 | 4.8477 | 4.2389 | 4.5273 | 4.5136 | 4.422 | 4.509 | -0.21515 | -7.0862 | -7.5577 | 115.9378 | 115.9012 | 0.20599 | 116.1163 | 0.42114 | 122.8134 | 0.091552 | -0.22888 | 123.0881 | 123.0835 | 122.9965 | 0.27008 | 0.18311 | 116.153 | 115.9882 | 0.27466 | 0.28839 | 116.4597 | 0.60883 | 116.2445 | 123.4222 | -123.5458 | -0.51727 | 115.773 | 123.1018 | 112.7792 | 119.0781
2060.4844 | 123.3353 | -118.5699 | 4.747 | 0.0033567 | 0.0041935 | 0.11783 | 0.0038751 | 0.0019077 | 0.0030612 | -0.00073913 | -0.038483 | 0.13768 | 0.001694 | -0.006791 | -0.0002478 | 0.001115 | 0.00073706 | -6.0837 | -2.2797 | -118.8721 | -2.774 | -2.6093 | -118.483 | -2.6276 | 0.81482 | 4.8294 | 4.1794 | 4.5044 | 4.4861 | 4.3625 | 4.4586 | -0.30212 | -7.0267 | -7.5211 | 115.9607 | 115.9424 | 0.086975 | 116.2445 | 0.3891 | 122.7493 | 0.082398 | -0.24261 | 123.056 | 123.0286 | 122.9324 | 0.27924 | 0.18311 | 116.2628 | 116.098 | 0.3067 | 0.32501 | 116.5924 | 0.65002 | 116.2903 | 123.3994 | -123.6191 | -0.56763 | 115.7959 | 123.0743 | 112.4863 | 119.3848
2061.5469 | 123.317 | -118.428 | 4.9255 | 0.010986 | 0.0039799 | 0.11996 | 0.0047295 | -0.0019377 | 0.0011386 | -9.8328e-05 | -0.038483 | 0.13747 | 0.0055392 | 0.001113 | -3.4196e-05 | -0.003371 | -0.00075834 | -7.8094 | -2.3621 | -118.6935 | -2.8244 | -2.6321 | -118.3273 | -2.6871 | 0.52185 | 4.9622 | 4.3121 | 4.6692 | 4.6143 | 4.5273 | 4.6097 | -0.2655 | -7.2876 | -7.7499 | 115.7959 | 115.741 | 0.10071 | 116.0065 | 0.36621 | 122.7402 | 0.036621 | -0.25635 | 123.0423 | 123.0377 | 122.9553 | 0.29755 | 0.21515 | 116.0614 | 115.8691 | 0.30212 | 0.35705 | 116.3315 | 0.65002 | 116.066 | 123.3902 | -123.6191 | -0.6134 | 115.6036 | 123.0972 | 110.6186 | 118.9499
2062.4844 | 123.3444 | -118.4006 | 4.9118 | 0.026245 | 0.0035525 | 0.11975 | 0.0066523 | 0.0023349 | 0.0011386 | 0.00075627 | -0.10257 | 0.13832 | 0.004471 | -0.0031594 | -0.003025 | -0.0012348 | -0.00075834 | -2.8336 | -2.3529 | -118.7393 | -2.7466 | -2.5589 | -118.2861 | -2.6367 | 0.70038 | 4.9438 | 4.4083 | 4.7058 | 4.715 | 4.6234 | 4.7241 | -0.33874 | -7.2647 | -7.6584 | 115.8417 | 115.7639 | 0.11444 | 116.1026 | 0.45319 | 122.8088 | 0.032044 | -0.20599 | 123.1155 | 123.1247 | 123.024 | 0.31586 | 0.21515 | 116.1804 | 115.9927 | 0.3067 | 0.29755 | 116.3864 | 0.53558 | 116.0477 | 123.3444 | -123.6511 | -0.50354 | 115.654 | 123.1064 | 115.567 | 119.101
2063.5469 | 123.3536 | -118.5013 | 4.8157 | -0.011902 | 0.0018435 | 0.11975 | 0.0036615 | 0.0027621 | -0.0027066 | -0.0011663 | -0.062897 | 0.13768 | 0.0019076 | 0.0019674 | -0.0025976 | -0.00059378 | -0.00097194 | -11.7462 | -2.3529 | -118.8034 | -2.8152 | -2.6642 | -118.3502 | -2.6733 | 0.61798 | 4.8843 | 4.2847 | 4.5868 | 4.5868 | 4.509 | 4.6097 | -0.30212 | -7.1686 | -7.6309 | 115.8371 | 115.8279 | 0.15106 | 116.1301 | 0.45319 | 122.7859 | 0.068664 | -0.22888 | 123.0881 | 123.111 | 123.0103 | 0.32501 | 0.2243 | 116.1392 | 115.9882 | 0.30212 | 0.30212 | 116.4505 | 0.59967 | 116.1484 | 123.3856 | -123.6191 | -0.53101 | 115.686 | 123.0881 | 106.7551 | 119.1193
2064.4844 | 123.4131 | -118.3777 | 4.866 | 0.010986 | 0.0037661 | 0.11911 | 0.0047295 | 0.0019077 | -0.0016384 | -0.0018073 | -0.041534 | 0.1379 | 0.0027622 | -0.0010232 | -0.0025976 | -0.0018756 | 0.0026597 | -31.485 | -2.2751 | -118.7714 | -2.7603 | -2.6276 | -118.3731 | -2.6505 | 0.63629 | 4.9118 | 4.3213 | 4.6143 | 4.6005 | 4.5273 | 4.6143 | -0.39368 | -7.1411 | -7.6263 | 115.7501 | 115.7272 | 0.004578 | 116.1209 | 0.39825 | 122.699 | 0.045776 | -0.25177 | 122.9782 | 122.9919 | 122.905 | 0.29297 | 0.20599 | 116.1438 | 116.011 | 0.27924 | 0.29297 | 116.4963 | 0.59051 | 116.1026 | 123.2895 | -123.6374 | -0.54474 | 115.6174 | 122.9919 | 86.8927 | 119.014
2065.4844 | 123.4085 | -118.0893 | 5.1773 | -0.042419 | 0.0029117 | 0.11932 | 0.0030207 | 0.0036165 | -0.00014322 | -0.0022345 | -0.096466 | 0.13811 | 0.004471 | 0.00389 | -0.001316 | -0.001662 | -0.00054474 | -15.0833 | -2.298 | -118.4692 | -2.6825 | -2.5085 | -118.0389 | -2.5909 | 0.75073 | 5.191 | 4.6463 | 4.985 | 4.9667 | 4.8843 | 5.0079 | -0.37994 | -7.4753 | -7.8598 | 115.5807 | 115.4984 | 0.050354 | 115.8783 | 0.4303 | 122.7356 | 0.013733 | -0.19226 | 123.056 | 123.0972 | 122.9736 | 0.36163 | 0.23804 | 115.9607 | 115.7867 | 0.32043 | 0.33874 | 116.1713 | 0.54474 | 115.7913 | 123.2803 | -123.6465 | -0.53101 | 115.4068 | 123.0743 | 103.006 | 118.84
2066.5469 | 123.3398 | -118.2861 | 5.04 | 0.056763 | 0.0033389 | 0.11697 | 0.0053705 | -0.0015103 | 0.00092498 | -0.0020209 | -0.047638 | 0.1396 | 0.0042574 | -0.0055094 | -0.0017432 | -0.001662 | 0.00073706 | -15.9714 | -2.2476 | -118.6249 | -2.71 | -2.5635 | -118.2449 | -2.5864 | 0.61798 | 5.0674 | 4.4724 | 4.7607 | 4.7791 | 4.66 | 4.8065 | -0.33874 | -7.2876 | -7.7499 | 115.7227 | 115.6998 | 0.041199 | 116.0385 | 0.37994 | 122.7585 | 0.027466 | -0.27924 | 123.0652 | 123.0927 | 122.9462 | 0.33417 | 0.18768 | 116.0614 | 115.9149 | 0.3067 | 0.28839 | 116.3773 | 0.59509 | 116.0385 | 123.3536 | -123.6649 | -0.56763 | 115.5762 | 123.0469 | 102.3148 | 118.9041
2067.4844 | 123.3673 | -118.4738 | 4.834 | -0.011902 | 0.0037661 | 0.11953 | 0.0049433 | 0.0029757 | 0.0022068 | -0.00095273 | -0.081207 | 0.13939 | 0.0055392 | 0.00068579 | -0.0015296 | -0.00038018 | -0.00075834 | -11.1465 | -2.2705 | -118.7897 | -2.6917 | -2.5406 | -118.4189 | -2.5772 | 0.66376 | 4.8981 | 4.335 | 4.6371 | 4.6555 | 4.5502 | 4.6738 | -0.31586 | -7.1045 | -7.5256 | 115.9332 | 115.8966 | 0.054932 | 116.2125 | 0.37079 | 122.8088 | 0.064087 | -0.19684 | 123.1293 | 123.1476 | 123.024 | 0.33874 | 0.21515 | 116.2491 | 116.098 | 0.32043 | 0.30212 | 116.5192 | 0.56305 | 116.2033 | 123.3719 | -123.6237 | -0.49896 | 115.7822 | 123.111 | 107.3273 | 119.1376
2068.5469 | 123.4406 | -118.5745 | 4.6646 | -0.027161 | 0.0020573 | 0.12039 | 0.0036615 | -0.0025785 | 0.00071138 | 0.0026789 | 0.019501 | 0.13597 | 0.001694 | -0.004014 | -0.0032386 | -0.0029438 | 0.0011643 | -6.4819 | -2.3209 | -118.8492 | -2.623 | -2.4353 | -118.4052 | -2.4948 | 0.77362 | 4.7379 | 4.2435 | 4.5731 | 4.6188 | 4.5456 | 4.628 | -0.27466 | -6.9855 | -7.2876 | 116.1392 | 116.0797 | 0.16937 | 116.3544 | 0.44403 | 122.818 | 0.073242 | -0.091553 | 123.1934 | 123.2025 | 123.1201 | 0.38452 | 0.30212 | 116.4139 | 116.2262 | 0.37537 | 0.32959 | 116.5283 | 0.49438 | 116.2537 | 123.3124 | -123.5138 | -0.42114 | 115.9515 | 123.1476 | 112.0926 | 119.3481
2069.4844 | 123.3307 | -118.5379 | 4.7653 | -0.019531 | 0.0029117 | 0.11996 | 0.0047295 | 0.0031893 | 0.00092498 | 0.00075627 | -0.11172 | 0.1396 | 0.0031894 | -0.00038241 | -0.0025976 | -0.00016658 | 0.0011643 | -4.0512 | -2.2934 | -118.8263 | -2.7328 | -2.5818 | -118.4875 | -2.6413 | 0.64087 | 4.834 | 4.2435 | 4.5456 | 4.4815 | 4.3808 | 4.509 | -0.28839 | -7.0587 | -7.4982 | 115.9561 | 115.8966 | 0.050354 | 116.185 | 0.33875 | 122.7814 | 0.068664 | -0.21973 | 123.0194 | 123.0469 | 122.9187 | 0.2655 | 0.13733 | 116.2445 | 116.0934 | 0.23804 | 0.30212 | 116.5329 | 0.59051 | 116.2445 | 123.3719 | -123.5916 | -0.52185 | 115.8051 | 123.0835 | 114.4867 | 119.1788
2070.5469 | 123.3215 | -118.5333 | 4.7882 | -0.0042723 | 0.0044071 | 0.11847 | 0.0028069 | 0.0029757 | 0.00071138 | 0.0016107 | -0.032379 | 0.13597 | 0.0010532 | 0.0021812 | -0.0034522 | -0.0035846 | -0.0039627 | -3.7765 | -2.3621 | -118.7714 | -2.7237 | -2.5818 | -118.396 | -2.6184 | 0.62714 | 4.8614 | 4.2343 | 4.5639 | 4.5227 | 4.4357 | 4.4998 | -0.23804 | -7.1503 | -7.5119 | 115.9515 | 115.9149 | 0.13733 | 116.153 | 0.37537 | 122.7676 | 0.073242 | -0.2243 | 123.056 | 123.0331 | 122.9691 | 0.2655 | 0.20142 | 116.1896 | 116.0477 | 0.28839 | 0.32959 | 116.4093 | 0.62714 | 116.1713 | 123.3948 | -123.5596 | -0.55389 | 115.8096 | 123.0972 | 114.7568 | 119.1605
2071.4844 | 123.317 | -118.4326 | 4.866 | -0.03479 | 0.0031253 | 0.11889 | 0.0070795 | 0.0019077 | 0.00049778 | -0.00073913 | -0.12698 | 0.13747 | 0.005112 | -0.0072184 | -0.003025 | -0.0010212 | 9.6064e-05 | -4.097 | -2.2797 | -118.7714 | -2.7557 | -2.6093 | -118.4235 | -2.6688 | 0.56305 | 4.9118 | 4.2709 | 4.628 | 4.5364 | 4.4266 | 4.5731 | -0.33875 | -7.1457 | -7.6218 | 115.8234 | 115.7639 | 0.009155 | 116.1026 | 0.3479 | 122.7036 | 0.045776 | -0.23804 | 122.9691 | 123.0057 | 122.8592 | 0.30212 | 0.15564 | 116.1621 | 116.0156 | 0.2655 | 0.35706 | 116.4917 | 0.64087 | 116.153 | 123.3444 | -123.6374 | -0.59509 | 115.6769 | 123.0606 | 114.3356 | 118.9957
2072.5469 | 123.4131 | -118.2999 | 4.953 | 0.010986 | 0.0026981 | 0.11953 | 0.0047295 | 0.0029757 | 7.0582e-05 | -0.00073913 | -0.096466 | 0.1396 | 0.00083965 | -0.0010232 | -0.002384 | -0.0035846 | -0.0016129 | -3.5843 | -2.3483 | -118.6661 | -2.774 | -2.6184 | -118.3594 | -2.655 | 0.61798 | 5.0125 | 4.4449 | 4.7653 | 4.7562 | 4.6555 | 4.7791 | -0.36621 | -7.3013 | -7.7271 | 115.6815 | 115.6448 | -0.059509 | 116.011 | 0.3067 | 122.7448 | 0.059509 | -0.18768 | 123.056 | 123.0789 | 122.9553 | 0.33417 | 0.21057 | 116.0477 | 115.892 | 0.31128 | 0.32043 | 116.3177 | 0.56763 | 115.9515 | 123.3124 | -123.6191 | -0.50812 | 115.5258 | 123.0652 | 114.7156 | 118.9178
2073.4844 | 123.3627 | -118.222 | 5.0583 | -0.019531 | 0.0014163 | 0.12082 | 0.0045159 | 0.0036165 | 0.00049778 | 0.00054267 | -0.096466 | 0.13768 | 0.0025484 | -0.0027322 | -0.0038794 | -0.0010212 | 9.6064e-05 | -3.0075 | -2.3438 | -118.5013 | -2.774 | -2.6001 | -117.9794 | -2.6871 | 0.62256 | 5.1224 | 4.5914 | 4.8569 | 4.834 | 4.7333 | 4.8569 | -0.27924 | -7.402 | -7.8323 | 115.6219 | 115.535 | 0.24262 | 115.8142 | 0.52185 | 122.8134 | 0.064086 | -0.20142 | 123.056 | 123.0789 | 122.9553 | 0.2655 | 0.14191 | 115.9012 | 115.7272 | 0.24261 | 0.2655 | 116.1575 | 0.531 | 115.8783 | 123.3444 | -123.5596 | -0.46692 | 115.448 | 123.0789 | 115.2145 | 118.8446
2074.5469 | 123.468 | -118.2083 | 5.0171 | -0.057678 | 0.0031253 | 0.11804 | 0.0023797 | -0.00065586 | 7.0582e-05 | -0.0054389 | 0.022552 | 0.13683 | 0.0038302 | -0.0065774 | -0.0025976 | -0.0037982 | 0.00073706 | -2.7695 | -2.3117 | -118.4921 | -2.623 | -2.4216 | -118.0481 | -2.4948 | 0.75531 | 5.0629 | 4.5593 | 4.9164 | 4.9118 | 4.8889 | 4.9713 | -0.28381 | -7.3288 | -7.6401 | 115.7867 | 115.7135 | 0.16022 | 115.9973 | 0.44403 | 122.7676 | 0.045776 | -0.10071 | 123.1201 | 123.1796 | 123.0972 | 0.41199 | 0.32959 | 116.0706 | 115.8691 | 0.35248 | 0.35706 | 116.1804 | 0.50354 | 115.8966 | 123.2712 | -123.5092 | -0.45776 | 115.5853 | 123.1247 | 115.4388 | 118.9636
2075.4844 | 123.3261 | -118.3044 | 5.0079 | -0.10345 | 0.0054751 | 0.11975 | 0.0036615 | 0.0010531 | 0.00071138 | -0.0028753 | -0.13004 | 0.13704 | 0.0025484 | 0.0013266 | -0.0036658 | -0.0010212 | 0.0041551 | -4.2938 | -2.2476 | -118.6295 | -2.7328 | -2.6093 | -118.2724 | -2.6093 | 0.54932 | 5.1132 | 4.5044 | 4.7791 | 4.5959 | 4.6555 | 4.7928 | -0.32501 | -7.2556 | -7.7408 | 115.6952 | 115.6952 | 0.032043 | 116.0202 | 0.35706 | 122.8088 | 0.10529 | -0.22888 | 122.9004 | 123.0972 | 122.9599 | 0.28839 | 0.15106 | 116.0202 | 115.8966 | 0.091552 | 0.27466 | 116.3818 | 0.60883 | 116.0568 | 123.4177 | -123.6374 | -0.50354 | 115.5716 | 123.0835 | 114.0106 | 118.8538
2076.5469 | 123.3307 | -118.3365 | 5.0171 | 0.041504 | 0.0046207 | 0.11847 | 0.0060113 | 0.00019874 | -0.0012112 | -0.0052251 | -0.053741 | 0.1379 | 0.0036166 | 4.4788e-05 | -0.004093 | -0.0029438 | -0.0011855 | -4.0009 | -2.0508 | -118.5883 | -2.4994 | -2.3392 | -118.277 | -2.3666 | 0.6134 | 5.1086 | 4.541 | 4.7882 | 4.6555 | 4.7195 | 4.8203 | -0.25177 | -7.0679 | -7.5165 | 115.9973 | 115.9698 | 0.059509 | 116.2216 | 0.31128 | 122.8775 | 0.091553 | -0.22888 | 122.9919 | 123.1567 | 123.056 | 0.27923 | 0.17853 | 116.2491 | 116.0889 | 0.11444 | 0.24719 | 116.5375 | 0.56763 | 116.2857 | 123.4451 | -123.6053 | -0.47607 | 115.8371 | 123.1247 | 114.3356 | 118.9499
2077.4844 | 123.317 | -118.5333 | 4.7836 | -0.042419 | 0.0037661 | 0.12039 | 0.0064385 | 0.0019077 | 7.0582e-05 | -0.00052553 | -0.11783 | 0.1396 | 0.0038302 | 4.4788e-05 | -0.0021704 | -0.0025164 | 0.00052346 | -5.1636 | -2.1011 | -118.8217 | -2.5909 | -2.449 | -118.515 | -2.4857 | 0.52643 | 4.866 | 4.2709 | 4.5547 | 4.5273 | 4.4357 | 4.5685 | -0.28839 | -6.8848 | -7.3746 | 116.0843 | 116.0477 | 0.01831 | 116.3361 | 0.3067 | 122.8043 | 0.082398 | -0.22888 | 123.0606 | 123.1018 | 122.9691 | 0.29755 | 0.1648 | 116.3727 | 116.2308 | 0.25635 | 0.28381 | 116.7206 | 0.59509 | 116.4322 | 123.3994 | -123.6053 | -0.51269 | 115.9424 | 123.0881 | 113.3698 | 119.0598
2078.5469 | 123.3078 | -118.5837 | 4.7653 | -0.057678 | 0.0024845 | 0.11932 | 0.0030207 | -0.0027921 | 0.00071138 | -0.00073913 | -0.035431 | 0.13875 | 0.0042574 | -0.005082 | -0.0028112 | -0.00080758 | 0.0015915 | -4.0329 | -2.1744 | -118.8446 | -2.6184 | -2.449 | -117.5858 | -2.4811 | 0.62256 | 4.8386 | 4.248 | 4.4952 | 4.3716 | 4.4357 | 4.5273 | -0.26093 | -6.9397 | -7.3837 | 116.1346 | 116.1026 | 0.99793 | 116.3635 | 1.2589 | 122.8317 | 0.073242 | -0.27008 | 122.9553 | 123.111 | 123.0194 | 0.27924 | 0.18768 | 116.3956 | 116.2262 | 0.1236 | 0.24719 | 116.6702 | 0.59051 | 116.4093 | 123.4222 | -123.6099 | -0.51727 | 115.9653 | 123.0789 | 114.5508 | 119.2062
2079.4844 | 123.2712 | -118.5333 | 4.7882 | -0.011902 | 0.0046207 | 0.11868 | 0.0064385 | 0.0023349 | 0.00028418 | 0.00011527 | -0.10867 | 0.13811 | 0.0055392 | 0.002822 | -0.003025 | -0.00016658 | 0.00073706 | -5.5435 | -2.2385 | -118.8812 | -2.6825 | -2.5681 | -118.6249 | -2.5955 | 0.56305 | 4.8614 | 4.2847 | 4.5547 | 4.3304 | 4.4495 | 4.5822 | -0.3479 | -7.0267 | -7.4707 | 115.9653 | 115.9378 | -0.091553 | 116.2857 | 0.25635 | 122.818 | 0.073242 | -0.23346 | 122.8638 | 123.1155 | 122.9828 | 0.29755 | 0.16479 | 116.3132 | 116.1987 | 0.045776 | 0.27008 | 116.6428 | 0.57678 | 116.2949 | 123.3948 | -123.6694 | -0.50354 | 115.8508 | 123.0881 | 112.9898 | 119.0964
2080.5469 | 123.3902 | -118.3823 | 4.8523 | -0.088196 | 0.0037661 | 0.12039 | 0.0023797 | -0.0010831 | 0.0028476 | -0.0018073 | -0.029327 | 0.13747 | 0.0031894 | -0.0020914 | -0.003025 | -0.0040118 | 0.0035141 | -4.5959 | -2.2385 | -118.689 | -2.5818 | -2.4261 | -117.8192 | -2.4719 | 0.66376 | 4.9026 | 4.4083 | 4.6921 | 4.5227 | 4.6738 | 4.7653 | -0.3067 | -7.0908 | -7.4341 | 115.9561 | 115.9103 | 0.56305 | 116.217 | 0.86975 | 122.7905 | 0.050354 | -0.16022 | 122.905 | 123.1476 | 123.056 | 0.35706 | 0.2655 | 116.2628 | 116.1072 | 0.11444 | 0.28381 | 116.4505 | 0.49439 | 116.1438 | 123.2849 | -123.5413 | -0.44403 | 115.8005 | 123.0743 | 113.7863 | 119.046
2081.4844 | 123.3032 | -118.3868 | 4.9026 | -0.088196 | 0.0048343 | 0.11847 | 0.0060113 | -0.0012967 | 0.0032748 | 0.00096987 | 0.040863 | 0.13875 | 0.0036166 | 0.0015402 | -0.0043066 | -0.0031574 | -0.0035355 | -6.0883 | -2.1835 | -118.6981 | -2.6459 | -2.5131 | -118.364 | -2.5406 | 0.52185 | 4.9988 | 4.4312 | 4.6783 | 4.4128 | 4.5868 | 4.7241 | -0.31128 | -7.0862 | -7.5485 | 115.8737 | 115.8463 | 0.022888 | 116.1575 | 0.33417 | 122.818 | 0.09613 | -0.2243 | 122.7997 | 123.111 | 122.9736 | 0.29297 | 0.15564 | 116.185 | 116.0522 | -0.01831 | 0.24719 | 116.5146 | 0.56763 | 116.2033 | 123.3856 | -123.6008 | -0.4715 | 115.741 | 123.0652 | 112.2986 | 118.9087
2082.5469 | 123.3261 | -118.364 | 4.9301 | 0.0033567 | 0.0039799 | 0.11761 | 0.0066523 | 0.0016939 | 0.00028418 | -0.0033025 | -0.093414 | 0.13896 | 0.0057528 | 0.0021812 | -0.0036658 | -0.0014484 | -0.0024673 | -6.4865 | -2.1286 | -118.6935 | -2.6276 | -2.4765 | -118.2724 | -2.504 | 0.59967 | 4.9759 | 4.4312 | 4.6875 | 4.4724 | 4.6326 | 4.7333 | -0.32959 | -7.0587 | -7.5577 | 115.8875 | 115.86 | 0.091553 | 116.1896 | 0.42114 | 122.7951 | 0.045776 | -0.24261 | 122.8363 | 123.0972 | 122.9965 | 0.30212 | 0.20142 | 116.217 | 116.066 | 0.041199 | 0.25635 | 116.5649 | 0.54474 | 116.2354 | 123.3398 | -123.6237 | -0.49896 | 115.7364 | 123.0515 | 111.8774 | 118.9636
2083.4844 | 123.2666 | -118.364 | 4.9301 | -0.050049 | 0.0031253 | 0.11825 | 0.0053705 | -1.486e-05 | -0.00099762 | -0.0020209 | -0.096466 | 0.13811 | 0.0025484 | 0.0021812 | -0.0002478 | -0.00016658 | -0.0046035 | -5.896 | -2.1698 | -118.6981 | -2.6413 | -2.5223 | -118.3914 | -2.5269 | 0.5722 | 4.9942 | 4.4266 | 4.6921 | 4.4769 | 4.7928 | 4.834 | -0.33417 | -7.0999 | -7.5714 | 115.8417 | 115.8371 | -0.027465 | 116.1713 | 0.3067 | 122.7905 | 0.064087 | -0.23804 | 122.8409 | 123.1979 | 123.1567 | 0.40741 | 0.36621 | 116.1758 | 116.0568 | 0.050354 | 0.2655 | 116.5283 | 0.56763 | 116.1942 | 123.3582 | -123.6282 | -0.50354 | 115.7227 | 123.056 | 112.468 | 118.9362
2084.5469 | 123.3124 | -118.2632 | 5.0491 | -0.011902 | 0.0041935 | 0.11932 | 0.0036615 | -0.0010831 | -0.00057042 | -0.0026617 | -0.020172 | 0.13661 | 0.00618 | -0.0072184 | -0.0032386 | -0.0029438 | 0.0028733 | -4.5181 | -2.0782 | -118.5379 | -2.4399 | -2.2568 | -118.0801 | -2.3071 | 0.63629 | 5.0858 | 4.5502 | 4.7974 | 4.6143 | 4.7607 | 4.834 | -0.27466 | -7.1274 | -7.489 | 116.0065 | 115.9561 | 0.18311 | 116.2308 | 0.45776 | 122.8134 | 0.036621 | -0.25177 | 122.8775 | 123.0972 | 123.024 | 0.28381 | 0.21057 | 116.2811 | 116.098 | 0.064087 | 0.24719 | 116.4597 | 0.53558 | 116.185 | 123.349 | -123.587 | -0.49896 | 115.8234 | 123.0606 | 113.7451 | 118.8995
2085.4844 | 123.2849 | -118.2587 | 5.0446 | -0.050049 | 0.0039799 | 0.11911 | 0.0057977 | 0.0021213 | 0.0019932 | -0.0018073 | -0.11172 | 0.13832 | 0.0031894 | 0.00389 | -0.0034522 | -0.0014484 | 0.00052346 | -3.7079 | -1.9272 | -118.5974 | -2.4078 | -2.2659 | -118.3136 | -2.2934 | 0.56305 | 5.1041 | 4.5319 | 4.8019 | 4.4861 | 4.6967 | 4.8294 | -0.33875 | -6.9717 | -7.4524 | 115.9927 | 115.9653 | -0.054932 | 116.304 | 0.28381 | 122.7905 | 0.059509 | -0.24261 | 122.7448 | 123.0881 | 122.9553 | 0.29755 | 0.16479 | 116.3315 | 116.1896 | -0.045776 | 0.27008 | 116.6702 | 0.57221 | 116.3315 | 123.3627 | -123.642 | -0.5127 | 115.8508 | 123.0606 | 114.5508 | 118.8217
2086.5469 | 123.2986 | -118.2129 | 5.0995 | -0.019531 | 0.0029117 | 0.11932 | 0.0030207 | 0.00041234 | 0.00049778 | -0.0024481 | -0.032379 | 0.13939 | 0.0048984 | -0.0035868 | -0.0034522 | -0.0046528 | -0.0013991 | -5.6671 | -1.9455 | -118.5059 | -2.4033 | -2.2385 | -118.1808 | -2.2522 | 0.63171 | 5.1544 | 4.5639 | 4.834 | 4.5776 | 4.7882 | 4.8843 | -0.29297 | -7.045 | -7.5027 | 115.9744 | 115.9607 | 0.032044 | 116.2537 | 0.32501 | 122.7768 | 0.054932 | -0.2655 | 122.7905 | 123.0972 | 123.0011 | 0.32043 | 0.2243 | 116.2674 | 116.1026 | 0.013733 | 0.27008 | 116.5604 | 0.59051 | 116.2674 | 123.3673 | -123.6053 | -0.53558 | 115.8096 | 123.0469 | 112.5458 | 118.8446
2087.4844 | 123.3032 | -118.1625 | 5.1361 | -0.042419 | 0.0044071 | 0.1206 | 0.0045159 | 0.0010531 | 0.0022068 | -0.00095273 | -0.13919 | 0.14003 | 0.0036166 | 0.0019674 | -0.0025976 | -0.0012348 | -0.00075834 | -4.4998 | -1.9592 | -118.4875 | -2.4124 | -2.2522 | -118.1992 | -2.3163 | 0.6546 | 5.1819 | 4.628 | 4.8889 | 4.8294 | 4.7791 | 4.9164 | -0.32501 | -7.0953 | -7.5485 | 115.9103 | 115.8463 | -0.036621 | 116.1713 | 0.28839 | 122.7905 | 0.045777 | -0.24719 | 122.9919 | 123.0789 | 122.9416 | 0.28839 | 0.15106 | 116.2354 | 116.0751 | 0.20142 | 0.26093 | 116.5283 | 0.55389 | 116.2033 | 123.3444 | -123.6237 | -0.50812 | 115.7501 | 123.0515 | 113.6627 | 118.8171
2088.5469 | 123.3032 | -118.222 | 5.0949 | 0.026245 | 0.0039799 | 0.11911 | 0.0028069 | 0.0016939 | 0.0022068 | -0.0020209 | -0.041534 | 0.1379 | 0.0027622 | -0.00059601 | -0.0021704 | -0.0023028 | 0.0013779 | -5.0262 | -2.092 | -118.4647 | -2.5406 | -2.3758 | -118.1671 | -2.4033 | 0.62256 | 5.1727 | 4.5959 | 4.8569 | 4.8935 | 4.8203 | 4.8889 | -0.24262 | -7.1869 | -7.6355 | 115.8463 | 115.8188 | 0.054932 | 116.0614 | 0.29755 | 122.818 | 0.077819 | -0.23804 | 123.1155 | 123.111 | 123.0423 | 0.29297 | 0.2243 | 116.0889 | 115.9241 | 0.29755 | 0.26093 | 116.3727 | 0.57678 | 116.1301 | 123.3948 | -123.5596 | -0.49896 | 115.6815 | 123.0789 | 113.1958 | 118.8446
2089.4844 | 123.3078 | -118.19 | 5.0766 | -0.057678 | 0.0029117 | 0.12018 | 0.0045159 | 0.00062594 | 0.00049778 | -0.0024481 | -0.12088 | 0.13854 | 0.0031894 | -0.0014504 | -0.0025976 | 0.00068782 | -0.00075834 | -5.8044 | -2.1927 | -118.4921 | -2.6276 | -2.5177 | -118.2404 | -2.5131 | 0.59509 | 5.1636 | 4.6051 | 4.8843 | 4.6143 | 4.7928 | 4.921 | -0.30212 | -7.2693 | -7.7042 | 115.6723 | 115.6769 | -0.050354 | 115.979 | 0.25177 | 122.7951 | 0.086975 | -0.19226 | 122.8043 | 123.111 | 122.9828 | 0.31586 | 0.18768 | 115.9744 | 115.8646 | 0.009155 | 0.27923 | 116.2994 | 0.55847 | 115.9973 | 123.3536 | -123.5687 | -0.4715 | 115.5624 | 123.0743 | 112.3856 | 118.7851
2090.5469 | 123.3078 | -118.1671 | 5.1407 | 0.018616 | 0.0037661 | 0.11911 | -0.00039728 | 0.00062594 | 0.00071138 | 0.00054267 | -0.072052 | 0.13939 | 0.0070346 | 0.00624 | -0.003025 | -0.0018756 | 0.00095066 | -6.4865 | -2.092 | -118.4921 | -2.5955 | -2.3712 | -118.1351 | -2.4399 | 0.58136 | 5.2139 | 4.6555 | 4.8843 | 4.7562 | 4.834 | 4.953 | -0.32501 | -7.2327 | -7.7362 | 115.7959 | 115.7272 | 0.032043 | 116.0522 | 0.35706 | 122.8226 | 0.073242 | -0.25635 | 122.9233 | 123.1201 | 123.0011 | 0.29755 | 0.17853 | 116.1209 | 115.8966 | 0.10071 | 0.22888 | 116.4001 | 0.55847 | 116.0751 | 123.381 | -123.6328 | -0.48523 | 115.5716 | 123.0515 | 111.6806 | 118.7485
2091.4844 | 123.3902 | -118.103 | 5.1407 | -0.072937 | 0.0031253 | 0.12082 | 0.0047295 | -0.00065586 | 0.0019932 | -0.0039435 | -0.078156 | 0.13725 | 0.0029758 | -0.0044412 | -0.0028112 | -0.0012348 | 0.0018051 | -8.2214 | -2.0828 | -118.4555 | -2.4673 | -2.3209 | -118.0023 | -2.3666 | 0.6546 | 5.2048 | 4.6646 | 5.04 | 4.9988 | 4.9622 | 5.0766 | -0.35248 | -7.2235 | -7.608 | 115.7822 | 115.7364 | 0.10071 | 116.0889 | 0.45319 | 122.7676 | 0.064087 | -0.10071 | 123.1018 | 123.1796 | 123.0652 | 0.41199 | 0.29755 | 116.1346 | 115.9882 | 0.33417 | 0.37537 | 116.3727 | 0.54016 | 116.0202 | 123.3078 | -123.5962 | -0.47607 | 115.6357 | 123.143 | 109.8816 | 118.7576
2092.4844 | 123.3353 | -118.1305 | 5.1819 | 0.018616 | 0.0054751 | 0.11654 | 0.0062249 | -0.0010831 | -0.0012112 | -0.0037299 | -0.090363 | 0.13875 | 0.0029758 | 0.0013266 | -0.0049476 | 4.7018e-05 | -0.00097194 | -7.4203 | -2.092 | -118.4463 | -2.4948 | -2.211 | -117.8558 | -2.2888 | 0.65918 | 5.3101 | 4.7104 | 4.9896 | 4.7104 | 4.8981 | 5.0079 | -0.31586 | -7.2739 | -7.6767 | 115.9195 | 115.8417 | 0.27466 | 116.1575 | 0.59051 | 122.8409 | 0.12817 | -0.19226 | 122.8409 | 123.1384 | 123.0286 | 0.29755 | 0.18768 | 116.2354 | 115.9515 | 0 | 0.27924 | 116.3544 | 0.59967 | 116.0385 | 123.4406 | -123.6282 | -0.4715 | 115.6357 | 123.1201 | 110.7101 | 118.7897
2093.4844 | 123.3215 | -118.1305 | 5.1407 | -0.03479 | 0.0024845 | 0.11825 | 0.0043023 | -0.00044226 | 0.0019932 | -0.0015935 | -0.093414 | 0.13725 | 0.0042574 | 0.00025839 | -0.0043066 | -0.0023028 | 0.0028733 | -8.2123 | -2.124 | -118.4326 | -2.5543 | -2.3712 | -118.1717 | -2.4445 | 0.53101 | 5.2139 | 4.6371 | 4.9164 | 4.8203 | 4.8203 | 4.9393 | -0.30212 | -7.2647 | -7.695 | 115.7593 | 115.686 | -0.041199 | 115.9882 | 0.26093 | 122.7676 | 0.073242 | -0.2243 | 122.9507 | 123.0698 | 122.9507 | 0.30212 | 0.1831 | 116.0614 | 115.8783 | 0.1831 | 0.27924 | 116.3086 | 0.57678 | 116.0065 | 123.3444 | -123.5733 | -0.50354 | 115.5762 | 123.0469 | 109.9182 | 118.6615
2094.5469 | 123.3215 | -118.2175 | 5.0674 | -0.057678 | 0.0035525 | 0.11975 | 0.0030207 | -0.0017239 | 0.00092498 | -0.0015935 | -0.0018616 | 0.13747 | 0.0029758 | -0.0031594 | -0.0015296 | -0.0027302 | 0.00095066 | -8.6014 | -2.1606 | -118.483 | -2.5085 | -2.3163 | -115.3885 | -2.3804 | 0.67291 | 5.1086 | 4.5776 | 4.8706 | 4.6921 | 4.8294 | 4.9026 | -0.2655 | -7.2281 | -7.576 | 115.9012 | 115.8371 | 2.829 | 116.1026 | 3.0945 | 122.7951 | 0.041199 | -0.19684 | 122.9095 | 123.1201 | 123.0469 | 0.32501 | 0.25177 | 116.1667 | 115.9744 | 0.11444 | 0.29297 | 116.3223 | 0.53101 | 116.0568 | 123.3261 | -123.5504 | -0.48981 | 115.7089 | 123.0881 | 109.6161 | 118.8904
2095.4844 | 123.317 | -118.0389 | 5.2277 | -0.088196 | 0.0063297 | 0.11889 | 0.0057977 | 0.0034029 | 0.0015658 | -0.0011663 | -0.11783 | 0.13832 | 0.0031894 | 0.007308 | -0.0038794 | -0.00059378 | 0.0024461 | -6.926 | -2.092 | -118.3365 | -2.5131 | -2.4124 | -118.0435 | -2.4216 | 0.59509 | 5.3146 | 4.7424 | 5.0262 | 4.7104 | 4.9301 | 5.0629 | -0.29755 | -7.3196 | -7.7408 | 115.6265 | 115.6174 | -0.004578 | 115.9149 | 0.29297 | 122.7814 | 0.086975 | -0.20142 | 122.7493 | 123.1018 | 122.9691 | 0.32043 | 0.18768 | 115.9241 | 115.8234 | -0.032044 | 0.28381 | 116.2445 | 0.5722 | 115.947 | 123.3536 | -123.5641 | -0.48523 | 115.5258 | 123.0652 | 111.113 | 118.634
2096.5469 | 123.3032 | -118.1534 | 5.1682 | 0.026245 | 0.0037661 | 0.12039 | 0.0045159 | -0.0023649 | -0.00014322 | 0.00054267 | -0.078156 | 0.13619 | 0.0031894 | -0.0052958 | -0.0045202 | -0.0023028 | 0.0013779 | -5.5069 | -2.2339 | -118.4647 | -2.7557 | -2.6367 | -118.158 | -2.5772 | 0.58594 | 5.2505 | 4.6783 | 4.9255 | 4.5776 | 4.8752 | 4.9667 | -0.31128 | -7.402 | -7.9239 | 115.5167 | 115.5762 | -0.004578 | 115.8875 | 0.3067 | 122.8317 | 0.082397 | -0.24261 | 122.731 | 123.1201 | 123.0286 | 0.28839 | 0.19684 | 115.8279 | 115.7089 | -0.10071 | 0.24719 | 116.2308 | 0.5722 | 115.9195 | 123.4039 | -123.6328 | -0.48981 | 115.3976 | 123.0789 | 112.6465 | 118.7393
2097.4844 | 123.4268 | -117.9749 | 5.246 | -0.057678 | 0.0016299 | 0.1174 | 0.0045159 | 0.00019874 | 0.00092498 | -0.0020209 | -0.069 | 0.13661 | 0.0027622 | -0.0012368 | -0.0034522 | -0.003371 | -0.0024673 | -5.2597 | -2.3621 | -118.2816 | -2.6413 | -2.4765 | -117.8741 | -2.5726 | 0.737 | 5.3055 | 4.7974 | 5.1544 | 4.8294 | 5.0949 | 5.2231 | -0.3067 | -7.608 | -7.8873 | 115.4984 | 115.4022 | 0.10071 | 115.7089 | 0.40741 | 122.7722 | 0.059509 | -0.091553 | 122.8043 | 123.1979 | 123.0698 | 0.42572 | 0.29755 | 115.8051 | 115.6403 | 0.032044 | 0.35706 | 115.9195 | 0.50812 | 115.6128 | 123.2803 | -123.5275 | -0.44861 | 115.3336 | 123.1293 | 112.7151 | 118.7119
2098.5469 | 123.3398 | -44.6732 | 78.5019 | 0.010986 | 0.0031253 | 0.041349 | 0.0055841 | -0.00022866 | 0.00092498 | -0.0015935 | -0.059845 | 0.0022453 | 0.0029758 | 0.037002 | -0.002384 | -0.0035846 | 0.0028733 | -2.0599 | -1.0162 | -44.9432 | -1.4374 | -1.2955 | -44.9478 | -1.3092 | 2.1011 | 78.5706 | 3.7445 | 78.5156 | 3.9688 | 3.9871 | 4.0878 | -0.27008 | -79.5181 | -79.9393 | 43.3777 | 43.364 | -0.27466 | 43.634 | -0.004578 | 48.4177 | 0.068665 | 0.013733 | 48.642 | 48.761 | 48.6603 | 0.34332 | 0.24261 | 43.6478 | 43.5059 | 0.2243 | 74.7711 | 43.927 | 74.826 | 43.6569 | 123.2437 | -123.4451 | -74.7574 | 43.2358 | 123.1888 | 42.6132 | 46.7743
2099.4844 | 123.3673 | -44.7418 | 78.4195 | -0.019531 | 0.0020573 | 0.043912 | 0.0040887 | 0.0031893 | 0.0017794 | -0.0026617 | -0.065949 | 0.0011771 | 0.0036166 | 0.040206 | -0.0043066 | -0.0027302 | -0.00097194 | -3.3966 | -1.0025 | -45.0623 | -1.4008 | -1.2451 | -45.0806 | -1.2955 | 2.1561 | 78.4836 | 3.3463 | 78.4973 | 3.6026 | 3.6621 | 3.7857 | -0.32043 | -79.422 | -79.8203 | 43.4967 | 43.4464 | -0.33874 | 43.7668 | -0.01831 | 48.0881 | 0.064087 | 0.077819 | 48.3444 | 48.5275 | 48.4039 | 0.43945 | 0.31586 | 43.8171 | 43.6615 | 0.25635 | 75.1511 | 44.0598 | 75.1373 | 43.7393 | 123.2254 | -123.4818 | -75.0732 | 43.3411 | 123.2391 | 41.3452 | 46.8979
2100.5469 | 123.3307 | -44.3481 | 78.8498 | -0.0042723 | 0.0031253 | 0.039854 | 0.0036615 | -0.0025785 | -0.00057042 | -0.0045843 | -0.072052 | 0.0033133 | 0.0031894 | 0.040633 | -0.004093 | -0.0010212 | -0.0039627 | -2.1927 | -1.0117 | -45.0211 | -1.4465 | -1.3138 | -45.5612 | -1.3092 | 2.1149 | 78.891 | 4.5914 | 78.8727 | 4.8523 | 4.5685 | 4.6051 | -0.67291 | -79.8614 | -80.2963 | 43.0344 | 43.0389 | -1.2131 | 43.7119 | -0.54016 | 48.9395 | 0.041199 | 0.022889 | 49.2004 | 48.9532 | 48.9166 | 0.013733 | -0.022889 | 43.7073 | 43.5745 | 0.26092 | 74.2813 | 44.0094 | 74.2996 | 43.3365 | 123.2391 | -123.8708 | -74.2584 | 42.9016 | 123.2208 | 42.1555 | 46.463
2101.4844 | 123.4177 | -117.9611 | 5.2231 | -0.095825 | 0.0029117 | 0.12103 | 0.0043023 | 0.0012667 | -0.0012112 | -0.0022345 | -0.11172 | 0.13619 | 0.0048984 | 0.0068808 | -0.0034522 | -0.0012348 | 0.0022323 | -6.1203 | -2.2339 | -118.3594 | -2.6505 | -2.5589 | -117.7231 | -2.5681 | 0.5722 | 5.2963 | 4.7379 | 5.0217 | 4.8706 | 4.9255 | 5.0491 | -0.39825 | -7.457 | -7.8735 | 115.4022 | 115.3931 | 0.23804 | 115.7913 | 0.63629 | 122.699 | 0.073243 | -0.20142 | 122.8317 | 123.0103 | 122.8867 | 0.31128 | 0.18768 | 115.8005 | 115.7089 | 0.13275 | 0.28381 | 116.1255 | 0.55847 | 115.7272 | 123.2574 | -123.5825 | -0.48523 | 115.3107 | 122.9828 | 111.8408 | 118.5333
2102.5469 | 123.4085 | -118.7943 | 4.4724 | -0.027161 | 0.0016299 | 0.11953 | 0.0047295 | -0.0010831 | 0.0015658 | -0.0043707 | -0.078156 | 0.13896 | 0.003403 | -0.0027322 | -0.0004614 | -0.0035846 | 0.00052346 | -6.2347 | -2.1973 | -119.0964 | -2.6276 | -2.4811 | -118.721 | -2.5085 | 0.49439 | 4.5639 | 4.0237 | 4.2938 | 4.0283 | 4.2114 | 4.3167 | -0.30212 | -6.6696 | -7.0999 | 116.3132 | 116.2857 | 0.073242 | 116.5878 | 0.37537 | 122.818 | 0.091553 | -0.17853 | 122.8226 | 123.111 | 123.0057 | 0.29297 | 0.18768 | 116.6153 | 116.4688 | 0.004577 | 0.27008 | 116.8991 | 0.54016 | 116.597 | 123.3582 | -123.5687 | -0.44861 | 116.1667 | 123.0881 | 112.5595 | 119.2886
2103.4844 | 123.436 | -118.7576 | 4.4128 | -0.027161 | 0.0024845 | 0.11975 | 0.0036615 | 0.0029757 | -0.00078402 | -0.0011663 | -0.084259 | 0.14089 | 0.0021212 | 0.0041038 | -0.0032386 | -0.00038018 | 0.0043687 | -5.5206 | -2.3026 | -119.165 | -2.71 | -2.5452 | -118.0527 | -2.5909 | 0.59509 | 4.4907 | 3.9871 | 4.3167 | 4.0878 | 4.1931 | 4.3167 | -0.40741 | -6.7154 | -7.1228 | 116.2125 | 116.1667 | 0.70496 | 116.5741 | 1.1124 | 122.7448 | 0.07782 | -0.096131 | 122.8455 | 123.0743 | 122.9507 | 0.32959 | 0.20599 | 116.6199 | 116.4551 | 0.10071 | 0.32959 | 116.8625 | 0.50354 | 116.4551 | 123.2483 | -123.5779 | -0.42572 | 116.0477 | 123.0743 | 113.237 | 119.3527
2104.4844 | 123.3215 | -118.2816 | 5.0171 | -0.065308 | 0.0039799 | 0.12103 | 0.0043023 | 0.00041234 | -0.0014248 | -0.0020209 | -0.11172 | 0.13811 | 0.0038302 | 0.00389 | -0.0028112 | -0.0020892 | 0.0018051 | -4.7882 | -2.3804 | -118.6066 | -2.8656 | -2.7328 | -118.2816 | -2.7557 | 0.47607 | 5.0629 | 4.5044 | 4.7928 | 4.3991 | 4.6555 | 4.8157 | -0.32501 | -7.3975 | -7.8827 | 115.5487 | 115.5258 | 0 | 115.8508 | 0.32501 | 122.7859 | 0.045776 | -0.2243 | 122.6807 | 123.0972 | 122.937 | 0.31128 | 0.15106 | 115.8737 | 115.741 | -0.10529 | 0.28839 | 116.2262 | 0.55847 | 115.9012 | 123.3444 | -123.6237 | -0.51269 | 115.416 | 123.0743 | 113.4933 | 118.7576
2105.5625 | 123.4589 | -118.1396 | 5.0858 | -0.042419 | 0.0044071 | 0.11847 | 0.0036615 | -0.0023649 | 0.0017794 | 0.00011527 | -0.099518 | 0.13854 | 0.0027622 | -0.0020914 | -0.0025976 | -0.001662 | -0.0016129 | -5.0171 | -2.4033 | -118.4692 | -2.742 | -2.5818 | -118.1763 | -2.6459 | 0.64087 | 5.1544 | 4.6509 | 5.0125 | 4.715 | 4.9347 | 5.0537 | -0.32959 | -7.489 | -7.8278 | 115.5579 | 115.4938 | -0.036622 | 115.8234 | 0.29297 | 122.7905 | 0.068665 | -0.073242 | 122.8546 | 123.1934 | 123.0743 | 0.40283 | 0.28381 | 115.8875 | 115.7272 | 0.064087 | 0.36163 | 116.066 | 0.50354 | 115.7364 | 123.2941 | -123.555 | -0.43487 | 115.3976 | 123.1522 | 113.1226 | 118.7805
2106.4844 | 123.349 | -118.2312 | 5.0903 | -0.072937 | 0.0048343 | 0.12445 | 0.0045159 | 0.0023349 | -0.00057042 | 0.0011835 | -0.10867 | 0.13619 | 0.0025484 | 0.00047219 | -0.0028112 | -0.0037982 | 0.00052346 | -6.0287 | -2.3117 | -118.5013 | -2.7466 | -2.6459 | -118.2541 | -2.6413 | 0.51727 | 5.159 | 4.5868 | 4.8889 | 4.4907 | 4.7699 | 4.9164 | -0.27008 | -7.402 | -7.8369 | 115.5853 | 115.5899 | -0.022888 | 115.86 | 0.24719 | 122.818 | 0.068665 | -0.20142 | 122.7219 | 123.1476 | 123.0011 | 0.32959 | 0.18311 | 115.8554 | 115.7547 | -0.09613 | 0.30212 | 116.1896 | 0.57221 | 115.9195 | 123.3902 | -123.5916 | -0.50354 | 115.4846 | 123.1201 | 112.2025 | 118.7485
2107.5469 | 123.3627 | -118.1259 | 5.1865 | 0.0033567 | 0.0029117 | 0.1206 | 0.0053705 | -0.00065586 | 0.0013522 | -0.00073913 | -0.087311 | 0.13704 | 0.0029758 | -0.00038241 | -0.0021704 | -0.003371 | 0.00030966 | -6.6238 | -2.3254 | -118.4097 | -2.7054 | -2.5635 | -118.0252 | -2.6184 | 0.59052 | 5.2322 | 4.6921 | 5.0125 | 4.7699 | 4.9164 | 5.0217 | -0.28381 | -7.5119 | -7.8918 | 115.5624 | 115.5075 | 0.10071 | 115.7913 | 0.38452 | 122.818 | 0.045777 | -0.17395 | 122.8958 | 123.1476 | 123.0423 | 0.32959 | 0.2243 | 115.8463 | 115.7043 | 0.077819 | 0.32043 | 116.0843 | 0.54016 | 115.8005 | 123.3582 | -123.5962 | -0.49438 | 115.4205 | 123.1384 | 111.5021 | 118.7164
2108.4844 | 123.3307 | -118.1625 | 5.1682 | -0.0042723 | 0.0024845 | 0.12124 | 0.0036615 | 0.0051119 | 0.0028476 | 0.00032907 | -0.10867 | 0.13747 | 0.0036166 | -0.0012368 | -0.0008886 | -0.00038018 | 0.00073706 | -8.8623 | -2.3392 | -118.4418 | -2.7969 | -2.6367 | -117.6224 | -2.6962 | 0.62256 | 5.2414 | 4.6783 | 4.9347 | 4.5593 | 4.8614 | 4.985 | -0.27923 | -7.5073 | -7.9651 | 115.5258 | 115.4663 | 0.54016 | 115.7455 | 0.8194 | 122.8409 | 0.073242 | -0.23346 | 122.7219 | 123.1476 | 123.024 | 0.3067 | 0.1831 | 115.8051 | 115.6448 | -0.11902 | 0.25635 | 116.1026 | 0.56305 | 115.8234 | 123.4039 | -123.6099 | -0.48981 | 115.3656 | 123.0972 | 109.3002 | 118.7851
2109.4844 | 123.4406 | -118.1076 | 5.1453 | -0.03479 | 0.0024845 | 0.11996 | 0.0032343 | 0.00041234 | -0.00014322 | 0.00075627 | -0.047638 | 0.13576 | 0.0027622 | -0.00016881 | -0.002384 | 0.00026062 | -0.0013991 | -10.2081 | -2.3666 | -118.4006 | -2.6779 | -2.5131 | -118.0023 | -2.5726 | 0.66834 | 5.2139 | 4.7058 | 5.0766 | 4.66 | 4.985 | 5.1086 | -0.29297 | -7.5119 | -7.8232 | 115.5945 | 115.535 | 0.10529 | 115.8279 | 0.39826 | 122.8134 | 0.068664 | -0.068665 | 122.7676 | 123.2162 | 123.0927 | 0.40283 | 0.27923 | 115.8875 | 115.7227 | -0.045777 | 0.37079 | 116.0339 | 0.50812 | 115.741 | 123.3215 | -123.5458 | -0.43945 | 115.4297 | 123.1842 | 107.8995 | 118.7759
2110.5625 | 123.2986 | -45.7718 | 77.4261 | -0.11108 | 0.0041935 | 0.043272 | 0.0021661 | 0.0021213 | 0.0024204 | -0.00073913 | -0.026276 | 0.0039541 | 0.0036166 | 0.042983 | -0.0038794 | -0.0037982 | -0.0020401 | -4.5044 | -1.5472 | -46.0144 | -1.8082 | -1.6296 | -46.051 | -1.6983 | 1.8265 | 77.4261 | 1.8127 | 77.504 | 2.1332 | 2.0874 | 2.179 | -0.24261 | -78.9734 | -79.2343 | 44.1422 | 44.0735 | -0.27923 | 44.3161 | -0.036621 | 47.5845 | 0 | 0.07782 | 47.905 | 47.9507 | 47.8592 | 0.36621 | 0.27466 | 44.3848 | 44.2062 | 0.32044 | 75.6912 | 44.4672 | 75.6134 | 44.2245 | 123.1979 | -123.4406 | -75.6134 | 43.9636 | 123.2758 | 41.2674 | 47.5983
2111.4844 | 123.674 | -46.6187 | 75.8972 | -0.42389 | 0.0024845 | 0.04434 | 0.0043023 | 0.0016939 | 0.0032748 | 0.00054267 | -0.056793 | 0.0054495 | 0.005112 | 0.044051 | -0.004093 | -0.0023028 | 0.0056503 | -3.978 | -1.0574 | -45.1675 | -1.3641 | -1.2314 | -46.0556 | -1.2863 | 1.7761 | 77.4033 | 2.2385 | 77.0599 | 2.7237 | 2.9251 | 2.9388 | 1.4511 | -76.9547 | -77.2614 | 45.3873 | 45.3323 | 0.56305 | 43.8812 | -0.88806 | 48.8571 | 1.506 | 1.1627 | 49.3423 | 49.5575 | 49.5438 | 0.70038 | 0.68665 | 43.9362 | 43.8034 | 0.48523 | 74.8215 | 44.1101 | 75.1648 | 45.5612 | 124.0219 | -121.0648 | -73.6588 | 45.2545 | 123.6786 | 42.6407 | 48.3948
2112.4844 | 122.7585 | -44.2703 | 71.6492 | -0.25604 | 0.026837 | 0.0249 | -0.0057379 | -0.00065586 | -0.0031338 | -0.0045843 | -0.090363 | 0.0028861 | 0.00041225 | 0.042983 | -0.0008886 | -0.0042254 | -0.00033114 | -9.2377 | -1.2039 | -44.1284 | -1.4832 | -1.3458 | -45.2774 | -1.3916 | 1.03 | 77.5223 | 2.1835 | 78.1403 | 2.504 | 2.4353 | 2.5177 | 0.14191 | -72.8531 | -73.1323 | 42.9245 | 42.8787 | -1.0071 | 42.7368 | -1.149 | 46.4539 | 5.8731 | 6.4911 | 46.7743 | 46.788 | 46.7056 | 0.33417 | 0.25177 | 42.7826 | 42.6453 | 0.32043 | 75.9567 | 42.9245 | 75.3387 | 43.0664 | 121.7926 | -115.7776 | -69.4656 | 42.7872 | 122.4106 | 35.0327 | 45.3003
2113.5469 | 101.3535 | -44.9066 | 69.5847 | -0.14923 | -0.0013607 | 0.035795 | -0.0010383 | -0.0047147 | -0.0097562 | -0.0065069 | -0.18192 | -0.0056589 | -0.0064236 | 0.042769 | -0.0079382 | -0.013198 | -0.013789 | -11.9568 | -0.91553 | -44.7098 | -1.5152 | -1.4191 | -44.9982 | -1.2131 | 1.6479 | 76.1307 | 2.179 | 72.6837 | 2.3438 | 2.2385 | 2.3483 | 0.19684 | -70.5002 | -71.0999 | 43.4875 | 43.6935 | -0.091553 | 43.4967 | -0.28839 | 47.0856 | 6.546 | 3.0991 | 47.2504 | 47.2549 | 47.1451 | 0.16937 | 0.059509 | 43.2907 | 43.1946 | 0.16479 | 70.5048 | 43.7943 | 73.9517 | 43.9911 | 121.0373 | -114.2944 | -67.4057 | 43.3914 | 117.5903 | 32.9498 | 46.5546
2114.4844 | 107.6248 | -44.7189 | 77.6642 | -0.32471 | -0.0043515 | 0.031736 | -0.0097967 | 0.034806 | -0.014242 | -0.017615 | -0.2399 | -0.0099313 | -0.014541 | 0.033156 | -0.012211 | -0.018965 | -0.015712 | -12.1262 | -1.0986 | -44.5816 | -1.5289 | -1.4374 | -45.3598 | -1.2726 | 1.4694 | 78.0212 | 2.2842 | 73.9929 | 2.243 | 2.0325 | 2.1744 | 0.13733 | -78.7628 | -79.1931 | 43.2816 | 43.4464 | -0.64087 | 43.309 | -0.7782 | 47.0032 | 0.35706 | -3.6713 | 46.962 | 46.8933 | 46.7514 | -0.10986 | -0.25177 | 43.1442 | 43.0527 | -0.041199 | 71.7087 | 43.483 | 75.737 | 43.6203 | 122.7402 | -122.2458 | -75.3799 | 43.19 | 118.7119 | 32.5928 | 46.1884
2115.4844 | 123.3078 | -45.0165 | 78.1357 | -0.065308 | 0.0022709 | 0.04199 | 0.0034479 | -0.00022866 | -0.00035682 | -0.0039435 | 0.031708 | 0.0022453 | 0.0040438 | 0.036574 | -0.0019568 | -0.0018756 | 0.0011643 | -1.8265 | -1.0117 | -45.2545 | -1.355 | -1.1719 | -45.3094 | -1.2222 | 1.5564 | 78.1174 | 2.2659 | 78.2181 | 2.536 | 2.5177 | 2.623 | -0.23804 | -79.1473 | -79.4907 | 43.8446 | 43.7942 | -0.29297 | 44.0323 | -0.054931 | 47.2824 | -0.01831 | 0.082398 | 47.5525 | 47.6395 | 47.5342 | 0.35706 | 0.25177 | 44.0826 | 43.8995 | 0.27008 | 75.9521 | 44.2429 | 75.8514 | 44.0048 | 123.1338 | -123.3902 | -75.8698 | 43.6615 | 123.2346 | 43.19 | 46.5729
2116.5469 | 102.6443 | -45.2408 | 77.6642 | -0.25604 | 0.02406 | 0.028959 | -0.0072333 | 0.034592 | -0.012747 | -0.012061 | -0.18192 | 0.014422 | -0.0019376 | 0.041701 | -0.030155 | 0.015641 | -0.017848 | -1.9867 | -1.1536 | -44.6274 | -1.4328 | -1.4099 | -44.9158 | -1.3458 | 1.181 | 77.5635 | 2.3438 | 77.98 | 2.2568 | 2.1332 | 2.1927 | 0.6134 | -78.8177 | -79.097 | 43.8309 | 43.895 | 0.32501 | 43.2816 | -0.28839 | 47.5845 | -0.10071 | 0.31586 | 47.4976 | 47.4335 | 47.374 | -0.15106 | -0.21057 | 43.2175 | 43.1946 | -0.086975 | 75.6363 | 43.4738 | 75.2197 | 44.0872 | 122.8043 | -122.2916 | -75.3204 | 43.808 | 123.2208 | 43.2541 | 46.4218
2117.4844 | 123.2025 | -44.9524 | 77.9846 | -0.057678 | 0.0052615 | 0.044767 | 0.0036615 | -0.0027921 | -0.00057042 | -0.00052553 | -0.0018616 | 0.0043815 | 0.0031894 | 0.044692 | -0.0036658 | -0.00059378 | 0.00052346 | -1.8997 | -1.03 | -44.8654 | -1.3275 | -1.1627 | -45.163 | -1.2451 | 1.3229 | 78.0807 | 2.3895 | 78.3554 | 2.6733 | 2.6642 | 2.7878 | 0.086976 | -79.0146 | -79.3121 | 43.7897 | 43.7073 | -0.21057 | 43.6203 | -0.29755 | 47.3419 | 0.096131 | 0.37079 | 47.6257 | 47.7402 | 47.6166 | 0.39825 | 0.27466 | 43.7027 | 43.5379 | 0.28381 | 75.9659 | 43.8354 | 75.6912 | 43.9224 | 123.0331 | -122.85 | -75.5951 | 43.6249 | 123.3078 | 43.0527 | 46.2753
2118.4844 | 122.7219 | -44.6182 | 77.7008 | -0.17975 | 0.0031253 | 0.042844 | 0.0036615 | 0.00083954 | 0.0015658 | 0.00032907 | -0.038483 | 0.0030997 | 0.0040438 | 0.040633 | -0.0034522 | -0.0027302 | 0.00073706 | -1.712 | -0.97504 | -44.8196 | -1.387 | -1.2451 | -45.2179 | -1.268 | 1.442 | 78.0807 | 2.3987 | 78.3508 | 2.6642 | 2.6642 | 2.8015 | -0.20142 | -78.6758 | -79.0878 | 43.3731 | 43.3502 | -0.59967 | 43.5516 | -0.39826 | 47.0169 | 0.37994 | 0.65002 | 47.2824 | 47.4197 | 47.2824 | 0.40283 | 0.2655 | 43.5745 | 43.4326 | 0.2655 | 75.9521 | 43.8446 | 75.6821 | 43.6432 | 122.699 | -122.5204 | -75.3021 | 43.2312 | 122.9691 | 42.9062 | 46.0602
2119.5469 | 111.1633 | -44.6091 | 74.2081 | -0.17975 | 0.00056187 | 0.041135 | 0.0015253 | -0.0010831 | -0.001852 | -0.00095273 | -0.069 | 0.00074988 | -0.0012968 | 0.04106 | -0.001316 | -0.003371 | -0.0033219 | -1.9226 | -1.2131 | -44.9615 | -1.6708 | -1.5381 | -45.1721 | -1.5472 | 1.0986 | 77.7145 | 2.3849 | 77.5864 | 2.7054 | 2.4628 | 2.5406 | -0.35248 | -75.4211 | -75.8789 | 43.071 | 43.0618 | -0.56305 | 43.4143 | -0.21057 | 46.994 | 3.5065 | 3.3783 | 47.3145 | 47.1497 | 47.0718 | 0.15564 | 0.07782 | 43.4235 | 43.2907 | 0.32043 | 75.2014 | 43.7485 | 75.3296 | 43.396 | 122.3236 | -119.1696 | -71.8231 | 42.9382 | 122.1954 | 42.6865 | 45.7077
2120.4844 | 122.6166 | -44.9753 | 77.8748 | -0.0042723 | 0.0033389 | 0.041776 | 0.0038751 | 0.00041234 | -0.00099762 | -0.0028753 | 0.0072936 | 0.0030997 | 0.0053256 | 0.040633 | -0.0032386 | -0.0037982 | 0.0018051 | -1.9913 | -1.355 | -44.8837 | -1.7029 | -1.5335 | -45.1721 | -1.5656 | 1.4511 | 77.9205 | 2.3849 | 78.0807 | 2.6276 | 2.5864 | 2.6779 | 0.091553 | -79.2297 | -79.5776 | 43.4418 | 43.4097 | -0.19684 | 43.3182 | -0.28839 | 47.3602 | 0.045776 | 0.20599 | 47.6028 | 47.6532 | 47.5616 | 0.29297 | 0.20142 | 43.3502 | 43.1808 | 0.24261 | 75.6958 | 43.5287 | 75.5356 | 43.6203 | 122.8958 | -122.7585 | -75.4898 | 43.2724 | 123.056 | 42.984 | 46.4264
2121.5469 | 123.4451 | -117.3019 | 5.9189 | -0.057678 | 0.0056889 | 0.12146 | -0.0023199 | -0.010696 | -0.00762 | -0.017829 | -0.23074 | 0.12187 | -0.0083462 | -0.011704 | -0.007511 | -0.014479 | 0.0022323 | -4.2023 | -2.4445 | -117.7505 | -2.9205 | -2.8015 | -117.128 | -2.7924 | 0.3891 | 5.9647 | 5.2826 | 5.6763 | 5.3787 | 5.4291 | 5.5023 | -0.44861 | -8.3633 | -8.8394 | 114.5004 | 114.5096 | 0.17395 | 114.9582 | 0.62256 | 122.5845 | 0.045777 | -0.24261 | 122.6807 | 122.8043 | 122.731 | 0.21973 | 0.14648 | 114.949 | 114.83 | 0.09613 | 0.39368 | 115.3061 | 0.68207 | 114.8575 | 123.2666 | -123.6694 | -0.63629 | 114.3814 | 122.9782 | 113.0997 | 117.691
2122.4844 | 123.5092 | -117.8146 | 5.4794 | -0.072937 | 0.0024845 | 0.12082 | 0.0068659 | -0.0032193 | -0.0027066 | -0.0077887 | -0.13004 | 0.13491 | 0.0038302 | -0.0020914 | -0.000675 | -0.0018756 | 0.0026597 | -4.4449 | -2.3621 | -118.19 | -2.8336 | -2.7054 | -117.5308 | -2.7512 | 0.47607 | 5.5298 | 4.9347 | 5.3329 | 5.0354 | 5.0262 | 5.1453 | -0.37537 | -7.8415 | -8.313 | 115.1093 | 115.0635 | 0.28381 | 115.4388 | 0.65918 | 122.7493 | 0.050354 | -0.14648 | 122.85 | 122.9599 | 122.8409 | 0.21057 | 0.091553 | 115.4846 | 115.3564 | 0.10071 | 0.39825 | 115.8279 | 0.59509 | 115.4526 | 123.3444 | -123.6694 | -0.54474 | 114.9811 | 123.1476 | 113.3698 | 118.2907
2123.4844 | 123.5184 | -117.9794 | 5.2277 | -0.11108 | 0.0063297 | 0.12103 | 0.0043023 | -0.0030057 | 0.00092498 | -0.00095273 | -0.056793 | 0.13597 | 0.0014804 | 0.00068579 | -0.0028112 | 0.0015424 | 0.0028733 | -4.0558 | -2.3804 | -118.2678 | -2.7008 | -2.5314 | -117.8741 | -2.6047 | 0.56763 | 5.3467 | 4.8203 | 5.0446 | 5.246 | 5.1773 | 5.246 | -0.28839 | -7.608 | -7.9285 | 115.448 | 115.3748 | 0.10529 | 115.6631 | 0.39368 | 122.7997 | 0.11902 | -0.18311 | 123.2254 | 123.2254 | 123.1567 | 0.42572 | 0.35706 | 115.7364 | 115.567 | 0.42572 | 0.22431 | 115.8875 | 0.52643 | 115.5991 | 123.3261 | -123.4955 | -0.40741 | 115.2786 | 123.024 | 113.9236 | 118.5471
2124.5469 | 123.3582 | -118.0618 | 5.2643 | -0.03479 | 0.0035525 | 0.11889 | 0.0053705 | 0.00083954 | -0.00099762 | -0.0088567 | -0.2399 | 0.12316 | 0.0021212 | -0.0097818 | -0.0072974 | -0.017043 | -0.0050307 | -4.509 | -2.8839 | -118.3777 | -3.3554 | -3.2089 | -117.6865 | -3.2547 | 0.55389 | 5.3146 | 4.7424 | 5.04 | 4.6234 | 4.921 | 4.9393 | -0.31586 | -8.1482 | -8.6197 | 114.8529 | 114.8071 | 0.37537 | 115.123 | 0.69122 | 122.8043 | 0.050354 | -0.2243 | 122.6852 | 123.0011 | 122.9828 | 0.19684 | 0.17853 | 115.1688 | 115.0223 | -0.11902 | 0.29755 | 115.4938 | 0.5722 | 115.1779 | 123.3765 | -123.642 | -0.52185 | 114.7064 | 123.1018 | 113.5529 | 118.6157
2125.4844 | 123.4451 | -118.103 | 5.1819 | -0.042419 | 0.00077547 | 0.11889 | 0.0053705 | -0.00044226 | 0.0028476 | -9.8328e-05 | -0.05069 | 0.13555 | 0.0038302 | -0.002305 | -0.002384 | -0.0027302 | 0.0026597 | -4.4312 | -2.4261 | -118.4052 | -2.6962 | -2.5314 | -118.0069 | -2.5955 | 0.51727 | 5.2231 | 4.715 | 5.0858 | 5.0354 | 4.9988 | 5.1132 | -0.30212 | -7.608 | -7.8781 | 115.5716 | 115.5075 | 0.09613 | 115.8096 | 0.39825 | 122.818 | 0.041198 | -0.096131 | 123.1384 | 123.2162 | 123.1018 | 0.39825 | 0.28381 | 115.8737 | 115.7089 | 0.32043 | 0.37079 | 115.979 | 0.50812 | 115.6769 | 123.3261 | -123.587 | -0.46692 | 115.4068 | 123.1888 | 113.6719 | 118.6203
2126.5469 | 123.4131 | -118.2541 | 5.0949 | 0.0033567 | 0.0050479 | 0.11953 | 0.0049433 | -0.0049283 | 0.00071138 | 0.0018243 | -0.18802 | 0.12828 | 0.0010532 | -0.011491 | -0.0081518 | -0.020034 | -0.0011855 | -4.0329 | -2.3529 | -118.5196 | -2.7557 | -2.6001 | -117.9886 | -2.6596 | 0.46692 | 5.1636 | 4.6188 | 4.9301 | 4.7836 | 4.8386 | 4.8523 | -0.2655 | -7.4478 | -7.8506 | 115.654 | 115.5945 | 0.2655 | 115.86 | 0.53101 | 122.8729 | 0.068664 | -0.16479 | 123.0377 | 123.1064 | 123.0927 | 0.23346 | 0.21973 | 115.9195 | 115.7639 | 0.16479 | 0.31128 | 116.1667 | 0.54474 | 115.9012 | 123.4177 | -123.6145 | -0.47607 | 115.4984 | 123.1842 | 114.2212 | 118.721
2127.4844 | 123.4543 | -118.277 | 4.9942 | -0.065308 | 0.0037661 | 0.11804 | 0.0051569 | 0.0014803 | 0.0022068 | -9.8328e-05 | -0.020172 | 0.13683 | 0.0053256 | 0.00068579 | -0.0028112 | -0.0031574 | 9.6064e-05 | -5.0949 | -2.3849 | -118.5608 | -2.7054 | -2.5269 | -118.0756 | -2.5955 | 0.55389 | 5.04 | 4.5364 | 4.9118 | 4.9164 | 4.8386 | 4.9301 | -0.28381 | -7.3792 | -7.6996 | 115.7501 | 115.6815 | 0.20142 | 115.9653 | 0.48523 | 122.8134 | 0.045776 | -0.082398 | 123.1934 | 123.2071 | 123.1155 | 0.39368 | 0.30212 | 116.0339 | 115.8554 | 0.37994 | 0.37537 | 116.1758 | 0.50354 | 115.892 | 123.317 | -123.555 | -0.45776 | 115.5716 | 123.1888 | 113.1821 | 118.8309
2128.5469 | 123.4634 | -118.2083 | 5.0125 | -0.042419 | 0.0026981 | 0.11996 | 0.0040887 | -0.0032193 | 0.0019932 | -0.0080023 | -0.25211 | 0.11952 | -1.4954e-05 | -0.0097818 | -0.017124 | 0.015855 | -0.014858 | -4.5044 | -2.3117 | -118.5974 | -2.71 | -2.5452 | -117.7689 | -2.4765 | 0.50354 | 5.1544 | 4.5639 | 4.8431 | 4.8065 | 4.7333 | 4.7928 | -0.3891 | -7.3242 | -7.7225 | 115.6631 | 115.7318 | 0.43945 | 116.1209 | 0.82855 | 122.7722 | 0.14191 | -0.16937 | 123.0148 | 123.0011 | 122.9416 | 0.22888 | 0.16937 | 116.0522 | 115.8875 | 0.24261 | 0.27924 | 116.2857 | 0.59051 | 115.8966 | 123.3627 | -123.6099 | -0.44861 | 115.4984 | 123.0515 | 113.7039 | 118.7119
2129.4844 | 123.4772 | -118.3182 | 4.8843 | -0.10345 | 0.0035525 | 0.12124 | 0.0036615 | -0.00086946 | 0.00049778 | 0.0039607 | 0.046967 | 0.13896 | 0.0042574 | -0.0072184 | -0.0045202 | -0.0025164 | -0.00033114 | -5.072 | -2.3117 | -118.6432 | -2.6047 | -2.4445 | -118.5883 | -2.6596 | 0.59967 | 4.9164 | 4.4586 | 4.8386 | 4.4357 | 4.7562 | 4.8477 | -0.32501 | -7.196 | -7.489 | 115.8737 | 115.6586 | -0.27008 | 115.9836 | 0.054931 | 122.7768 | 0.032044 | -0.045776 | 122.7539 | 123.1659 | 123.0743 | 0.3891 | 0.29755 | 116.1987 | 116.0385 | -0.022888 | 0.37994 | 116.3315 | 0.45776 | 116.0065 | 123.2346 | -123.5275 | -0.42572 | 115.7135 | 123.1567 | 113.2462 | 118.9178
2130.4844 | 123.4314 | -118.1717 | 5.1086 | -0.080566 | 0.0033389 | 0.12146 | 0.0047295 | 0.0025485 | -0.00057042 | -0.0011663 | -0.11783 | 0.13875 | 0.0014804 | -0.0014504 | -0.0015296 | -0.00080758 | -0.0013991 | -6.3492 | -2.1378 | -118.5059 | -2.5909 | -2.4536 | -118.158 | -2.4811 | 0.41199 | 5.2048 | 4.6234 | 4.953 | 4.5502 | 4.834 | 4.953 | -0.33417 | -7.2464 | -7.6996 | 115.7181 | 115.6906 | 0.013733 | 116.0248 | 0.3479 | 122.7951 | 0.09613 | -0.15564 | 122.7219 | 123.1247 | 123.0057 | 0.32959 | 0.21057 | 116.0522 | 115.9149 | -0.073242 | 0.32959 | 116.3681 | 0.58136 | 116.0339 | 123.3765 | -123.6145 | -0.48523 | 115.5807 | 123.1247 | 111.8225 | 118.5837
2131.4844 | 123.4634 | -118.3273 | 4.8798 | -0.095825 | 0.0018435 | 0.11996 | 0.0032343 | 0.0029757 | 0.0037022 | -0.0041571 | -0.056793 | 0.13661 | 0.0038302 | 0.0036764 | -0.0025976 | -0.0012348 | 0.00073706 | -7.1594 | -2.0691 | -118.6249 | -2.3712 | -2.1927 | -118.3136 | -2.2797 | 0.25177 | 4.9255 | 4.4357 | 4.8294 | 4.7791 | 4.7699 | 4.8706 | -0.29755 | -6.9489 | -7.251 | 116.1346 | 116.0477 | 0.013733 | 116.3452 | 0.31128 | 122.7631 | 0.045776 | -0.050354 | 123.1064 | 123.1979 | 123.0972 | 0.43487 | 0.33417 | 116.4322 | 116.2537 | 0.34332 | 0.39368 | 116.5558 | 0.48981 | 116.2582 | 123.2529 | -123.5046 | -0.44403 | 115.9561 | 123.1567 | 111.1679 | 118.5791
2132.4844 | 123.3948 | -118.4967 | 4.7882 | -0.027161 | 0.0031253 | 0.12039 | 0.0043023 | 0.0014803 | -0.00014322 | 0.00075627 | -0.10562 | 0.13875 | 0.0048984 | -0.0010232 | -0.002384 | 0.00026062 | -0.00075834 | -3.9734 | -2.1835 | -118.8263 | -2.6413 | -2.4902 | -118.5059 | -2.5452 | 0.37079 | 4.8706 | 4.2801 | 4.6188 | 4.2389 | 4.4861 | 4.6326 | -0.32959 | -6.9717 | -7.4295 | 116.0065 | 115.9515 | -0.009155 | 116.2811 | 0.32044 | 122.7768 | 0.082397 | -0.16937 | 122.7356 | 123.1293 | 122.9828 | 0.35248 | 0.20599 | 116.3361 | 116.185 | -0.041198 | 0.33874 | 116.6428 | 0.59051 | 116.3132 | 123.3673 | -123.6145 | -0.50812 | 115.8554 | 123.1155 | 114.5233 | 118.8675
2133.4844 | 123.4268 | -118.5608 | 4.6921 | -0.027161 | 0.0041935 | 0.11953 | 0.0034479 | -0.00065586 | 0.00049778 | 0.0026789 | -0.053741 | 0.13768 | 0.0019076 | -0.002305 | -0.003025 | -0.0035846 | 0.0015915 | -3.36 | -2.4033 | -118.8583 | -2.6917 | -2.5223 | -118.4143 | -2.5864 | 0.5127 | 4.7607 | 4.2297 | 4.6143 | 4.5731 | 4.4815 | 4.5822 | -0.29755 | -7.0953 | -7.3837 | 116.0385 | 115.9744 | 0.14648 | 116.272 | 0.44403 | 122.7905 | 0.068664 | -0.07782 | 123.1338 | 123.143 | 123.0423 | 0.35248 | 0.25177 | 116.3361 | 116.1667 | 0.34332 | 0.38452 | 116.4551 | 0.53101 | 116.1575 | 123.3215 | -123.5504 | -0.46234 | 115.8691 | 123.175 | 115.2008 | 119.0735
2134.5469 | 123.3536 | -118.6707 | 4.6143 | -0.0042723 | 0.0031253 | 0.11889 | 0.0025933 | -0.00086946 | 0.00049778 | 0.0016107 | -0.059845 | 0.13768 | 0.0010532 | -0.004014 | -0.0025976 | -0.0046528 | -0.0020401 | -3.1174 | -2.3575 | -118.9728 | -2.6917 | -2.5223 | -118.5287 | -2.5726 | 0.5722 | 4.6921 | 4.1519 | 4.4403 | 4.4769 | 4.3762 | 4.4128 | -0.30212 | -6.9717 | -7.3059 | 116.1484 | 116.098 | 0.14191 | 116.4001 | 0.44403 | 122.8226 | 0.07782 | -0.17395 | 123.1476 | 123.0835 | 123.0469 | 0.26093 | 0.2243 | 116.4505 | 116.2811 | 0.32501 | 0.28839 | 116.6153 | 0.54016 | 116.3132 | 123.3627 | -123.587 | -0.46234 | 115.979 | 123.111 | 115.5533 | 119.2429
2135.4844 | 123.436 | -118.6615 | 4.5731 | -0.050049 | 0.0050479 | 0.1206 | 0.0045159 | 0.0019077 | 0.0039158 | -0.00095273 | -0.093414 | 0.13811 | 0.0014804 | 0.0032492 | -0.0045202 | -0.0025164 | -0.0013991 | -3.1357 | -2.2385 | -118.9728 | -2.536 | -2.3987 | -118.6432 | -2.4628 | 0.5127 | 4.6417 | 4.1611 | 4.5136 | 4.2114 | 4.4266 | 4.5685 | -0.31128 | -6.8115 | -7.1091 | 116.2628 | 116.1987 | 0.018311 | 116.51 | 0.32959 | 122.8226 | 0.068665 | -0.059509 | 122.8729 | 123.23 | 123.0881 | 0.40741 | 0.2655 | 116.5741 | 116.4368 | 0.050354 | 0.35248 | 116.7343 | 0.48065 | 116.423 | 123.3032 | -123.5458 | -0.41199 | 116.1255 | 123.175 | 115.5258 | 119.1742
2136.4844 | 123.4268 | -118.6615 | 4.5822 | -0.080566 | 0.0041935 | 0.12039 | 0.0045159 | 0.0012667 | 0.0019932 | -0.0047979 | -0.12698 | 0.13768 | 0.0031894 | 0.0030356 | -0.002384 | -0.0010212 | 0.0067185 | -3.3829 | -2.2156 | -119.0002 | -2.623 | -2.4857 | -118.634 | -2.536 | 0.41199 | 4.6738 | 4.1473 | 4.454 | 4.0695 | 4.3533 | 4.4769 | -0.33874 | -6.7978 | -7.2052 | 116.1758 | 116.1255 | 0.027466 | 116.4642 | 0.36621 | 122.8088 | 0.091553 | -0.12817 | 122.731 | 123.1384 | 123.0148 | 0.32959 | 0.20599 | 116.5146 | 116.3773 | -0.07782 | 0.3067 | 116.7847 | 0.52643 | 116.4459 | 123.3353 | -123.5825 | -0.43487 | 116.0385 | 123.1155 | 115.2786 | 119.0735
2137.5469 | 123.3536 | -118.6981 | 4.6097 | -0.050049 | 0.0037661 | 0.1206 | 0.0032343 | 0.0038303 | -0.00035682 | -0.0018073 | -0.15445 | 0.13256 | 0.00618 | 0.0032492 | -0.0025976 | -0.01277 | -0.0018265 | -3.8177 | -2.2751 | -118.9774 | -2.6642 | -2.4811 | -118.5883 | -2.5635 | 0.46234 | 4.6875 | 4.1428 | 4.4357 | 4.0512 | 4.3533 | 4.454 | -0.27924 | -6.8848 | -7.2739 | 116.217 | 116.1346 | 0.10986 | 116.4139 | 0.3891 | 122.8409 | 0.07782 | -0.17395 | 122.7493 | 123.1522 | 123.0515 | 0.31128 | 0.21057 | 116.4963 | 116.3132 | -0.091553 | 0.29297 | 116.7023 | 0.54474 | 116.423 | 123.3856 | -123.587 | -0.46692 | 116.0339 | 123.1339 | 114.8804 | 119.1605
2138.4844 | 123.349 | -118.7256 | 4.5685 | -0.019531 | 0.0026981 | 0.12039 | 0.0049433 | 0.00019874 | 0.00071138 | 0.0016107 | -0.12698 | 0.13854 | 0.00062585 | -0.00059601 | -0.0021704 | -0.0012348 | 0.0045823 | -5.0491 | -2.2385 | -119.0689 | -2.6688 | -2.5589 | -118.7805 | -2.5726 | 0.37537 | 4.6234 | 4.0741 | 4.39 | 3.9963 | 4.2938 | 4.4174 | -0.34332 | -6.8069 | -7.2372 | 116.1667 | 116.153 | -0.054932 | 116.4963 | 0.28839 | 122.7997 | 0.054932 | -0.17853 | 122.7219 | 123.143 | 123.0194 | 0.34332 | 0.21973 | 116.51 | 116.4001 | -0.07782 | 0.31586 | 116.8304 | 0.54932 | 116.4871 | 123.349 | -123.6374 | -0.49438 | 116.0568 | 123.1155 | 113.6765 | 119.101
2139.4844 | 123.4543 | -118.7714 | 4.4586 | -0.072937 | 0.0050479 | 0.1221 | 0.0032343 | -0.0021513 | 0.0024204 | -0.0043707 | -0.053741 | 0.13683 | 0.0014804 | -0.0048684 | 0.000393 | 0.00068782 | -0.00097194 | -5.3696 | -2.3529 | -119.0598 | -2.6596 | -2.4994 | -118.7576 | -2.5681 | 0.5127 | 4.5456 | 4.0558 | 4.3304 | 4.2938 | 4.3259 | 4.3854 | -0.28839 | -6.8115 | -7.1182 | 116.272 | 116.2033 | 0.013733 | 116.4917 | 0.30212 | 122.8271 | 0.086975 | -0.12817 | 123.0652 | 123.1567 | 123.0972 | 0.32959 | 0.27008 | 116.5604 | 116.4001 | 0.23804 | 0.27466 | 116.7068 | 0.48981 | 116.4185 | 123.317 | -123.5184 | -0.40283 | 116.1118 | 123.1018 | 113.4018 | 119.2841
2140.5469 | 123.349 | -118.7164 | 4.5868 | 0.010986 | 0.0039799 | 0.11932 | 0.0055841 | 0.0016939 | 0.00092498 | -9.8328e-05 | -0.099518 | 0.13704 | 0.0031894 | 0.00025839 | -0.0049476 | -0.00508 | 9.6064e-05 | -5.1498 | -2.3712 | -119.0506 | -2.7969 | -2.6596 | -118.5471 | -2.6917 | 0.38452 | 4.6783 | 4.0924 | 4.3808 | 4.0512 | 4.3488 | 4.4403 | -0.33417 | -6.958 | -7.3837 | 116.0568 | 116.0248 | 0.16937 | 116.3589 | 0.50354 | 122.8088 | 0.091553 | -0.20599 | 122.7676 | 123.1567 | 123.0652 | 0.3479 | 0.25635 | 116.391 | 116.2537 | -0.041199 | 0.28839 | 116.6794 | 0.58594 | 116.3452 | 123.3948 | -123.6374 | -0.49439 | 115.9195 | 123.0972 | 113.5666 | 119.101
2141.4844 | 123.3902 | -118.7302 | 4.5547 | 0.08728 | 0.0044071 | 0.12082 | 0.0036615 | -0.00044226 | 0.00049778 | -0.0011663 | -0.05069 | 0.13832 | 0.0029758 | 4.4788e-05 | -0.0021704 | -0.001662 | 0.00052346 | -5.3696 | -2.4216 | -119.0323 | -2.7145 | -2.5314 | -118.927 | -2.5864 | 0.48523 | 4.5914 | 4.0924 | 4.4312 | 4.0787 | 4.3625 | 4.4632 | -0.30212 | -6.9763 | -7.2693 | 116.1987 | 116.1438 | -0.19684 | 116.4459 | 0.10529 | 122.8226 | 0.036621 | -0.1236 | 122.8088 | 123.1934 | 123.0927 | 0.37079 | 0.27008 | 116.5009 | 116.3177 | -0.013733 | 0.33875 | 116.6107 | 0.49896 | 116.3086 | 123.3215 | -123.587 | -0.46234 | 116.0156 | 123.1613 | 113.3606 | 119.2154
2142.5469 | 123.3124 | -118.7256 | 4.628 | -0.0042723 | 0.0048343 | 0.1206 | 0.0047295 | 0.00062594 | 0.0041294 | 0.00075627 | -0.14529 | 0.13619 | 0.0019076 | -0.0076456 | -0.0008886 | -0.011702 | -0.0013991 | -7.3151 | -2.3483 | -119.0186 | -2.7969 | -2.6596 | -118.6249 | -2.7054 | 0.33875 | 4.6783 | 4.0604 | 4.3488 | 3.9093 | 4.2114 | 4.335 | -0.29297 | -6.9763 | -7.4249 | 116.066 | 116.0202 | 0.10071 | 116.3132 | 0.39368 | 122.786 | 0.050354 | -0.27924 | 122.6349 | 123.0606 | 122.937 | 0.27466 | 0.15106 | 116.3589 | 116.2216 | -0.15106 | 0.28839 | 116.6702 | 0.61798 | 116.3773 | 123.4039 | -123.6465 | -0.56763 | 115.9287 | 123.0743 | 111.4105 | 119.0643
2143.4844 | 123.4085 | -118.7485 | 4.4861 | -0.042419 | 0.0059025 | 0.11996 | 0.0015253 | 0.0021213 | 0.00071138 | -0.0018073 | -0.044586 | 0.13597 | 0.003403 | 0.00047219 | -0.0043066 | -0.0020892 | -0.00011754 | -5.3513 | -2.3666 | -119.0735 | -2.6871 | -2.4719 | -118.6615 | -2.5635 | 0.50354 | 4.5364 | 4.0421 | 4.3991 | 3.9963 | 4.3213 | 4.4357 | -0.32501 | -6.8527 | -7.1732 | 116.2766 | 116.185 | 0.086975 | 116.51 | 0.41199 | 122.7905 | 0.050354 | -0.086975 | 122.7448 | 123.1842 | 123.0698 | 0.39368 | 0.27924 | 116.6016 | 116.3864 | -0.045776 | 0.35706 | 116.7068 | 0.49439 | 116.3818 | 123.2849 | -123.5596 | -0.44403 | 116.0614 | 123.1476 | 113.3972 | 119.252
2144.5469 | 123.3215 | -118.7347 | 4.5456 | -0.050049 | 0.0035525 | 0.12039 | 0.0034479 | -0.0023649 | -0.00078402 | -0.00073913 | -0.10867 | 0.14003 | 0.0042574 | 0.00047219 | -0.0019568 | -0.0020892 | 0.0022323 | -5.2917 | -2.243 | -119.0781 | -2.742 | -2.5223 | -118.3365 | -2.6138 | 0.34332 | 4.6097 | 4.0924 | 4.3442 | 3.9047 | 4.2389 | 4.3808 | -0.34332 | -6.7886 | -7.2876 | 116.2125 | 116.1209 | 0.39825 | 116.4642 | 0.74158 | 122.8271 | 0.064087 | -0.20142 | 122.6395 | 123.1155 | 122.9736 | 0.28839 | 0.14649 | 116.5558 | 116.3361 | -0.18768 | 0.25177 | 116.835 | 0.51727 | 116.4917 | 123.3444 | -123.6237 | -0.45319 | 115.9927 | 123.0789 | 113.443 | 119.0781
2145.4844 | 123.3719 | -118.7119 | 4.509 | -0.065308 | 0.0029117 | 0.1206 | 0.0032343 | -0.0015103 | -0.0022794 | -0.0026617 | -0.041534 | 0.13725 | 0.0027622 | 0.00025839 | -0.0032386 | -0.0018756 | 0.0052231 | -4.8431 | -2.2614 | -119.0323 | -2.5864 | -2.4033 | -118.7668 | -2.4765 | 0.48523 | 4.5593 | 4.0695 | 4.3671 | 3.9734 | 4.3304 | 4.422 | -0.32043 | -6.7703 | -7.0953 | 116.3086 | 116.2354 | -0.054932 | 116.5558 | 0.2655 | 122.7814 | 0.050354 | -0.14191 | 122.6852 | 123.1339 | 123.0423 | 0.35248 | 0.26093 | 116.629 | 116.4459 | -0.09613 | 0.29755 | 116.7709 | 0.48981 | 116.4505 | 123.2712 | -123.5413 | -0.43945 | 116.1255 | 123.0789 | 113.8687 | 119.1971
2146.5469 | 123.3032 | -118.7622 | 4.5685 | -0.027161 | 0.0016299 | 0.11975 | 0.0049433 | 0.0014803 | -0.00035682 | -0.0033025 | -0.16055 | 0.13768 | 0.0012668 | -0.0063638 | -0.0025976 | -0.013411 | 0.0022323 | -4.4083 | -2.179 | -119.0735 | -2.6184 | -2.4811 | -118.4647 | -2.5589 | 0.42114 | 4.6234 | 4.0604 | 4.3167 | 3.891 | 4.2206 | 4.3625 | -0.31128 | -6.7474 | -7.1869 | 116.2811 | 116.2033 | 0.29755 | 116.5146 | 0.60882 | 122.8226 | 0.054932 | -0.25177 | 122.6532 | 123.1247 | 122.9828 | 0.30212 | 0.16022 | 116.5924 | 116.4551 | -0.16937 | 0.25635 | 116.8945 | 0.56305 | 116.5833 | 123.3856 | -123.642 | -0.50812 | 116.1438 | 123.0789 | 114.3539 | 119.1834
2147.4844 | 123.3948 | -118.6707 | 4.5685 | -0.072937 | 0.0046207 | 0.12018 | 0.0038751 | 0.0010531 | 0.0022068 | -0.0011663 | -0.05069 | 0.1364 | 0.0063938 | -0.0029458 | -0.0051612 | -0.0023028 | -0.00054474 | -7.933 | -2.211 | -118.9545 | -2.4994 | -2.3438 | -119.1696 | -2.417 | 0.3067 | 4.6234 | 4.1565 | 4.5044 | 4.0466 | 4.4312 | 4.5502 | -0.28381 | -6.7795 | -7.0679 | 116.3269 | 116.2537 | -0.49896 | 116.5375 | -0.21515 | 122.8271 | 0.054932 | -0.064086 | 122.7173 | 123.2208 | 123.1018 | 0.39368 | 0.27466 | 116.6107 | 116.4551 | -0.10986 | 0.3479 | 116.7435 | 0.46692 | 116.4597 | 123.2941 | -123.5229 | -0.41199 | 116.1713 | 123.175 | 110.7376 | 118.9774
2148.5469 | 123.2803 | -118.5928 | 4.7104 | -0.0042723 | 0.0039799 | 0.11975 | 0.00067072 | 0.0010531 | -0.00099762 | -0.0024481 | -0.078156 | 0.13811 | 0.005112 | -0.006791 | -0.0025976 | -0.0037982 | -0.00054474 | -22.7646 | -2.2247 | -118.9407 | -2.6962 | -2.536 | -118.5745 | -2.5543 | 0.35248 | 4.7516 | 4.1153 | 4.4128 | 3.9551 | 4.3213 | 4.39 | -0.3479 | -6.9351 | -7.4066 | 116.0568 | 116.0385 | 0.01831 | 116.3864 | 0.36621 | 122.7081 | 0.041199 | -0.29755 | 122.5479 | 122.9828 | 122.9141 | 0.27466 | 0.20599 | 116.4047 | 116.2445 | -0.16022 | 0.29755 | 116.716 | 0.63629 | 116.3681 | 123.3444 | -123.6511 | -0.59509 | 115.8966 | 123.0057 | 95.8282 | 118.9453
2149.4844 | 123.4268 | -118.7073 | 4.5364 | -0.11108 | 0.0029117 | 0.12231 | 0.0040887 | 0.0040439 | 0.00049778 | 0.00096987 | -0.056793 | 0.13896 | 0.0053256 | -0.003373 | -0.003025 | 0.001115 | -0.00097194 | -14.8773 | -2.3346 | -119.0002 | -2.623 | -2.4445 | -117.8513 | -2.536 | 0.52643 | 4.628 | 4.1153 | 4.4266 | 4.4724 | 4.3808 | 4.4678 | -0.29297 | -6.871 | -7.1594 | 116.2628 | 116.1713 | 0.85602 | 116.4642 | 1.149 | 122.8226 | 0.091553 | -0.10986 | 123.1796 | 123.175 | 123.0881 | 0.35248 | 0.2655 | 116.5558 | 116.3773 | 0.35706 | 0.31128 | 116.6656 | 0.5127 | 116.3727 | 123.3353 | -123.5367 | -0.42114 | 116.0843 | 123.1338 | 103.83 | 119.2337
2150.5469 | 123.349 | -118.689 | 4.5822 | -0.019531 | 0.0044071 | 0.12253 | 0.0057977 | 0.00041234 | 0.00092498 | -0.0015935 | -0.1514 | 0.13512 | 0.0025484 | 0.0060264 | -0.0034522 | -0.0042254 | 0.0035141 | -32.515 | -2.3529 | -119.0186 | -2.7512 | -2.6001 | -118.8354 | -2.6413 | 0.4303 | 4.6692 | 4.0604 | 4.3991 | 3.9459 | 4.2892 | 4.4037 | -0.32959 | -6.9351 | -7.3334 | 116.0889 | 116.0477 | -0.14648 | 116.3773 | 0.18311 | 122.7493 | 0.086975 | -0.1831 | 122.6349 | 123.0927 | 122.9782 | 0.34332 | 0.22888 | 116.4185 | 116.2674 | -0.11444 | 0.33875 | 116.6656 | 0.60883 | 116.3361 | 123.3582 | -123.6008 | -0.52185 | 115.9378 | 123.0881 | 86.174 | 119.1193
2151.4844 | 123.3765 | -45.5154 | 77.6733 | -0.072937 | 0.0033389 | 0.043058 | 0.0028069 | -0.0023649 | -0.00099762 | 0.00096987 | -0.011017 | 0.0035269 | 0.0027622 | 0.036147 | -0.0021704 | -0.0046528 | 0.00095066 | -11.9568 | -1.2177 | -45.7809 | -1.5335 | -1.5884 | -45.8313 | -1.5472 | 1.4282 | 77.655 | 1.6296 | 77.7191 | 1.9501 | 1.9455 | 2.0279 | -0.2655 | -78.891 | -79.2068 | 43.927 | 43.9682 | -0.31586 | 44.2337 | -0.050354 | 47.1451 | -0.018311 | 0.045776 | 47.4655 | 47.5433 | 47.4609 | 0.39825 | 0.31586 | 44.1925 | 44.2474 | 0.32043 | 76.0895 | 44.5633 | 76.0254 | 44.2978 | 123.1705 | -123.4543 | -76.0437 | 43.9819 | 123.2346 | 33.5587 | 46.9437
2152.4844 | 123.5092 | -118.3411 | 4.8065 | -0.03479 | 0.0054751 | 0.1206 | 0.0062249 | 0.00041234 | 7.0582e-05 | 0.00054267 | -0.10562 | 0.13939 | 0.0019076 | -0.0018778 | -0.0017432 | -0.0014484 | 0.0020187 | -32.0892 | -2.298 | -118.7256 | -2.6413 | -2.4948 | -118.1763 | -2.5406 | 0.48523 | 4.8981 | 4.3991 | 4.7516 | 4.248 | 4.6555 | 4.7791 | -0.38452 | -7.1045 | -7.4478 | 115.8463 | 115.8005 | 0.16479 | 116.185 | 0.54932 | 122.7402 | 0.091552 | -0.054932 | 122.5891 | 123.1201 | 122.9965 | 0.37994 | 0.25635 | 116.2308 | 116.0843 | -0.15106 | 0.35248 | 116.4276 | 0.49896 | 116.0431 | 123.2391 | -123.5321 | -0.40741 | 115.6998 | 123.0927 | 86.2518 | 118.8263
2153.5469 | 123.3719 | -118.0115 | 5.246 | -0.042419 | 0.0050479 | 0.11868 | 0.0060113 | 0.0023349 | 0.00049778 | 0.00032907 | -0.22769 | 0.13896 | 0.003403 | -0.0044412 | -0.002384 | 0.00026062 | 0.00073706 | -32.1487 | -2.1698 | -118.3594 | -2.6093 | -2.4811 | -118.1122 | -2.4994 | 1.442 | 5.3421 | 4.7516 | 5.0308 | 4.5044 | 4.9255 | 5.0537 | -0.3479 | -7.4158 | -7.8552 | 115.5304 | 115.5121 | -0.10071 | 115.86 | 0.24719 | 122.7631 | 0.09613 | -0.21515 | 122.5159 | 123.0652 | 122.937 | 0.30212 | 0.17395 | 115.8783 | 115.7501 | -0.24719 | 0.27924 | 116.1896 | 0.59051 | 115.8417 | 123.3536 | -123.6053 | -0.49439 | 115.4022 | 123.0423 | 85.8627 | 119.4534
2154.4844 | 123.4772 | -118.0069 | 5.1865 | -0.095825 | 0.0048343 | 0.11932 | 0.0070795 | -0.00086946 | 0.00092498 | -9.8328e-05 | -0.096466 | 0.13597 | 0.0023348 | 0.0015402 | -0.003025 | -0.0010212 | -0.0035355 | -32.2174 | -2.1744 | -118.364 | -2.5085 | -2.3666 | -118.634 | -2.4307 | 1.6434 | 5.2643 | 4.7607 | 5.1361 | 4.5776 | 5.0354 | 5.1544 | -0.35706 | -7.3608 | -7.695 | 115.6403 | 115.5762 | -0.62714 | 115.9332 | -0.27008 | 122.7676 | 0.07782 | -0.050354 | 122.5845 | 123.1613 | 123.0423 | 0.39368 | 0.27466 | 115.9973 | 115.8554 | -0.1831 | 0.37537 | 116.1896 | 0.50354 | 115.8325 | 123.2712 | -123.5504 | -0.42572 | 115.4984 | 123.143 | 85.7895 | 119.6503
2155.4844 | 123.4451 | -118.1259 | 5.0812 | -0.050049 | 0.0050479 | 0.11996 | 0.0036615 | 0.00041234 | 0.00092498 | -0.0026617 | -0.072052 | 0.13597 | 0.0036166 | -0.005723 | -0.0055884 | -0.0023028 | 0.0028733 | -32.3639 | -2.1927 | -118.4463 | -2.4719 | -2.3163 | -118.1122 | -2.3849 | 1.6342 | 5.1498 | 4.6555 | 5.0217 | 4.5547 | 4.921 | 5.0262 | -0.32043 | -7.2739 | -7.5531 | 115.8096 | 115.741 | 0.013733 | 116.0614 | 0.33417 | 122.7814 | 0.068664 | -0.05951 | 122.6807 | 123.1522 | 123.0469 | 0.37079 | 0.2655 | 116.1301 | 115.9744 | -0.10071 | 0.36621 | 116.2537 | 0.49438 | 115.9332 | 123.2758 | -123.5275 | -0.42572 | 115.654 | 123.1476 | 85.762 | 119.7601
2156.5469 | 123.3948 | -118.5883 | 4.7012 | -0.080566 | 0.0037661 | 0.11761 | 0.0053705 | 0.0023349 | 7.0582e-05 | 0.0011835 | -0.13309 | 0.13747 | 0.0023348 | 0.0030356 | -0.0015296 | -0.00080758 | 0.0020187 | -32.84 | -2.2018 | -119.0277 | -2.6093 | -2.4902 | -118.6203 | -2.5223 | 0.59967 | 4.66 | 4.1199 | 4.5731 | 4.0741 | 4.4678 | 4.5731 | -0.43945 | -6.9031 | -7.3105 | 116.098 | 116.066 | -0.032043 | 116.5054 | 0.40741 | 122.7081 | -0.041199 | -0.12817 | 122.6624 | 123.1613 | 123.056 | 0.45319 | 0.3479 | 116.5375 | 116.4185 | -0.045776 | 0.45319 | 116.8259 | 0.54016 | 116.3864 | 123.2483 | -123.7289 | -0.58136 | 115.979 | 123.1613 | 85.7483 | 119.1879
2157.4844 | 123.3902 | -118.1671 | 5.0949 | -0.072937 | 0.0050479 | 0.11761 | 0.0038751 | -0.0023649 | -0.0022794 | 0.00096987 | -0.038483 | 0.13875 | 0.0031894 | -0.0055094 | -0.0053748 | -0.003371 | -0.0031081 | -32.579 | -2.2659 | -118.428 | -2.6184 | -2.4765 | -118.1625 | -2.504 | 0.62256 | 5.1819 | 4.6417 | 4.9759 | 4.4769 | 4.9026 | 4.9988 | -0.26093 | -7.3608 | -7.7133 | 115.6906 | 115.6631 | 0.004577 | 115.9241 | 0.2655 | 122.8088 | 0.086975 | -0.11902 | 122.644 | 123.1659 | 123.0698 | 0.35705 | 0.26093 | 115.9515 | 115.8096 | -0.16479 | 0.33417 | 116.1621 | 0.54016 | 115.9012 | 123.349 | -123.5229 | -0.45319 | 115.5487 | 123.143 | 85.5881 | 118.7897
2158.4844 | 123.3994 | -118.1946 | 5.0629 | -0.11871 | 0.0063297 | 0.12018 | 0.0062249 | -0.0015103 | 0.002634 | 0.00032907 | -0.062897 | 0.13661 | 0.0023348 | 0.0017538 | -0.0049476 | -0.0020892 | 0.00073706 | -19.8532 | -2.2751 | -118.5242 | -2.5726 | -2.3804 | -118.1122 | -2.4673 | 0.70496 | 5.0812 | 4.6005 | 4.9438 | 4.454 | 4.8798 | 4.9896 | -0.32959 | -7.338 | -7.6355 | 115.8142 | 115.7272 | 0.082397 | 116.0568 | 0.41199 | 122.7951 | 0.018311 | -0.11902 | 122.6486 | 123.1842 | 123.0743 | 0.3891 | 0.27924 | 116.1438 | 115.9515 | -0.14648 | 0.34332 | 116.2491 | 0.48065 | 115.9195 | 123.2758 | -123.587 | -0.46234 | 115.6219 | 123.1384 | 98.3414 | 118.8995
2159.4844 | 123.4085 | -117.9794 | 5.3192 | -0.027161 | 0.0039799 | 0.11847 | 0.0032343 | -0.00086946 | 0.0015658 | -0.0028753 | -0.041534 | 0.13725 | 0.00083965 | -0.0046548 | -0.0017432 | -0.00059378 | 0.0013779 | -33.0002 | -2.3575 | -118.2587 | -2.7008 | -2.5497 | -117.7963 | -2.5772 | 0.62714 | 5.3284 | 4.8294 | 5.159 | 4.6829 | 5.0674 | 5.1773 | -0.27924 | -7.6767 | -8.02 | 115.4297 | 115.4022 | 0.18311 | 115.6815 | 0.46234 | 122.8088 | 0.009155 | -0.16022 | 122.6624 | 123.1567 | 123.0469 | 0.3479 | 0.23804 | 115.7089 | 115.5579 | -0.14649 | 0.32959 | 115.9012 | 0.49896 | 115.6219 | 123.3078 | -123.5779 | -0.48981 | 115.2786 | 123.1384 | 84.9792 | 118.6066
2160.5469 | 122.6257 | -44.8837 | 77.9892 | -0.0042723 | 0.0024845 | 0.042417 | 0.0038751 | 0.00062594 | 0.0022068 | -0.0013799 | -0.075104 | 0.0050223 | 0.0027622 | 0.038924 | -0.004093 | -0.0012348 | -0.0041763 | -12.1536 | -0.96588 | -45.0073 | -1.4191 | -1.2863 | -45.4971 | -1.3046 | 1.4648 | 78.0304 | 2.3529 | 77.9617 | 2.4948 | 2.536 | 2.6367 | -0.1236 | -78.9551 | -79.4083 | 43.5974 | 43.5791 | -0.6134 | 43.7027 | -0.48981 | 47.2366 | 0.041199 | -0.027466 | 47.3785 | 47.5204 | 47.4197 | 0.28381 | 0.18311 | 43.721 | 43.5883 | 0.14191 | 75.6088 | 44.0414 | 75.6775 | 43.9178 | 122.9141 | -122.9965 | -75.6363 | 43.4647 | 122.8455 | 32.7301 | 46.3486
2161.4844 | 123.3582 | -44.6136 | 78.5614 | -0.042419 | 0.0050479 | 0.044126 | 0.0028069 | -0.0053555 | -0.00078402 | -0.0024481 | -0.032379 | 0.0048087 | 0.0025484 | 0.042342 | -0.0049476 | -0.0020892 | 0.00052346 | -12.1033 | -1.0529 | -44.8792 | -1.3824 | -1.2177 | -44.7784 | -1.2863 | 1.6708 | 78.6209 | 2.5314 | 78.6392 | 2.6871 | 2.7786 | 2.8564 | -0.2655 | -79.6143 | -79.9438 | 43.396 | 43.3273 | -0.16479 | 43.5928 | 0.10071 | 47.1451 | 0.05951 | 0.07782 | 47.3007 | 47.4701 | 47.3923 | 0.32501 | 0.24719 | 43.6615 | 43.4967 | 0.15564 | 76.1078 | 43.8263 | 76.0895 | 43.5608 | 123.2346 | -123.4406 | -76.03 | 43.2312 | 123.2529 | 32.5104 | 46.2845
2162.4844 | 123.4268 | -45.1126 | 78.0212 | -0.050049 | 0.0050479 | 0.043912 | 0.0045159 | 0.0038303 | 7.0582e-05 | -0.0018073 | -0.072052 | 0.0037405 | 0.0021212 | 0.036361 | -0.0025976 | -0.0027302 | -0.0048171 | -12.3367 | -1.0483 | -45.3644 | -1.2955 | -1.149 | -45.3278 | -1.2222 | 1.5198 | 78.1311 | 2.4536 | 78.1219 | 2.3575 | 2.7649 | 2.9114 | -0.25177 | -79.0695 | -79.3167 | 43.9636 | 43.8904 | -0.21515 | 44.1422 | 0.036621 | 47.5662 | 0.10986 | 0.10071 | 47.4701 | 48.024 | 47.8775 | 0.45776 | 0.31128 | 44.2154 | 44.0689 | -0.09613 | 75.6683 | 44.3161 | 75.6775 | 44.0643 | 123.2437 | -123.3856 | -75.5676 | 43.8171 | 123.2346 | 32.7759 | 46.6324
2163.5469 | 122.7264 | -44.6823 | 77.7191 | -0.065308 | -0.0011471 | 0.038572 | -0.0076605 | -0.0062101 | -0.002493 | -0.010566 | -0.19107 | -0.0071543 | -0.0038602 | 0.034865 | -0.0087928 | -0.018111 | -0.0037491 | -12.41 | -0.97046 | -45.1721 | -1.3458 | -1.2085 | -45.3415 | -1.2634 | 1.2497 | 78.1815 | 2.3575 | 78.1952 | 2.4857 | 2.5589 | 2.6642 | -0.48981 | -78.6896 | -79.0649 | 43.4738 | 43.4189 | -0.65918 | 43.9087 | -0.16937 | 47.0398 | 0.46234 | 0.47607 | 47.168 | 47.3465 | 47.2412 | 0.3067 | 0.20142 | 43.9636 | 43.8263 | 0.12817 | 75.8377 | 44.2017 | 75.824 | 43.7119 | 122.8638 | -122.8912 | -75.3616 | 43.3365 | 122.8775 | 32.2723 | 45.932
2164.4844 | 123.3673 | -45.2316 | 77.9343 | -0.027161 | 0.0020573 | 0.041776 | 0.0028069 | -0.0010831 | 0.0015658 | -0.0015935 | -0.0079652 | 0.0024589 | 0.0023348 | 0.035079 | -0.0028112 | -0.0023028 | 0.0037277 | -12.7396 | -1.1719 | -45.4559 | -1.506 | -1.355 | -45.4697 | -1.3916 | 1.2085 | 78.0258 | 2.449 | 78.0304 | 2.6642 | 2.7054 | 2.7878 | -0.22431 | -79.1061 | -79.4403 | 43.8766 | 43.84 | -0.23804 | 44.0643 | -0.013733 | 47.6807 | 0.091553 | 0.096131 | 47.8958 | 48.0194 | 47.937 | 0.33874 | 0.25635 | 44.101 | 43.9499 | 0.21515 | 75.5814 | 44.2841 | 75.5768 | 44.0598 | 123.2574 | -123.3902 | -75.4852 | 43.7256 | 123.262 | 32.4921 | 46.4401
2165.5469 | 123.4451 | -117.9474 | 5.246 | -0.019531 | 0.0033389 | 0.11868 | 0.0010981 | -0.013687 | -0.0033474 | -0.019538 | -0.1636 | 0.1223 | -0.0064236 | -0.013413 | -0.010074 | -0.0037982 | -0.0024673 | -34.6298 | -3.0624 | -118.3228 | -3.511 | -3.3554 | -117.9428 | -3.4332 | 0.43488 | 5.3238 | 4.7836 | 5.0629 | 4.5273 | 4.9438 | 5.0766 | -0.37537 | -8.3084 | -8.757 | 114.592 | 114.5142 | 0.004578 | 114.8895 | 0.37994 | 122.731 | 0.07782 | -0.18311 | 122.4747 | 123.024 | 122.8912 | 0.29297 | 0.16022 | 114.9673 | 114.8117 | -0.25635 | 0.27924 | 115.2603 | 0.54016 | 114.8849 | 123.2712 | -123.5687 | -0.46234 | 114.4363 | 123.0103 | 83.3176 | 118.3823
2166.4844 | 123.4726 | -117.9062 | 5.2963 | -0.072937 | 0.0050479 | 0.1206 | 0.0034479 | 0.00083954 | 0.00071138 | -0.0011663 | -0.087311 | 0.13533 | 0.0014804 | -0.0014504 | -0.003025 | -0.0048664 | 0.0013779 | -33.902 | -2.3483 | -118.3136 | -2.623 | -2.449 | -117.984 | -2.5223 | 0.4715 | 5.3146 | 4.7974 | 5.191 | 4.6738 | 5.1453 | 5.246 | -0.40741 | -7.6447 | -7.9193 | 115.4572 | 115.3839 | -0.07782 | 115.7913 | 0.32959 | 122.7036 | 0.01831 | -0.10529 | 122.58 | 123.1522 | 123.0515 | 0.44861 | 0.3479 | 115.8646 | 115.6906 | -0.1236 | 0.39368 | 115.9653 | 0.51727 | 115.5579 | 123.2208 | -123.6099 | -0.49896 | 115.2832 | 123.0972 | 84.0042 | 118.3777
2167.5469 | 122.4014 | -45.3781 | 77.861 | -0.68329 | -0.0067013 | 0.042631 | -0.0014655 | -0.0070645 | -0.0027066 | -0.010352 | -0.13309 | -0.0039499 | 0.0025484 | 0.042556 | -0.0038794 | -0.0072162 | -0.0013991 | -12.5473 | -1.1627 | -45.1263 | -1.6113 | -1.474 | -45.7397 | -1.5015 | 3.5339 | 77.6321 | 2.092 | 77.8748 | 2.1835 | 2.3987 | 2.4719 | 0.25177 | -79.0237 | -79.4724 | 43.9041 | 43.8766 | -0.36163 | 43.6249 | -0.6134 | 47.4701 | -0.22888 | 0.013733 | 47.5616 | 47.85 | 47.7768 | 0.37994 | 0.3067 | 43.6523 | 43.515 | 0.091553 | 75.7828 | 43.9636 | 75.5402 | 44.2154 | 123.0103 | -122.9874 | -75.769 | 43.7668 | 123.2529 | 32.8308 | 48.912
2168.4844 | 123.381 | -45.282 | 77.8931 | -0.080566 | 0.0033389 | 0.045194 | 0.0030207 | 0.0014803 | -0.00099762 | 0.00054267 | -0.05069 | 0.0013907 | 0.00041225 | 0.039779 | -0.0028112 | -0.0025164 | 0.0011643 | -12.6663 | -1.0849 | -45.3369 | -1.3412 | -1.1856 | -45.488 | -1.2497 | 2.9434 | 77.9526 | 2.124 | 78.035 | 2.3849 | 2.4353 | 2.5452 | -0.054932 | -78.978 | -79.2343 | 44.0964 | 44.0323 | -0.20599 | 44.0872 | -0.15106 | 47.406 | 0.05951 | 0.14191 | 47.6669 | 47.8271 | 47.7173 | 0.42114 | 0.31128 | 44.1513 | 43.9957 | 0.26093 | 75.9109 | 44.252 | 75.8286 | 44.1971 | 123.2346 | -123.23 | -75.769 | 43.9407 | 123.317 | 32.6157 | 48.2254
2169.5469 | 123.5092 | -117.9932 | 5.1544 | -0.057678 | 0.0029117 | 0.1206 | 0.0062249 | 0.00083954 | -0.0029202 | 0.00054267 | -0.090363 | 0.13832 | 0.0040438 | -0.0012368 | -0.001316 | -0.0020892 | -0.0011855 | -34.4147 | -2.211 | -118.3914 | -2.5772 | -2.4261 | -117.984 | -2.4719 | 1.0162 | 5.2505 | 4.7287 | 5.1132 | 4.6051 | 5.0034 | 5.1453 | -0.39825 | -7.3654 | -7.7316 | 115.567 | 115.5212 | 0.009155 | 115.9195 | 0.40741 | 122.7219 | 0.09613 | -0.041199 | 122.5983 | 123.1384 | 122.9965 | 0.41657 | 0.27466 | 115.9653 | 115.8142 | -0.1236 | 0.38452 | 116.1804 | 0.52185 | 115.7822 | 123.2437 | -123.5458 | -0.42572 | 115.416 | 123.1064 | 83.5785 | 119.0094
2170.4844 | 123.4818 | -118.0252 | 5.1819 | -0.32471 | 0.0044071 | 0.12039 | 0.0028069 | -0.00044226 | -0.00078402 | -0.00031193 | -0.047638 | 0.13683 | 0.0036166 | 0.002822 | -0.0032386 | -0.0029438 | 0.0035141 | -34.3872 | -2.2476 | -118.3868 | -2.5269 | -2.3392 | -117.9291 | -2.4261 | 1.0483 | 5.2505 | 4.7195 | 5.1407 | 4.509 | 5.0125 | 5.1178 | -0.36163 | -7.4295 | -7.7087 | 115.686 | 115.5991 | 0.096131 | 115.9607 | 0.45776 | 122.7448 | 0.068664 | -0.041199 | 122.5342 | 123.143 | 123.0377 | 0.39825 | 0.29297 | 116.0477 | 115.86 | -0.21057 | 0.42114 | 116.1392 | 0.53101 | 115.7776 | 123.2758 | -123.5687 | -0.46234 | 115.4984 | 123.1659 | 83.638 | 119.0735
2171.5469 | 123.349 | -45.3461 | 77.8656 | -0.057678 | 0.0033389 | 0.04434 | 0.0038751 | -0.0038603 | 0.0015658 | -0.0011663 | -0.01712 | 0.0018179 | -0.00044215 | 0.039779 | -0.003025 | -0.0020892 | -0.00033114 | -12.5839 | -1.0025 | -45.5566 | -1.3138 | -1.181 | -45.5978 | -1.2131 | 2.0187 | 77.9434 | 1.8814 | 77.9892 | 2.1744 | 2.1103 | 2.2064 | -0.21057 | -78.8681 | -79.1794 | 44.165 | 44.133 | -0.25177 | 44.3436 | -0.041198 | 47.2275 | 0.077819 | 0.1236 | 47.5204 | 47.5525 | 47.4564 | 0.32501 | 0.22888 | 44.3756 | 44.2429 | 0.29297 | 76.1078 | 44.5541 | 76.062 | 44.3436 | 123.2895 | -123.4222 | -75.9842 | 44.0323 | 123.3353 | 32.7621 | 47.3648
2172.4844 | 123.3719 | -45.2087 | 77.9984 | -0.042419 | 0.0037661 | 0.042417 | 0.0055841 | -0.0012967 | 0.0011386 | -0.0028753 | -0.011017 | 0.0016043 | 0.0029758 | 0.033797 | -0.0028112 | -0.001662 | -0.00097194 | -12.7441 | -1.0529 | -45.4514 | -1.3458 | -1.1948 | -45.4697 | -1.2451 | 2.5681 | 78.067 | 2.1286 | 78.0762 | 2.3804 | 2.3712 | 2.3987 | -0.24262 | -79.0512 | -79.3442 | 44.014 | 43.9636 | -0.26093 | 44.2062 | -0.018311 | 47.3373 | 0.068665 | 0.07782 | 47.5891 | 47.6074 | 47.58 | 0.27008 | 0.24261 | 44.2566 | 44.1055 | 0.25177 | 75.9476 | 44.3985 | 75.9384 | 44.1559 | 123.2758 | -123.4497 | -75.8698 | 43.8629 | 123.2849 | 32.4646 | 47.7768
2173.4844 | 123.3902 | -45.1904 | 77.9984 | -0.065308 | 0.00013467 | 0.041776 | 0.0030207 | -0.00044226 | -0.001852 | -0.0033025 | 0.0072936 | 0.0013907 | 0.0048984 | 0.037215 | -0.0032386 | -0.0031574 | 0.0013779 | -12.9913 | -1.1902 | -45.52 | -1.474 | -1.3229 | -45.4605 | -1.3321 | 1.9409 | 78.0304 | 2.1561 | 78.0945 | 2.3987 | 2.4353 | 2.4948 | -0.32959 | -79.1885 | -79.4724 | 43.8675 | 43.8583 | -0.27008 | 44.1879 | 0.05951 | 47.3465 | 0.032044 | 0.09613 | 47.5891 | 47.6852 | 47.6257 | 0.33874 | 0.27924 | 44.1971 | 44.046 | 0.24261 | 75.9384 | 44.3298 | 75.8743 | 44.0002 | 123.2208 | -123.5184 | -75.8423 | 43.7164 | 123.2849 | 32.1991 | 47.1313
2174.5469 | 123.3765 | -45.2087 | 77.9984 | -0.10345 | 0.0037661 | 0.043699 | 0.0030207 | -0.0021513 | 0.0024204 | -0.0026617 | -0.056793 | 0.0039541 | 0.0021212 | 0.042129 | -0.0036658 | -0.0031574 | 0.00095066 | -12.5336 | -1.1719 | -45.4788 | -1.4465 | -1.2726 | -45.4376 | -1.3321 | 2.0325 | 78.0533 | 2.1561 | 78.1082 | 2.3758 | 2.4033 | 2.5085 | -0.27008 | -79.1702 | -79.4449 | 43.9362 | 43.8766 | -0.22888 | 44.1467 | 0.041199 | 47.3648 | 0.054932 | 0.10986 | 47.5845 | 47.7173 | 47.612 | 0.35248 | 0.24719 | 44.2062 | 44.0323 | 0.21973 | 75.9521 | 44.3069 | 75.8972 | 44.0369 | 123.262 | -123.4772 | -75.8423 | 43.7622 | 123.317 | 32.6752 | 47.2412
2175.4844 | 123.436 | -45.1584 | 78.0258 | -0.03479 | 0.0033389 | 0.041563 | 0.0043023 | 0.00062594 | 0.0015658 | -0.0041571 | -0.01712 | 0.0011771 | 0.0046848 | 0.04106 | -0.0025976 | -0.0035846 | 0.0026597 | -12.4237 | -1.1398 | -45.3964 | -1.4465 | -1.3138 | -44.1376 | -1.3229 | 2.0279 | 78.0853 | 2.1973 | 78.1082 | 2.4628 | 2.4765 | 2.5223 | -0.23804 | -79.1656 | -79.4724 | 43.8446 | 43.8354 | 1.0208 | 44.0735 | 1.2588 | 47.3557 | 0.059509 | 0.082397 | 47.6212 | 47.6807 | 47.6349 | 0.32501 | 0.27923 | 44.0826 | 43.9499 | 0.2655 | 75.9109 | 44.2566 | 75.8881 | 44.0186 | 123.2437 | -123.4222 | -75.8286 | 43.7119 | 123.2666 | 32.7347 | 47.1863
2176.4844 | 123.3582 | -45.2545 | 77.9572 | -0.095825 | 0.0026981 | 0.043485 | 0.0043023 | 0.00041234 | -0.0014248 | -0.0037299 | -0.0079652 | 0.00074988 | 0.0021212 | 0.037856 | -0.0043066 | -0.0070026 | 0.0045823 | -12.8311 | -1.2314 | -45.4376 | -1.5747 | -1.4282 | -45.4651 | -1.4465 | 1.7807 | 78.0807 | 2.1606 | 78.0304 | 2.2751 | 2.3941 | 2.4673 | -0.1831 | -79.1885 | -79.5319 | 43.8263 | 43.808 | -0.21057 | 43.9911 | -0.027466 | 47.4152 | 0.1236 | 0.073243 | 47.5296 | 47.7219 | 47.6486 | 0.3067 | 0.23346 | 44.0094 | 43.8629 | 0.11444 | 75.8698 | 44.2062 | 75.9201 | 44.0231 | 123.3353 | -123.3948 | -75.7965 | 43.6798 | 123.2849 | 32.4234 | 47.0352
2177.5469 | 123.1659 | -45.2362 | 77.9846 | -0.62225 | -0.011188 | 0.039854 | -0.0036017 | -0.0085599 | -0.00014322 | -0.012488 | -0.19717 | -0.0086495 | -0.00065575 | 0.04576 | -0.0038794 | -0.0029438 | -0.0018265 | -13.0508 | -1.355 | -45.5612 | -1.7715 | -1.6891 | -45.726 | -1.6983 | 1.9913 | 78.0716 | 2.2156 | 78.1586 | 2.1835 | 2.5223 | 2.6825 | -0.32501 | -79.3396 | -79.7562 | 43.5471 | 43.5379 | -0.48981 | 43.8629 | -0.1648 | 47.4518 | 0.086975 | 0.17395 | 47.4197 | 47.9187 | 47.7585 | 0.46692 | 0.3067 | 43.8721 | 43.7897 | -0.032043 | 75.943 | 44.2062 | 75.856 | 43.8812 | 123.3078 | -123.5458 | -75.769 | 43.4647 | 123.3948 | 32.1854 | 47.2275
2178.4844 | 123.4039 | -45.2179 | 77.9755 | -0.088196 | 0.0026981 | 0.038999 | 0.0025933 | 0.00041234 | 0.0032748 | -0.0035163 | 0.0072936 | 0.0022453 | 0.0048984 | 0.038497 | -0.0028112 | -0.0042254 | -0.00054474 | -13.1195 | -1.3321 | -45.52 | -1.6708 | -1.5335 | -45.4742 | -1.5793 | 2.0233 | 78.0304 | 2.2247 | 78.0167 | 2.4628 | 2.4902 | 2.5681 | -0.30212 | -79.3076 | -79.6463 | 43.6844 | 43.6386 | -0.25635 | 43.9407 | 0.045777 | 47.4426 | 0.054932 | 0.041199 | 47.6807 | 47.7859 | 47.7081 | 0.34332 | 0.2655 | 43.9865 | 43.8492 | 0.23804 | 75.7919 | 44.1879 | 75.8057 | 43.8858 | 123.2483 | -123.4955 | -75.7507 | 43.5471 | 123.2346 | 32.0984 | 47.2412
2179.5469 | 123.4039 | -45.3369 | 77.8976 | -0.03479 | 0.0024845 | 0.04434 | 0.0072931 | -0.00086946 | 0.0011386 | 0.00032907 | -0.0018616 | 0.0026725 | 0.0038302 | 0.042983 | -0.003025 | -0.0018756 | 0.0024461 | -13.4125 | -1.5198 | -45.6207 | -1.8494 | -1.712 | -45.6024 | -1.7395 | 2.124 | 77.9068 | 2.1744 | 77.948 | 2.3575 | 2.4399 | 2.5223 | -0.28381 | -79.4174 | -79.747 | 43.6249 | 43.5974 | -0.2655 | 43.8812 | 0.018311 | 47.5113 | 0.009155 | 0.050354 | 47.6944 | 47.8592 | 47.7768 | 0.3479 | 0.2655 | 43.9087 | 43.7714 | 0.18311 | 75.7736 | 44.101 | 75.7324 | 43.8171 | 123.2437 | -123.5184 | -75.7233 | 43.4875 | 123.2849 | 31.9244 | 47.4609
2180.4844 | 123.3948 | -45.3735 | 77.8152 | -0.065308 | 0.0035525 | 0.042844 | 0.0049433 | -0.0051419 | 0.0034884 | -0.0020209 | -0.026276 | 0.0028861 | 0.0036166 | 0.039138 | -0.0036658 | -0.0012348 | 0.0026597 | -13.4445 | -1.4053 | -45.6436 | -1.8814 | -1.7212 | -45.6985 | -1.712 | 2.1149 | 77.8427 | 1.6342 | 77.8885 | 1.9363 | 1.9409 | 2.0325 | -0.27008 | -79.2206 | -79.6967 | 43.6523 | 43.6615 | -0.32501 | 43.9316 | -0.054931 | 47.0078 | 0.027465 | 0.073242 | 47.3099 | 47.406 | 47.3145 | 0.39826 | 0.3067 | 43.9224 | 43.7622 | 0.30212 | 76.2543 | 44.2383 | 76.2085 | 43.9682 | 123.2162 | -123.4589 | -76.181 | 43.4921 | 123.262 | 31.929 | 47.4884
2181.4844 | 123.4177 | -46.1243 | 76.9821 | -0.057678 | 0.0035525 | 0.04434 | 0.0040887 | -0.0021513 | -0.0012112 | -0.0013799 | -0.035431 | 0.0056631 | 0.001694 | 0.03807 | -0.004093 | -0.0018756 | 0.00030966 | -13.3621 | -1.5701 | -45.8908 | -1.8539 | -1.6663 | -46.0831 | -1.7441 | 2.3438 | 77.4078 | 1.7258 | 77.1469 | 1.9913 | 1.9638 | 1.9958 | 0.23346 | -78.5522 | -78.8361 | 44.458 | 44.3802 | 0.041199 | 44.1467 | -0.19226 | 47.85 | 0.42572 | 0.16479 | 48.1155 | 48.1201 | 48.0881 | 0.27008 | 0.23804 | 44.2245 | 44.0369 | 0.2655 | 75.4211 | 44.3207 | 75.6821 | 44.5541 | 123.5321 | -122.8729 | -75.2563 | 44.2703 | 123.2712 | 32.7621 | 48.468
2182.4844 | 123.4177 | -45.3461 | 77.8748 | -0.042419 | 0.0029117 | 0.043272 | 0.0066523 | -0.0010831 | 0.0017794 | 0.00011527 | -0.029327 | 0.0026725 | 0.0012668 | 0.039779 | -0.004093 | -0.003371 | -0.0018265 | -13.6047 | -1.355 | -45.6573 | -1.6937 | -1.5839 | -45.5933 | -1.5884 | 2.0142 | 77.9022 | 1.6891 | 77.9114 | 1.9592 | 1.9226 | 2.0187 | -0.31128 | -79.2297 | -79.5685 | 43.7622 | 43.7576 | -0.24719 | 44.0689 | 0.064087 | 47.0352 | 0.027466 | 0.036621 | 47.3053 | 47.3648 | 47.2687 | 0.32959 | 0.23346 | 44.0735 | 43.9636 | 0.27008 | 76.2222 | 44.3024 | 76.2131 | 43.9911 | 123.2483 | -123.5321 | -76.1856 | 43.6523 | 123.2574 | 31.7413 | 47.3602
2183.5469 | 123.4863 | -45.4697 | 77.6733 | -0.065308 | 0.0048343 | 0.044553 | 0.0055841 | -0.00022866 | 0.00028418 | 0.00054267 | -0.099518 | 0.0030997 | 0.0031894 | 0.04341 | -0.0028112 | -0.0023028 | -0.0016129 | -13.5818 | -1.3824 | -45.6161 | -1.6205 | -1.5015 | -45.6253 | -1.5747 | 2.1194 | 77.8748 | 1.6663 | 77.7924 | 1.7624 | 1.7487 | 1.9135 | -0.14648 | -79.0558 | -79.2938 | 43.9682 | 43.895 | -0.15564 | 44.0414 | -0.009155 | 47.1359 | 0.20142 | 0.11902 | 47.2321 | 47.3831 | 47.2183 | 0.24719 | 0.082397 | 44.1147 | 43.9957 | 0.09613 | 76.1261 | 44.2337 | 76.2085 | 44.0872 | 123.3444 | -123.2895 | -76.0071 | 43.8492 | 123.262 | 31.8878 | 47.5891
2184.4844 | 123.4634 | -45.3094 | 77.8656 | -0.019531 | 0.0018435 | 0.042631 | 0.0030207 | -0.0059965 | 0.0022068 | -0.0011663 | -0.0079652 | 0.00096348 | 0.0055392 | 0.037856 | -0.0043066 | -0.003371 | -0.00075834 | -13.5178 | -1.387 | -45.5795 | -1.6388 | -1.4786 | -45.5292 | -1.5289 | 2.0508 | 77.9572 | 1.7075 | 78.0258 | 2.0142 | 2.037 | 2.0874 | -0.27008 | -79.2526 | -79.5044 | 43.8309 | 43.7805 | -0.21973 | 44.0506 | 0.050354 | 47.0169 | 0.091552 | 0.16022 | 47.3236 | 47.3969 | 47.3465 | 0.37994 | 0.32959 | 44.101 | 43.9407 | 0.3067 | 76.3184 | 44.1925 | 76.2497 | 43.9224 | 123.2666 | -123.4451 | -76.1581 | 43.6707 | 123.3353 | 31.7917 | 47.3602
2185.5469 | 123.4222 | -45.3415 | 77.8564 | -0.042419 | 0.0026981 | 0.041776 | 0.0038751 | 0.00019874 | 0.0032748 | -9.8328e-05 | -0.026276 | 0.0043815 | 0.005112 | 0.039352 | -0.0034522 | -0.0027302 | -0.0022537 | -13.71 | -1.355 | -45.6161 | -1.6388 | -1.4877 | -45.607 | -1.5244 | 2.0691 | 77.8885 | 1.7441 | 77.9617 | 2.0554 | 2.0645 | 2.1286 | -0.27466 | -79.2114 | -79.4952 | 43.8538 | 43.8171 | -0.2655 | 44.0918 | 0.009155 | 47.0856 | 0.032044 | 0.10529 | 47.3969 | 47.4701 | 47.406 | 0.38452 | 0.32043 | 44.1284 | 43.9774 | 0.31128 | 76.2177 | 44.2612 | 76.1444 | 43.9865 | 123.23 | -123.4726 | -76.1124 | 43.7027 | 123.3032 | 31.6315 | 47.4106
2186.5 | 122.7356 | -44.9844 | 77.9892 | -0.18738 | 0.023633 | 0.026182 | -0.0044561 | -0.010055 | -0.0084744 | -0.0075751 | -0.26736 | -0.011 | -0.014755 | 0.034652 | -0.0062292 | -0.014693 | 0.0011643 | -13.7375 | -1.2909 | -45.639 | -1.6571 | -1.5152 | -45.5887 | -1.5976 | 1.9592 | 78.0029 | 1.712 | 77.9343 | 2.1194 | 2.0645 | 2.0737 | -0.6546 | -79.2801 | -79.6463 | 43.4692 | 43.3868 | -0.60425 | 44.0414 | 0.050354 | 46.6965 | 0.013733 | -0.054932 | 47.1039 | 47.0581 | 47.049 | 0.36163 | 0.35248 | 44.1238 | 43.9819 | 0.40741 | 76.2222 | 44.3481 | 76.2909 | 43.6935 | 122.9874 | -123.6282 | -76.2772 | 43.3273 | 122.9187 | 31.2469 | 46.9437
2187.5469 | 123.4222 | -45.3415 | 77.829 | -0.057678 | 0.0026981 | 0.044553 | 0.0049433 | 0.00041234 | 0.0041294 | 0.00054267 | -0.029327 | 0.0028861 | 0.001694 | 0.041274 | -0.0015296 | -0.0020892 | 0.00052346 | -13.8748 | -1.387 | -45.5978 | -1.7944 | -1.4236 | -45.52 | -1.6342 | 2.1332 | 77.9022 | 1.6846 | 77.9755 | 1.973 | 1.9913 | 2.0599 | -0.25635 | -79.216 | -79.6234 | 43.9178 | 43.7073 | -0.17853 | 43.9636 | 0.077819 | 47.0261 | 0.073243 | 0.14648 | 47.3145 | 47.4014 | 47.3328 | 0.37537 | 0.3067 | 44.1742 | 43.8034 | 0.28839 | 76.2909 | 44.2108 | 76.2177 | 43.9545 | 123.2437 | -123.4268 | -76.1444 | 43.5471 | 123.317 | 31.4667 | 47.4747
2188.4844 | 123.3307 | -45.369 | 77.8244 | -0.080566 | 0.0046207 | 0.041135 | 0.0038751 | 0.0012667 | 0.0013522 | -0.0013799 | -0.0079652 | 0.0035269 | 0.003403 | 0.04042 | -0.0032386 | -0.0037982 | 0.00095066 | -13.7283 | -1.4557 | -45.6802 | -1.7578 | -1.5427 | -45.5933 | -1.6296 | 2.1103 | 77.9022 | 1.6846 | 77.9297 | 1.9775 | 2.0004 | 2.0187 | -0.31128 | -79.2801 | -79.5822 | 43.8263 | 43.7393 | -0.2243 | 44.0506 | 0.086975 | 47.0535 | 0.07782 | 0.10528 | 47.3465 | 47.3877 | 47.3694 | 0.33417 | 0.31586 | 44.1376 | 43.9224 | 0.29297 | 76.2451 | 44.2245 | 76.2177 | 43.9133 | 123.2712 | -123.5046 | -76.1398 | 43.6111 | 123.2986 | 31.6406 | 47.4792
2189.4844 | 122.9691 | -45.3369 | 77.9297 | -0.1416 | 0.0024845 | 0.043272 | 0.0019525 | 0.0014803 | 7.0582e-05 | -0.0030889 | -0.059845 | 0.0030997 | 0.0023348 | 0.038497 | -0.0034522 | -0.0031574 | 0.00073706 | -13.9023 | -1.4053 | -45.5887 | -1.7761 | -1.6342 | -45.5566 | -1.6571 | 2.0462 | 78.0212 | 1.6617 | 77.9022 | 1.8677 | 1.8677 | 1.9455 | -0.25177 | -79.335 | -79.7058 | 43.7027 | 43.6798 | -0.21973 | 43.9316 | 0.032043 | 46.9986 | 0.091553 | -0.027465 | 47.2046 | 47.2824 | 47.2046 | 0.28381 | 0.20599 | 43.9545 | 43.8126 | 0.20599 | 76.2405 | 44.1833 | 76.3596 | 43.9316 | 123.3582 | -123.5184 | -76.268 | 43.5608 | 123.2391 | 31.4346 | 47.3831
2190.4844 | 123.4497 | -45.3049 | 77.8976 | -0.027161 | 0.0020573 | 0.041349 | 0.0034479 | -0.0015103 | 0.00028418 | -0.0015935 | -0.0079652 | 0.00074988 | 0.0021212 | 0.036361 | -0.0028112 | -0.0018756 | 0.0011643 | -13.9572 | -1.4511 | -45.5704 | -1.7441 | -1.5793 | -45.5063 | -1.6296 | 2.1835 | 77.9572 | 1.6479 | 78.0075 | 1.9455 | 1.9409 | 1.9913 | -0.2655 | -79.3488 | -79.6417 | 43.7256 | 43.6752 | -0.20142 | 43.9407 | 0.064087 | 46.9528 | 0.059509 | 0.10986 | 47.2504 | 47.2961 | 47.2458 | 0.34332 | 0.29297 | 43.9911 | 43.8263 | 0.29755 | 76.3596 | 44.1193 | 76.3092 | 43.8538 | 123.262 | -123.468 | -76.2497 | 43.5608 | 123.3124 | 31.3477 | 47.4884
2191.5625 | 123.4131 | -45.2454 | 77.9755 | -0.21027 | 0.0035525 | 0.043485 | 0.0066523 | 0.0012667 | 0.0022068 | 0.0020379 | -0.072052 | 0.0035269 | 0.0046848 | 0.037002 | -0.0038794 | -0.0012348 | 9.6064e-05 | -13.623 | -1.3367 | -45.4788 | -1.5701 | -1.4511 | -45.4697 | -1.506 | 2.0325 | 78.0487 | 1.6342 | 78.0487 | 1.6479 | 1.9409 | 2.0691 | -0.23346 | -79.3121 | -79.5456 | 43.7943 | 43.7393 | -0.2243 | 43.9728 | 0.009155 | 46.8796 | 0.073242 | 0.073242 | 46.8933 | 47.3145 | 47.1863 | 0.43488 | 0.3067 | 44.0277 | 43.9087 | 0.013733 | 76.4145 | 44.1422 | 76.4145 | 43.9087 | 123.2941 | -123.4543 | -76.3412 | 43.6752 | 123.2941 | 31.6223 | 47.2778
2192.4844 | 123.2391 | -45.2454 | 78.0212 | -0.080566 | 0.0018435 | 0.042844 | 0.0043023 | 0.0012667 | 0.0015658 | -9.8328e-05 | -0.020172 | 0.0028861 | 0.0021212 | 0.035506 | -0.0038794 | -0.0027302 | -0.0028945 | -13.6826 | -1.3138 | -45.4926 | -1.6846 | -1.5381 | -45.4651 | -1.5656 | 1.973 | 78.1082 | 1.6067 | 77.9984 | 1.8311 | 1.7944 | 1.8677 | -0.24719 | -79.335 | -79.7058 | 43.7073 | 43.6798 | -0.21973 | 43.927 | 0.027466 | 46.8521 | 0.086975 | -0.022888 | 47.0764 | 47.113 | 47.0398 | 0.26093 | 0.18768 | 43.9545 | 43.808 | 0.22431 | 76.3916 | 44.1788 | 76.5015 | 43.9316 | 123.3536 | -123.5138 | -76.4145 | 43.5608 | 123.2437 | 31.5628 | 47.2183
2193.4844 | 122.8958 | -44.989 | 77.9755 | -0.12634 | -0.011828 | 0.033231 | 0.0051569 | -0.010269 | -0.0054836 | -0.017188 | -0.099518 | -0.0062997 | -0.0066374 | 0.043624 | -0.0032386 | -0.017256 | -0.0016129 | -13.916 | -1.4099 | -45.5795 | -1.7853 | -1.6479 | -45.5109 | -1.6754 | 1.9089 | 78.0624 | 1.6296 | 77.9755 | 1.8768 | 1.8539 | 1.9501 | -0.59052 | -79.3854 | -79.7607 | 43.3411 | 43.3136 | -0.52185 | 43.9041 | 0.068665 | 46.6187 | 0.086975 | 0 | 46.8658 | 46.9391 | 46.843 | 0.32043 | 0.2243 | 43.9316 | 43.7943 | 0.24719 | 76.3458 | 44.1696 | 76.4328 | 43.5791 | 123.0515 | -123.555 | -76.3458 | 43.2037 | 122.9645 | 31.073 | 46.8979
2194.5469 | 123.3902 | -45.2225 | 77.9526 | -0.072937 | 0.0033389 | 0.044126 | 0.0038751 | 0.0023349 | 0.0024204 | -0.0015935 | -0.038483 | 0.0052359 | 0.0029758 | 0.040847 | -0.0047338 | -0.0029438 | 0.0024461 | -13.6139 | -1.3184 | -45.5566 | -1.5884 | -1.4008 | -45.5292 | -1.4832 | 1.918 | 78.0258 | 1.6571 | 78.0853 | 1.9913 | 1.9455 | 2.037 | -0.33417 | -79.2709 | -79.541 | 43.8217 | 43.7393 | -0.3067 | 44.0735 | 0.027466 | 46.8796 | 0.073242 | 0.13275 | 47.2137 | 47.2595 | 47.168 | 0.37994 | 0.28839 | 44.1559 | 43.9682 | 0.33417 | 76.4282 | 44.2383 | 76.3687 | 43.9041 | 123.2483 | -123.5092 | -76.2955 | 43.634 | 123.3078 | 31.6086 | 47.1405
2195.4844 | 123.4726 | -118.5699 | 4.6921 | -0.03479 | 0.0056889 | 0.12103 | 0.0066523 | 0.0010531 | 0.00071138 | -0.00052553 | -0.093414 | 0.14003 | 0.0036166 | 0.002822 | -0.0045202 | -0.0020892 | -0.0024673 | -36.4792 | -2.1652 | -118.9407 | -2.6367 | -2.4948 | -118.5928 | -2.5085 | 0.32044 | 4.7836 | 4.2023 | 4.454 | 4.0375 | 4.39 | 4.5044 | -0.37079 | -6.8573 | -7.3288 | 116.0751 | 116.0614 | -0.022888 | 116.4322 | 0.3479 | 122.7722 | 0.091552 | -0.23804 | 122.6074 | 123.0743 | 122.9599 | 0.30212 | 0.18768 | 116.4459 | 116.304 | -0.16479 | 0.25177 | 116.7755 | 0.58136 | 116.4047 | 123.3536 | -123.6328 | -0.48981 | 115.9332 | 123.024 | 82.0908 | 118.8904
2196.5625 | 123.4497 | -118.6203 | 4.66 | -0.03479 | 0.0039799 | 0.11825 | 0.0068659 | -0.0072781 | -0.001852 | -0.017615 | -0.16055 | 0.12999 | -0.002792 | -0.0087136 | -0.014133 | -0.0044392 | -0.016139 | -36.1404 | -2.1744 | -119.0002 | -2.4857 | -2.2751 | -118.7302 | -2.3666 | 0.47607 | 4.7745 | 4.2068 | 4.4815 | 3.9825 | 4.3762 | 4.4861 | -0.37994 | -6.8344 | -7.1457 | 116.3452 | 116.2537 | -0.10986 | 116.6336 | 0.27008 | 122.8271 | 0.11444 | -0.17853 | 122.6028 | 123.1064 | 122.9965 | 0.27924 | 0.16937 | 116.7252 | 116.5146 | -0.2243 | 0.27466 | 116.8259 | 0.56763 | 116.4459 | 123.3948 | -123.6603 | -0.45319 | 116.1346 | 123.1018 | 82.4799 | 119.0964
2197.4844 | 123.4222 | -118.7302 | 4.628 | -0.057678 | 0.0018435 | 0.11932 | 0.0051569 | 0.0036165 | -0.002493 | -0.0020209 | -0.081207 | 0.13918 | 0.0042574 | -0.0052958 | -0.0025976 | -0.0035846 | 0.00095066 | -36.1221 | -2.2614 | -119.014 | -2.7283 | -2.5726 | -118.6386 | -2.6093 | 0.39825 | 4.7104 | 4.1428 | 4.3945 | 3.9093 | 4.3121 | 4.4128 | -0.28381 | -6.8893 | -7.3563 | 116.1575 | 116.1209 | 0.091553 | 116.4047 | 0.37537 | 122.8729 | 0.082397 | -0.23346 | 122.6395 | 123.143 | 123.0423 | 0.27008 | 0.16937 | 116.4413 | 116.2857 | -0.23346 | 0.25177 | 116.7526 | 0.56763 | 116.4688 | 123.4406 | -123.642 | -0.48523 | 116.0019 | 123.1247 | 82.608 | 119.1284
2198.5469 | 123.5001 | -118.6569 | 4.6143 | -0.14923 | 0.0033389 | 0.12103 | 0.0064385 | 0.0021213 | 0.0017794 | 0.0011835 | -0.059845 | 0.13896 | 0.0042574 | -0.0027322 | -0.004093 | -0.0020892 | 0.0015915 | -35.4034 | -2.3392 | -118.9819 | -2.6505 | -2.4719 | -118.5654 | -2.7924 | 0.85144 | 4.6417 | 4.1245 | 4.5456 | 3.9871 | 4.4312 | 4.5319 | -0.32501 | -6.9534 | -7.2647 | 116.185 | 115.8646 | 0.091552 | 116.1896 | 0.41656 | 122.7814 | 0.027466 | -0.068665 | 122.644 | 123.1888 | 123.0881 | 0.40741 | 0.3067 | 116.51 | 116.3315 | -0.13733 | 0.42114 | 116.6428 | 0.51727 | 116.3177 | 123.2986 | -123.5962 | -0.48981 | 116.0065 | 123.2025 | 83.2535 | 119.5084
2199.4844 | 123.4085 | -118.1808 | 5.159 | 0.0033567 | 0.0031253 | 0.11932 | 0.0070795 | -0.0015103 | -0.00099762 | -0.0084295 | -0.12393 | 0.13512 | 0.0012668 | -0.009141 | -0.0090064 | -0.01982 | -0.0084487 | -26.1887 | -2.2888 | -118.483 | -2.6779 | -2.5177 | -118.0939 | -2.5818 | 0.70038 | 5.2231 | 4.6417 | 4.9896 | 4.8935 | 4.866 | 4.9667 | -0.30212 | -7.4478 | -7.8369 | 115.6631 | 115.5991 | 0.086975 | 115.9012 | 0.3891 | 122.8226 | 0.064086 | -0.16937 | 123.0743 | 123.1476 | 123.0469 | 0.32501 | 0.2243 | 115.9653 | 115.8051 | 0.25177 | 0.3479 | 116.1942 | 0.58136 | 115.892 | 123.4039 | -123.642 | -0.51727 | 115.5029 | 123.1705 | 91.9922 | 118.8812
2200.4844 | 122.5433 | -45.1218 | 78.1677 | -0.32471 | -7.913e-05 | 0.042203 | 0.0053705 | -0.0036465 | -0.00035682 | -0.00073913 | -0.029327 | 0.0033133 | 0.0025484 | 0.039992 | -0.0028112 | -0.0014484 | 0.00095066 | -12.8036 | -1.1032 | -44.5724 | -1.5335 | -1.387 | -45.3781 | -1.4053 | 2.1744 | 77.5955 | 2.2156 | 78.1403 | 2.5269 | 2.3438 | 2.4216 | 0.54932 | -79.2709 | -79.7012 | 43.7347 | 43.7164 | -0.25635 | 43.1671 | -0.80566 | 47.3373 | -0.57221 | -0.027466 | 47.6486 | 47.5433 | 47.4655 | 0.20599 | 0.12817 | 43.1854 | 43.0389 | 0.31128 | 75.9247 | 43.4692 | 75.3799 | 44.0186 | 122.7173 | -122.7402 | -75.9521 | 43.5883 | 123.262 | 32.3181 | 47.2961
2201.4844 | 107.8629 | -44.6274 | 78.1448 | -0.26367 | 0.023847 | 0.049253 | -0.0074469 | 0.035019 | -0.01531 | 0.049889 | -0.28873 | 0.014635 | -0.00086935 | 0.043197 | 0.26336 | 0.015641 | 0.033421 | -12.6297 | -1.268 | -44.7601 | -1.6754 | -1.4877 | -45.3094 | -1.5427 | 1.9409 | 77.5085 | 2.5497 | 77.8793 | 2.5497 | 2.5864 | 2.6413 | -0.13275 | -79.4128 | -79.8203 | 43.1396 | 43.0847 | -0.68207 | 43.2175 | -0.54932 | 47.1771 | -0.63629 | -0.2655 | 47.1771 | 47.2687 | 47.2137 | 0.091552 | 0.036621 | 43.2724 | 43.0847 | 0 | 75.3296 | 43.4921 | 74.9588 | 43.3594 | 122.1359 | -122.905 | -75.5951 | 42.952 | 122.5067 | 31.9977 | 46.5683
2202.4844 | 122.9187 | -45.1126 | 78.1357 | -0.088196 | 0.0029117 | 0.042417 | 0.0051569 | 0.0012667 | 0.00092498 | -0.0022345 | 0.004242 | 0.00053628 | 0.0027622 | 0.039992 | -0.0032386 | -0.0029438 | 0.0026597 | -12.6846 | -1.1902 | -45.2362 | -1.4877 | -1.3046 | -45.2911 | -1.3779 | 1.9958 | 78.1631 | 2.2064 | 78.1952 | 2.4399 | 2.4902 | 2.5452 | -0.1236 | -79.3259 | -79.6234 | 43.808 | 43.7347 | -0.17853 | 43.8583 | -0.054932 | 47.319 | 0.027466 | 0.059509 | 47.5525 | 47.6578 | 47.6028 | 0.33874 | 0.28381 | 43.9316 | 43.7485 | 0.23346 | 75.9888 | 44.046 | 75.9567 | 43.9224 | 123.2758 | -123.3719 | -75.9293 | 43.6249 | 123.3078 | 32.428 | 47.1085
2203.5469 | 123.2758 | -45.1584 | 78.0396 | 0.018616 | 0.0035525 | 0.043912 | 0.0051569 | -0.0025785 | 0.0011386 | -0.0020209 | -0.014069 | 0.0018179 | 0.003403 | 0.038497 | -0.0019568 | -0.0023028 | -0.0013991 | -12.9959 | -1.4145 | -45.4285 | -1.712 | -1.5472 | -45.3827 | -1.5976 | 1.767 | 78.067 | 2.243 | 78.154 | 2.5772 | 2.5635 | 2.6138 | -0.27008 | -79.454 | -79.7516 | 43.6111 | 43.5608 | -0.2243 | 43.8309 | 0.045777 | 47.4014 | 0.027466 | 0.11444 | 47.7356 | 47.7722 | 47.7219 | 0.37079 | 0.32043 | 43.8812 | 43.7164 | 0.33417 | 75.9109 | 44.014 | 75.824 | 43.7439 | 123.2254 | -123.468 | -75.7965 | 43.4464 | 123.3124 | 32.1625 | 46.9254
2204.4844 | 123.111 | -45.0623 | 77.8702 | -0.088196 | 0.0035525 | 0.042844 | 0.0040887 | -0.00044226 | -0.00014322 | -0.00031193 | 0.0011902 | 0.0022453 | 0.0040438 | 0.03807 | -0.0019568 | -0.0046528 | -0.0020401 | -13.0508 | -1.3733 | -45.3918 | -1.6846 | -1.4969 | -45.2911 | -1.5518 | 1.8082 | 78.1586 | 2.2293 | 78.186 | 2.4719 | 2.5269 | 2.5772 | -0.32959 | -79.2435 | -79.5547 | 43.5654 | 43.5104 | -0.22888 | 43.84 | 0.10071 | 47.2916 | 0.28839 | 0.31586 | 47.5342 | 47.6395 | 47.5891 | 0.3479 | 0.29755 | 43.895 | 43.7073 | 0.24261 | 75.9567 | 44.0186 | 75.9293 | 43.689 | 123.2208 | -123.262 | -75.6409 | 43.3777 | 123.2483 | 32.0114 | 46.8704
2205.5469 | 123.3261 | -45.0897 | 78.067 | -0.17975 | 0.0037661 | 0.043699 | 0.0064385 | 0.0025485 | 0.00071138 | -0.0028753 | -0.023224 | 0.00074988 | 0.0040438 | 0.043197 | -0.0025976 | -0.0035846 | -0.00097194 | -13.0966 | -1.4328 | -45.3964 | -1.7075 | -1.4694 | -45.433 | -1.6067 | 2.3026 | 78.1219 | 2.1973 | 78.2043 | 2.4261 | 2.4811 | 2.5909 | -0.3067 | -79.4998 | -79.7745 | 43.6203 | 43.483 | -0.34332 | 43.7897 | -0.036621 | 47.287 | 0.054931 | 0.13733 | 47.5159 | 47.6807 | 47.5708 | 0.39368 | 0.28381 | 43.927 | 43.689 | 0.22888 | 76.0071 | 43.9636 | 75.9247 | 43.6569 | 123.2117 | -123.4634 | -75.8698 | 43.3823 | 123.2941 | 31.9931 | 47.3923
2206.4844 | 123.0972 | -45.0989 | 76.8173 | -0.26367 | 0.02406 | 0.11313 | -0.011506 | 0.035447 | 0.055613 | 0.050317 | -0.1575 | 0.014849 | 0.01323 | 0.032729 | -0.027378 | 0.015855 | -0.016994 | -13.1973 | -1.474 | -45.4559 | -1.8997 | -1.7761 | -45.4926 | -1.8402 | 1.973 | 77.9114 | 2.1423 | 77.0187 | 2.2842 | 2.2888 | 2.3987 | -0.35706 | -78.2913 | -78.717 | 43.3228 | 43.2587 | -0.39368 | 43.6157 | -0.036621 | 47.2412 | 1.0941 | 0.20142 | 47.3831 | 47.4976 | 47.3877 | 0.25635 | 0.14648 | 43.6798 | 43.5562 | 0.14191 | 74.8764 | 43.9819 | 75.769 | 43.6249 | 123.0103 | -122.2733 | -74.675 | 43.1992 | 122.1176 | 31.9016 | 47.0718
2207.4844 | 122.5296 | -44.8746 | 77.4857 | -0.38574 | 0.00098907 | 0.041563 | 0.0064385 | 0.0019077 | 0.00092498 | -0.0056525 | -0.075104 | 0.0045951 | 0.006821 | 0.049605 | -0.002384 | -0.001662 | -0.00097194 | -13.2156 | -1.4969 | -45.5887 | -1.9318 | -1.8402 | -45.5658 | -1.8036 | 1.6754 | 78.0487 | 2.1698 | 77.3163 | 2.2888 | 2.4811 | 2.4994 | -0.71411 | -78.9825 | -79.4174 | 43.0344 | 43.071 | -0.69122 | 43.7851 | 0.022888 | 47.0444 | 0.56305 | -0.16937 | 47.1634 | 47.374 | 47.3557 | 0.32959 | 0.31128 | 43.7485 | 43.6569 | 0.11902 | 75.1465 | 44.0918 | 75.8789 | 43.3777 | 122.9233 | -123.0743 | -75.3159 | 42.9428 | 122.1909 | 31.6589 | 46.55
2208.4844 | 123.5229 | -117.7505 | 5.4703 | -0.03479 | 0.0061161 | 0.12039 | 0.0038751 | 0.0019077 | 0.0024204 | -0.00031193 | -0.011017 | 0.13661 | 0.0023348 | -0.0016642 | -0.0025976 | -0.0042254 | 0.0039413 | -35.3851 | -2.449 | -118.1488 | -2.7649 | -2.6093 | -117.7048 | -2.6505 | 0.48065 | 5.5161 | 4.9759 | 5.2643 | 4.9347 | 5.246 | 5.3329 | -0.39825 | -7.9193 | -8.2352 | 115.1413 | 115.1001 | 0.045776 | 115.4984 | 0.44403 | 122.7264 | 0.045776 | -0.20599 | 122.6852 | 123.0835 | 122.9965 | 0.35706 | 0.27008 | 115.5396 | 115.3839 | -0.041199 | 0.28839 | 115.6998 | 0.54016 | 115.3015 | 123.2666 | -123.6191 | -0.49439 | 114.9857 | 123.0148 | 82.3654 | 118.2312
2209.4844 | 123.4589 | -118.1213 | 5.1956 | -0.042419 | 0.0026981 | 0.11761 | 0.0038751 | -0.00044226 | 0.0028476 | 0.00011527 | -0.13309 | 0.14025 | 0.0021212 | -0.0031594 | -0.0025976 | -0.0020892 | -0.0016129 | -35.0327 | -2.3346 | -118.4967 | -2.7924 | -2.655 | -117.7414 | -2.4994 | 0.42114 | 5.3055 | 4.7012 | 4.9393 | 4.4678 | 4.8798 | 4.9988 | -0.37537 | -7.5302 | -7.988 | 115.4663 | 115.6219 | 0.37994 | 115.9973 | 0.75531 | 122.8226 | 0.10986 | -0.25635 | 122.5891 | 123.1201 | 123.0011 | 0.29755 | 0.17853 | 115.8417 | 115.7043 | -0.23346 | 0.23804 | 116.1621 | 0.60425 | 115.7867 | 123.4268 | -123.6923 | -0.49438 | 115.329 | 123.0606 | 83.0887 | 118.5425
2210.5469 | 123.5458 | -118.1992 | 5.0812 | 0.0033567 | 0.0046207 | 0.12039 | 0.0034479 | -0.0038603 | -0.0014248 | -9.8328e-05 | -0.023224 | 0.13747 | 0.0042574 | 0.0021812 | -0.003025 | -0.001662 | -0.0022537 | -34.6252 | -2.2934 | -118.483 | -2.5909 | -2.3987 | -118.0435 | -2.4628 | 0.5722 | 5.1453 | 4.628 | 5.0034 | 4.6005 | 4.953 | 5.0217 | -0.28381 | -7.3746 | -7.6721 | 115.8005 | 115.7364 | 0.15564 | 116.0202 | 0.43945 | 122.8271 | 0.064087 | -0.07782 | 122.7997 | 123.2208 | 123.1522 | 0.39368 | 0.32501 | 116.0843 | 115.892 | -0.027466 | 0.37537 | 116.1896 | 0.51727 | 115.9058 | 123.3444 | -123.5641 | -0.45319 | 115.6082 | 123.2025 | 83.5739 | 118.7714
2211.4844 | 123.4589 | -118.1854 | 5.1727 | 0.033875 | 0.0041935 | 0.12146 | 0.0047295 | 0.0023349 | -0.00035682 | 0.0016107 | -0.099518 | 0.13448 | 0.0038302 | 0.00047219 | -0.0047338 | -0.0052936 | -0.0024673 | -34.7443 | -2.3529 | -118.5104 | -2.8015 | -2.6733 | -118.0893 | -2.6917 | 0.3891 | 5.2414 | 4.66 | 4.9576 | 4.5136 | 4.8614 | 4.9896 | -0.32501 | -7.5256 | -7.9742 | 115.5121 | 115.4938 | 0.096131 | 115.8188 | 0.42114 | 122.8455 | 0.068665 | -0.21515 | 122.699 | 123.175 | 123.0469 | 0.32959 | 0.20142 | 115.8371 | 115.7089 | -0.14648 | 0.29755 | 116.1575 | 0.58136 | 115.8325 | 123.4268 | -123.6832 | -0.5127 | 115.3839 | 123.143 | 83.4412 | 118.5745
2212.5469 | 123.5275 | -118.071 | 5.191 | -0.011902 | 0.0035525 | 0.11932 | 0.0051569 | -0.0032193 | 0.0017794 | -0.0013799 | -0.0049134 | 0.13854 | 0.0040438 | -0.0080728 | -0.0021704 | -0.0035846 | 0.0020187 | -34.3781 | -2.3163 | -118.364 | -2.6138 | -2.449 | -117.9428 | -2.5131 | 0.59052 | 5.2322 | 4.7562 | 5.127 | 4.6646 | 5.072 | 5.1498 | -0.29297 | -7.5073 | -7.8049 | 115.6219 | 115.5579 | 0.12817 | 115.8508 | 0.42114 | 122.8271 | 0.041199 | -0.064087 | 122.7356 | 123.2208 | 123.143 | 0.39368 | 0.31586 | 115.9149 | 115.7501 | -0.091553 | 0.37079 | 116.0477 | 0.47607 | 115.7547 | 123.3032 | -123.555 | -0.43487 | 115.4572 | 123.1979 | 83.6929 | 118.6615
2213.4844 | 123.4039 | -118.1763 | 5.1727 | -0.057678 | 0.0056889 | 0.12295 | 0.0062249 | 0.0021213 | 0.0019932 | -0.0060797 | -0.19412 | 0.12721 | 0.0027622 | 0.0047446 | -0.0021704 | -0.014693 | -0.00011754 | -34.4879 | -2.2842 | -118.4647 | -2.6733 | -2.5085 | -117.9977 | -2.5726 | 0.48523 | 5.2505 | 4.6738 | 5.0079 | 4.4769 | 4.8981 | 5.0171 | -0.28839 | -7.457 | -7.8461 | 115.6677 | 115.6036 | 0.17853 | 115.892 | 0.46692 | 122.85 | 0.07782 | -0.16479 | 122.6532 | 123.1934 | 123.0743 | 0.34332 | 0.2243 | 115.9561 | 115.7913 | -0.19684 | 0.33417 | 116.1804 | 0.57678 | 115.892 | 123.4268 | -123.6374 | -0.49896 | 115.5029 | 123.1842 | 83.6884 | 118.6615
2214.5469 | 123.4451 | -118.2404 | 5.0629 | -0.10345 | 0.0052615 | 0.11953 | 0.0030207 | 0.0019077 | 0.0028476 | -0.0015935 | -0.032379 | 0.13683 | 0.0019076 | -0.0020914 | -0.000675 | -0.0040118 | 0.0020187 | -34.5108 | -2.3026 | -118.5287 | -2.6505 | -2.4994 | -118.1396 | -2.5314 | 0.47607 | 5.1453 | 4.6051 | 4.9164 | 4.4403 | 4.8431 | 4.985 | -0.28839 | -7.3654 | -7.7133 | 115.741 | 115.7089 | 0.10071 | 115.9973 | 0.3891 | 122.8455 | 0.082398 | -0.14648 | 122.6807 | 123.2254 | 123.0835 | 0.37994 | 0.23804 | 116.0294 | 115.8783 | -0.16479 | 0.31128 | 116.2262 | 0.54016 | 115.9378 | 123.3856 | -123.5916 | -0.45776 | 115.5899 | 123.1567 | 83.7296 | 118.7164
2215.4844 | 123.3765 | -118.0573 | 5.2689 | 0.018616 | 0.0054751 | 0.12124 | 0.0045159 | 0.0034029 | -0.00078402 | -0.0022345 | -0.16055 | 0.13106 | 0.0031894 | 0.004531 | -0.0004614 | -0.011489 | 0.0020187 | -34.2911 | -2.2797 | -118.4189 | -2.6779 | -2.5406 | -117.9474 | -2.5864 | 0.51727 | 5.3329 | 4.7653 | 5.0995 | 4.7836 | 4.985 | 5.0995 | -0.36163 | -7.5485 | -7.9468 | 115.5167 | 115.4709 | 0.10986 | 115.8325 | 0.4715 | 122.8226 | 0.064087 | -0.16937 | 122.8409 | 123.1567 | 123.0423 | 0.33417 | 0.21973 | 115.8783 | 115.741 | 0.01831 | 0.33417 | 116.1392 | 0.56763 | 115.7776 | 123.3902 | -123.6877 | -0.50354 | 115.3793 | 123.1567 | 83.7662 | 118.5745
2216.5469 | 123.3948 | -118.0069 | 5.3055 | -0.065308 | 0.0046207 | 0.1206 | 0.0032343 | 0.0048983 | 0.00071138 | 0.00032907 | -0.059845 | 0.13918 | 0.0019076 | -0.0059366 | -0.0034522 | -0.0023028 | -0.0028945 | -10.7529 | -2.3849 | -118.2632 | -2.6733 | -2.5177 | -117.8741 | -2.5818 | 0.60425 | 5.3696 | 4.8477 | 5.1682 | 4.5822 | 5.0949 | 5.2094 | -0.25635 | -7.6904 | -7.9788 | 115.4892 | 115.4251 | 0.13275 | 115.6815 | 0.3891 | 122.8546 | 0.064087 | -0.13733 | 122.5891 | 123.2162 | 123.1018 | 0.36163 | 0.24719 | 115.7455 | 115.5899 | -0.2655 | 0.32043 | 115.8783 | 0.52185 | 115.6219 | 123.3765 | -123.5687 | -0.45776 | 115.3336 | 123.175 | 107.254 | 118.6111
2217.4844 | 123.436 | -118.0069 | 5.2734 | 0.0033567 | 0.0022709 | 0.11761 | 0.0047295 | 0.0044711 | 0.0013522 | -0.0020209 | -0.099518 | 0.13725 | 0.0027622 | 0.0015402 | -0.0036658 | -0.001662 | 0.0013779 | -23.0209 | -2.4261 | -118.3548 | -2.8381 | -2.7512 | -118.0206 | -2.7328 | 0.50354 | 5.3604 | 4.7653 | 5.0491 | 4.5456 | 4.9438 | 5.04 | -0.3479 | -7.6996 | -8.1116 | 115.2557 | 115.274 | -0.013733 | 115.6219 | 0.33417 | 122.7722 | 0.086976 | -0.2243 | 122.5525 | 123.0469 | 122.9507 | 0.27466 | 0.17853 | 115.6036 | 115.5167 | -0.21973 | 0.28381 | 115.9287 | 0.59509 | 115.5807 | 123.3673 | -123.6282 | -0.50812 | 115.1688 | 123.056 | 94.986 | 118.5104
2218.5469 | 123.4772 | -117.8009 | 5.484 | -0.072937 | 0.0035525 | 0.11911 | 0.0038751 | -0.00044226 | -0.00078402 | -0.0024481 | -0.044586 | 0.13683 | 0.003403 | -0.0035868 | -0.0036658 | -0.003371 | 0.00030966 | -15.4587 | -2.4261 | -118.0801 | -2.7786 | -2.623 | -117.7185 | -2.6733 | 0.67291 | 5.5298 | 4.9301 | 5.3513 | 4.6967 | 5.1819 | 5.278 | -0.27924 | -7.9102 | -8.2626 | 115.1779 | 115.1276 | 0.082397 | 115.4068 | 0.36163 | 122.731 | 0.045776 | -0.13275 | 122.4976 | 123.0789 | 122.9828 | 0.3479 | 0.25177 | 115.4572 | 115.3015 | -0.23346 | 0.42114 | 115.654 | 0.59967 | 115.3748 | 123.3307 | -123.5641 | -0.55389 | 115.0223 | 123.1522 | 102.3422 | 118.4738
2219.4844 | 110.7925 | -44.8059 | 78.447 | -0.2713 | 0.023847 | 0.038572 | 0.00088432 | -0.0083463 | -0.01232 | 0.054589 | -0.14835 | 0.015276 | -0.0040738 | 0.023971 | -0.02866 | 0.015641 | -0.019557 | -12.5931 | -1.0849 | -44.4901 | -1.4511 | -1.3184 | -45.0439 | -1.3733 | 1.9547 | 78.5431 | 3.3096 | 78.4927 | 3.3325 | 3.511 | 3.6255 | 0.31586 | -79.5319 | -79.8981 | 43.4875 | 43.4326 | -0.23804 | 43.1168 | -0.55389 | 48.1155 | 0.096131 | 0.045777 | 48.1384 | 48.4314 | 48.317 | 0.31586 | 0.20142 | 43.1717 | 43.0389 | 0.022889 | 75.1831 | 43.4052 | 75.2335 | 43.721 | 123.349 | -122.937 | -75.1373 | 43.3548 | 123.2986 | 32.2128 | 46.7606
2220.5469 | 123.5275 | -117.6178 | 5.5435 | -0.095825 | 0.0035525 | 0.1206 | 0.0038751 | -0.00044226 | -0.0016384 | -0.00073913 | -0.05069 | 0.13619 | -1.4954e-05 | 0.0013266 | -0.003025 | -0.00016658 | 0.0024461 | -7.7408 | -2.3346 | -118.0344 | -2.623 | -2.4399 | -117.6727 | -2.5223 | 0.59509 | 5.6168 | 5.0125 | 5.4565 | 5.191 | 5.3055 | 5.4108 | -0.41657 | -7.8781 | -8.1665 | 115.1779 | 115.0955 | -0.054931 | 115.5121 | 0.36163 | 122.6303 | 0.073242 | -0.086975 | 122.8088 | 123.0286 | 122.9233 | 0.39825 | 0.29297 | 115.5945 | 115.4114 | 0.17853 | 0.44403 | 115.6998 | 0.60425 | 115.2832 | 123.2346 | -123.5779 | -0.53101 | 114.9948 | 123.0743 | 109.877 | 118.2129
2221.4844 | 112.8525 | -44.8883 | 78.3875 | -0.55359 | -0.0047787 | 0.028745 | -0.0025335 | -0.014328 | -0.002493 | -0.016334 | -0.31314 | -0.0011727 | -0.010269 | 0.033156 | -0.017551 | 0.016069 | -0.013149 | -11.9888 | -0.97504 | -44.339 | -1.2085 | -1.0025 | -45.1126 | -1.149 | 1.9638 | 78.4882 | 2.7649 | 78.1815 | 2.948 | 2.8748 | 2.9984 | 0.54932 | -79.3625 | -79.5959 | 43.8858 | 43.7393 | -0.2243 | 43.19 | -0.77362 | 47.6532 | 0.10071 | -0.20599 | 47.8363 | 47.8867 | 47.7631 | 0.23346 | 0.10986 | 43.3365 | 43.1305 | 0.18311 | 75.4166 | 43.364 | 75.7233 | 43.9133 | 123.3765 | -122.7264 | -75.6226 | 43.6798 | 123.0698 | 32.8995 | 46.8521
2222.4844 | 122.7814 | -44.7739 | 78.511 | -0.019531 | 0.0046207 | 0.04199 | 0.0043023 | -1.486e-05 | 0.00049778 | -0.00073913 | 0.0011902 | 0.0041679 | 0.0042574 | 0.040633 | -0.004093 | -0.0010212 | -0.0024673 | -1.5884 | -0.9201 | -44.664 | -1.3412 | -1.1673 | -44.9982 | -1.2085 | 1.7715 | 78.5751 | 2.9022 | 78.4653 | 3.186 | 3.1265 | 3.1815 | 0.10986 | -79.4312 | -79.8523 | 43.6066 | 43.5654 | -0.2243 | 43.4555 | -0.33417 | 47.6761 | 0.064087 | -0.045776 | 47.9599 | 47.9553 | 47.9004 | 0.27924 | 0.2243 | 43.4967 | 43.3228 | 0.28381 | 75.563 | 43.7439 | 75.6729 | 43.8538 | 123.349 | -123.175 | -75.6088 | 43.4326 | 123.2391 | 43.1854 | 46.5454
2223.4844 | 114.917 | -44.7601 | 78.4515 | -0.30182 | -0.0062741 | 0.037504 | 0.00067072 | -0.0079191 | -0.0012112 | -0.0082159 | -0.20023 | -0.0082223 | -0.0072782 | 0.03807 | -0.007511 | -0.016402 | -0.0086623 | -1.9272 | -1.0162 | -45.0256 | -1.3916 | -1.2451 | -45.1492 | -1.2863 | 1.8814 | 78.4973 | 2.861 | 78.0167 | 3.067 | 3.067 | 3.1448 | -0.2655 | -79.4678 | -79.8431 | 43.515 | 43.4738 | -0.3891 | 43.7393 | -0.1236 | 47.6212 | 0.045776 | -0.43488 | 47.8271 | 47.905 | 47.8271 | 0.28381 | 0.20599 | 43.7805 | 43.634 | 0.20599 | 75.1556 | 44.0094 | 75.6363 | 43.7439 | 123.2574 | -123.4772 | -75.5905 | 43.3685 | 122.7768 | 42.8329 | 46.6415
2224.5469 | 123.5275 | -117.627 | 5.571 | -0.027161 | 0.0020573 | 0.11868 | 0.0034479 | 0.0059665 | 0.00049778 | 0.0016107 | -0.0079652 | 0.13555 | 0.0038302 | 0.00025839 | -0.003025 | -0.0025164 | 0.00052346 | -3.0945 | -2.3849 | -118.0252 | -2.6688 | -2.5269 | -117.6086 | -2.5635 | 0.62714 | 5.6351 | 5.0812 | 5.4703 | 5.2597 | 5.4199 | 5.4932 | -0.39826 | -7.9559 | -8.2397 | 115.1001 | 115.0635 | 0.01831 | 115.4617 | 0.41657 | 122.7081 | 0.064087 | -0.10071 | 122.8867 | 123.1201 | 123.0469 | 0.41199 | 0.33874 | 115.4984 | 115.3564 | 0.17853 | 0.3891 | 115.6403 | 0.55389 | 115.242 | 123.262 | -123.5962 | -0.48981 | 114.9582 | 123.0972 | 114.5325 | 118.2541
2225.4844 | 123.4039 | -118.1259 | 5.1636 | -0.065308 | 0.0041935 | 0.1206 | 0.0066523 | -0.0017239 | 0.00049778 | -0.014411 | -0.2399 | 0.12593 | -0.00086935 | -0.0031594 | -0.0064428 | -0.016188 | -0.0065261 | -3.4012 | -2.2888 | -118.4875 | -2.7283 | -2.5864 | -118.0939 | -2.655 | 0.44403 | 5.2414 | 4.6646 | 4.9622 | 4.66 | 4.8248 | 4.9667 | -0.36163 | -7.4524 | -7.8918 | 115.5396 | 115.4709 | 0.032044 | 115.8325 | 0.39368 | 122.7905 | 0.07782 | -0.20142 | 122.7859 | 123.0927 | 122.9507 | 0.30212 | 0.16022 | 115.9012 | 115.7593 | -0.004578 | 0.29755 | 116.1987 | 0.57678 | 115.8371 | 123.3673 | -123.6511 | -0.49896 | 115.3976 | 123.0881 | 114.7247 | 118.5699
2226.5469 | 123.5046 | -118.1763 | 5.1041 | -0.0042723 | 0.0039799 | 0.11911 | 0.0032343 | -0.0032193 | 0.00092498 | 0.0024653 | -0.035431 | 0.1379 | 0.0036166 | 0.0023948 | -0.0021704 | -0.0020892 | 0.00073706 | -4.8157 | -2.3117 | -118.4463 | -2.623 | -2.4307 | -117.9794 | -2.504 | 0.60883 | 5.1727 | 4.6555 | 5.0629 | 4.5731 | 4.9942 | 5.0766 | -0.27008 | -7.4158 | -7.7271 | 115.7455 | 115.6723 | 0.19684 | 115.9424 | 0.46692 | 122.8317 | 0.068664 | -0.041199 | 122.7493 | 123.2529 | 123.1705 | 0.42114 | 0.33874 | 116.0156 | 115.8234 | -0.082398 | 0.40741 | 116.1346 | 0.51727 | 115.8646 | 123.349 | -123.5504 | -0.44861 | 115.5533 | 123.2391 | 113.3606 | 118.7851
2227.4844 | 123.3994 | -118.1992 | 5.1315 | -0.088196 | 0.0046207 | 0.12082 | 0.0075067 | -0.0055691 | -0.00035682 | -0.0082159 | -0.16971 | 0.12444 | 0.001694 | 0.00089939 | -0.0068702 | -0.011275 | -0.0031081 | -2.742 | -2.3209 | -118.483 | -2.7283 | -2.5635 | -118.0801 | -2.4948 | 0.67291 | 5.2551 | 4.6829 | 4.9622 | 4.5776 | 4.8477 | 4.9713 | -0.28381 | -7.4524 | -7.8598 | 115.6357 | 115.7043 | 0.11902 | 115.9882 | 0.40283 | 122.8821 | 0.1236 | -0.16937 | 122.7768 | 123.1705 | 123.0469 | 0.28839 | 0.1648 | 115.9195 | 115.7547 | -0.10528 | 0.27924 | 116.1621 | 0.57221 | 115.8783 | 123.4543 | -123.6145 | -0.44861 | 115.4709 | 123.1613 | 115.4572 | 118.8721
2228.4844 | 123.3444 | -118.2587 | 5.1361 | -0.042419 | 0.0044071 | 0.11932 | 0.0053705 | 0.00041234 | -0.001852 | 0.0011835 | -0.081207 | 0.14025 | 0.003403 | 4.4788e-05 | -0.0025976 | -0.0023028 | -0.0039627 | -2.8152 | -2.2705 | -118.5516 | -2.7649 | -2.5909 | -118.1763 | -2.6184 | 0.5127 | 5.1682 | 4.5822 | 4.9026 | 4.4083 | 4.8019 | 4.9118 | -0.29297 | -7.4066 | -7.901 | 115.6677 | 115.6403 | 0.082397 | 115.9332 | 0.37537 | 122.8409 | 0.032044 | -0.23346 | 122.6669 | 123.1705 | 123.0606 | 0.32959 | 0.21973 | 115.9607 | 115.7867 | -0.17395 | 0.32044 | 116.2811 | 0.58594 | 115.9882 | 123.4268 | -123.6877 | -0.55389 | 115.4938 | 123.1613 | 115.4434 | 118.7714
2229.5469 | 123.3948 | -118.721 | 4.6005 | -0.027161 | 0.0052615 | 0.12103 | 0.0030207 | -0.0030057 | 0.0013522 | -0.0020209 | -0.044586 | 0.13811 | 0.0023348 | -0.0038004 | -0.0032386 | -0.0046528 | -0.0022537 | -5.3192 | -2.3254 | -118.9865 | -2.6596 | -2.4811 | -118.5379 | -2.5406 | 0.5722 | 4.6875 | 4.1519 | 4.4174 | 4.0695 | 4.3625 | 4.4586 | -0.2655 | -6.926 | -7.2601 | 116.2399 | 116.1804 | 0.1831 | 116.4459 | 0.44861 | 122.8729 | 0.086975 | -0.18311 | 122.7905 | 123.1796 | 123.0835 | 0.3067 | 0.21057 | 116.5054 | 116.3269 | -0.082398 | 0.2655 | 116.6611 | 0.53558 | 116.3956 | 123.4085 | -123.587 | -0.44861 | 116.0614 | 123.1384 | 113.4018 | 119.2932
2230.4844 | 123.381 | -118.364 | 4.9576 | -0.03479 | 0.0035525 | 0.12018 | 0.0049433 | 0.0034029 | 0.0024204 | 0.0016107 | -0.096466 | 0.1379 | 0.0031894 | -0.00059601 | -0.0053748 | -0.0046528 | -0.0035355 | -5.9326 | -2.2568 | -118.6523 | -2.7054 | -2.5681 | -118.2495 | -2.6047 | 0.52185 | 5.0629 | 4.4769 | 4.7607 | 4.2801 | 4.6921 | 4.7928 | -0.28839 | -7.2144 | -7.663 | 115.7959 | 115.7593 | 0.11444 | 116.0477 | 0.40283 | 122.8409 | 0.10528 | -0.19684 | 122.644 | 123.1567 | 123.056 | 0.31586 | 0.21515 | 116.0843 | 115.947 | -0.19684 | 0.28381 | 116.3956 | 0.58594 | 116.1072 | 123.4268 | -123.6099 | -0.48065 | 115.6586 | 123.1247 | 112.4313 | 118.8858
2231.4844 | 123.3627 | -118.4463 | 4.8935 | -0.057678 | 0.0041935 | 0.11996 | 0.0047295 | -0.00086946 | 0.0032748 | 0.0013971 | -0.13919 | 0.13405 | 0.0023348 | 4.4788e-05 | -0.0017432 | -0.0074298 | -0.0016129 | -5.0262 | -2.2522 | -118.7805 | -2.6367 | -2.4765 | -118.3685 | -2.5497 | 0.58136 | 4.9622 | 4.3945 | 4.6875 | 4.1977 | 4.6005 | 4.7058 | -0.33417 | -7.1457 | -7.5302 | 115.9698 | 115.8966 | 0.07782 | 116.2308 | 0.41199 | 122.8409 | 0.068664 | -0.20599 | 122.644 | 123.1522 | 123.0469 | 0.31128 | 0.20599 | 116.304 | 116.1438 | -0.19684 | 0.29297 | 116.5283 | 0.56763 | 116.1942 | 123.4085 | -123.674 | -0.49896 | 115.8096 | 123.1338 | 113.4201 | 119.0277
2232.4844 | 123.381 | -118.4784 | 4.8431 | -0.03479 | 0.0044071 | 0.12018 | 0.0062249 | 0.0016939 | 7.0582e-05 | -9.8328e-05 | -0.059845 | 0.13725 | 0.003403 | -0.0020914 | -0.0025976 | -0.00016658 | 0.0024461 | -5.5939 | -2.2385 | -118.7988 | -2.6917 | -2.5452 | -118.3502 | -2.5772 | 0.54932 | 4.9072 | 4.3442 | 4.6463 | 4.5502 | 4.5502 | 4.6555 | -0.32043 | -7.0816 | -7.5348 | 115.9332 | 115.9012 | 0.12817 | 116.2216 | 0.44861 | 122.8226 | 0.064087 | -0.19684 | 123.0286 | 123.1339 | 123.0286 | 0.31128 | 0.20599 | 116.2537 | 116.1072 | 0.20599 | 0.30212 | 116.5604 | 0.56305 | 116.2399 | 123.3856 | -123.642 | -0.49896 | 115.7867 | 123.1247 | 112.8845 | 119.0277
2233.5469 | 123.4726 | -118.3731 | 4.8706 | -0.019531 | 0.0031253 | 0.11847 | 0.0055841 | -0.0019377 | -0.00078402 | -0.0024481 | -0.01712 | 0.13683 | 0.0042574 | -0.002305 | -0.0028112 | -0.0027302 | -0.00011754 | -4.5181 | -2.2751 | -118.7027 | -2.5864 | -2.4216 | -118.2953 | -2.449 | 0.6958 | 4.9484 | 4.4357 | 4.7836 | 4.3304 | 4.747 | 4.8065 | -0.32959 | -7.1457 | -7.457 | 115.9515 | 115.9241 | 0.07782 | 116.2537 | 0.40741 | 122.8088 | 0.07782 | -0.086975 | 122.7036 | 123.1796 | 123.1201 | 0.37079 | 0.31128 | 116.2811 | 116.1163 | -0.10529 | 0.3479 | 116.4276 | 0.51269 | 116.098 | 123.3215 | -123.5733 | -0.43487 | 115.7867 | 123.1567 | 113.855 | 119.0689
2234.4844 | 123.2758 | -118.1076 | 5.1498 | -0.03479 | 0.0035525 | 0.11825 | 0.0049433 | 0.0010531 | -0.00035682 | -0.0015935 | -0.11783 | 0.13597 | 0.0036166 | -0.0048684 | -0.0032386 | -0.0059344 | -0.0035355 | -7.0953 | -2.2705 | -118.5013 | -2.6505 | -2.5085 | -118.1305 | -2.5589 | 0.68665 | 5.1773 | 4.6326 | 4.9301 | 4.3991 | 4.8386 | 5.0217 | -0.39368 | -7.4203 | -7.8003 | 115.5991 | 115.5487 | -0.022888 | 115.9424 | 0.37079 | 122.7402 | 0.027466 | -0.21973 | 122.5067 | 123.1293 | 122.9462 | 0.3891 | 0.20599 | 115.9927 | 115.8508 | -0.23346 | 0.29755 | 116.2308 | 0.54474 | 115.8371 | 123.2849 | -123.6511 | -0.51727 | 115.4572 | 123.0377 | 111.0123 | 118.7943
2235.5469 | 123.3948 | -118.1946 | 5.0995 | -0.080566 | 0.0046207 | 0.11804 | 0.0062249 | -0.0042875 | 0.0015658 | -0.00031193 | 0.010345 | 0.13533 | 0.0019076 | -0.00080961 | -0.0021704 | -0.0018756 | 0.0015915 | -3.8223 | -2.2842 | -118.515 | -2.5955 | -2.4445 | -118.0756 | -2.4948 | 0.70496 | 5.1361 | 4.6005 | 4.9347 | 4.4586 | 4.9164 | 4.985 | -0.32044 | -7.3837 | -7.695 | 115.7501 | 115.6998 | 0.11902 | 116.0202 | 0.43945 | 122.7951 | 0.036621 | -0.16479 | 122.6532 | 123.1796 | 123.111 | 0.38452 | 0.31586 | 116.0706 | 115.9195 | -0.14191 | 0.33417 | 116.2308 | 0.53558 | 115.9103 | 123.3307 | -123.6145 | -0.49896 | 115.5991 | 123.1293 | 114.3723 | 118.8995
2236.4844 | 123.3582 | -118.2587 | 5.0903 | -0.03479 | 0.0052615 | 0.1206 | 0.0064385 | 0.0014803 | 0.0013522 | -9.8328e-05 | -0.1575 | 0.13341 | 0.0040438 | 0.0017538 | -0.002384 | -0.001662 | -0.00075834 | -2.9984 | -2.2568 | -118.5974 | -2.6688 | -2.5177 | -118.1763 | -2.5589 | 0.65918 | 5.0858 | 4.5502 | 4.8798 | 4.3213 | 4.7928 | 4.8935 | -0.33875 | -7.3471 | -7.7591 | 115.741 | 115.6998 | 0.082397 | 116.0385 | 0.42114 | 122.8088 | -0.004578 | -0.21057 | 122.58 | 123.1522 | 123.0515 | 0.34332 | 0.24262 | 116.0797 | 115.9287 | -0.22888 | 0.32959 | 116.3406 | 0.53558 | 116.0019 | 123.3444 | -123.6877 | -0.54016 | 115.5899 | 123.1384 | 115.2603 | 118.9178
2237.4844 | 123.3124 | -118.3044 | 5.0079 | -0.065308 | 0.0024845 | 0.12039 | 0.0064385 | 0.0016939 | -0.00035682 | 0.00075627 | -0.13919 | 0.13576 | 0.0027622 | 0.0053854 | -0.002384 | -0.0014484 | 0.00095066 | -3.2181 | -2.2476 | -118.5974 | -2.6917 | -2.5314 | -118.2632 | -2.6047 | 0.59052 | 5.0812 | 4.5319 | 4.7791 | 4.248 | 4.6875 | 4.8111 | -0.29297 | -7.2556 | -7.6996 | 115.773 | 115.6998 | 0.041198 | 115.9927 | 0.33417 | 122.8363 | 0.073242 | -0.22888 | 122.5525 | 123.1155 | 122.9919 | 0.27924 | 0.15564 | 116.066 | 115.9058 | -0.28381 | 0.24719 | 116.3498 | 0.54932 | 116.0568 | 123.3856 | -123.6053 | -0.47607 | 115.6128 | 123.0835 | 115.0864 | 118.895
2238.5469 | 123.3215 | -118.3685 | 4.9805 | -0.019531 | 0.0048343 | 0.11932 | 0.0040887 | -0.0021513 | 0.00049778 | -0.0022345 | -0.035431 | 0.13725 | 0.0027622 | -0.00059601 | -0.0036658 | -0.0031574 | 0.0022323 | -4.5456 | -2.2568 | -118.6432 | -2.7008 | -2.5177 | -118.277 | -2.5635 | 0.54932 | 5.0629 | 4.4632 | 4.7241 | 4.2755 | 4.6692 | 4.7745 | -0.27466 | -7.2372 | -7.6813 | 115.8508 | 115.8051 | 0.091552 | 116.0797 | 0.36621 | 122.8317 | 0.082397 | -0.25635 | 122.644 | 123.143 | 123.0377 | 0.31128 | 0.20599 | 116.1255 | 115.9424 | -0.18768 | 0.26093 | 116.3864 | 0.59967 | 116.1118 | 123.4314 | -123.6237 | -0.51727 | 115.6677 | 123.0927 | 113.8229 | 118.9178
2239.4844 | 123.3124 | -118.4189 | 4.921 | -0.072937 | 0.0041935 | 0.12039 | 0.0057977 | 0.0025485 | -0.00078402 | -0.0026617 | -0.10867 | 0.1364 | 0.0031894 | 0.00025839 | -0.000675 | -0.0014484 | 0.00095066 | -3.4149 | -2.2888 | -118.7164 | -2.7557 | -2.6321 | -118.3823 | -2.6871 | 0.50812 | 4.9988 | 4.4083 | 4.6875 | 4.1794 | 4.5822 | 4.7195 | -0.29755 | -7.2098 | -7.6767 | 115.7867 | 115.7318 | 0.036621 | 116.0294 | 0.33417 | 122.8271 | 0.07782 | -0.23346 | 122.5983 | 123.1384 | 123.0011 | 0.31128 | 0.17395 | 116.0843 | 115.9607 | -0.22888 | 0.27924 | 116.4276 | 0.59051 | 116.1301 | 123.4177 | -123.6374 | -0.51269 | 115.6631 | 123.1064 | 115.004 | 118.927
2240.5469 | 123.3536 | -118.4463 | 4.8752 | -0.011902 | 0.0037661 | 0.11697 | 0.0047295 | 0.0034029 | 0.0019932 | -0.0028753 | -0.05069 | 0.13811 | 0.0027622 | -0.0076456 | -0.0036658 | -0.00059378 | 0.0024461 | -3.685 | -2.2797 | -118.7622 | -2.7283 | -2.5818 | -118.3823 | -2.5955 | 0.6134 | 4.9393 | 4.3533 | 4.6051 | 4.1199 | 4.5639 | 4.6463 | -0.31586 | -7.1548 | -7.6035 | 115.8646 | 115.8508 | 0.064087 | 116.1667 | 0.37994 | 122.7997 | 0.064087 | -0.27008 | 122.5662 | 123.0927 | 123.0103 | 0.29297 | 0.21057 | 116.1804 | 116.0339 | -0.23346 | 0.25177 | 116.4825 | 0.58594 | 116.1667 | 123.3856 | -123.6374 | -0.52185 | 115.7181 | 123.0515 | 114.7614 | 119.0598
2241.4844 | 123.3398 | -118.4235 | 4.8798 | -0.03479 | 0.0020573 | 0.11996 | 0.0057977 | 0.00083954 | 0.00071138 | -9.8328e-05 | -0.096466 | 0.1396 | 0.005112 | -0.0035868 | -0.0032386 | -0.0027302 | 9.6064e-05 | -4.01 | -2.2888 | -118.721 | -2.742 | -2.6047 | -118.4143 | -2.6413 | 0.58594 | 4.9484 | 4.39 | 4.6692 | 4.1473 | 4.5639 | 4.7012 | -0.29755 | -7.1686 | -7.6218 | 115.8188 | 115.7822 | 0.009155 | 116.0797 | 0.3067 | 122.8134 | 0.068664 | -0.21057 | 122.5708 | 123.1247 | 122.9874 | 0.31128 | 0.17395 | 116.1163 | 115.979 | -0.24262 | 0.27923 | 116.4322 | 0.55847 | 116.1346 | 123.3719 | -123.6008 | -0.48981 | 115.6815 | 123.0927 | 114.4135 | 119.0094
2242.4844 | 123.3536 | -118.4692 | 4.8843 | -0.027161 | 0.0048343 | 0.12103 | 0.0057977 | 0.00083954 | -0.001852 | -0.0022345 | -0.11172 | 0.13939 | 0.00618 | 0.0013266 | -0.003025 | -0.0010212 | -0.00075834 | -7.2784 | -2.3071 | -118.6661 | -2.7054 | -2.536 | -118.3456 | -2.6138 | 0.64545 | 4.9484 | 4.4312 | 4.6646 | 4.1382 | 4.5685 | 4.6967 | -0.19684 | -7.1915 | -7.5897 | 115.9332 | 115.8554 | 0.1236 | 116.0522 | 0.32044 | 122.9004 | 0.064087 | -0.21973 | 122.6074 | 123.1659 | 123.0377 | 0.2655 | 0.13733 | 116.1301 | 115.9607 | -0.29297 | 0.23346 | 116.3589 | 0.51727 | 116.1621 | 123.4177 | -123.5504 | -0.45319 | 115.7639 | 123.1339 | 111.1908 | 119.1147
2243.4844 | 123.3444 | -118.4692 | 4.8843 | -0.050049 | 0.0061161 | 0.11953 | 0.0045159 | 0.0029757 | 0.0011386 | 0.00054267 | -0.10867 | 0.1379 | 0.0048984 | 0.0043174 | -0.0032386 | -0.0012348 | -0.00054474 | -2.8656 | -2.2888 | -118.7988 | -2.7649 | -2.6321 | -118.4784 | -2.6459 | 0.55389 | 4.9347 | 4.3396 | 4.6188 | 4.097 | 4.3945 | 4.5227 | -0.32959 | -7.1732 | -7.6492 | 115.8371 | 115.8234 | -0.009156 | 116.153 | 0.32043 | 122.8088 | 0.050354 | -0.2655 | 122.5662 | 122.9919 | 122.8638 | 0.18311 | 0.054931 | 116.1667 | 116.0339 | -0.24261 | 0.27923 | 116.51 | 0.59509 | 116.1804 | 123.4039 | -123.6832 | -0.54474 | 115.7043 | 123.0881 | 115.6036 | 119.0231
2244.5469 | 123.3444 | -118.483 | 4.866 | 0.026245 | 0.0031253 | 0.11804 | 0.0045159 | 0.00019874 | 0.0032748 | -0.0033025 | -0.056793 | 0.13704 | 0.0023348 | -0.003373 | -0.0028112 | -0.003371 | 9.6064e-05 | -4.1428 | -2.2888 | -118.7897 | -2.7512 | -2.5955 | -118.483 | -2.6276 | 0.56305 | 4.8935 | 4.3076 | 4.5547 | 4.0695 | 4.5044 | 4.6143 | -0.3067 | -7.1548 | -7.6172 | 115.8875 | 115.8554 | 0 | 116.1621 | 0.3067 | 122.7905 | 0.027466 | -0.31128 | 122.5525 | 123.0972 | 122.9874 | 0.3067 | 0.19684 | 116.1942 | 116.0385 | -0.23804 | 0.24719 | 116.5009 | 0.58594 | 116.1942 | 123.3765 | -123.6557 | -0.55847 | 115.7318 | 123.0377 | 114.3402 | 119.046
2245.4844 | 122.7173 | -45.2271 | 77.7145 | -0.095825 | -0.0028561 | 0.043912 | 0.0045159 | -0.0021513 | 0.00092498 | -0.0011663 | -0.047638 | 0.0037405 | 0.0048984 | 0.04106 | -0.0038794 | -0.00038018 | 0.0015915 | -1.3779 | -1.0117 | -45.4834 | -1.4465 | -1.3 | -45.9549 | -1.3275 | 1.8677 | 77.7786 | 1.4832 | 77.742 | 1.8127 | 1.7166 | 1.8036 | -0.25635 | -78.7262 | -79.1611 | 43.927 | 43.8995 | -0.72784 | 44.1559 | -0.4715 | 46.7102 | 0.064086 | 0.027465 | 47.0398 | 47.0306 | 46.9437 | 0.32044 | 0.23346 | 44.1833 | 44.0369 | 0.32959 | 76.2588 | 44.4717 | 76.2955 | 44.2154 | 123.0057 | -123.1979 | -76.2314 | 43.7805 | 122.9691 | 43.8492 | 47.0947
2246.5469 | 122.7219 | -45.0989 | 77.8931 | 0.064392 | 0.0039799 | 0.041776 | 0.0066523 | 0.0019077 | -0.001852 | -0.0028753 | -0.053741 | 0.0026725 | 0.003403 | 0.044051 | -0.002384 | 0.00026062 | 0.0024461 | -1.9226 | -1.0483 | -44.8563 | -1.5106 | -1.3779 | -45.3827 | -1.3916 | 2.2659 | 78.1723 | 2.4078 | 77.8519 | 2.5818 | 2.6413 | 2.7466 | 0.24262 | -78.9413 | -79.4037 | 43.721 | 43.7073 | -0.28381 | 43.4647 | -0.52643 | 47.5067 | 0.27924 | -0.041198 | 47.6807 | 47.8455 | 47.7402 | 0.33875 | 0.23346 | 43.4784 | 43.3456 | 0.17395 | 75.444 | 43.808 | 75.7645 | 44.0506 | 123.2712 | -122.7493 | -75.4852 | 43.5883 | 122.9507 | 43.1763 | 47.3648
2247.4844 | 123.381 | -45.1355 | 78.0212 | -0.12634 | 0.0048343 | 0.043058 | 0.0017389 | 0.0014803 | 0.0058384 | -0.0013799 | 0.0072936 | 0.0018179 | 0.0021212 | 0.041701 | -0.0025976 | -0.003371 | -0.0013991 | -2.1515 | -1.1856 | -45.2087 | -1.4877 | -1.1902 | -45.4376 | -1.3962 | 2.2018 | 78.067 | 2.4811 | 78.2089 | 2.7374 | 2.7832 | 2.8381 | -0.073242 | -79.2068 | -79.509 | 43.9453 | 43.7393 | -0.30212 | 43.8126 | -0.22888 | 47.6166 | 0.045777 | 0.18768 | 47.8729 | 47.9736 | 47.9187 | 0.35706 | 0.30212 | 44.0186 | 43.721 | 0.25635 | 75.7278 | 44.0231 | 75.5859 | 43.9499 | 123.2025 | -123.23 | -75.5402 | 43.6478 | 123.3444 | 42.984 | 47.3373
2248.5469 | 119.7601 | -44.87 | 77.7649 | 0.0033567 | 0.0037661 | 0.044126 | 0.0045159 | -0.00022866 | 0.0017794 | -0.0054389 | -0.069 | 0.0039541 | 0.0025484 | 0.040206 | -0.0032386 | -0.0023028 | 0.0018051 | -1.4603 | -1.1032 | -45.0897 | -1.5015 | -1.3367 | -45.3735 | -1.3962 | 2.1652 | 78.1952 | 2.536 | 78.067 | 2.7512 | 2.7832 | 2.8748 | -0.21973 | -78.8681 | -79.2664 | 43.5333 | 43.4738 | -0.50354 | 43.6935 | -0.28381 | 47.406 | 0.4303 | 0.30212 | 47.6212 | 47.7448 | 47.6532 | 0.33875 | 0.24719 | 43.7531 | 43.5883 | 0.21515 | 75.531 | 43.9865 | 75.6592 | 43.7668 | 123.0652 | -122.8546 | -75.2289 | 43.3685 | 122.937 | 43.4097 | 47.0352
2249.4844 | 123.5321 | -118.1671 | 5.0079 | -0.088196 | 0.0037661 | 0.12231 | 0.0053705 | -1.486e-05 | 0.00049778 | 0.00032907 | -0.059845 | 0.13918 | 0.0040438 | 0.0013266 | -0.0038794 | -0.0044392 | 0.0039413 | -2.6276 | -2.3483 | -118.5883 | -2.655 | -2.449 | -118.158 | -2.5589 | 0.63629 | 5.0995 | 4.4998 | 4.9438 | 4.4769 | 4.8065 | 4.9026 | -0.42114 | -7.3563 | -7.663 | 115.7181 | 115.6082 | 0.009155 | 116.0294 | 0.4303 | 122.6669 | 0.091552 | -0.064087 | 122.644 | 123.0698 | 122.9736 | 0.40283 | 0.3067 | 116.1392 | 115.9332 | -0.022888 | 0.44403 | 116.2399 | 0.59967 | 115.8188 | 123.2666 | -123.5962 | -0.50812 | 115.5121 | 123.111 | 115.5396 | 118.8034
2250.4844 | 122.7402 | -45.3461 | 77.9663 | -0.22552 | -0.0047787 | 0.039426 | 0.0032343 | -0.0066373 | 0.00092498 | -0.0043707 | -0.093414 | 0.0018179 | 0.0025484 | 0.043624 | -0.0038794 | -0.0031574 | -0.0026809 | -1.2909 | -0.94757 | -44.8746 | -1.4008 | -1.268 | -45.4514 | -1.3138 | 2.0279 | 78.2547 | 2.916 | 78.1494 | 2.4261 | 1.8631 | 2.2888 | 0.4715 | -78.9139 | -79.3671 | 44.0781 | 44.0323 | -0.10529 | 43.5608 | -0.57678 | 48.262 | 0.28839 | 0.1831 | 47.7722 | 47.6349 | 47.2092 | -0.62714 | -1.0529 | 43.6066 | 43.4738 | -0.48981 | 75.2335 | 43.927 | 75.3387 | 44.3985 | 123.6008 | -122.8409 | -75.0504 | 43.9453 | 123.4955 | 44.0552 | 47.374
2251.5469 | 123.436 | -117.9062 | 5.2826 | -0.088196 | 0.0054751 | 0.1221 | 0.0072931 | 0.0027621 | 0.002634 | -0.0062933 | -0.11783 | 0.13555 | 0.00062585 | -0.0052958 | -0.0017432 | -0.006148 | 0.0037277 | -2.7695 | -2.3026 | -118.309 | -2.742 | -2.5909 | -117.9611 | -2.655 | 0.49896 | 5.3833 | 4.7333 | 5.0766 | 4.8111 | 4.8981 | 5.0262 | -0.40283 | -7.5851 | -8.0246 | 115.3152 | 115.2512 | -0.054932 | 115.654 | 0.3479 | 122.6395 | 0.10071 | -0.20599 | 122.7173 | 122.9324 | 122.8043 | 0.29297 | 0.16479 | 115.7181 | 115.567 | 0.07782 | 0.34332 | 116.0065 | 0.65003 | 115.6036 | 123.2895 | -123.5916 | -0.54932 | 115.1642 | 122.9828 | 115.1367 | 118.4052
2252.4844 | 123.3765 | -118.2495 | 5.0262 | -0.057678 | 0.0022709 | 0.12082 | 0.0049433 | 0.0025485 | 0.0011386 | 0.00075627 | -0.10867 | 0.13939 | 0.0046848 | 4.4788e-05 | -0.0021704 | -0.00016658 | 0.00095066 | -3.035 | -2.3346 | -118.634 | -2.7969 | -2.6505 | -118.2861 | -2.6871 | 0.70038 | 5.1086 | 4.5136 | 4.7974 | 4.4724 | 4.6829 | 4.8203 | -0.38452 | -7.3608 | -7.8232 | 115.5991 | 115.5624 | -0.036621 | 115.947 | 0.3479 | 122.7631 | 0.082398 | -0.22888 | 122.7219 | 123.0698 | 122.9324 | 0.3067 | 0.16937 | 115.9836 | 115.8371 | -0.041199 | 0.28381 | 116.2994 | 0.59509 | 115.9149 | 123.3582 | -123.6603 | -0.51269 | 115.4526 | 123.0469 | 115.2145 | 118.9499
2253.5469 | 123.3719 | -118.3914 | 4.9438 | -0.011902 | 0.0041935 | 0.12103 | 0.0068659 | 0.00019874 | -0.00099762 | -0.00031193 | -0.093414 | 0.14025 | 0.0042574 | -0.003373 | -0.003025 | -0.00080758 | 0.00030966 | -2.8381 | -2.3483 | -118.7439 | -2.8244 | -2.6917 | -118.4052 | -2.7054 | 0.55847 | 5.0034 | 4.422 | 4.6875 | 4.3762 | 4.5822 | 4.7287 | -0.35248 | -7.2922 | -7.7683 | 115.6998 | 115.686 | -0.013733 | 116.0385 | 0.33875 | 122.8134 | 0.059509 | -0.25635 | 122.7676 | 123.1201 | 122.9736 | 0.3067 | 0.16022 | 116.0522 | 115.9195 | -0.045776 | 0.2655 | 116.3956 | 0.58136 | 116.0431 | 123.3948 | -123.6877 | -0.52185 | 115.567 | 123.0789 | 115.5533 | 118.9499
2254.4844 | 123.4634 | -118.3823 | 4.9164 | -0.072937 | 0.0018435 | 0.11868 | 0.0049433 | 0.00083954 | 0.0015658 | 0.0013971 | -0.081207 | 0.13896 | 0.0023348 | -0.0018778 | -0.004093 | -0.0031574 | 0.0047959 | -3.0075 | -2.3483 | -118.7027 | -2.7924 | -2.623 | -118.3182 | -2.6733 | 0.65918 | 4.9805 | 4.4495 | 4.8157 | 4.5227 | 4.6875 | 4.8248 | -0.32044 | -7.2647 | -7.7087 | 115.7593 | 115.7089 | 0.064087 | 116.0294 | 0.38452 | 122.8317 | 0.064087 | -0.10071 | 122.905 | 123.2071 | 123.0698 | 0.37537 | 0.23804 | 116.0797 | 115.9103 | 0.073242 | 0.36621 | 116.3544 | 0.53101 | 116.0339 | 123.3627 | -123.6191 | -0.46692 | 115.5899 | 123.1979 | 115.3748 | 119.0414
2255.5469 | 123.3765 | -118.3594 | 4.9393 | 0.09491 | 0.0048343 | 0.12231 | 0.0055841 | 0.00041234 | 0.00049778 | -0.0018073 | -0.11478 | 0.13939 | 0.0023348 | -0.005082 | -0.0032386 | -0.0025164 | 0.0018051 | -2.8564 | -2.3163 | -118.6432 | -2.8061 | -2.6505 | -118.3044 | -2.6779 | 0.67749 | 5.0217 | 4.4678 | 4.7562 | 4.4632 | 4.66 | 4.7699 | -0.28381 | -7.2556 | -7.7454 | 115.7089 | 115.6815 | 0.054932 | 115.9653 | 0.33874 | 122.8271 | 0.082397 | -0.1831 | 122.8226 | 123.1293 | 123.0194 | 0.30212 | 0.19226 | 115.9927 | 115.8371 | -0.004577 | 0.28839 | 116.3269 | 0.55389 | 116.0431 | 123.381 | -123.5825 | -0.4715 | 115.5533 | 123.1155 | 115.5029 | 119.0369
2256.4844 | 123.4406 | -118.3594 | 4.9255 | -0.050049 | 0.0031253 | 0.12103 | 0.0047295 | 0.0025485 | 0.0011386 | -0.00073913 | -0.084259 | 0.13811 | 0.0025484 | 0.001113 | -0.0055884 | -0.0029438 | 0.0011643 | -2.7832 | -2.3529 | -118.6707 | -2.7924 | -2.6321 | -118.309 | -2.6779 | 0.66376 | 5.0217 | 4.422 | 4.8203 | 4.4724 | 4.6738 | 4.7928 | -0.31128 | -7.2784 | -7.7179 | 115.7272 | 115.6815 | 0.050354 | 115.9927 | 0.36163 | 122.7814 | 0.09613 | -0.10529 | 122.8317 | 123.1522 | 123.0331 | 0.37079 | 0.25177 | 116.0385 | 115.8783 | 0.050354 | 0.39825 | 116.3177 | 0.59967 | 116.0065 | 123.381 | -123.5962 | -0.50354 | 115.567 | 123.1796 | 115.5762 | 119.0231
2257.5469 | 123.3719 | -118.1671 | 5.1498 | 0.010986 | 0.0029117 | 0.11783 | 0.0043023 | 0.00062594 | 0.0011386 | 0.0011835 | -0.14224 | 0.13768 | 0.0036166 | 0.0077354 | -0.001316 | -0.00059378 | 0.00030966 | -2.8931 | -2.4445 | -118.4463 | -2.916 | -2.8152 | -117.7231 | -2.6871 | 0.75531 | 5.2734 | 4.66 | 4.9255 | 4.5822 | 4.8386 | 4.9347 | -0.27924 | -7.5943 | -8.0658 | 115.3519 | 115.48 | 0.44403 | 115.7593 | 0.72327 | 122.8271 | 0.1236 | -0.2243 | 122.7493 | 123.1018 | 123.0057 | 0.27466 | 0.17853 | 115.6311 | 115.5304 | -0.07782 | 0.2655 | 116.0019 | 0.6134 | 115.7227 | 123.4406 | -123.5962 | -0.48981 | 115.2512 | 123.0927 | 115.274 | 118.9224
2258.4844 | 123.3856 | -118.1808 | 5.1086 | -0.027161 | 0.0044071 | 0.12103 | 0.0049433 | 0.0055393 | 0.0011386 | 0.00075627 | -0.065949 | 0.13854 | 0.0055392 | -0.0012368 | -0.004093 | -0.0012348 | 0.0015915 | -3.0029 | -2.449 | -118.4967 | -2.98 | -2.5589 | -118.0801 | -2.8519 | 0.65918 | 5.2139 | 4.6326 | 4.9255 | 4.5547 | 4.7928 | 4.921 | -0.31586 | -7.5577 | -8.0887 | 115.6219 | 115.329 | 0.10071 | 115.6448 | 0.41656 | 122.8134 | 0.10529 | -0.18311 | 122.7356 | 123.1018 | 122.9736 | 0.28839 | 0.16022 | 115.9378 | 115.5167 | -0.077819 | 0.29297 | 116.0477 | 0.58136 | 115.7318 | 123.3948 | -123.6053 | -0.47607 | 115.2008 | 123.1064 | 115.1779 | 118.84
2259.4844 | 123.5229 | -118.1213 | 5.0903 | -0.080566 | 0.0018435 | 0.1206 | 0.0043023 | 0.0014803 | 0.00028418 | 0.0018243 | -0.059845 | 0.13704 | 0.0036166 | -0.0025186 | -0.003025 | -0.001662 | -0.00097194 | -3.0808 | -2.4857 | -118.4692 | -2.7969 | -2.6321 | -118.0389 | -2.71 | 0.70496 | 5.1544 | 4.6371 | 5.0446 | 4.6143 | 4.8981 | 5.0491 | -0.3479 | -7.576 | -7.8873 | 115.4892 | 115.4114 | 0.082398 | 115.7593 | 0.4303 | 122.7585 | 0.064087 | -0.045776 | 122.7356 | 123.1705 | 123.0194 | 0.41199 | 0.26092 | 115.8371 | 115.6723 | -0.022888 | 0.40741 | 115.9836 | 0.51727 | 115.6357 | 123.2758 | -123.5596 | -0.45319 | 115.3244 | 123.1659 | 115.0406 | 118.8263
2260.4844 | 122.9141 | -45.0485 | 78.1403 | -0.057678 | 0.0022709 | 0.043485 | 0.0034479 | -0.00022866 | -0.00014322 | 0.00054267 | -0.05069 | 0.0037405 | 0.0029758 | 0.04341 | -0.0055884 | -0.0014484 | 0.00095066 | -1.4053 | -0.96588 | -44.6274 | -1.3779 | -1.2222 | -45.3781 | -1.2634 | 2.33 | 78.2135 | 2.33 | 78.2501 | 2.7008 | 2.5772 | 2.7008 | 0.42114 | -79.1061 | -79.5181 | 43.8263 | 43.7851 | -0.32959 | 43.364 | -0.75073 | 47.3785 | 0.073242 | 0.10986 | 47.7493 | 47.7493 | 47.6257 | 0.37079 | 0.24719 | 43.4052 | 43.2495 | 0.37079 | 75.9201 | 43.6615 | 75.8835 | 44.0826 | 123.262 | -122.7676 | -75.8102 | 43.6707 | 123.2986 | 43.6432 | 47.3785
2261.4844 | 123.3536 | -45.0302 | 78.1677 | -0.080566 | 0.0031253 | 0.043058 | 0.0038751 | 0.0021213 | -0.00014322 | -0.0013799 | -0.023224 | 0.0037405 | 0.0025484 | 0.044478 | -0.002384 | 4.7018e-05 | 0.0045823 | -1.3916 | -0.96588 | -45.3461 | -1.268 | -1.0986 | -45.0119 | -1.1581 | 2.2247 | 78.1906 | 3.2455 | 78.2272 | 2.7969 | 2.6779 | 2.7008 | -0.31586 | -79.1336 | -79.4357 | 43.9316 | 43.8721 | 0.01831 | 44.1879 | 0.33417 | 48.2758 | 0.022888 | 0.059509 | 47.8271 | 47.731 | 47.7081 | -0.54474 | -0.56763 | 44.2474 | 44.0781 | -0.44861 | 74.9817 | 44.3802 | 74.9451 | 44.0643 | 123.2208 | -123.5138 | -74.9222 | 43.7622 | 123.2574 | 43.6386 | 47.2549
2262.5469 | 123.4451 | -118.2037 | 4.9896 | -0.057678 | 0.0054751 | 0.1221 | 0.0051569 | 0.00019874 | 0.00049778 | -0.0013799 | -0.13004 | 0.13085 | 0.0057528 | -0.011491 | -0.013065 | 0.015428 | -0.012294 | -2.0279 | -1.4145 | -118.5516 | -1.7807 | -1.6342 | -118.2129 | -1.6983 | 0.55847 | 5.0995 | 4.5319 | 4.834 | 4.6555 | 4.7195 | 4.8386 | -0.3479 | -6.4041 | -6.7703 | 116.5695 | 116.5054 | -0.009156 | 116.8533 | 0.33875 | 122.7356 | 0.10986 | -0.15564 | 122.8592 | 123.0423 | 122.9233 | 0.3067 | 0.18768 | 116.9174 | 116.7709 | 0.1236 | 0.30212 | 117.1371 | 0.56763 | 116.7892 | 123.3032 | -123.5413 | -0.45776 | 116.423 | 123.0377 | 116.1758 | 118.7622
2263.4844 | 123.4634 | -118.2404 | 5.0354 | -0.057678 | 0.0020573 | 0.12018 | 0.0036615 | -1.486e-05 | 0.00092498 | 0.00096987 | -0.041534 | 0.13939 | 0.0029758 | -0.003373 | -0.000675 | -0.0023028 | 0.0030869 | -1.8356 | -1.3916 | -118.5104 | -1.712 | -1.5427 | -118.1396 | -1.593 | 0.62714 | 5.1178 | 4.5731 | 4.9118 | 4.5181 | 4.8157 | 4.9255 | -0.27008 | -6.427 | -6.7474 | 116.6977 | 116.6473 | 0.10071 | 116.9174 | 0.37079 | 122.8134 | 0.082398 | -0.1236 | 122.7585 | 123.1659 | 123.056 | 0.35248 | 0.24261 | 116.9678 | 116.7984 | -0.054932 | 0.33875 | 117.1188 | 0.54474 | 116.8488 | 123.3582 | -123.5458 | -0.46234 | 116.5283 | 123.1522 | 116.4047 | 118.8675
2264.5469 | 123.3948 | -118.2175 | 5.0583 | -0.050049 | 0.0033389 | 0.11761 | 0.0066523 | -0.0012967 | 0.0022068 | -9.8328e-05 | -0.12088 | 0.13426 | 0.003403 | -0.0063638 | -0.00922 | -0.0048664 | -0.012294 | -1.8036 | -1.4053 | -118.4372 | -1.7761 | -1.6296 | -118.1122 | -1.7075 | 0.66834 | 5.1636 | 4.6143 | 4.9393 | 4.4449 | 4.7699 | 4.8935 | -0.21973 | -6.4636 | -6.8344 | 116.5878 | 116.51 | 0.10528 | 116.7297 | 0.32501 | 122.8317 | 0.10528 | -0.11902 | 122.6624 | 123.111 | 122.9874 | 0.27924 | 0.15564 | 116.8076 | 116.6611 | -0.16937 | 0.32501 | 117.0319 | 0.54932 | 116.8121 | 123.381 | -123.4955 | -0.44403 | 116.4413 | 123.1567 | 116.4139 | 118.8858
2265.4844 | 123.436 | -118.2404 | 5.0354 | -0.065308 | 0.0035525 | 0.12082 | 0.0032343 | 0.0012667 | -0.00014322 | -0.00052553 | -0.01712 | 0.1364 | 0.0031894 | -0.0046548 | -0.0021704 | -0.00016658 | 0.0018051 | -2.3254 | -1.4328 | -118.483 | -1.7899 | -1.6113 | -118.1396 | -1.68 | 0.79651 | 5.1041 | 4.5776 | 4.9164 | 4.4907 | 4.8111 | 4.9301 | -0.24262 | -6.4682 | -6.8253 | 116.629 | 116.5604 | 0.10071 | 116.803 | 0.34332 | 122.818 | 0.068665 | -0.11902 | 122.731 | 123.1705 | 123.0515 | 0.35248 | 0.23346 | 116.8716 | 116.6931 | -0.086975 | 0.33874 | 117.0502 | 0.52643 | 116.8076 | 123.3444 | -123.5184 | -0.45776 | 116.4505 | 123.1567 | 115.9149 | 119.0369
2266.5469 | 122.5845 | -45.1492 | 78.0762 | 0.033875 | 0.0056889 | 0.042203 | 0.0057977 | -0.00044226 | 0.00049778 | -0.00095273 | -0.072052 | 0.0041679 | 0.0040438 | 0.045333 | -0.0025976 | -0.0023028 | -0.0016129 | -3.653 | -0.45776 | -45.0989 | -0.92468 | -0.78735 | -45.4605 | -0.8194 | 2.1835 | 78.1219 | 1.5747 | 78.0579 | 1.9409 | 1.7944 | 1.9089 | 0.050354 | -78.5339 | -79.0009 | 44.3619 | 44.3298 | -0.31128 | 44.2795 | -0.36163 | 46.7239 | 0.045776 | -0.018311 | 47.0901 | 47.0581 | 46.9437 | 0.33417 | 0.21973 | 44.3115 | 44.1742 | 0.36621 | 76.4832 | 44.6411 | 76.5472 | 44.6915 | 123.2712 | -123.175 | -76.5015 | 44.2245 | 123.2071 | 41.4963 | 47.3328
2267.5 | 123.4863 | -118.3228 | 4.8798 | -0.0042723 | -0.00029273 | 0.12167 | 0.0064385 | 0.0025485 | -0.0022794 | -9.8328e-05 | -0.053741 | 0.14195 | 0.0031894 | 0.004531 | -0.0034522 | -0.0031574 | 0.00095066 | -2.3987 | -1.5015 | -118.6844 | -1.8082 | -1.6571 | -118.2495 | -1.6937 | 0.73242 | 4.953 | 4.422 | 4.7195 | 4.6005 | 4.6646 | 4.7516 | -0.36163 | -6.3812 | -6.6879 | 116.6656 | 116.629 | 0.073242 | 116.9907 | 0.43488 | 122.7448 | 0.073242 | -0.16022 | 122.9233 | 123.0743 | 122.9874 | 0.32959 | 0.24261 | 117.0273 | 116.8762 | 0.17853 | 0.29755 | 117.1829 | 0.53101 | 116.8213 | 123.2758 | -123.5641 | -0.45776 | 116.5146 | 123.0423 | 115.9241 | 119.0552
2268.5469 | 123.4039 | -118.5333 | 4.7607 | -0.019531 | 0.00034827 | 0.12167 | 0.0064385 | -0.0096281 | -0.0016384 | -0.0011663 | -0.18802 | 0.12721 | 0.0023348 | -0.017472 | -0.019687 | 0.015428 | -0.013789 | -3.8589 | -1.4969 | -118.808 | -1.8906 | -1.7166 | -118.4143 | -1.8036 | 0.64087 | 4.8386 | 4.3213 | 4.5868 | 4.3716 | 4.4632 | 4.5914 | -0.27466 | -6.2576 | -6.6513 | 116.8167 | 116.7297 | 0.11902 | 117.0044 | 0.39368 | 122.8546 | 0.07782 | -0.17395 | 122.905 | 123.1247 | 122.9965 | 0.27008 | 0.14191 | 117.0914 | 116.9174 | 0.050354 | 0.2655 | 117.3111 | 0.51727 | 117.0364 | 123.3719 | -123.5687 | -0.43945 | 116.6428 | 123.1201 | 114.6744 | 119.1742
2269.4844 | 123.4131 | -118.5104 | 4.7333 | -0.027161 | 0.0044071 | 0.12103 | 0.0021661 | 0.0023349 | -0.00035682 | -0.0013799 | -0.023224 | 0.13875 | 0.0038302 | -0.0038004 | -0.002384 | -0.0031574 | 0.0043687 | -3.6713 | -1.5335 | -118.7576 | -1.8906 | -1.7395 | -118.364 | -1.7715 | 0.54474 | 4.8431 | 4.3579 | 4.66 | 4.2801 | 4.5639 | 4.6829 | -0.24719 | -6.2668 | -6.6238 | 116.7709 | 116.7389 | 0.14648 | 116.9861 | 0.39368 | 122.8683 | 0.10986 | -0.073242 | 122.7905 | 123.1934 | 123.0743 | 0.32501 | 0.20599 | 117.0181 | 116.8671 | -0.07782 | 0.30212 | 117.2241 | 0.48523 | 116.9769 | 123.3536 | -123.4909 | -0.37537 | 116.6199 | 123.1705 | 114.8392 | 119.0552
2270.4844 | 123.4772 | -118.1259 | 5.1086 | -0.065308 | 0.0033389 | 0.11932 | 0.0045159 | 0.0014803 | 0.00049778 | 0.00032907 | -0.072052 | 0.13768 | 0.001694 | -0.0012368 | -0.004093 | -0.003371 | -0.00033114 | -4.4724 | -1.593 | -118.4326 | -1.8631 | -1.7258 | -118.0389 | -1.7761 | 0.6546 | 5.1819 | 4.6143 | 5.0537 | 4.9347 | 4.8889 | 5.0308 | -0.3067 | -6.7017 | -6.9717 | 116.4001 | 116.3498 | 0.086976 | 116.6565 | 0.39368 | 122.7402 | 0.073242 | -0.054932 | 123.0606 | 123.1567 | 123.0148 | 0.41656 | 0.27466 | 116.7068 | 116.5695 | 0.32043 | 0.43945 | 116.8396 | 0.56763 | 116.5329 | 123.3078 | -123.5413 | -0.49438 | 116.2628 | 123.1796 | 113.6536 | 118.7805
2271.5469 | 123.468 | -118.1671 | 5.072 | -0.03479 | 0.0050479 | 0.11996 | 0.0066523 | 0.0027621 | 0.0013522 | 0.00075627 | -0.11783 | 0.13896 | 0.003403 | -0.00080961 | -0.0043066 | -0.0020892 | 0.0013779 | -32.2998 | -1.4282 | -118.4967 | -1.8036 | -1.6571 | -118.1488 | -1.712 | 0.60425 | 5.1544 | 4.6097 | 4.985 | 4.7516 | 4.9072 | 5.0262 | -0.32959 | -6.5002 | -6.8756 | 116.51 | 116.4551 | 0.01831 | 116.7847 | 0.3479 | 122.7768 | 0.082398 | -0.086975 | 122.9187 | 123.1934 | 123.0743 | 0.41657 | 0.29755 | 116.8396 | 116.6931 | 0.14191 | 0.37537 | 117.0685 | 0.54474 | 116.7389 | 123.3215 | -123.5687 | -0.46234 | 116.3635 | 123.1522 | 85.8673 | 118.7714
2272.5 | 123.3307 | -118.2541 | 5.1132 | -0.019531 | 0.0020573 | 0.11953 | 0.0066523 | -0.0023649 | -0.00078402 | 0.00011527 | -0.075104 | 0.13875 | 0.0042574 | -0.0012368 | -0.0015296 | -0.0014484 | 0.0020187 | -34.8083 | -1.474 | -118.5562 | -1.9089 | -1.7807 | -118.1717 | -1.7944 | 0.62256 | 5.1498 | 4.5822 | 4.8706 | 4.6555 | 4.7882 | 4.8889 | -0.30212 | -6.5872 | -7.0221 | 116.4734 | 116.4597 | 0.082397 | 116.7618 | 0.38452 | 122.8363 | 0.036621 | -0.24261 | 122.9095 | 123.143 | 123.0423 | 0.3067 | 0.20599 | 116.7755 | 116.6473 | 0.073243 | 0.28839 | 117.0822 | 0.56763 | 116.7801 | 123.4039 | -123.6694 | -0.53101 | 116.3452 | 123.1247 | 83.4457 | 118.8766
2273.5469 | 123.436 | -118.2495 | 5.0308 | -0.057678 | 0.0044071 | 0.12103 | 0.0038751 | -0.00065586 | -0.0020658 | -0.0018073 | -0.041534 | 0.13811 | 0.0027622 | -0.0020914 | -0.004093 | -0.0025164 | -0.00033114 | -34.5337 | -1.5747 | -118.5562 | -1.8311 | -1.6708 | -118.1259 | -1.7303 | 0.66834 | 5.0858 | 4.5685 | 4.953 | 4.7195 | 4.8706 | 4.9713 | -0.3067 | -6.6055 | -6.8619 | 116.5787 | 116.5192 | 0.1236 | 116.8259 | 0.4303 | 122.818 | 0.054931 | -0.07782 | 122.9691 | 123.2208 | 123.1201 | 0.40283 | 0.30212 | 116.8854 | 116.7252 | 0.15106 | 0.38452 | 116.9815 | 0.51727 | 116.6748 | 123.3353 | -123.587 | -0.46234 | 116.4185 | 123.2025 | 83.7158 | 118.9178
2274.4844 | 123.3948 | -118.2358 | 5.072 | -0.11871 | 0.0050479 | 0.12039 | 0.0040887 | -0.0021513 | 0.0045566 | 0.00054267 | -0.035431 | 0.13661 | 0.001694 | -0.007432 | -0.0028112 | -0.0023028 | -0.0016129 | -3.7537 | -1.5656 | -118.5196 | -1.8768 | -1.7029 | -118.1717 | -1.7578 | 0.65002 | 5.0949 | 4.6051 | 4.9301 | 4.6967 | 4.8569 | 4.9484 | -0.28381 | -6.6376 | -6.9489 | 116.5329 | 116.478 | 0.064087 | 116.7618 | 0.3479 | 122.8409 | 0.022889 | -0.14191 | 122.9324 | 123.1842 | 123.0927 | 0.34332 | 0.25177 | 116.8167 | 116.6428 | 0.091552 | 0.32501 | 116.954 | 0.48981 | 116.6702 | 123.3307 | -123.5916 | -0.46692 | 116.3589 | 123.1659 | 114.4821 | 118.8858
2275.5469 | 123.4177 | -118.2312 | 5.0262 | -0.10345 | 0.0065433 | 0.11975 | 0.0036615 | -0.0034329 | 0.0015658 | -0.00031193 | -0.072052 | 0.13811 | 0.001694 | 0.0017538 | -0.0034522 | -0.0020892 | 0.00052346 | -2.655 | -1.6983 | -118.5471 | -2.0279 | -1.8494 | -118.0939 | -1.9135 | 0.65002 | 5.0583 | 4.5639 | 4.9622 | 4.6417 | 4.8431 | 4.9393 | -0.31586 | -6.7245 | -7.0541 | 116.3818 | 116.3177 | 0.13733 | 116.6336 | 0.45319 | 122.7951 | 0.032044 | -0.064087 | 122.8729 | 123.1705 | 123.0743 | 0.37537 | 0.27924 | 116.6977 | 116.5192 | 0.07782 | 0.39825 | 116.8488 | 0.49439 | 116.5329 | 123.2895 | -123.5733 | -0.46234 | 116.2033 | 123.1934 | 115.5762 | 118.8812
2276.4844 | 123.3673 | -118.2037 | 5.0354 | -0.088196 | 0.0041935 | 0.11911 | 0.0060113 | 0.0019077 | 0.0019932 | 0.00011527 | -0.078156 | 0.1379 | 0.001694 | 0.001113 | -0.0008886 | -0.0031574 | 0.0028733 | -2.4353 | -1.7212 | -118.515 | -1.9867 | -1.8127 | -118.1305 | -1.8997 | 0.66834 | 5.1041 | 4.6005 | 4.9438 | 4.5685 | 4.8523 | 4.9667 | -0.31128 | -6.7566 | -7.0221 | 116.391 | 116.304 | 0.073242 | 116.6153 | 0.38452 | 122.8043 | 0.068665 | -0.091552 | 122.7722 | 123.1705 | 123.056 | 0.36621 | 0.25177 | 116.7023 | 116.5283 | -0.032044 | 0.34332 | 116.7938 | 0.50354 | 116.4825 | 123.3078 | -123.5504 | -0.43487 | 116.217 | 123.1476 | 115.7684 | 118.8721
2277.5 | 123.3307 | -118.2541 | 5.0674 | 0.27802 | 0.0018435 | 0.12317 | 0.0060113 | 0.00083954 | -0.00057042 | 0.00011527 | -0.099518 | 0.13875 | 0.0031894 | 4.4788e-05 | -0.0025976 | -0.0014484 | 0.0011643 | -2.3254 | -1.5564 | -118.5059 | -2.0279 | -1.9089 | -118.1717 | -1.918 | 0.5127 | 5.1682 | 4.5959 | 4.834 | 4.4632 | 4.7562 | 4.866 | -0.25177 | -6.6238 | -7.0953 | 116.3452 | 116.3361 | 0.082397 | 116.5878 | 0.33417 | 122.85 | 0.10071 | -0.23346 | 122.7173 | 123.1201 | 123.0103 | 0.27008 | 0.16022 | 116.597 | 116.478 | -0.13275 | 0.23804 | 116.9495 | 0.57221 | 116.6977 | 123.4222 | -123.5733 | -0.4715 | 116.2262 | 123.0881 | 115.9286 | 118.7668
2278.5469 | 123.3261 | -118.2495 | 5.0629 | -0.03479 | 0.0020573 | 0.1206 | 0.0045159 | 0.0046847 | 0.00092498 | -0.0013799 | -0.14529 | 0.13875 | 0.0014804 | 0.0015402 | -0.0015296 | -0.0035846 | -0.0024673 | -2.0462 | -1.6708 | -118.5837 | -2.1332 | -2.0142 | -118.222 | -2.0279 | 0.5127 | 5.1315 | 4.5547 | 4.9301 | 4.3579 | 4.7653 | 4.8843 | -0.33417 | -6.7337 | -7.196 | 116.2354 | 116.2216 | 0.027466 | 116.5558 | 0.36163 | 122.8043 | 0.068665 | -0.13275 | 122.6074 | 123.1338 | 123.0148 | 0.32959 | 0.21057 | 116.5695 | 116.4505 | -0.19684 | 0.37537 | 116.9128 | 0.57678 | 116.5787 | 123.381 | -123.6465 | -0.50812 | 116.1163 | 123.1796 | 116.2033 | 118.7622
2279.4844 | 123.4039 | -118.19 | 5.0766 | -0.019531 | 0.0041935 | 0.11783 | 0.0038751 | -0.0021513 | -0.00035682 | -0.0030889 | -0.01712 | 0.13918 | 0.0036166 | -0.0070046 | -0.002384 | -0.0023028 | 0.0082139 | -2.037 | -1.7029 | -118.4509 | -2.0416 | -1.8906 | -118.0847 | -1.918 | 0.59052 | 5.1636 | 4.6509 | 4.953 | 4.5959 | 4.8843 | 5.0171 | -0.26093 | -6.7795 | -7.1182 | 116.2994 | 116.272 | 0.10529 | 116.5329 | 0.36621 | 122.8409 | 0.086975 | -0.1236 | 122.7859 | 123.2071 | 123.0743 | 0.36621 | 0.23346 | 116.5604 | 116.4093 | -0.054932 | 0.30212 | 116.748 | 0.51269 | 116.4871 | 123.3536 | -123.5275 | -0.42572 | 116.1484 | 123.143 | 116.153 | 118.7805
2280.5469 | 122.7905 | -44.1971 | 78.2867 | -0.027161 | 0.0041935 | 0.042631 | 0.0045159 | -1.486e-05 | -0.00099762 | -0.00073913 | -0.11478 | 0.0022453 | 0.004471 | 0.044906 | -0.0008886 | -0.0076434 | -0.0028945 | -1.5701 | -0.39825 | -44.8975 | -0.83771 | -0.68665 | -45.1859 | -0.70953 | 2.4582 | 78.3371 | 1.8906 | 78.3096 | 2.179 | 2.1469 | 2.2064 | -0.70038 | -78.685 | -79.1245 | 43.5104 | 43.4875 | -0.98877 | 44.1879 | -0.28839 | 46.0876 | 0.050354 | 0.022888 | 46.376 | 46.4035 | 46.344 | 0.31586 | 0.25635 | 44.2108 | 44.0598 | 0.28839 | 76.4191 | 44.4992 | 76.4465 | 43.7988 | 122.5342 | -123.1842 | -76.3962 | 43.3594 | 122.5067 | 42.627 | 46.6553
2281.4844 | 123.436 | -44.8883 | 78.3005 | -0.065308 | 0.0048343 | 0.041349 | 0.0034479 | -0.0010831 | 0.0015658 | -0.0013799 | -0.01712 | 0.0013907 | 0.0031894 | 0.039565 | -0.0015296 | 0.00026062 | 0.00095066 | -1.1444 | -0.43488 | -45.1492 | -0.71869 | -0.54474 | -45.0668 | -0.62256 | 2.5314 | 78.4058 | 1.9684 | 78.447 | 2.2293 | 2.1927 | 2.2934 | -0.26093 | -78.7354 | -79.0192 | 44.3436 | 44.2657 | -0.17853 | 44.5267 | 0.082398 | 46.8567 | 0.10529 | 0.14648 | 47.1176 | 47.1817 | 47.081 | 0.32501 | 0.2243 | 44.6045 | 44.4305 | 0.26093 | 76.4786 | 44.7144 | 76.4374 | 44.4534 | 123.2941 | -123.4497 | -76.3321 | 44.1696 | 123.3353 | 43.7439 | 47.4197
2282.5 | 123.4863 | -117.8146 | 5.3696 | 0.033875 | 0.0044071 | 0.11932 | 0.0062249 | -1.486e-05 | 0.002634 | -0.0018073 | -0.11783 | 0.13896 | 0.004471 | 4.4788e-05 | -0.0047338 | -0.0055072 | 0.00095066 | -2.4353 | -1.5518 | -118.2587 | -1.9821 | -1.8677 | -117.8467 | -1.8723 | 0.66376 | 5.4657 | 4.866 | 5.1636 | 4.7745 | 5.1041 | 5.2048 | -0.44403 | -6.9214 | -7.3517 | 115.947 | 115.9424 | -0.032044 | 116.3864 | 0.41199 | 122.6807 | 0.09613 | -0.20599 | 122.5891 | 123.0194 | 122.9187 | 0.33875 | 0.23804 | 116.391 | 116.2766 | -0.091553 | 0.29755 | 116.7068 | 0.59967 | 116.2628 | 123.2803 | -123.6282 | -0.50354 | 115.8325 | 122.9782 | 115.3793 | 118.4784
2283.5469 | 123.5001 | -117.9794 | 5.2139 | -0.0042723 | 0.0039799 | 0.12103 | 0.0064385 | 0.0025485 | 0.0015658 | 0.00054267 | -0.11478 | 0.1396 | 0.0046848 | -0.0042276 | -0.0028112 | -0.0010212 | 0.00030966 | -3.8635 | -1.4877 | -118.3868 | -1.8631 | -1.7258 | -118.0115 | -1.7624 | 0.68665 | 5.2963 | 4.7287 | 5.1361 | 4.6509 | 4.9988 | 5.1361 | -0.40741 | -6.7017 | -7.077 | 116.2537 | 116.217 | -0.032044 | 116.6245 | 0.37537 | 122.7081 | 0.082398 | -0.07782 | 122.6303 | 123.1155 | 122.9782 | 0.40741 | 0.27008 | 116.6611 | 116.5237 | -0.07782 | 0.40741 | 116.8991 | 0.56763 | 116.4917 | 123.2758 | -123.6008 | -0.48523 | 116.1163 | 123.1155 | 114.1159 | 118.6661
2284.4844 | 123.4589 | -118.0252 | 5.1956 | -0.027161 | 0.0035525 | 0.12167 | 0.0032343 | -0.0012967 | 0.002634 | -0.0024481 | -0.072052 | 0.13918 | 0.0031894 | 4.4788e-05 | -0.0017432 | -0.0027302 | -0.0043899 | -1.5976 | -1.0483 | -118.364 | -1.355 | -1.1581 | -117.9977 | -1.2268 | 0.68207 | 5.2551 | 4.6921 | 5.1178 | 4.6005 | 4.9484 | 5.0629 | -0.33874 | -6.2439 | -6.5506 | 116.8671 | 116.7984 | 0.027466 | 117.1371 | 0.36621 | 122.7173 | 0.059509 | -0.07782 | 122.6257 | 123.0881 | 122.9736 | 0.37079 | 0.25635 | 117.2058 | 117.009 | -0.091553 | 0.42572 | 117.3157 | 0.56305 | 116.9769 | 123.2803 | -123.5596 | -0.50354 | 116.6702 | 123.143 | 116.4276 | 118.7073
2285.5469 | 123.3765 | -118.158 | 5.1773 | -0.050049 | 0.0039799 | 0.11932 | 0.0040887 | 0.0019077 | 0.00028418 | -0.0013799 | -0.32535 | 0.13811 | 0.00083965 | 0.00624 | -0.0032386 | -0.0014484 | 0.0028733 | -1.8951 | -1.2177 | -118.4647 | -1.6754 | -1.5335 | -118.103 | -1.5884 | 0.72327 | 5.2551 | 4.6646 | 4.9484 | 4.4678 | 4.8477 | 5.0125 | -0.3067 | -6.395 | -6.8527 | 116.6245 | 116.5695 | 0.054932 | 116.8762 | 0.36163 | 122.8226 | 0.07782 | -0.22888 | 122.6257 | 123.1705 | 123.0057 | 0.3479 | 0.18311 | 116.9312 | 116.7892 | -0.19684 | 0.28381 | 117.247 | 0.59051 | 116.9403 | 123.4131 | -123.642 | -0.51269 | 116.4825 | 123.1064 | 116.2628 | 118.8812
2286.4844 | 123.4268 | -118.0939 | 5.1544 | -0.03479 | 0.0039799 | 0.1206 | 0.0045159 | 0.0021213 | 0.0024204 | -0.00052553 | -0.081207 | 0.13832 | -0.00022855 | -0.0035868 | -0.0034522 | -0.0027302 | -0.00075834 | -1.4694 | -1.1398 | -118.3868 | -1.4374 | -1.2451 | -117.9749 | -1.3229 | 0.72327 | 5.2094 | 4.7058 | 5.0949 | 4.5639 | 4.9713 | 5.1041 | -0.29297 | -6.2943 | -6.5918 | 116.8488 | 116.7709 | 0.11902 | 117.0639 | 0.41199 | 122.7997 | 0.054932 | -0.059509 | 122.6578 | 123.1979 | 123.0652 | 0.39825 | 0.2655 | 117.1417 | 116.9495 | -0.14191 | 0.3891 | 117.247 | 0.50354 | 116.954 | 123.3032 | -123.5413 | -0.44861 | 116.6565 | 123.1888 | 116.6245 | 118.8171
2287.4844 | 123.4543 | -118.1213 | 5.1086 | -0.057678 | 0.0037661 | 0.11975 | 0.0036615 | -0.0015103 | 0.00028418 | -0.0013799 | -0.026276 | 0.13918 | 0.0019076 | 0.0015402 | -0.0077246 | -0.003371 | 0.00095066 | -2.2247 | -1.561 | -118.4006 | -1.9318 | -1.7807 | -117.9932 | -1.7944 | 0.62714 | 5.2368 | 4.7058 | 4.9759 | 4.5181 | 4.9255 | 5.0354 | -0.27924 | -6.6696 | -7.0404 | 116.3406 | 116.3269 | 0.12817 | 116.6061 | 0.40741 | 122.8271 | 0.12817 | -0.13275 | 122.6395 | 123.1567 | 123.0469 | 0.32959 | 0.21973 | 116.6199 | 116.4688 | -0.18768 | 0.27008 | 116.8396 | 0.53101 | 116.5604 | 123.3582 | -123.5092 | -0.40283 | 116.1896 | 123.0972 | 115.8966 | 118.7485
2288.5469 | 123.3582 | -117.984 | 5.3329 | 0.049133 | 0.0026981 | 0.11975 | 0.0070795 | 0.0014803 | -0.0022794 | 0.00075627 | -0.1575 | 0.13811 | 0.0046848 | 0.0019674 | -0.0019568 | -0.00080758 | 0.0013779 | -3.7308 | -1.6479 | -118.2907 | -2.0828 | -1.9638 | -117.9428 | -2.0004 | 0.6134 | 5.397 | 4.7928 | 5.1498 | 4.5593 | 4.9805 | 5.1453 | -0.3067 | -6.9809 | -7.4158 | 116.0202 | 115.9836 | 0.041199 | 116.2903 | 0.3479 | 122.7768 | 0.064087 | -0.18311 | 122.5433 | 123.1293 | 122.9645 | 0.35248 | 0.18768 | 116.3269 | 116.2079 | -0.23346 | 0.35705 | 116.6428 | 0.60425 | 116.3361 | 123.381 | -123.6237 | -0.54016 | 115.9012 | 123.1338 | 114.2532 | 118.5974
2289.4844 | 123.4589 | -117.8009 | 5.4382 | 0.0033567 | 0.0012027 | 0.11868 | 0.0045159 | -0.0025785 | 0.00049778 | -0.0022345 | -0.0079652 | 0.13725 | 0.0029758 | -0.0035868 | -0.0025976 | -0.0037982 | -0.0018265 | -2.1698 | -1.6296 | -118.0893 | -1.8906 | -1.7258 | -117.6498 | -1.8127 | 0.72784 | 5.5435 | 4.9622 | 5.3833 | 4.8065 | 5.2963 | 5.3558 | -0.28839 | -7.0679 | -7.3288 | 116.0751 | 115.9882 | 0.15106 | 116.2766 | 0.43945 | 122.7631 | 0.10529 | -0.054931 | 122.6074 | 123.1567 | 123.0972 | 0.39368 | 0.33417 | 116.3635 | 116.1987 | -0.15564 | 0.42114 | 116.4597 | 0.58136 | 116.1713 | 123.3444 | -123.5275 | -0.47607 | 115.9103 | 123.1842 | 115.6311 | 118.5287
2290.5469 | 123.3124 | -117.8879 | 5.4474 | -0.03479 | 0.0056889 | 0.12039 | 0.0077203 | 0.0010531 | 0.00071138 | 0.0011835 | -0.1636 | 0.13811 | 0.003403 | 0.0026084 | -0.0028112 | -0.006148 | -0.0020401 | -2.7695 | -1.6525 | -118.1854 | -2.1011 | -1.9775 | -117.8604 | -2.005 | 0.47607 | 5.5344 | 4.9301 | 5.2322 | 4.6692 | 5.0995 | 5.2551 | -0.29755 | -7.0999 | -7.5485 | 115.9103 | 115.8829 | 0.027465 | 116.1804 | 0.32501 | 122.818 | 0.086975 | -0.21515 | 122.5571 | 123.143 | 122.9874 | 0.32501 | 0.16937 | 116.2079 | 116.0843 | -0.26093 | 0.30212 | 116.5329 | 0.60425 | 116.2354 | 123.4222 | -123.6328 | -0.51727 | 115.7867 | 123.1201 | 115.1184 | 118.364
2291.4844 | 123.4131 | -117.7139 | 5.5573 | -0.11871 | 0.0026981 | 0.11889 | 0.0043023 | -0.0040739 | 0.00071138 | -0.00095273 | -0.093414 | 0.13811 | 0.0014804 | 0.00025839 | -0.0032386 | -0.001662 | -0.0013991 | -4.097 | -0.90179 | -118.0023 | -1.2177 | -1.0666 | -117.6727 | -1.2268 | 0.64545 | 5.5527 | 5.0446 | 5.4199 | 4.8935 | 5.3467 | 5.4703 | -0.28839 | -6.459 | -6.7749 | 116.6473 | 116.4871 | 0.041199 | 116.7755 | 0.32959 | 122.7585 | -0.004578 | -0.13733 | 122.6074 | 123.1842 | 123.0606 | 0.42572 | 0.30212 | 116.9357 | 116.7847 | -0.15106 | 0.37537 | 117.1005 | 0.50812 | 116.8121 | 123.2666 | -123.5596 | -0.51269 | 116.4963 | 123.1338 | 113.6169 | 118.3594
2292.5469 | 123.381 | -117.8101 | 5.4749 | -0.065308 | 0.0037661 | 0.11719 | 0.0060113 | -0.00022866 | -0.00057042 | -0.00031193 | -0.16055 | 0.13939 | 0.0038302 | 0.0023948 | -0.0021704 | -0.0023028 | -0.0018265 | -34.552 | -1.6937 | -118.1396 | -2.1103 | -1.9775 | -117.7826 | -2.0325 | 0.59967 | 5.5527 | 4.9667 | 5.3101 | 4.715 | 5.1819 | 5.3238 | -0.32959 | -7.1686 | -7.5851 | 115.8325 | 115.7776 | 0.027466 | 116.1072 | 0.35705 | 122.7768 | 0.077819 | -0.16479 | 122.525 | 123.1339 | 122.9919 | 0.35706 | 0.21515 | 116.1621 | 116.0294 | -0.25177 | 0.34332 | 116.4459 | 0.58594 | 116.1163 | 123.3627 | -123.6145 | -0.50812 | 115.6998 | 123.1201 | 83.2581 | 118.4097
2293.4844 | 123.3261 | -44.8059 | 78.3646 | -0.042419 | 0.0050479 | 0.043699 | 0.0023797 | -0.00086946 | 0.0011386 | -0.0030889 | -0.026276 | 0.0030997 | 0.0019076 | 0.035934 | -0.0043066 | -0.0031574 | 0.0039413 | -12.442 | -0.33875 | -45.0073 | -0.67291 | -0.54474 | -45.0211 | -0.56305 | 2.124 | 78.511 | 2.6917 | 78.5294 | 2.7969 | 2.8931 | 2.9984 | -0.20142 | -78.7033 | -79.0375 | 44.2612 | 44.2429 | -0.21515 | 44.4443 | -0.013733 | 47.4976 | 0.14648 | 0.16479 | 47.6028 | 47.8043 | 47.699 | 0.3067 | 0.20142 | 44.4626 | 44.3344 | 0.10529 | 75.8377 | 44.6686 | 75.8194 | 44.4672 | 123.317 | -123.3719 | -75.6729 | 44.133 | 123.3353 | 32.3639 | 46.9299
2294.5469 | 122.7219 | -44.3848 | 78.6072 | -0.065308 | 0.0024845 | 0.042844 | 0.0043023 | 0.00041234 | 0.0024204 | 0.0022517 | -0.084259 | 0.0035269 | 0.006821 | 0.043838 | -0.0032386 | 4.7018e-05 | 0.0033005 | -12.5656 | -0.24261 | -44.7144 | -0.66834 | -0.45776 | -44.9936 | -0.5722 | 2.3849 | 78.6713 | 2.6733 | 78.598 | 2.916 | 2.8656 | 2.9938 | -0.32959 | -78.8498 | -79.2755 | 43.927 | 43.8126 | -0.60883 | 44.1422 | -0.27924 | 47.0581 | 0.064087 | -0.009156 | 47.3007 | 47.3785 | 47.2504 | 0.32043 | 0.19226 | 44.2566 | 44.046 | 0.24261 | 75.9247 | 44.4717 | 75.9979 | 44.1422 | 123.056 | -123.3215 | -75.9338 | 43.7164 | 122.9828 | 31.8192 | 46.7697
2295.4844 | 123.436 | -44.5358 | 78.6163 | -0.019531 | 0.0041935 | 0.041563 | 0.0034479 | -0.0025785 | -0.0014248 | 0.00096987 | 0.0072936 | 0.0020315 | 0.0019076 | 0.03807 | -0.003025 | -0.003371 | 0.0050095 | -12.5885 | -0.2243 | -44.8242 | -0.51727 | -0.35706 | -44.7693 | -0.39368 | 1.8768 | 78.6896 | 2.6047 | 78.7537 | 2.9572 | 2.9343 | 2.9846 | -0.28839 | -78.8406 | -79.1336 | 44.1788 | 44.1422 | -0.23346 | 44.4305 | 0.054932 | 47.1405 | 0.073242 | 0.13733 | 47.493 | 47.5204 | 47.4701 | 0.37994 | 0.32959 | 44.4672 | 44.3069 | 0.35248 | 76.149 | 44.5999 | 76.0849 | 44.3115 | 123.2254 | -123.4406 | -76.0117 | 44.0186 | 123.2895 | 31.9473 | 46.4127
2296.5469 | 122.6944 | -44.0048 | 78.7262 | -0.1416 | 0.0020573 | 0.042203 | -0.0021063 | -0.016891 | -0.0065518 | -0.0080023 | -0.1575 | -0.0011727 | -0.00065575 | 0.034865 | -0.0034522 | -0.017897 | -0.0011855 | -12.7121 | -0.26093 | -44.7739 | -0.70496 | -0.58594 | -44.8517 | -0.61798 | 2.2797 | 78.8132 | 2.7374 | 78.6575 | 2.9526 | 2.9297 | 3.0533 | -0.76904 | -78.9871 | -79.4312 | 43.4189 | 43.3868 | -0.84686 | 44.1559 | -0.07782 | 46.7422 | 0.086975 | -0.068664 | 46.9574 | 47.0581 | 46.9345 | 0.31586 | 0.19226 | 44.1879 | 44.0689 | 0.21515 | 75.9201 | 44.5129 | 76.0757 | 43.7439 | 122.818 | -123.5001 | -75.9888 | 43.2999 | 122.6624 | 31.2927 | 46.2845
2297.4844 | 123.3902 | -44.6091 | 78.5889 | -0.011902 | 0.0018435 | 0.043485 | 0.0047295 | -0.00065586 | 0.0032748 | -0.00031193 | -0.023224 | 0.0035269 | 0.0036166 | 0.039352 | -0.0034522 | -0.0040118 | -0.0020401 | -2.0279 | -0.32959 | -44.8334 | -0.67291 | -0.52643 | -44.8196 | -0.55389 | 2.1286 | 78.6804 | 2.4811 | 78.5568 | 2.6642 | 2.6459 | 2.7283 | -0.2243 | -78.9185 | -79.2618 | 44.0826 | 44.0552 | -0.21057 | 44.2795 | 0.013733 | 47.0901 | 0.091553 | -0.032043 | 47.2733 | 47.3373 | 47.2549 | 0.24719 | 0.1648 | 44.3069 | 44.1605 | 0.18311 | 76.0757 | 44.5038 | 76.1993 | 44.2795 | 123.2895 | -123.4222 | -76.1078 | 43.9362 | 123.1659 | 42.5812 | 46.7377
2298.5469 | 122.7173 | -44.6411 | 78.392 | -0.45441 | -0.00029273 | 0.047758 | 0.0070795 | 0.0027621 | -0.00099762 | 0.00032907 | -0.11172 | 0.0043815 | 0.0055392 | 0.045974 | -0.0032386 | -0.00080758 | -0.00097194 | -0.90637 | -0.43488 | -45.0806 | -0.84228 | -0.74158 | -45.1584 | -0.75531 | 2.179 | 78.4882 | 1.8768 | 78.4058 | 2.1423 | 2.0737 | 2.1835 | -0.43945 | -78.8269 | -79.2343 | 43.8995 | 43.8858 | -0.51727 | 44.3253 | -0.07782 | 46.5179 | 0.09613 | 0.013733 | 46.7834 | 46.8246 | 46.7148 | 0.3067 | 0.19684 | 44.339 | 44.2383 | 0.2655 | 76.5289 | 44.6457 | 76.6113 | 44.2062 | 123.1293 | -123.4726 | -76.5152 | 43.7988 | 123.0469 | 43.7347 | 46.8201
2299.4844 | 123.3673 | -44.6457 | 78.5248 | -0.10345 | 0.0029117 | 0.043699 | 0.0038751 | -0.0017239 | 0.0011386 | -0.0037299 | -0.032379 | 0.0022453 | 0.0036166 | 0.037002 | -0.0051612 | -0.0027302 | 0.0018051 | -0.5722 | -0.23346 | -44.8975 | -0.52643 | -0.3479 | -44.902 | -0.42114 | 2.1881 | 78.6163 | 1.8494 | 78.6026 | 2.1698 | 2.1286 | 2.2018 | -0.25177 | -78.7582 | -79.0512 | 44.2978 | 44.2245 | -0.25635 | 44.4763 | -0.004578 | 46.4951 | 0.091553 | 0.07782 | 46.8155 | 46.8475 | 46.7743 | 0.35248 | 0.27924 | 44.5496 | 44.371 | 0.32044 | 76.7532 | 44.664 | 76.767 | 44.4122 | 123.262 | -123.4222 | -76.6754 | 44.1193 | 123.2483 | 44.0735 | 46.8338
2300.4844 | 123.3856 | -44.6594 | 78.4927 | -0.080566 | 0.0035525 | 0.045621 | 0.0051569 | -1.486e-05 | 0.0015658 | -0.00052553 | -0.053741 | 0.0013907 | 0.0048984 | 0.038711 | -0.005802 | -0.003371 | 9.6064e-05 | -0.62256 | -0.27924 | -44.9249 | -0.54932 | -0.39825 | -44.9112 | -0.48065 | 2.2064 | 78.5797 | 1.8906 | 78.653 | 2.1606 | 2.211 | 2.2705 | -0.2655 | -78.772 | -79.0421 | 44.2612 | 44.1788 | -0.25177 | 44.4443 | 0.013733 | 46.55 | 0.086975 | 0.16022 | 46.8201 | 46.9299 | 46.8704 | 0.37994 | 0.32044 | 44.5267 | 44.3756 | 0.27008 | 76.7624 | 44.6457 | 76.6891 | 44.3802 | 123.2391 | -123.4177 | -76.6022 | 44.1101 | 123.3124 | 44.0369 | 46.8658
2301.5469 | 123.0972 | -44.577 | 78.4882 | -0.22552 | 0.0014163 | 0.043699 | 0.0021661 | -0.0074919 | 0.0011386 | -0.0035163 | -0.10257 | 0.0048087 | 0.0025484 | 0.049178 | -0.0036658 | -0.0052936 | 0.0011643 | -0.70953 | -0.26093 | -44.9524 | -0.69122 | -0.59052 | -44.9799 | -0.60425 | 1.8356 | 78.6987 | 1.8997 | 78.5614 | 2.0966 | 2.3575 | 2.3758 | -0.37537 | -78.7491 | -79.1794 | 43.9865 | 43.9728 | -0.40283 | 44.3481 | -0.027465 | 46.4767 | 0.21057 | 0.073242 | 46.6736 | 46.9528 | 46.9345 | 0.47607 | 0.45776 | 44.3619 | 44.2612 | 0.19684 | 76.6617 | 44.6915 | 76.799 | 44.3161 | 123.2758 | -123.4406 | -76.5884 | 43.8858 | 123.1384 | 43.8675 | 46.4127
2302.4844 | 123.4085 | -44.4168 | 78.7262 | -0.24841 | 0.0037661 | 0.042844 | 0.0032343 | -0.0021513 | 0.00028418 | -0.0035163 | -0.047638 | 0.00074988 | 0.004471 | 0.041274 | -0.0043066 | -0.0031574 | -0.00011754 | -0.70953 | -0.45776 | -44.7647 | -0.71411 | -0.55389 | -44.7006 | -0.62256 | 2.005 | 78.7994 | 2.7786 | 78.8727 | 3.0258 | 3.0899 | 3.1815 | -0.3479 | -79.184 | -79.4403 | 43.8629 | 43.7942 | -0.28381 | 44.1422 | 0.064086 | 47.1954 | 0.073242 | 0.14648 | 47.4426 | 47.5983 | 47.5067 | 0.40283 | 0.31128 | 44.2108 | 44.0506 | 0.24719 | 76.0941 | 44.3069 | 76.0208 | 43.959 | 123.2162 | -123.4909 | -75.9476 | 43.7027 | 123.2895 | 43.7073 | 46.4218
2303.5469 | 123.2208 | -44.5312 | 78.5843 | -0.027161 | 0.0056889 | 0.045194 | 0.0060113 | -0.0027921 | 0.0030612 | 0.00032907 | -0.087311 | 0.0028861 | 0.0031894 | 0.044265 | -0.003025 | 0.00026062 | 0.00030966 | -0.97961 | -0.41199 | -44.8425 | -0.78278 | -0.6546 | -44.87 | -0.68665 | 2.0004 | 78.7033 | 2.4261 | 78.7399 | 2.7008 | 2.7191 | 2.8244 | -0.31128 | -78.9963 | -79.3671 | 43.8766 | 43.8446 | -0.33875 | 44.1559 | -0.027466 | 46.9574 | 0.11902 | 0.15564 | 47.2321 | 47.3557 | 47.2504 | 0.39826 | 0.29297 | 44.1879 | 44.0598 | 0.27466 | 76.3138 | 44.4305 | 76.2772 | 44.1193 | 123.2346 | -123.4268 | -76.1581 | 43.7485 | 123.2712 | 43.5516 | 46.5317
2304.4844 | 123.3765 | -44.5999 | 78.5751 | -0.10345 | 0.0056889 | 0.043485 | 0.0025933 | -0.00086946 | -0.0027066 | -0.00031193 | -0.056793 | 0.0041679 | 0.005112 | 0.03572 | -0.0055884 | -0.003371 | -0.00033114 | -0.66376 | -0.34332 | -44.87 | -0.6134 | -0.44403 | -44.8608 | -0.5127 | 2.0645 | 78.6484 | 2.0325 | 78.685 | 2.2934 | 2.298 | 2.3758 | -0.27008 | -78.9185 | -79.1885 | 44.1559 | 44.0872 | -0.26093 | 44.3573 | 0.009155 | 46.6324 | 0.073242 | 0.10986 | 46.8933 | 46.9757 | 46.8979 | 0.34332 | 0.2655 | 44.426 | 44.2566 | 0.26092 | 76.6525 | 44.5267 | 76.6159 | 44.2566 | 123.2483 | -123.4451 | -76.5427 | 43.9865 | 123.2849 | 43.9362 | 46.6644
2305.5469 | 122.9187 | -44.664 | 78.3234 | 0.0033567 | 0.0026981 | 0.042844 | 0.0021661 | -0.0015103 | -0.00078402 | -0.0069341 | -0.099518 | 0.0028861 | 0.004471 | 0.042769 | -0.0034522 | -0.001662 | -0.00033114 | -0.75989 | -0.3067 | -44.9753 | -0.75989 | -0.65918 | -45.0165 | -0.6546 | 1.6983 | 78.6667 | 1.8631 | 78.5065 | 2.1881 | 2.037 | 2.1286 | -0.31128 | -78.6301 | -79.0833 | 44.0048 | 44.0094 | -0.35248 | 44.3207 | -0.041198 | 46.5271 | 0.34332 | 0.18311 | 46.8521 | 46.7926 | 46.701 | 0.2655 | 0.17395 | 44.3161 | 44.2154 | 0.32501 | 76.6434 | 44.6686 | 76.8036 | 44.3573 | 123.3307 | -123.2986 | -76.4603 | 43.9041 | 123.1705 | 43.9041 | 46.3623
2306.4844 | 123.0515 | -44.6686 | 78.3417 | -0.042419 | 0.0044071 | 0.043272 | 0.0066523 | -0.00044226 | 0.00092498 | -0.0013799 | -0.093414 | 0.0045951 | 0.0038302 | 0.04576 | -0.004093 | -0.0020892 | -0.0022537 | -0.8194 | -0.43945 | -44.9524 | -0.81482 | -0.67291 | -44.989 | -0.70953 | 1.7532 | 78.5797 | 2.0782 | 78.6255 | 2.449 | 2.3163 | 2.4445 | -0.28381 | -78.7811 | -79.1565 | 43.9957 | 43.959 | -0.32043 | 44.2429 | -0.036621 | 46.7468 | 0.23804 | 0.28381 | 47.1176 | 47.113 | 46.9849 | 0.36621 | 0.23804 | 44.2795 | 44.1376 | 0.37079 | 76.5472 | 44.5129 | 76.5015 | 44.2291 | 123.2483 | -123.2941 | -76.2634 | 43.8538 | 123.2941 | 43.8492 | 46.4218
2307.4844 | 123.5275 | -117.6636 | 5.4886 | -0.11871 | 0.0044071 | 0.12103 | 0.0060113 | -0.0017239 | 0.0022068 | 0.00054267 | -0.059845 | 0.14025 | 0.004471 | 0.00047219 | -0.004093 | -0.0010212 | -0.0013991 | -1.3596 | -0.75531 | -118.1396 | -1.03 | -0.8606 | -117.6315 | -0.93384 | 0.49896 | 5.5664 | 5.0217 | 5.4245 | 4.9896 | 5.3421 | 5.4428 | -0.47607 | -6.2439 | -6.5186 | 116.803 | 116.7297 | 0.032043 | 117.2058 | 0.50812 | 122.6852 | 0.07782 | -0.064086 | 122.6532 | 123.1064 | 123.0057 | 0.42114 | 0.32043 | 117.2791 | 117.1097 | -0.032043 | 0.40283 | 117.3843 | 0.54474 | 116.9083 | 123.23 | -123.6282 | -0.46692 | 116.6336 | 123.0881 | 116.304 | 118.1625
2308.4844 | 123.5184 | -117.8833 | 5.3329 | -0.088196 | 0.0031253 | 0.12167 | 0.0053705 | -0.0021513 | 0.00071138 | 0.0018243 | -0.10562 | 0.1396 | 0.0027622 | -0.0016642 | -0.0038794 | -0.00059378 | -0.0041763 | -1.2314 | -0.83771 | -118.2358 | -1.1536 | -1.0117 | -117.7597 | -1.062 | 0.60883 | 5.4291 | 4.8981 | 5.3055 | 4.7058 | 5.191 | 5.3055 | -0.35248 | -6.1707 | -6.4865 | 116.8716 | 116.8213 | 0.1236 | 117.1738 | 0.47607 | 122.7814 | 0.09613 | -0.027466 | 122.5891 | 123.1888 | 123.0743 | 0.40741 | 0.29297 | 117.2241 | 117.0822 | -0.19226 | 0.40741 | 117.3981 | 0.53101 | 117.0456 | 123.3124 | -123.5687 | -0.43488 | 116.7297 | 123.1888 | 116.6519 | 118.4921
2309.5469 | 123.381 | -117.9291 | 5.3558 | -0.042419 | 0.0041935 | 0.11953 | 0.0066523 | 0.0025485 | 0.00049778 | -0.0062933 | -0.11783 | 0.13768 | 0.0029758 | -0.0065774 | -0.0077246 | -0.007857 | -0.0037491 | -1.7258 | -1.2863 | -118.2632 | -1.7029 | -1.5564 | -117.8833 | -1.6296 | 0.45319 | 5.4474 | 4.8798 | 5.1727 | 4.7791 | 5.0537 | 5.1956 | -0.33417 | -6.6422 | -7.0587 | 116.3727 | 116.2994 | 0.045776 | 116.6336 | 0.37994 | 122.8088 | 0.091553 | -0.18311 | 122.7081 | 123.1247 | 122.9828 | 0.31586 | 0.17395 | 116.7068 | 116.5604 | -0.10071 | 0.29297 | 116.9769 | 0.56763 | 116.6428 | 123.3765 | -123.6191 | -0.47607 | 116.2262 | 123.1018 | 116.2033 | 118.3823
2310.4844 | 123.5092 | -117.9062 | 5.3329 | -0.03479 | 0.0035525 | 0.1221 | 0.0051569 | 0.0025485 | 0.0024204 | -0.00031193 | -0.056793 | 0.13768 | 0.00019865 | -0.00059601 | -0.001316 | -0.0012348 | 0.00073706 | -2.0279 | -1.7258 | -118.19 | -2.0004 | -1.8402 | -117.778 | -1.9135 | 0.56763 | 5.397 | 4.921 | 5.2277 | 5.04 | 5.1727 | 5.2872 | -0.28381 | -7.0587 | -7.3334 | 116.066 | 115.9927 | 0.12817 | 116.2766 | 0.41199 | 122.8271 | 0.064087 | -0.10529 | 122.9462 | 123.1934 | 123.0789 | 0.36621 | 0.25177 | 116.3498 | 116.1896 | 0.11902 | 0.3067 | 116.4642 | 0.47607 | 116.1804 | 123.3032 | -123.5229 | -0.41199 | 115.9058 | 123.1338 | 115.8783 | 118.4738
2311.4844 | 123.4268 | -117.9611 | 5.3238 | -0.050049 | 0.0031253 | 0.11911 | 0.0057977 | 0.0031893 | 0.0015658 | -0.0015935 | -0.078156 | 0.13982 | 0.0038302 | 0.0019674 | -0.0025976 | -0.00080758 | -0.0013991 | -2.0645 | -1.7487 | -118.2861 | -2.0416 | -1.8539 | -117.8558 | -1.9135 | 0.61798 | 5.3879 | 4.8523 | 5.2505 | 4.8614 | 5.1407 | 5.2597 | -0.32501 | -7.0724 | -7.3654 | 116.1072 | 116.0477 | 0.10529 | 116.3727 | 0.4303 | 122.8134 | 0.064086 | -0.073243 | 122.8226 | 123.2208 | 123.1018 | 0.40741 | 0.28839 | 116.4322 | 116.2445 | 0.009155 | 0.39825 | 116.5375 | 0.53558 | 116.2125 | 123.349 | -123.6099 | -0.4715 | 115.9195 | 123.2117 | 115.8966 | 118.5791
2312.4844 | 123.4451 | -118.0069 | 5.2643 | -0.019531 | 0.0031253 | 0.1206 | 0.0066523 | 0.0010531 | 7.0582e-05 | 0.00075627 | -0.12393 | 0.13854 | 0.0025484 | 0.001113 | -0.0034522 | -0.00080758 | -0.0022537 | -2.0874 | -1.68 | -118.3777 | -2.0737 | -1.9409 | -117.9886 | -1.9684 | 0.69122 | 5.3375 | 4.7745 | 5.1407 | 4.6921 | 5.0354 | 5.1865 | -0.37079 | -6.9443 | -7.338 | 116.066 | 116.0385 | 0.018311 | 116.4093 | 0.3891 | 122.7814 | 0.073242 | -0.1236 | 122.699 | 123.1934 | 123.0423 | 0.41199 | 0.26093 | 116.4368 | 116.304 | -0.082397 | 0.36621 | 116.6977 | 0.56305 | 116.3269 | 123.3444 | -123.642 | -0.48981 | 115.9332 | 123.1476 | 115.9195 | 118.6981
2313.4844 | 123.1979 | -44.7327 | 78.4287 | -0.088196 | 0.0035525 | 0.045408 | 0.0013117 | 0.0012667 | 7.0582e-05 | 0.0011835 | -0.047638 | 0.0039541 | 0.0036166 | 0.041488 | -0.0036658 | -0.0020892 | 0.0045823 | -0.91553 | -0.65002 | -44.8792 | -0.93842 | -0.7782 | -44.9799 | -0.83313 | 2.0096 | 78.4927 | 2.4765 | 78.5889 | 2.7695 | 2.7603 | 2.861 | -0.14648 | -79.0787 | -79.3671 | 43.9545 | 43.8995 | -0.24719 | 44.046 | -0.10071 | 47.2092 | 0.064087 | 0.16022 | 47.5021 | 47.5937 | 47.493 | 0.38452 | 0.28381 | 44.101 | 43.9407 | 0.29297 | 76.1124 | 44.2291 | 76.0162 | 44.0826 | 123.2254 | -123.3078 | -75.9521 | 43.7943 | 123.3215 | 43.8171 | 46.7422
2314.4844 | 123.2071 | -44.7922 | 78.3691 | -0.027161 | 0.0046207 | 0.044981 | 0.0049433 | 0.0021213 | -0.00035682 | 0.00032907 | -0.047638 | 0.0018179 | 0.0027622 | 0.04106 | -0.0021704 | -0.00080758 | 0.0052231 | -1.062 | -0.74158 | -44.989 | -1.0712 | -0.87891 | -45.0348 | -0.96588 | 1.9135 | 78.4973 | 2.4078 | 78.5522 | 2.6642 | 2.6917 | 2.7786 | -0.19684 | -79.1107 | -79.4403 | 43.9133 | 43.8263 | -0.24262 | 44.0231 | -0.045776 | 47.2 | 0.12817 | 0.1831 | 47.4564 | 47.5708 | 47.4838 | 0.37079 | 0.28381 | 44.1101 | 43.9178 | 0.25635 | 76.1444 | 44.2474 | 76.0895 | 44.0506 | 123.2895 | -123.3582 | -75.9613 | 43.721 | 123.3444 | 43.7302 | 46.7056
2315.5469 | 122.9095 | -44.7601 | 78.4927 | -0.095825 | 0.0037661 | 0.041776 | 0.0049433 | -1.486e-05 | 0.00092498 | -0.00052553 | -0.023224 | 0.0039541 | 0.0025484 | 0.040633 | -0.003025 | -0.0025164 | -0.00075834 | -1.1215 | -0.73242 | -44.9295 | -1.1719 | -1.0529 | -45.1126 | -1.0666 | 1.7532 | 78.5751 | 2.4261 | 78.4882 | 2.6047 | 2.6093 | 2.7191 | -0.16937 | -79.2252 | -79.6646 | 43.7073 | 43.6935 | -0.35248 | 43.8629 | -0.18311 | 47.1863 | 0.082397 | -0.004578 | 47.3648 | 47.4792 | 47.3694 | 0.29297 | 0.18311 | 43.8766 | 43.7576 | 0.17853 | 76.062 | 44.1971 | 76.149 | 44.0277 | 123.3353 | -123.4222 | -76.0666 | 43.5883 | 123.2483 | 43.6386 | 46.5134
2316.4844 | 123.468 | -44.7968 | 78.3737 | -0.050049 | 0.0012027 | 0.045835 | 0.0053705 | -0.0012967 | -0.0014248 | 0.00032907 | -0.01712 | 0.0024589 | 0.0029758 | 0.044478 | -0.004093 | -0.0025164 | 0.0024461 | -1.149 | -0.84686 | -45.0302 | -1.1398 | -0.97046 | -45.0119 | -1.0437 | 1.8997 | 78.4927 | 2.4536 | 78.6026 | 2.3758 | 2.7054 | 2.8473 | -0.23346 | -79.2206 | -79.5135 | 43.8263 | 43.7531 | -0.21515 | 43.9865 | 0.01831 | 47.2504 | 0.11902 | 0.22888 | 47.1725 | 47.644 | 47.5021 | 0.39368 | 0.25177 | 44.0598 | 43.8904 | -0.07782 | 76.149 | 44.1833 | 76.0391 | 43.9499 | 123.2895 | -123.4039 | -75.9201 | 43.6569 | 123.3994 | 43.6478 | 46.6965
2317.5469 | 123.2986 | -44.7556 | 78.447 | 0.018616 | 0.0022709 | 0.042631 | 0.0066523 | 0.0036165 | 0.00092498 | -0.0026617 | -0.075104 | 0.0041679 | 0.0055392 | 0.04106 | -0.004093 | -0.0012348 | 0.0041551 | -1.1536 | -0.71869 | -45.0439 | -1.1719 | -1.0345 | -45.0714 | -1.062 | 2.005 | 78.5843 | 2.4353 | 78.5156 | 2.623 | 2.6505 | 2.7695 | -0.28839 | -79.1656 | -79.6188 | 43.721 | 43.6935 | -0.31586 | 43.9819 | -0.027466 | 47.1909 | 0.13733 | 0.068665 | 47.3785 | 47.525 | 47.406 | 0.33417 | 0.21515 | 44.0094 | 43.8721 | 0.18768 | 76.0803 | 44.3253 | 76.149 | 44.0369 | 123.3398 | -123.4909 | -76.0117 | 43.5837 | 123.2712 | 43.602 | 46.7606
2318.4844 | 123.4451 | -44.7189 | 78.4378 | -0.072937 | 0.0056889 | 0.042844 | 0.0051569 | 0.0023349 | 0.0034884 | -0.00052553 | -0.041534 | 0.0033133 | 0.0042574 | 0.046401 | -0.0053748 | -0.0010212 | -0.00054474 | -2.2202 | -0.79651 | -45.0211 | -1.1032 | -0.95215 | -45.0165 | -1.0208 | 1.9867 | 78.5065 | 2.5497 | 78.598 | 2.829 | 2.8244 | 2.9297 | -0.30212 | -79.2343 | -79.541 | 43.7668 | 43.6981 | -0.29755 | 44.0002 | 0.004578 | 47.2687 | 0.068665 | 0.16022 | 47.5479 | 47.6486 | 47.5433 | 0.37994 | 0.27466 | 44.0689 | 43.9178 | 0.27923 | 76.0483 | 44.2245 | 75.9567 | 43.9224 | 123.2254 | -123.4589 | -75.8881 | 43.6157 | 123.317 | 42.4988 | 46.7056
2319.5469 | 122.9553 | -45.0394 | 77.8244 | -0.042419 | 0.0046207 | 0.044981 | 0.0057977 | 0.0019077 | 0.0013522 | -0.00052553 | -0.093414 | 0.0052359 | 0.0031894 | 0.042769 | -0.004093 | -0.0023028 | 9.6064e-05 | -1.2817 | -0.68665 | -45.314 | -1.0757 | -0.92926 | -45.3415 | -0.96588 | 2.1286 | 78.2639 | 1.7212 | 78.2822 | 2.092 | 2.0004 | 2.0966 | -0.27466 | -78.511 | -78.9001 | 44.1101 | 44.0735 | -0.30212 | 44.3481 | -0.027466 | 46.7606 | 0.43945 | 0.45776 | 47.1313 | 47.1359 | 47.0398 | 0.37537 | 0.27924 | 44.3848 | 44.2383 | 0.37079 | 76.561 | 44.6274 | 76.5427 | 44.3527 | 123.3032 | -123.1384 | -76.1032 | 43.9636 | 123.3215 | 43.7576 | 47.168
2320.4844 | 123.4955 | -117.9428 | 5.2597 | -0.057678 | 0.0026981 | 0.1206 | 0.0090021 | -0.00022866 | 0.0011386 | 0.0024653 | -0.099518 | 0.13875 | 0.0036166 | -0.0031594 | -0.0060156 | -0.00080758 | -0.00011754 | -2.1881 | -1.7258 | -118.4052 | -2.1652 | -2.0142 | -118.0161 | -2.0599 | 0.64087 | 5.3284 | 4.7699 | 5.0949 | 4.9301 | 4.985 | 5.1041 | -0.46234 | -6.9855 | -7.4249 | 115.9286 | 115.8829 | -0.073242 | 116.3452 | 0.3891 | 122.7127 | 0.068664 | -0.1648 | 122.8729 | 123.0469 | 122.9279 | 0.33417 | 0.21515 | 116.391 | 116.2399 | 0.16022 | 0.32501 | 116.6794 | 0.55847 | 116.217 | 123.2712 | -123.6649 | -0.48981 | 115.7776 | 123.0377 | 115.7547 | 118.5837
2321.5469 | 123.4177 | -117.9474 | 5.3513 | -0.027161 | 0.0031253 | 0.12103 | 0.0072931 | 0.0034029 | -0.0014248 | -0.00073913 | -0.13614 | 0.13747 | 0.0010532 | -0.017259 | -0.026096 | 0.015855 | -0.021907 | -2.3529 | -1.8036 | -118.2632 | -2.2568 | -2.0737 | -117.897 | -2.1698 | 0.83771 | 5.4245 | 4.8752 | 5.159 | 4.8706 | 5.0354 | 5.1727 | -0.31586 | -7.1548 | -7.608 | 115.8737 | 115.7776 | 0.050354 | 116.0934 | 0.36621 | 122.8226 | 0.073243 | -0.19226 | 122.818 | 123.1201 | 122.9828 | 0.29755 | 0.16022 | 116.1896 | 116.0065 | -0.004578 | 0.28381 | 116.4597 | 0.54932 | 116.1438 | 123.3719 | -123.6145 | -0.47607 | 115.6906 | 123.1064 | 115.5945 | 118.7851
2322.4844 | 123.4314 | -118.3594 | 4.9118 | -0.12634 | 0.0024845 | 0.12082 | 0.0062249 | 0.0040439 | -0.00099762 | 0.00032907 | -0.065949 | 0.14003 | 0.0029758 | -0.0044412 | -0.003025 | -0.001662 | -0.00033114 | -2.3483 | -1.8402 | -118.6249 | -2.1698 | -1.9913 | -118.19 | -2.0691 | 0.90179 | 5.0262 | 4.509 | 4.8798 | 4.7928 | 4.7836 | 4.9438 | -0.2655 | -6.752 | -7.0816 | 116.3681 | 116.2903 | 0.16937 | 116.5558 | 0.43488 | 122.8683 | 0.11444 | -0.032043 | 123.1522 | 123.3032 | 123.143 | 0.43488 | 0.27466 | 116.6336 | 116.4551 | 0.28381 | 0.37079 | 116.7847 | 0.51727 | 116.5192 | 123.3856 | -123.5367 | -0.40283 | 116.1896 | 123.2391 | 116.011 | 119.2612
2323.5469 | 123.4177 | -118.1396 | 5.1727 | -0.088196 | 0.0037661 | 0.12146 | 0.0064385 | 0.0014803 | 0.0019932 | 0.00096987 | -0.11478 | 0.13832 | 0.0038302 | -0.013841 | -0.0077246 | -0.013198 | -0.012935 | -2.2659 | -1.8997 | -118.4647 | -2.3117 | -2.1423 | -118.0389 | -2.211 | 0.74616 | 5.2322 | 4.6921 | 5.0217 | 4.8523 | 4.9118 | 5.0125 | -0.32501 | -7.0724 | -7.4844 | 115.9973 | 115.9286 | 0.10071 | 116.2537 | 0.42572 | 122.8317 | 0.05951 | -0.15106 | 122.9919 | 123.1522 | 123.0515 | 0.32043 | 0.21973 | 116.3223 | 116.153 | 0.16022 | 0.32959 | 116.5649 | 0.54016 | 116.2399 | 123.3719 | -123.6374 | -0.48065 | 115.8279 | 123.1613 | 115.8737 | 118.8858
2324.4844 | 123.4818 | -117.9382 | 5.3375 | -0.10345 | 0.0048343 | 0.12103 | 0.0060113 | -1.486e-05 | -0.00014322 | 0.00054267 | -0.062897 | 0.13832 | 0.0042574 | -0.0016642 | -0.004093 | -0.0012348 | 0.0035141 | -2.0096 | -1.6983 | -118.2678 | -2.005 | -1.8448 | -117.8146 | -1.9135 | 0.84686 | 5.3879 | 4.8569 | 5.2643 | 5.1086 | 5.1682 | 5.2963 | -0.32959 | -7.0358 | -7.3425 | 116.0934 | 116.0248 | 0.1236 | 116.3544 | 0.45319 | 122.7951 | 0.050354 | -0.073242 | 123.0469 | 123.2346 | 123.1064 | 0.43945 | 0.31128 | 116.423 | 116.2628 | 0.25177 | 0.40741 | 116.5695 | 0.531 | 116.2399 | 123.3261 | -123.6053 | -0.48065 | 115.9332 | 123.2025 | 115.9286 | 118.7851
2325.4844 | 123.4634 | -118.1076 | 5.1498 | -0.072937 | 0.0050479 | 0.12253 | 0.0038751 | -0.0045011 | 0.002634 | -0.00095273 | -0.053741 | 0.13661 | 0.0019076 | -0.0014504 | -0.004093 | -0.0040118 | -0.0024673 | -3.0167 | -2.0416 | -118.4875 | -2.3117 | -2.1423 | -118.0115 | -2.2293 | 0.88806 | 5.191 | 4.7012 | 5.0629 | 4.9438 | 4.9805 | 5.1132 | -0.37994 | -7.1915 | -7.4615 | 115.9653 | 115.8783 | 0.09613 | 116.2582 | 0.47607 | 122.8088 | 0.041199 | -0.086975 | 123.0515 | 123.2208 | 123.0881 | 0.41199 | 0.27924 | 116.3452 | 116.1758 | 0.24261 | 0.36163 | 116.4459 | 0.48981 | 116.066 | 123.2986 | -123.6374 | -0.44861 | 115.7959 | 123.1705 | 115.0909 | 118.9957
2326.5469 | 123.3902 | -118.0664 | 5.2597 | 0.010986 | 0.0022709 | 0.12018 | 0.0055841 | -0.0017239 | 0.00028418 | 0.00011527 | -0.093414 | 0.13896 | 0.00019865 | -0.0029458 | -0.0045202 | -0.0029438 | 0.0028733 | -2.0187 | -1.5976 | -118.3868 | -2.0416 | -1.9043 | -117.9749 | -1.9226 | 0.74158 | 5.3375 | 4.747 | 5.0629 | 4.9484 | 4.9759 | 5.0903 | -0.32044 | -6.8573 | -7.3013 | 116.1621 | 116.1438 | 0.091552 | 116.4642 | 0.41199 | 122.8134 | 0.077819 | -0.19684 | 123.0148 | 123.1567 | 123.0423 | 0.34332 | 0.22888 | 116.4825 | 116.3452 | 0.20142 | 0.31586 | 116.7892 | 0.59051 | 116.4688 | 123.4039 | -123.6465 | -0.5127 | 116.0248 | 123.1293 | 116.0477 | 118.808
2327.4844 | 123.4177 | -118.0618 | 5.2048 | -0.088196 | 0.0031253 | 0.11953 | 0.0053705 | 0.00062594 | -0.00014322 | -0.0020209 | -0.029327 | 0.1396 | 0.003403 | 0.0034628 | -0.003025 | 4.7018e-05 | 0.00052346 | -2.5452 | -1.8265 | -118.3777 | -2.1469 | -1.973 | -117.9932 | -2.0462 | 0.87891 | 5.246 | 4.7424 | 5.0766 | 5.0079 | 5.0079 | 5.1315 | -0.31586 | -7.0312 | -7.3517 | 116.0889 | 116.0156 | 0.068665 | 116.3315 | 0.38452 | 122.8043 | 0.041199 | -0.12817 | 123.0698 | 123.1934 | 123.0698 | 0.3891 | 0.2655 | 116.4047 | 116.2308 | 0.2655 | 0.33417 | 116.5512 | 0.50354 | 116.2354 | 123.3078 | -123.5825 | -0.46234 | 115.9149 | 123.1384 | 115.5167 | 118.9407
2328.5469 | 123.3719 | -118.0023 | 5.3329 | -0.065308 | 0.0029117 | 0.12103 | 0.0066523 | 0.00083954 | -0.0022794 | -0.0022345 | -0.12393 | 0.13832 | 0.0031894 | -0.0010232 | -0.0015296 | -0.013411 | -0.0039627 | -2.7237 | -1.8127 | -118.3319 | -2.2018 | -2.0416 | -117.8833 | -2.1149 | 0.97504 | 5.3925 | 4.7791 | 5.159 | 5.1407 | 5.0034 | 5.1361 | -0.32959 | -7.1457 | -7.5348 | 115.9607 | 115.8875 | 0.11902 | 116.217 | 0.44861 | 122.7814 | 0.059509 | -0.17395 | 123.143 | 123.1384 | 123.0057 | 0.35705 | 0.2243 | 116.2903 | 116.1301 | 0.36163 | 0.37994 | 116.5192 | 0.6134 | 116.1896 | 123.3948 | -123.6649 | -0.55389 | 115.8005 | 123.1613 | 115.2786 | 118.9774
2329.4844 | 123.4177 | -118.0481 | 5.2505 | -0.11108 | 0.0037661 | 0.11569 | 0.0021661 | -0.0012967 | 0.0028476 | -0.0022345 | -0.0018616 | 0.13768 | 0.0040438 | -0.00016881 | -0.0028112 | 0.00026062 | 0.0026597 | -2.916 | -1.7944 | -118.428 | -2.1515 | -2.0004 | -117.9382 | -2.0142 | 0.97504 | 5.2917 | 4.7287 | 5.1224 | 5.0079 | 5.0308 | 5.1224 | -0.37994 | -7.045 | -7.402 | 116.0477 | 116.0339 | 0.10986 | 116.4139 | 0.48981 | 122.7768 | 0.041199 | -0.12817 | 123.056 | 123.1705 | 123.0789 | 0.39368 | 0.30212 | 116.4276 | 116.2766 | 0.27924 | 0.39368 | 116.6336 | 0.56305 | 116.2537 | 123.3398 | -123.6786 | -0.52185 | 115.8966 | 123.1705 | 115.1321 | 119.0231
2330.4844 | 123.4314 | -117.984 | 5.2963 | -0.11108 | 0.0050479 | 0.12082 | 0.0057977 | 0.0027621 | 0.00028418 | 0.0031061 | -0.096466 | 0.13832 | 0.0012668 | 0.0032492 | -0.0049476 | -0.00016658 | 0.0026597 | -2.6779 | -1.7075 | -118.3228 | -1.9958 | -1.8539 | -117.9062 | -1.9318 | 1.0803 | 5.3238 | 4.7287 | 5.2048 | 5.1178 | 4.9942 | 5.1453 | -0.33875 | -7.0038 | -7.2922 | 116.1301 | 116.0522 | 0.07782 | 116.391 | 0.41657 | 122.7127 | 0.027466 | -0.091553 | 123.1018 | 123.1293 | 122.9782 | 0.41657 | 0.2655 | 116.4688 | 116.3269 | 0.3891 | 0.47607 | 116.6153 | 0.59509 | 116.2766 | 123.3078 | -123.6191 | -0.56763 | 115.9882 | 123.1888 | 115.3061 | 119.0643
2331.5469 | 117.5629 | -44.1193 | 78.5889 | -0.38574 | -0.0071285 | 0.043058 | 0.0060113 | 0.0016939 | 0.00049778 | -0.0020209 | -0.13919 | -0.0024545 | 0.00019865 | 0.031875 | -0.029728 | 0.015855 | -0.01144 | -12.4512 | -0.31128 | -44.2383 | -0.68665 | -0.54016 | -44.9203 | -0.59509 | 3.6072 | 78.7537 | 2.4902 | 78.653 | 2.8107 | 2.6733 | 2.7878 | -0.11902 | -78.9001 | -79.2755 | 43.5791 | 43.5242 | -0.80109 | 43.6432 | -0.68207 | 46.6095 | 0.1648 | 0.064087 | 46.9299 | 46.907 | 46.7926 | 0.29755 | 0.18311 | 43.6981 | 43.5516 | 0.32043 | 76.1627 | 43.927 | 76.2634 | 43.808 | 122.8729 | -122.8271 | -76.0986 | 43.4326 | 122.7722 | 31.6681 | 47.7264
2332.4844 | 123.5229 | -117.9199 | 5.2734 | -0.042419 | 0.0039799 | 0.1206 | 0.0060113 | 0.00019874 | 0.0015658 | 0.00011527 | -0.056793 | 0.13704 | 0.0027622 | -0.0031594 | -0.0011022 | -0.0018756 | 0.0011643 | -34.4147 | -1.6342 | -118.2678 | -1.9775 | -2.0004 | -117.9611 | -1.7258 | 0.66376 | 5.3055 | 4.8019 | 5.2048 | 5.1224 | 5.0812 | 5.1956 | -0.3479 | -6.9077 | -7.251 | 115.9195 | 116.1942 | -0.041199 | 116.5421 | 0.3067 | 122.7219 | 0.032044 | -0.068664 | 123.0423 | 123.1155 | 123.0011 | 0.39368 | 0.27924 | 116.2674 | 116.2903 | 0.32043 | 0.40283 | 116.6336 | 0.50354 | 116.2857 | 123.2254 | -123.5413 | -0.4715 | 115.9424 | 123.1247 | 83.5052 | 118.5837
2333.5469 | 123.1247 | -44.9478 | 78.2318 | -0.11871 | 0.0069705 | 0.04434 | 0.0049433 | -0.00065586 | 7.0582e-05 | -0.0020209 | -0.065949 | 0.0048087 | 0.00062585 | 0.043838 | -0.0025976 | -0.0025164 | 0.00073706 | -12.7396 | -0.54474 | -44.9661 | -0.83771 | -0.68665 | -45.195 | -0.74616 | 2.417 | 78.3051 | 1.799 | 78.4103 | 2.2202 | 2.0554 | 2.1835 | -0.01831 | -78.7766 | -79.0695 | 44.2612 | 44.2017 | -0.24719 | 44.22 | -0.22888 | 46.7468 | 0.073242 | 0.17853 | 47.168 | 47.1313 | 47.0032 | 0.38452 | 0.25635 | 44.2795 | 44.1284 | 0.42114 | 76.6113 | 44.4214 | 76.506 | 44.4031 | 123.2529 | -123.1979 | -76.4328 | 44.1101 | 123.3582 | 32.2083 | 47.3648
2334.4844 | 123.5504 | -117.9886 | 5.1315 | -0.12634 | 0.0050479 | 0.12359 | 0.0043023 | 0.00019874 | 0.00049778 | 0.00075627 | 0.0011902 | 0.13854 | 0.0027622 | 0.0021812 | -0.0021704 | -0.0046528 | 0.0015915 | -2.2156 | -1.5976 | -118.4052 | -1.8997 | -1.767 | -118.3411 | -1.799 | 0.58136 | 5.1498 | 4.6921 | 5.0812 | 4.9667 | 4.9942 | 5.1315 | -0.41657 | -6.7291 | -7.0312 | 116.2216 | 116.1896 | -0.35248 | 116.6061 | 0.064087 | 122.6807 | 0.01831 | -0.050354 | 122.9553 | 123.1201 | 122.9828 | 0.43945 | 0.30212 | 116.6382 | 116.5054 | 0.27466 | 0.3891 | 116.8076 | 0.45776 | 116.391 | 123.1384 | -123.5367 | -0.43945 | 116.0889 | 123.0698 | 115.773 | 118.5699
2335.4844 | 123.5001 | -118.3594 | 4.8752 | 0.010986 | 0.0052615 | 0.1206 | 0.0036615 | 0.00083954 | -0.002493 | -0.00073913 | -0.029327 | 0.13683 | 0.0019076 | 0.0013266 | -0.0049476 | -0.0023028 | 0.0043687 | -3.3051 | -2.7283 | -118.6844 | -3.1036 | -2.9617 | -118.277 | -2.9984 | 0.65918 | 4.9347 | 4.39 | 4.7745 | 4.6417 | 4.66 | 4.7562 | -0.32501 | -7.6035 | -7.9788 | 115.3976 | 115.361 | 0.082397 | 115.686 | 0.40741 | 122.7493 | 0.059509 | -0.10071 | 123.0011 | 123.1155 | 123.0194 | 0.36621 | 0.27008 | 115.7227 | 115.5807 | 0.25177 | 0.38452 | 115.9561 | 0.54474 | 115.6311 | 123.2941 | -123.5596 | -0.48523 | 115.2557 | 123.1338 | 115.0543 | 119.0186
2336.5469 | 122.7631 | -45.2042 | 78.0167 | -0.11871 | 0.0033389 | 0.044553 | 0.0053705 | 0.0019077 | -0.00057042 | -0.0015935 | -0.10562 | 0.0016043 | 0.0023348 | 0.045547 | -0.001316 | -0.001662 | 0.0039413 | -2.0416 | -1.3962 | -44.9295 | -1.8082 | -1.6617 | -45.5109 | -1.712 | 2.9388 | 77.8976 | 2.4582 | 78.1357 | 2.8107 | 2.71 | 2.8198 | 0.27466 | -79.4128 | -79.8248 | 43.5425 | 43.4921 | -0.3067 | 43.2175 | -0.58136 | 47.6624 | -0.11902 | 0.11902 | 48.0148 | 48.024 | 47.9141 | 0.36163 | 0.25177 | 43.2678 | 43.1213 | 0.35248 | 75.6775 | 43.5333 | 75.4395 | 43.808 | 123.1018 | -122.9462 | -75.5585 | 43.396 | 123.3398 | 43.1625 | 48.143
2337.4844 | 123.4543 | -45.1813 | 78.0121 | 0.010986 | 0.0026981 | 0.042417 | 0.0023797 | -1.486e-05 | 0.0019932 | -0.0022345 | 0.010345 | 0.0016043 | 0.003403 | 0.034225 | -0.0038794 | -0.0025164 | -0.0020401 | -2.1194 | -1.4969 | -45.4285 | -1.7944 | -1.6479 | -45.3644 | -1.6663 | 2.98 | 78.0899 | 2.5269 | 78.1631 | 2.9343 | 2.9068 | 2.9205 | -0.24719 | -79.509 | -79.8065 | 43.5333 | 43.515 | -0.18311 | 43.7622 | 0.064087 | 47.7081 | 0.07782 | 0.15106 | 48.1155 | 48.1018 | 48.0881 | 0.39368 | 0.37994 | 43.7805 | 43.634 | 0.40741 | 75.6363 | 43.9316 | 75.5631 | 43.6844 | 123.2712 | -123.4406 | -75.4852 | 43.3868 | 123.3444 | 43.0618 | 48.1613
2338.5469 | 122.9736 | -44.4397 | 78.6758 | -0.10345 | 0.0020573 | 0.042631 | -0.011933 | -0.0038603 | -0.0089016 | -0.015906 | -0.33145 | -0.011427 | -0.0036466 | 0.036361 | -0.010715 | -0.020034 | -0.012508 | -0.54016 | -0.14191 | -44.7052 | -0.55389 | -0.44403 | -44.9112 | -0.46692 | 2.8564 | 78.7308 | 1.9089 | 78.6621 | 2.211 | 2.037 | 2.1881 | -0.2655 | -78.8177 | -79.2297 | 43.9957 | 43.9728 | -0.4715 | 44.2383 | -0.20599 | 46.3486 | 0.054932 | -0.013733 | 46.6507 | 46.6278 | 46.4767 | 0.27923 | 0.12817 | 44.2612 | 44.1513 | 0.30212 | 76.7532 | 44.5633 | 76.8219 | 44.2978 | 123.1705 | -123.381 | -76.767 | 43.8858 | 123.1018 | 43.8995 | 47.2961
2339.4844 | 123.4451 | -44.7601 | 78.4287 | -0.065308 | 0.0029117 | 0.043272 | 0.0047295 | -0.0015103 | 0.0011386 | -0.0030889 | 0.019501 | 0.0022453 | 0.0023348 | 0.039779 | -0.0021704 | -0.0023028 | 0.0028733 | -0.82855 | -0.55389 | -45.0348 | -0.85602 | -0.68665 | -44.957 | -0.73242 | 2.7786 | 78.5019 | 1.9684 | 78.5522 | 2.417 | 2.2797 | 2.3621 | -0.27466 | -78.9825 | -79.2847 | 44.0735 | 44.0277 | -0.19684 | 44.3024 | 0.07782 | 46.7285 | 0.073242 | 0.1236 | 47.1771 | 47.1222 | 47.0398 | 0.39368 | 0.31128 | 44.3481 | 44.1788 | 0.44861 | 76.5839 | 44.4809 | 76.5335 | 44.2062 | 123.262 | -123.4634 | -76.4603 | 43.9041 | 123.3124 | 43.9316 | 47.5388
2340.5469 | 123.1522 | -44.696 | 78.5019 | -0.095825 | 0.0024845 | 0.042844 | 0.0064385 | 0.0029757 | 0.00028418 | -0.0013799 | -0.084259 | 0.0035269 | 0.004471 | 0.04341 | -0.003025 | -0.00059378 | 0.0033005 | -1.0529 | -0.66834 | -44.9936 | -1.0757 | -0.94299 | -45.0211 | -0.97504 | 2.3529 | 78.5889 | 2.4124 | 78.5843 | 2.7649 | 2.6596 | 2.7603 | -0.29755 | -79.1702 | -79.5776 | 43.7531 | 43.721 | -0.32501 | 44.0186 | -0.027466 | 47.1085 | 0.086975 | 0.082398 | 47.4609 | 47.4564 | 47.3557 | 0.3479 | 0.24719 | 44.0506 | 43.9178 | 0.35248 | 76.1719 | 44.3253 | 76.1765 | 44.0277 | 123.2849 | -123.4955 | -76.0895 | 43.6203 | 123.2803 | 43.6432 | 47.0489
2341.4844 | 123.5229 | -118.222 | 4.985 | -0.057678 | 0.0033389 | 0.11889 | 0.0060113 | -0.00044226 | 0.0022068 | -0.0035163 | -0.044586 | 0.13725 | 0.0036166 | -0.0048684 | -0.0028112 | -0.0025164 | -0.0031081 | -3.4424 | -3.1128 | -118.6249 | -3.6713 | -3.3737 | -118.3502 | -3.4058 | 0.80566 | 4.9805 | 4.4952 | 4.8294 | 4.7562 | 4.7882 | 4.8752 | -0.40283 | -8.0978 | -8.6563 | 114.8483 | 114.8163 | -0.12817 | 115.2191 | 0.27466 | 122.7173 | -0.004577 | -0.15564 | 122.9782 | 123.0972 | 123.0103 | 0.37994 | 0.29297 | 115.2512 | 114.9536 | 0.26093 | 0.33417 | 115.5121 | 0.48523 | 115.1093 | 123.2025 | -123.6099 | -0.48981 | 114.5508 | 123.0515 | 114.7797 | 119.0277
2342.5469 | 123.4314 | -118.222 | 5.04 | -0.027161 | 0.0037661 | 0.12103 | 0.0072931 | -0.012405 | 0.0011386 | -0.013343 | -0.33755 | 0.1458 | 0.0036166 | -0.020463 | -0.0098608 | 0.015641 | -0.0060989 | -2.3804 | -1.9867 | -118.5562 | -2.4261 | -2.2751 | -118.2129 | -2.3621 | 0.8606 | 5.1224 | 4.5364 | 4.8523 | 4.6921 | 4.6875 | 4.8248 | -0.33417 | -7.0267 | -7.4661 | 115.947 | 115.86 | 0.009155 | 116.1942 | 0.34332 | 122.7585 | 0.082397 | -0.18768 | 122.9141 | 123.0469 | 122.9095 | 0.28839 | 0.15106 | 116.2811 | 116.1301 | 0.15564 | 0.31586 | 116.5695 | 0.58594 | 116.2354 | 123.3444 | -123.5962 | -0.50354 | 115.7959 | 123.0743 | 115.8417 | 119.0826
2343.5 | 123.3902 | -118.158 | 5.159 | -0.03479 | 0.0048343 | 0.11932 | 0.0064385 | -0.0038603 | 0.00092498 | -0.0088567 | -0.22464 | 0.12337 | 0.0014804 | -0.0014504 | -0.0090064 | -0.0099934 | -0.010371 | -3.0899 | -2.3254 | -118.4647 | -2.7786 | -2.6184 | -118.0939 | -2.6962 | 0.97046 | 5.246 | 4.5502 | 4.9576 | 4.715 | 4.7012 | 4.8569 | -0.3067 | -7.4844 | -7.9376 | 115.5396 | 115.4617 | 0.064087 | 115.7684 | 0.37079 | 122.7081 | 0.086975 | -0.20142 | 122.8729 | 123.0148 | 122.8592 | 0.3067 | 0.15106 | 115.8463 | 115.686 | 0.1648 | 0.40741 | 116.1392 | 0.6958 | 115.8325 | 123.4039 | -123.6237 | -0.60883 | 115.3793 | 123.1155 | 115.0681 | 119.1284
2344.5469 | 123.4634 | -118.2495 | 5.0308 | 0.072021 | 0.0037661 | 0.12018 | 0.0066523 | 0.0063937 | 0.002634 | -0.0028753 | -0.15445 | 0.12572 | 0.0057528 | -0.00059601 | -0.0090064 | -0.015761 | -0.015926 | -4.2572 | -2.1927 | -118.634 | -2.6047 | -2.4353 | -118.2404 | -2.5177 | 0.78278 | 5.1315 | 4.5639 | 4.8752 | 4.7699 | 4.7424 | 4.8706 | -0.38452 | -7.2235 | -7.6355 | 115.8142 | 115.7318 | 0.009156 | 116.1163 | 0.39368 | 122.8134 | 0.10071 | -0.15564 | 123.0194 | 123.1201 | 122.9919 | 0.3067 | 0.17853 | 116.1987 | 116.0294 | 0.20599 | 0.31128 | 116.4413 | 0.56763 | 116.0568 | 123.381 | -123.6649 | -0.46692 | 115.6448 | 123.1247 | 113.9923 | 119.0323
2345.4844 | 123.5367 | -118.2541 | 4.9988 | -0.042419 | 0.0054751 | 0.11975 | 0.0030207 | 0.00062594 | 0.00049778 | -0.0039435 | 0.019501 | 0.13768 | 0.0040438 | -0.0042276 | -0.0025976 | -0.0044392 | 0.0026597 | -2.7374 | -2.1286 | -118.5333 | -2.4719 | -2.2797 | -118.103 | -2.3209 | 0.87433 | 5.0903 | 4.5776 | 4.9484 | 4.8843 | 4.8752 | 4.9576 | -0.27924 | -7.1274 | -7.4707 | 115.9744 | 115.9332 | 0.15106 | 116.2125 | 0.4303 | 122.8317 | 0.091553 | -0.050354 | 123.1384 | 123.2117 | 123.1293 | 0.37994 | 0.29755 | 116.2537 | 116.0614 | 0.3067 | 0.37079 | 116.4047 | 0.51269 | 116.1255 | 123.3444 | -123.5321 | -0.42114 | 115.7822 | 123.2025 | 115.5167 | 119.1284
2346.5469 | 123.4955 | -118.5013 | 4.7836 | -0.088196 | 0.0039799 | 0.12274 | 0.0047295 | 0.0016939 | 0.0019932 | -0.00073913 | -0.087311 | 0.13854 | 0.0040438 | 0.002822 | -0.0062292 | -0.0029438 | -0.00033114 | -2.8381 | -2.2568 | -118.7668 | -2.5406 | -2.3895 | -118.3777 | -2.4628 | 0.89264 | 4.8614 | 4.3442 | 4.7333 | 4.6143 | 4.6188 | 4.7424 | -0.2655 | -7.0404 | -7.3242 | 116.1118 | 116.0385 | 0.1236 | 116.304 | 0.3891 | 122.8455 | 0.07782 | -0.050354 | 123.1155 | 123.2437 | 123.1201 | 0.39825 | 0.27466 | 116.3773 | 116.2262 | 0.27008 | 0.3891 | 116.51 | 0.51727 | 116.2445 | 123.3627 | -123.5504 | -0.43945 | 115.9607 | 123.2346 | 115.6631 | 119.3939
2347.4844 | 123.3307 | -118.5654 | 4.7195 | -0.019531 | 0.0024845 | 0.11953 | 0.0060113 | -0.00065586 | 7.0582e-05 | -0.0013799 | -0.020172 | 0.13768 | 0.0010532 | -0.003373 | -0.0053748 | -0.0025164 | -0.0011855 | -2.5406 | -2.1835 | -118.8217 | -2.4811 | -2.2888 | -118.3273 | -2.3483 | 1.0071 | 4.7974 | 4.3076 | 4.6509 | 4.4861 | 4.7607 | 4.7836 | -0.25635 | -6.9031 | -7.2006 | 116.2766 | 116.217 | 0.23804 | 116.4734 | 0.49438 | 122.8729 | 0.07782 | -0.068664 | 123.0515 | 123.349 | 123.3261 | 0.47607 | 0.45319 | 116.5329 | 116.3406 | 0.17853 | 0.34332 | 116.6382 | 0.48981 | 116.3818 | 123.3627 | -123.5413 | -0.41199 | 116.0843 | 123.2162 | 116.0248 | 119.5724
2348.5625 | 123.4039 | -118.4143 | 4.9118 | -0.027161 | 0.0031253 | 0.12039 | 0.0072931 | -0.0017239 | -0.0014248 | -0.0020209 | -0.038483 | 0.13982 | 0.004471 | 0.00068579 | -0.0025976 | -0.0029438 | 0.0018051 | -3.0487 | -1.8173 | -118.7393 | -2.2659 | -2.2018 | -117.9474 | -2.2202 | 0.41199 | 4.9301 | 4.3533 | 4.6463 | 4.5685 | 4.3442 | 4.3991 | -0.32501 | -6.7291 | -7.1777 | 116.2125 | 116.1942 | 0.46692 | 116.5192 | 0.79193 | 122.7676 | 0.018311 | -0.2655 | 122.9828 | 122.8134 | 122.7585 | 0.045776 | -0.009156 | 116.5375 | 116.4734 | 0.21515 | 0.29297 | 116.922 | 0.57678 | 116.597 | 123.3444 | -123.6511 | -0.55847 | 116.1484 | 123.0606 | 115.3656 | 118.8263
2349.4844 | 123.5458 | -118.4692 | 4.7562 | -0.050049 | 0.0033389 | 0.11996 | 0.0043023 | -0.00022866 | -0.0014248 | -0.0041571 | 0.025604 | 0.13896 | 0.0025484 | -0.0070046 | -0.0019568 | -0.0059344 | 0.0033005 | -2.5085 | -1.8997 | -118.8034 | -2.2156 | -2.0187 | -118.2541 | -2.1103 | 0.70953 | 4.834 | 4.3121 | 4.6646 | 4.5731 | 4.39 | 4.5868 | -0.33417 | -6.6559 | -6.9717 | 116.4505 | 116.3589 | 0.21515 | 116.6931 | 0.54932 | 122.7814 | 0.077819 | -0.091553 | 123.0423 | 123.056 | 122.8592 | 0.27466 | 0.07782 | 116.7847 | 116.5878 | 0.26092 | 0.35248 | 116.9037 | 0.52185 | 116.5695 | 123.3032 | -123.5596 | -0.44403 | 116.2537 | 123.1339 | 115.9607 | 119.1788
2350.5469 | 123.4909 | -122.5937 | 0.6546 | -0.11108 | -0.0096921 | 0.0073827 | 0.0092157 | 0.0021213 | -0.00035682 | -0.0011663 | 0.065277 | 0.013994 | 0.0038302 | 0.001113 | -0.0051612 | -0.0020892 | 0.0011643 | -0.027466 | 0.21973 | -0.27924 | -0.07782 | -0.032043 | -0.18768 | -0.16479 | 0.14191 | 0.75531 | 0.28381 | 0.56305 | 0.53558 | 0.23804 | 0.42572 | 122.3145 | -0.43488 | -0.73242 | 122.5616 | 122.4289 | 122.406 | 0.11444 | 0.091553 | 122.8775 | 0.10071 | -0.091553 | 123.1293 | 123.0194 | 122.8317 | 0.14191 | -0.045776 | 0.24719 | 0.20142 | 0.25177 | 0.27924 | 0.49896 | 0.4715 | 122.8134 | 123.349 | -0.93384 | -0.37079 | 122.5159 | 123.1567 | 122.5662 | 122.7356
2351.4844 | 123.4039 | -122.4976 | 0.71869 | 0.010986 | -0.0094785 | 0.0037511 | 0.0064385 | -0.0038603 | -0.001852 | -0.00073913 | 0.11411 | 0.013567 | 0.0040438 | -0.0052958 | -0.0043066 | -0.0018756 | -0.00033114 | -0.009155 | 0.2243 | -0.27008 | -0.073242 | 0.11444 | -0.027466 | 0.018311 | 0.2655 | 0.81482 | 0.36621 | 0.55389 | 0.52643 | 0.61798 | 0.70496 | 122.2275 | -0.49439 | -0.79193 | 122.612 | 122.5159 | 122.4701 | 0.28839 | 0.24262 | 122.8638 | 0.09613 | -0.1648 | 123.024 | 123.2025 | 123.1155 | 0.33875 | 0.25177 | 0.38452 | 0.19684 | 0.16022 | 0.18768 | 0.49439 | 0.44861 | 122.7219 | 123.3124 | -0.98877 | -0.35248 | 122.4243 | 123.0515 | 122.4884 | 122.7631
2352.5469 | 123.4222 | -122.5113 | 0.75531 | -0.072937 | -0.0084103 | 0.0043921 | 0.0096429 | 0.0010531 | 0.00028418 | -0.0020209 | 0.068329 | 0.015276 | -1.4954e-05 | -0.0070046 | -0.002384 | -0.0020892 | -0.0011855 | -0.045776 | 0.20142 | -0.29297 | -0.07782 | 0.091553 | -0.073242 | -0.013733 | 0.23346 | 0.8194 | 0.39825 | 0.62714 | 0.60425 | 0.58136 | 0.6958 | 122.2183 | -0.55389 | -0.83313 | 122.6028 | 122.4976 | 122.4381 | 0.27924 | 0.21973 | 122.9095 | 0.064087 | -0.12817 | 123.1155 | 123.2071 | 123.0927 | 0.29755 | 0.18311 | 0.38452 | 0.21515 | 0.20599 | 0.22888 | 0.49438 | 0.42114 | 122.7127 | 123.3307 | -1.0483 | -0.35706 | 122.4335 | 123.1384 | 122.4655 | 122.7448
2353.5 | 123.3719 | -122.5342 | 0.7782 | -0.057678 | -0.0060605 | 0.0052465 | -0.0057379 | -0.016464 | 0.00071138 | -0.0058661 | -0.28873 | 0.0052359 | 0.00083965 | -0.0087136 | -0.022892 | 0.015641 | -0.015712 | 0.10986 | 0.25177 | -0.28381 | -0.12817 | -0.21057 | -0.46234 | 0.11902 | 0.18768 | 0.88806 | 0.3891 | 0.5722 | 0.54016 | 0.3891 | 0.36621 | 122.2504 | -0.52643 | -0.90637 | 122.3236 | 122.6532 | 122.0718 | 0.40283 | -0.17853 | 122.9233 | 0.10986 | -0.20599 | 123.0743 | 122.9004 | 122.9233 | -0.022888 | 0 | 0.073242 | 0.15564 | 0.15106 | 0.18311 | 0.53558 | 0.49896 | 122.7859 | 123.4222 | -1.062 | -0.3891 | 122.406 | 123.1064 | 122.644 | 122.7219
2354.5469 | 123.3627 | -122.5571 | 0.80566 | -0.011902 | -0.010333 | 0.0043921 | 0.0083611 | -0.0023649 | -0.00099762 | -0.0026617 | -0.090363 | 0.017412 | 0.0025484 | -0.00038241 | -0.0028112 | -0.0031574 | -0.00011754 | -0.091553 | 0.27008 | -0.29755 | -0.17853 | -0.045776 | -0.31128 | -0.32959 | 0.11444 | 0.88348 | 0.37537 | 0.54932 | 0.53101 | 0.48981 | 0.63629 | 122.2595 | -0.53558 | -0.98419 | 122.5113 | 122.2275 | 122.2458 | -0.032044 | -0.013733 | 122.9324 | 0.07782 | -0.25635 | 123.0881 | 123.1934 | 123.0469 | 0.26093 | 0.11444 | 0.25177 | 0.11902 | 0.15564 | 0.17395 | 0.56763 | 0.50812 | 122.8271 | 123.4406 | -1.1032 | -0.4303 | 122.3785 | 123.1064 | 122.4655 | 122.6715
2355.4844 | 123.4589 | -122.5204 | 0.78278 | -0.019531 | -0.0067013 | 0.0033239 | 0.0083611 | -0.00044226 | 0.00092498 | -0.0018073 | 0.068329 | 0.0077995 | 0.0029758 | -0.005723 | -0.0045202 | -0.0040118 | -0.0011855 | 0.022888 | 0.20599 | -0.28381 | -0.068665 | 0.11444 | -0.036621 | 0.050354 | 0.46234 | 0.8606 | 0.40741 | 0.63171 | 0.71411 | 0.63171 | 0.71869 | 122.2366 | -0.57678 | -0.85144 | 122.6349 | 122.5708 | 122.4838 | 0.33417 | 0.24719 | 122.9279 | 0.07782 | -0.15106 | 123.2346 | 123.2391 | 123.1522 | 0.31128 | 0.2243 | 0.39825 | 0.21515 | 0.3067 | 0.2243 | 0.48981 | 0.45319 | 122.7264 | 123.381 | -1.0666 | -0.37537 | 122.4518 | 123.1522 | 122.5433 | 122.9828
2356.4844 | 123.4543 | -122.4792 | 0.8194 | -0.065308 | -0.0094785 | 0.0031103 | 0.0064385 | -0.0064237 | -0.00057042 | -0.0013799 | 0.074432 | 0.01549 | 0.0042574 | -0.002305 | -0.003025 | -0.003371 | -0.0022537 | -0.045776 | 0.21057 | -0.28839 | -0.10529 | 0.064087 | -0.064087 | 0.041199 | 0.24719 | 0.87433 | 0.4303 | 0.67291 | 0.6958 | 0.65918 | 0.74616 | 122.1909 | -0.60883 | -0.92468 | 122.5433 | 122.5204 | 122.4152 | 0.32959 | 0.2243 | 122.9095 | 0.054932 | -0.14648 | 123.175 | 123.2254 | 123.1384 | 0.31586 | 0.22888 | 0.35248 | 0.18311 | 0.2655 | 0.24261 | 0.49896 | 0.44403 | 122.6898 | 123.3536 | -1.1078 | -0.3891 | 122.374 | 123.1522 | 122.4335 | 122.7264
2357.5469 | 123.381 | -122.5388 | 0.82855 | 0.010986 | -0.0086239 | 0.0048193 | 0.0092157 | 0.0029757 | -0.0012112 | -0.0013799 | -0.072052 | 0.016131 | 0.0042574 | 0.0023948 | -0.004093 | 0.00047422 | 0.0013779 | -0.068665 | 0.23804 | -0.32044 | -0.16022 | -0.054932 | -0.17853 | -0.13733 | 0.14648 | 0.89722 | 0.39368 | 0.60425 | 0.59509 | 0.53101 | 0.67291 | 122.2183 | -0.59051 | -0.98877 | 122.4838 | 122.4014 | 122.3602 | 0.18311 | 0.14191 | 122.9324 | 0.068665 | -0.2243 | 123.1339 | 123.2117 | 123.0698 | 0.27924 | 0.13733 | 0.2655 | 0.16022 | 0.20142 | 0.21057 | 0.55847 | 0.50354 | 122.7768 | 123.436 | -1.149 | -0.43487 | 122.3785 | 123.143 | 122.4701 | 122.6852
2358.5 | 123.3765 | -122.5204 | 0.87891 | -0.080566 | -0.014605 | -0.011843 | 0.011352 | -0.0045011 | -0.011038 | -0.0090703 | -0.28567 | 0.012713 | -0.003433 | -0.00016881 | -0.0047338 | -0.013625 | -0.0075943 | 0.004578 | 0.25635 | -0.28839 | -0.1236 | 0.013733 | -0.1831 | -0.26093 | 0.20599 | 0.88806 | 0.40741 | 0.81482 | 0.63629 | 0.64545 | 0.6958 | 122.2321 | -0.62256 | -1.0025 | 122.5342 | 122.2595 | 122.3373 | 0.027466 | 0.10529 | 122.9279 | 0.009156 | -0.064087 | 123.1567 | 123.2162 | 123.1659 | 0.28839 | 0.23804 | 0.30212 | 0.1648 | 0.22888 | 0.40741 | 0.54474 | 0.48065 | 122.7768 | 123.4085 | -1.1673 | -0.4715 | 122.3969 | 123.3353 | 122.525 | 122.7264
2359.4844 | 123.4314 | -122.5204 | 0.80109 | -0.011902 | -0.01311 | 0.0050329 | 0.0083611 | -0.00086946 | -0.00035682 | -0.0024481 | 0.031708 | 0.016131 | 0.0042574 | -0.0016642 | -0.002384 | -0.0031574 | -0.00054474 | 0.11902 | 0.23804 | -0.29297 | -0.054932 | 0.10986 | -0.059509 | 0.054932 | 0.27008 | 0.87891 | 0.41199 | 0.62714 | 0.66834 | 0.64545 | 0.70953 | 122.2275 | -0.56305 | -0.85602 | 122.6303 | 122.5754 | 122.4609 | 0.3479 | 0.23346 | 122.9324 | 0.07782 | -0.17395 | 123.1888 | 123.23 | 123.1659 | 0.29755 | 0.23346 | 0.40283 | 0.23804 | 0.25635 | 0.21515 | 0.53101 | 0.46692 | 122.7585 | 123.3994 | -1.0941 | -0.3891 | 122.4655 | 123.1476 | 122.6395 | 122.7905
2360.5469 | 123.4451 | -122.612 | 0.75989 | -0.027161 | -0.0069149 | 0.0041785 | 0.0079339 | 0.0023349 | -0.0016384 | -0.00095273 | 0.034759 | 0.016344 | 0.0040438 | -0.0027322 | -0.0038794 | -0.0025164 | 0.0020187 | -0.036621 | 0.22888 | -0.28839 | -0.10529 | 0.032043 | -0.10529 | 0.027466 | 0.20599 | 0.88348 | 0.42114 | 0.63171 | 0.66376 | 0.60425 | 0.54932 | 122.3236 | -0.53101 | -0.86517 | 122.644 | 122.6395 | 122.5067 | 0.31586 | 0.18311 | 123.0331 | 0.1236 | -0.12817 | 123.2758 | 123.1613 | 123.2162 | 0.12817 | 0.18311 | 0.32043 | 0.18311 | 0.24261 | 0.21057 | 0.51727 | 0.46234 | 122.8409 | 123.4955 | -1.0483 | -0.33875 | 122.5067 | 123.2437 | 122.5754 | 122.818
2361.4844 | 123.3536 | -122.5296 | 0.83313 | -0.019531 | -0.0090511 | 0.0035375 | 0.010284 | 0.00041234 | -0.0016384 | -0.00095273 | 0.025604 | 0.015062 | 0.0023348 | 0.0026084 | -0.0036658 | -0.0027302 | 0.0013779 | -0.036621 | 0.27008 | -0.28839 | -0.14191 | -0.018311 | -0.10529 | -0.018311 | 0.17853 | 0.92468 | 0.39825 | 0.55389 | 0.5722 | 0.54016 | 0.63171 | 122.2412 | -0.56305 | -0.97504 | 122.5113 | 122.5113 | 122.4243 | 0.27008 | 0.18311 | 122.9279 | 0.091553 | -0.27924 | 123.1018 | 123.1613 | 123.0698 | 0.23346 | 0.14191 | 0.27008 | 0.14648 | 0.17395 | 0.15564 | 0.55847 | 0.52643 | 122.7997 | 123.4543 | -1.1215 | -0.43488 | 122.3877 | 123.0835 | 122.493 | 122.7081
2362.4844 | 123.4177 | -122.5113 | 0.8194 | -0.0042723 | -0.0092649 | 0.0033239 | 0.0075067 | 0.00062594 | 0.0011386 | -0.0024481 | 0.037811 | 0.016131 | 0.0029758 | 0.0021812 | -0.0032386 | -0.00080758 | 9.6064e-05 | 0.004578 | 0.23804 | -0.26093 | -0.050354 | 0.10986 | -0.022888 | 0.054932 | 0.3067 | 0.88348 | 0.44403 | 0.59967 | 0.66834 | 0.67291 | 0.77362 | 122.2504 | -0.58136 | -0.86975 | 122.6212 | 122.5662 | 122.4884 | 0.31586 | 0.23804 | 122.9553 | 0.064087 | -0.21973 | 123.1796 | 123.2849 | 123.1842 | 0.32959 | 0.22888 | 0.37079 | 0.21057 | 0.2243 | 0.15564 | 0.49896 | 0.43945 | 122.7493 | 123.3948 | -1.0803 | -0.37537 | 122.4609 | 123.111 | 122.5159 | 122.818
2363.5469 | 123.4726 | -122.493 | 0.8194 | -0.019531 | -0.0090511 | 0.0035375 | 0.0075067 | -0.00044226 | 0.00028418 | -0.0013799 | 0.046967 | 0.015917 | 0.001694 | 0.0043174 | -0.0043066 | -0.0025164 | -0.00075834 | 0.009155 | 0.21057 | -0.24261 | -0.027466 | 0.14648 | -0.041199 | 0.09613 | 0.35248 | 0.88348 | 0.44861 | 0.66376 | 0.71411 | 0.6958 | 0.75531 | 122.2504 | -0.60883 | -0.84686 | 122.6395 | 122.5891 | 122.4518 | 0.33874 | 0.20142 | 122.9416 | 0.064087 | -0.15564 | 123.2071 | 123.2483 | 123.1888 | 0.3067 | 0.24719 | 0.3891 | 0.21515 | 0.2655 | 0.21515 | 0.45319 | 0.43488 | 122.7036 | 123.3765 | -1.062 | -0.37079 | 122.4655 | 123.1567 | 122.5021 | 122.8455
2364.4844 | 123.3948 | -122.5296 | 0.85602 | -0.011902 | -0.0073423 | 0.0031103 | 0.010284 | 0.0019077 | 0.00092498 | -0.0033025 | 0.019501 | 0.013567 | 0.001694 | -0.0012368 | -0.0038794 | -0.0031574 | 0.0011643 | 0.018311 | 0.23346 | -0.29297 | -0.068665 | 0.068665 | -0.068665 | 0.027466 | 0.23804 | 0.90179 | 0.4303 | 0.60425 | 0.62714 | 0.59509 | 0.68665 | 122.2366 | -0.62256 | -0.92468 | 122.5983 | 122.5571 | 122.4609 | 0.32043 | 0.2243 | 122.9599 | 0.045776 | -0.25177 | 123.1567 | 123.2162 | 123.1247 | 0.25635 | 0.16479 | 0.36163 | 0.2243 | 0.19684 | 0.17395 | 0.52643 | 0.4715 | 122.7631 | 123.4314 | -1.149 | -0.42572 | 122.4609 | 123.1338 | 122.5479 | 122.7676
2365.4844 | 123.3627 | -122.5662 | 0.86517 | 0.15594 | -0.0079831 | 0.0054601 | 0.0092157 | 0.00041234 | -0.0020658 | -0.0035163 | -0.087311 | 0.015276 | 0.0021212 | 0.0030356 | -0.004093 | -0.0035846 | -0.0031081 | -0.13733 | 0.29297 | -0.25177 | -0.16479 | -0.032043 | -0.1236 | -0.045776 | 0.15564 | 0.93842 | 0.4303 | 0.5722 | 0.59509 | 0.53558 | 0.65002 | 122.3145 | -0.5722 | -1.03 | 122.5342 | 122.5204 | 122.4426 | 0.20599 | 0.12817 | 122.9965 | 0.073243 | -0.29297 | 123.1613 | 123.2162 | 123.1018 | 0.21973 | 0.10529 | 0.21973 | 0.086975 | 0.16479 | 0.14191 | 0.54474 | 0.50812 | 122.8592 | 123.5046 | -1.1169 | -0.43487 | 122.4014 | 123.1384 | 122.4289 | 122.7219
2366.5469 | 123.4314 | -122.5067 | 0.84228 | -0.088196 | -0.0079831 | 0.0050329 | 0.0057977 | -0.00065586 | -0.0016384 | -0.0015935 | 0.040863 | 0.015703 | 0.0038302 | -0.002305 | -0.002384 | -0.0010212 | 0.0018051 | -0.059509 | 0.24261 | -0.2655 | -0.10529 | 0.027466 | -0.11902 | 0.018311 | 0.20599 | 0.90637 | 0.44403 | 0.66376 | 0.68665 | 0.63171 | 0.73242 | 122.2412 | -0.59967 | -0.94757 | 122.5342 | 122.525 | 122.3877 | 0.28381 | 0.14648 | 122.9507 | 0.064087 | -0.17853 | 123.1934 | 123.2391 | 123.1384 | 0.28839 | 0.18768 | 0.29297 | 0.16022 | 0.24261 | 0.21973 | 0.50812 | 0.46234 | 122.7493 | 123.4131 | -1.1078 | -0.39825 | 122.4014 | 123.1705 | 122.4472 | 122.7127
2367.4844 | 123.3902 | -122.5433 | 0.85602 | 0.010986 | -0.0084103 | 0.0037511 | 0.0072931 | 0.0012667 | -0.0014248 | -0.0020209 | -0.10257 | 0.012713 | 0.003403 | 0.0019674 | -0.0025976 | -0.0020892 | 0.00095066 | -0.050354 | 0.27924 | -0.28839 | -0.14648 | -0.050354 | -0.15564 | -0.064087 | 0.14648 | 0.93842 | 0.41199 | 0.58594 | 0.59967 | 0.56763 | 0.66376 | 122.2549 | -0.57678 | -1.0025 | 122.493 | 122.4792 | 122.3877 | 0.2243 | 0.13275 | 122.9553 | 0.082398 | -0.27008 | 123.143 | 123.2071 | 123.111 | 0.25177 | 0.15564 | 0.23804 | 0.14191 | 0.18768 | 0.17395 | 0.56763 | 0.52643 | 122.8226 | 123.4818 | -1.1444 | -0.44403 | 122.3969 | 123.1293 | 122.493 | 122.6898
2368.5469 | 123.5046 | -122.4838 | 0.84228 | -0.042419 | -0.0086239 | 0.0039649 | 0.0083611 | -0.0015103 | -0.00099762 | -0.0020209 | 0.043915 | 0.015703 | 0.003403 | -0.0046548 | -0.004093 | -0.0029438 | 0.0013779 | 0 | 0.23346 | -0.23804 | -0.050354 | 0.13733 | -0.022888 | 0.073242 | 0.33417 | 0.91095 | 0.45319 | 0.70496 | 0.75073 | 0.72784 | 0.78278 | 122.2458 | -0.60883 | -0.89264 | 122.6212 | 122.5571 | 122.4609 | 0.31128 | 0.21515 | 122.937 | 0.068665 | -0.13733 | 123.2346 | 123.2666 | 123.2117 | 0.32959 | 0.27466 | 0.37537 | 0.18768 | 0.29755 | 0.25177 | 0.4715 | 0.45776 | 122.7173 | 123.3948 | -1.0803 | -0.3891 | 122.4335 | 123.1888 | 122.4838 | 122.818
2369.4844 | 123.4085 | -122.5342 | 0.8606 | -0.03479 | -0.0069149 | 0.0031103 | 0.0098565 | 0.0010531 | -0.0012112 | -0.0020209 | -0.19107 | 0.010576 | 0.00083965 | 0.00047219 | -0.004093 | -0.00080758 | -0.0024673 | -0.050354 | 0.25635 | -0.30212 | -0.15106 | -0.036621 | -0.14648 | -0.068665 | 0.1831 | 0.94299 | 0.41199 | 0.63171 | 0.65002 | 0.56763 | 0.6958 | 122.2321 | -0.60425 | -1.0117 | 122.4976 | 122.4655 | 122.3877 | 0.23346 | 0.15564 | 122.9462 | 0.082397 | -0.22888 | 123.1842 | 123.23 | 123.1018 | 0.28381 | 0.15564 | 0.2655 | 0.15106 | 0.23804 | 0.21973 | 0.55847 | 0.53101 | 122.7905 | 123.4772 | -1.1627 | -0.44861 | 122.3831 | 123.1659 | 122.4838 | 122.7173
2370.4844 | 123.3673 | -122.5479 | 0.86517 | -0.011902 | -0.0094785 | 0.0050329 | 0.010284 | 0.0040439 | 0.00028418 | -0.0018073 | -0.056793 | 0.016344 | 0.0038302 | 0.00025839 | -0.0021704 | -0.0018756 | -0.0033219 | -0.050354 | 0.25177 | -0.31586 | -0.13275 | -0.027466 | -0.16937 | -0.041199 | 0.15564 | 0.97046 | 0.43488 | 0.59967 | 0.62256 | 0.59509 | 0.66834 | 122.2321 | -0.6134 | -0.99792 | 122.5204 | 122.5067 | 122.3785 | 0.27466 | 0.14648 | 122.9828 | 0.10529 | -0.2655 | 123.1705 | 123.2162 | 123.143 | 0.23346 | 0.16022 | 0.28839 | 0.18311 | 0.18768 | 0.1648 | 0.56763 | 0.53558 | 122.7997 | 123.5184 | -1.181 | -0.4303 | 122.4152 | 123.1476 | 122.4976 | 122.7036
2371.5469 | 123.5001 | -122.5159 | 0.85602 | -0.03479 | -0.0092649 | 0.0052465 | 0.0066523 | -0.00044226 | -0.0012112 | -0.0026617 | 0.040863 | 0.015703 | 0.0031894 | -0.00038241 | -0.0045202 | -0.003371 | 9.6064e-05 | 0.013733 | 0.23804 | -0.26093 | -0.050354 | 0.1236 | -0.018311 | 0.068665 | 0.35248 | 0.91553 | 0.46234 | 0.70496 | 0.74616 | 0.71411 | 0.79193 | 122.2549 | -0.61798 | -0.90637 | 122.6395 | 122.5845 | 122.4976 | 0.32959 | 0.24261 | 122.9782 | 0.059509 | -0.15106 | 123.262 | 123.3078 | 123.23 | 0.32959 | 0.25177 | 0.38452 | 0.21057 | 0.28381 | 0.24262 | 0.49896 | 0.45319 | 122.7539 | 123.4314 | -1.1169 | -0.39368 | 122.4655 | 123.2208 | 122.5296 | 122.8683
2372.4844 | 123.4039 | -122.5204 | 0.87891 | -0.0042723 | -0.010119 | 0.0018285 | 0.0092157 | 0.00062594 | -0.0029202 | -0.0022345 | -0.056793 | 0.01848 | 0.0042574 | 0.0034628 | -0.0047338 | -0.0040118 | 0.0015915 | -0.054932 | 0.28381 | -0.28381 | -0.15106 | -0.041199 | -0.14648 | -0.054932 | 0.17853 | 0.95673 | 0.44403 | 0.60425 | 0.61798 | 0.58136 | 0.69122 | 122.2366 | -0.59509 | -1.03 | 122.4792 | 122.4655 | 122.374 | 0.22888 | 0.13733 | 122.9645 | 0.07782 | -0.27466 | 123.1384 | 123.2117 | 123.1018 | 0.24719 | 0.13733 | 0.24261 | 0.13275 | 0.17395 | 0.16022 | 0.56763 | 0.51269 | 122.8043 | 123.4772 | -1.1627 | -0.43487 | 122.3694 | 123.1247 | 122.4655 | 122.699
2373.5469 | 123.3627 | -122.5113 | 0.87433 | 0.0033567 | -0.0079831 | 0.0046057 | 0.0070795 | -0.0017239 | -0.00014322 | -0.0018073 | -0.053741 | 0.015276 | 0.0042574 | 0.004531 | -0.0034522 | -0.0014484 | -0.0026809 | -0.068665 | 0.26093 | -0.3067 | -0.082397 | -0.14648 | -0.18768 | -0.018311 | 0.16022 | 1.0071 | 0.48523 | 0.61798 | 0.64545 | 0.57678 | 0.67291 | 122.2046 | -0.6134 | -0.95673 | 122.3648 | 122.493 | 122.3236 | 0.28839 | 0.11902 | 122.9965 | 0.13275 | -0.25635 | 123.1567 | 123.1842 | 123.0881 | 0.18768 | 0.091553 | 0.16022 | 0.2243 | 0.16022 | 0.13275 | 0.56763 | 0.52185 | 122.7722 | 123.5184 | -1.181 | -0.3891 | 122.4289 | 123.1293 | 122.4426 | 122.6715
2374.4844 | 123.3536 | -122.5479 | 0.87433 | 0.026245 | -0.0090511 | 0.0046057 | 0.0066523 | -0.0017239 | 0.00071138 | -0.00073913 | 0.013397 | 0.015276 | 0.0048984 | -0.0031594 | -0.0034522 | -0.0031574 | 0.0035141 | -0.032043 | 0.25177 | -0.29297 | -0.14191 | 0.009155 | -0.15564 | -0.054932 | 0.17395 | 0.97046 | 0.46692 | 0.59509 | 0.61798 | 0.57678 | 0.67291 | 122.2549 | -0.62256 | -1.0162 | 122.5571 | 122.493 | 122.3923 | 0.23804 | 0.13733 | 123.0148 | 0.09613 | -0.27924 | 123.1659 | 123.2208 | 123.1247 | 0.20599 | 0.10986 | 0.30212 | 0.15106 | 0.15106 | 0.12817 | 0.54474 | 0.50354 | 122.7997 | 123.5184 | -1.1673 | -0.40741 | 122.406 | 123.143 | 122.5159 | 122.7219
2375.5469 | 123.381 | -122.5342 | 0.88806 | 0.010986 | -0.0099057 | 0.0026831 | 0.0053705 | -0.00086946 | -0.001852 | -0.0024481 | -0.0018616 | 0.015917 | 0.0036166 | -0.00059601 | -0.003025 | -0.0023028 | 0.0022323 | -0.004578 | 0.2243 | -0.2655 | -0.082397 | 0.059509 | -0.07782 | 0 | 0.22888 | 0.95673 | 0.46234 | 0.63171 | 0.6546 | 0.62714 | 0.70038 | 122.2687 | -0.66376 | -0.97046 | 122.5937 | 122.5342 | 122.4564 | 0.2655 | 0.18768 | 122.9965 | 0.068664 | -0.25635 | 123.1888 | 123.2346 | 123.1613 | 0.23804 | 0.1648 | 0.32501 | 0.18311 | 0.19226 | 0.16937 | 0.48981 | 0.49438 | 122.7585 | 123.4909 | -1.1536 | -0.42572 | 122.4518 | 123.1659 | 122.5296 | 122.7631
2376.4844 | 123.4131 | -122.5113 | 0.89264 | 0.010986 | -0.0084103 | 0.00033334 | 0.011138 | -0.01326 | -0.003561 | -0.012061 | -0.096466 | 0.0052359 | -0.00621 | 0.0013266 | -0.0028112 | -0.0070026 | -0.00033114 | -0.027466 | 0.26093 | -0.29297 | -0.12817 | 0.032043 | -0.1236 | -0.041199 | 0.23804 | 0.94757 | 0.46234 | 0.66376 | 0.6546 | 0.64087 | 0.72784 | 122.2183 | -0.63171 | -1.0208 | 122.5433 | 122.4701 | 122.3877 | 0.25177 | 0.16937 | 122.9736 | 0.054932 | -0.22888 | 123.1659 | 123.2391 | 123.1522 | 0.2655 | 0.17853 | 0.32501 | 0.16479 | 0.19226 | 0.20142 | 0.55389 | 0.48523 | 122.7722 | 123.4589 | -1.1856 | -0.4303 | 122.3831 | 123.175 | 122.4838 | 122.7493
2377.4844 | 123.3673 | -122.5067 | 0.88348 | -0.027161 | -0.0071285 | 0.0041785 | 0.0087885 | 0.0014803 | 0.0013522 | 0.00075627 | -0.062897 | 0.018267 | 0.0055392 | 0.0051718 | -0.0032386 | -0.0040118 | -0.0037491 | -0.082397 | 0.24261 | -0.3067 | -0.18768 | -0.07782 | -0.21057 | -0.091553 | -0.059509 | 0.97046 | 0.45319 | 0.6546 | 0.58594 | 0.54932 | 0.6958 | 122.2 | -0.64087 | -1.0712 | 122.4289 | 122.4152 | 122.2961 | 0.21515 | 0.096131 | 122.9599 | 0.086975 | -0.22888 | 123.0927 | 123.2025 | 123.056 | 0.24262 | 0.09613 | 0.22888 | 0.11902 | 0.13275 | 0.20142 | 0.54932 | 0.51727 | 122.7493 | 123.4772 | -1.1902 | -0.4303 | 122.319 | 123.1613 | 122.4243 | 122.4472
2378.5469 | 123.5046 | -122.4838 | 0.86517 | 0.010986 | -0.0073423 | 0.0035375 | 0.0077203 | -0.0017239 | 0.00092498 | -0.0011663 | 0.046967 | 0.01549 | 0.0040438 | -0.0016642 | -0.0036658 | -0.003371 | 0.0015915 | -0.009155 | 0.23346 | -0.25635 | -0.036621 | 0.13733 | -0.022888 | 0.091553 | 0.32959 | 0.95673 | 0.50354 | 0.73242 | 0.79193 | 0.75073 | 0.81482 | 122.2275 | -0.63171 | -0.90179 | 122.6212 | 122.5754 | 122.4609 | 0.3479 | 0.23346 | 122.9874 | 0.091553 | -0.13275 | 123.2758 | 123.2986 | 123.2346 | 0.31128 | 0.24719 | 0.39368 | 0.21973 | 0.28839 | 0.22888 | 0.48981 | 0.45319 | 122.7173 | 123.4406 | -1.1215 | -0.36163 | 122.4472 | 123.2162 | 122.4747 | 122.8134
2379.4844 | 123.3673 | -122.525 | 0.90179 | 0.018616 | -0.0090511 | 0.0056737 | 0.0083611 | -0.0034329 | -0.0012112 | -0.0084295 | -0.096466 | 0.017412 | 0.0029758 | -0.0016642 | -0.005802 | -0.0014484 | 9.6064e-05 | -0.073242 | 0.24261 | -0.31128 | -0.17853 | -0.068665 | -0.21973 | -0.10986 | 0.086975 | 0.9613 | 0.44861 | 0.62714 | 0.60425 | 0.54474 | 0.69122 | 122.2137 | -0.65918 | -1.0803 | 122.4564 | 122.4152 | 122.3053 | 0.20142 | 0.091552 | 122.9736 | 0.05951 | -0.27466 | 123.1293 | 123.2162 | 123.0698 | 0.24262 | 0.096131 | 0.24261 | 0.13275 | 0.15564 | 0.17853 | 0.55389 | 0.5127 | 122.7676 | 123.4863 | -1.2131 | -0.45319 | 122.3465 | 123.1522 | 122.4518 | 122.612
2380.5469 | 123.3765 | -122.5479 | 0.90637 | 0.010986 | -0.0086239 | 0.0020421 | 0.0064385 | 0.0012667 | -0.00035682 | -0.0033025 | 0.022552 | 0.015062 | 0.0029758 | 0.0043174 | -0.0017432 | -0.0029438 | 0.0015915 | -0.082397 | 0.27008 | -0.30212 | -0.17853 | -0.027466 | -0.13733 | -0.050354 | 0.13733 | 0.97504 | 0.43488 | 0.6134 | 0.63629 | 0.60883 | 0.68665 | 122.2458 | -0.63629 | -1.0849 | 122.5204 | 122.4976 | 122.4106 | 0.25177 | 0.16479 | 122.9828 | 0.068665 | -0.29297 | 123.1842 | 123.2346 | 123.1567 | 0.25177 | 0.17395 | 0.27466 | 0.1236 | 0.20142 | 0.17853 | 0.57221 | 0.54016 | 122.818 | 123.5229 | -1.2085 | -0.4715 | 122.3694 | 123.1613 | 122.4655 | 122.6852
2381.4844 | 123.317 | -122.493 | 0.90637 | -0.042419 | -0.0086239 | 0.0037511 | 0.0094293 | 0.00062594 | 0.00071138 | -0.00031193 | -0.069 | 0.016771 | 0.0031894 | 0.002822 | -0.0038794 | -0.0029438 | 0.0030869 | -0.10529 | 0.26093 | -0.30212 | -0.18768 | -0.073242 | -0.21057 | -0.09613 | 0.10986 | 0.98877 | 0.44861 | 0.64545 | 0.61798 | 0.65002 | 0.70496 | 122.1909 | -0.64545 | -1.0941 | 122.4197 | 122.3969 | 122.2824 | 0.20599 | 0.091553 | 122.9416 | 0.082398 | -0.26092 | 123.111 | 123.1979 | 123.143 | 0.25635 | 0.20142 | 0.22888 | 0.11444 | 0.16937 | 0.19684 | 0.56305 | 0.54016 | 122.7539 | 123.4818 | -1.2085 | -0.45776 | 122.3053 | 123.1384 | 122.3877 | 122.6028
2382.5469 | 123.4314 | -122.5159 | 0.87891 | -0.050049 | -0.010333 | 0.0026831 | 0.0081475 | 0.0027621 | 0.00028418 | 0.00054267 | -0.053741 | 0.01549 | 0.00083965 | -0.002305 | -0.003025 | -0.0029438 | 0.0020187 | -0.041199 | 0.26093 | -0.3067 | -0.12817 | 0.022888 | -0.13275 | -0.041199 | 0.2243 | 0.96588 | 0.46234 | 0.67749 | 0.67749 | 0.61798 | 0.75073 | 122.2092 | -0.61798 | -1.0071 | 122.5388 | 122.4747 | 122.3831 | 0.2655 | 0.17395 | 122.9782 | 0.086975 | -0.20142 | 123.1934 | 123.2666 | 123.1338 | 0.28839 | 0.15564 | 0.32959 | 0.17853 | 0.21515 | 0.21515 | 0.56763 | 0.50354 | 122.7768 | 123.4817 | -1.1856 | -0.41656 | 122.3877 | 123.1934 | 122.4747 | 122.7402
2383.4844 | 123.3902 | -122.5479 | 0.90637 | -0.019531 | -0.0071285 | 0.0022559 | 0.0087885 | 0.0027621 | -0.0020658 | -0.00052553 | -0.05069 | 0.017199 | 0.0029758 | 0.0060264 | -0.0032386 | -0.0035846 | 0.0030869 | -0.10529 | 0.24719 | -0.30212 | -0.20142 | -0.059509 | -0.21515 | -0.086975 | 0.11444 | 0.97504 | 0.46234 | 0.72327 | 0.59052 | 0.59967 | 0.73242 | 122.2458 | -0.65918 | -1.1078 | 122.4884 | 122.4609 | 122.3328 | 0.21515 | 0.086975 | 123.0103 | 0.068665 | -0.1831 | 123.1384 | 123.2803 | 123.1476 | 0.27008 | 0.13733 | 0.24261 | 0.10071 | 0.12817 | 0.26093 | 0.54932 | 0.5127 | 122.7951 | 123.5229 | -1.2085 | -0.44403 | 122.3465 | 123.2712 | 122.4426 | 122.6624
2384.5469 | 123.4268 | -122.493 | 0.91095 | -0.0042723 | -0.0092649 | 0.0031103 | 0.0079339 | 0.0014803 | -0.00057042 | 0.00096987 | -0.047638 | 0.018267 | 0.0029758 | -0.00080961 | -0.004093 | -0.0029438 | -0.00054474 | -0.036621 | 0.23346 | -0.3067 | -0.15106 | 0.027466 | -0.086975 | -0.036621 | 0.2243 | 0.99335 | 0.4715 | 0.68207 | 0.6958 | 0.64087 | 0.74616 | 122.1863 | -0.67749 | -1.062 | 122.5204 | 122.4564 | 122.406 | 0.27008 | 0.21973 | 122.9645 | 0.082397 | -0.22888 | 123.1888 | 123.2391 | 123.1338 | 0.27466 | 0.16937 | 0.33417 | 0.15564 | 0.2243 | 0.21057 | 0.54016 | 0.52185 | 122.7264 | 123.4863 | -1.2177 | -0.43945 | 122.3419 | 123.175 | 122.4564 | 122.7173
2385.4844 | 123.4543 | -122.5159 | 0.87433 | -0.072937 | -0.0096921 | 0.0052465 | 0.0079339 | 0.0016939 | 0.0019932 | 0.00075627 | -0.053741 | 0.016558 | 0.0048984 | -0.00038241 | -0.0043066 | -0.00080758 | -0.00011754 | -0.09613 | 0.2655 | -0.3067 | -0.17853 | -0.018311 | -0.19226 | -0.073242 | 0.17395 | 0.97046 | 0.46234 | 0.67749 | 0.67749 | 0.61798 | 0.75531 | 122.2092 | -0.60883 | -1.0529 | 122.4976 | 122.4426 | 122.3236 | 0.23346 | 0.11444 | 122.9782 | 0.09613 | -0.19684 | 123.1934 | 123.2712 | 123.1338 | 0.29297 | 0.15564 | 0.28839 | 0.12817 | 0.21515 | 0.21515 | 0.5722 | 0.50812 | 122.7814 | 123.4863 | -1.181 | -0.41199 | 122.3373 | 123.1934 | 122.4197 | 122.6898
2386.4844 | 123.4039 | -122.5159 | 0.87891 | -0.057678 | -0.0071285 | 0.0065283 | 0.0087885 | 0.0027621 | -0.0020658 | -0.0028753 | -0.044586 | 0.016344 | 0.003403 | -0.0018778 | -0.0047338 | -0.0037982 | 0.00095066 | -0.045776 | 0.28839 | -0.23346 | -0.14648 | 0.013733 | -0.12817 | -0.064087 | 0.21973 | 0.97046 | 0.46692 | 0.65002 | 0.63629 | 0.58594 | 0.72327 | 122.2824 | -0.59051 | -1.0254 | 122.5296 | 122.4518 | 122.3877 | 0.16937 | 0.10528 | 122.9828 | 0.091553 | -0.22888 | 123.1522 | 123.2391 | 123.1018 | 0.25635 | 0.11902 | 0.24719 | 0.086975 | 0.16937 | 0.18311 | 0.52185 | 0.50354 | 122.8043 | 123.4863 | -1.1124 | -0.41199 | 122.3694 | 123.1659 | 122.4701 | 122.7356
2387.5469 | 123.3536 | -122.4609 | 0.95215 | 0.0033567 | -0.0075559 | 0.0031103 | 0.0087885 | 0.0010531 | 7.0582e-05 | -0.0015935 | -0.0018616 | 0.017199 | 0.0014804 | -0.0027322 | -0.0038794 | -0.0042254 | 0.0018051 | -0.10071 | 0.26093 | -0.30212 | -0.19226 | -0.036621 | -0.16022 | -0.050354 | 0.16937 | 0.97046 | 0.4715 | 0.66376 | 0.95215 | 0.63629 | 0.66376 | 122.1588 | -0.69122 | -1.1444 | 122.4243 | 122.4106 | 122.3007 | 0.25177 | 0.14191 | 122.9324 | 0.018311 | -0.28839 | 123.4131 | 123.1247 | 123.0972 | 0.19226 | 0.16479 | 0.2655 | 0.10986 | 0.48065 | 0.19226 | 0.56305 | 0.49896 | 122.7219 | 123.4314 | -1.2543 | -0.48065 | 122.2687 | 123.1247 | 122.3602 | 122.6303
2388.4844 | 123.4085 | -122.5159 | 0.91095 | 0.0033567 | -0.0073423 | 0.0052465 | 0.010284 | -0.0038603 | -0.0016384 | -0.0022345 | -0.05069 | 0.016558 | 0.0042574 | -0.005082 | -0.0032386 | -0.0025164 | -0.00075834 | -0.027466 | 0.29297 | -0.18768 | -0.13275 | 0.027466 | -0.1236 | -0.041199 | 0.2243 | 0.98877 | 0.48981 | 0.68665 | 0.65002 | 0.60425 | 0.72327 | 122.3282 | -0.61798 | -1.0437 | 122.5433 | 122.4747 | 122.3923 | 0.14648 | 0.064087 | 123.0057 | 0.07782 | -0.2243 | 123.1659 | 123.2391 | 123.1201 | 0.23346 | 0.11444 | 0.21515 | 0.054932 | 0.16022 | 0.19684 | 0.48065 | 0.49896 | 122.8088 | 123.5046 | -1.0986 | -0.42114 | 122.3831 | 123.2025 | 122.4884 | 122.7402
2389.5469 | 123.4131 | -122.493 | 0.92468 | 0.026245 | -0.0081967 | 0.0050329 | 0.0077203 | 0.00062594 | 0.0015658 | -0.00052553 | -0.0079652 | 0.017412 | 0.0040438 | 0.00068579 | -0.003025 | -0.001662 | -0.00097194 | -0.073242 | 0.3067 | -0.24719 | -0.16479 | -0.032043 | -0.14191 | -0.045776 | 0.16479 | 0.99335 | 0.4715 | 0.64087 | 0.66376 | 0.62714 | 0.72784 | 122.2458 | -0.61798 | -1.0895 | 122.4609 | 122.4472 | 122.3511 | 0.20142 | 0.10528 | 122.9645 | 0.068664 | -0.28381 | 123.1567 | 123.2208 | 123.1201 | 0.25635 | 0.15564 | 0.21515 | 0.082397 | 0.19226 | 0.16937 | 0.55389 | 0.52185 | 122.7997 | 123.4863 | -1.1719 | -0.45319 | 122.3282 | 123.1338 | 122.4197 | 122.6578
2390.4844 | 123.317 | -122.4564 | 0.91095 | -0.050049 | -0.0094785 | 0.0058875 | 0.0096429 | 0.0012667 | -0.0012112 | -9.8328e-05 | -0.038483 | 0.01549 | 0.0025484 | -0.00038241 | -0.0038794 | -0.00016658 | -0.00097194 | -0.10529 | 0.25635 | -0.3067 | -0.18768 | -0.064087 | -0.21515 | -0.091553 | 0.16479 | 1.0117 | 0.49439 | 0.66376 | 0.64087 | 0.57678 | 0.92926 | 122.1497 | -0.6546 | -1.0986 | 122.3923 | 122.3648 | 122.2412 | 0.21515 | 0.091553 | 122.9507 | 0.10071 | -0.24719 | 123.0972 | 123.3856 | 123.0331 | 0.43487 | 0.082397 | 0.24261 | 0.11902 | 0.14648 | 0.16937 | 0.56305 | 0.51727 | 122.7127 | 123.468 | -1.2177 | -0.41657 | 122.2687 | 123.1201 | 122.3511 | 122.6212
2391.4844 | 123.5184 | -122.4564 | 0.89264 | -0.0042723 | -0.0069149 | 0.0037511 | 0.010498 | 0.0019077 | -0.0020658 | 0.00054267 | -0.023224 | 0.01784 | 0.0027622 | 4.4788e-05 | -0.0051612 | -0.0018756 | -0.00033114 | -0.086975 | 0.24261 | -0.28839 | -0.11902 | 0.041199 | -0.11902 | -0.022888 | 0.28381 | 0.96588 | 0.51727 | 0.75531 | 0.74158 | 0.71411 | 0.85144 | 122.168 | -0.65002 | -1.0117 | 122.4976 | 122.4335 | 122.3373 | 0.2655 | 0.16937 | 122.9736 | 0.073242 | -0.13733 | 123.1979 | 123.3078 | 123.1705 | 0.33417 | 0.19684 | 0.32959 | 0.16937 | 0.2243 | 0.23804 | 0.53101 | 0.44861 | 122.699 | 123.4222 | -1.181 | -0.37537 | 122.3373 | 123.2117 | 122.3694 | 122.7402
2392.5469 | 123.5229 | -122.4655 | 0.90179 | -0.088196 | -0.0069149 | 0.0033239 | 0.0085749 | -0.0045011 | 0.0022068 | -0.0020209 | 0.083588 | 0.01549 | 0.0057528 | -0.0061502 | -0.0021704 | -0.0014484 | -0.00033114 | 0.009155 | 0.22888 | -0.23346 | -0.045776 | 0.13733 | -0.009155 | 0.091553 | 0.37079 | 0.97046 | 0.53558 | 0.76446 | 0.79651 | 0.77362 | 0.8606 | 122.2321 | -0.67291 | -0.94757 | 122.6028 | 122.5571 | 122.4564 | 0.32501 | 0.2243 | 123.0011 | 0.068665 | -0.13733 | 123.262 | 123.3261 | 123.2391 | 0.32501 | 0.23804 | 0.37079 | 0.18768 | 0.26093 | 0.22888 | 0.46234 | 0.43488 | 122.6944 | 123.436 | -1.1353 | -0.36621 | 122.4197 | 123.23 | 122.4747 | 122.8363
2393.4844 | 123.4909 | -122.4792 | 0.88348 | -0.072937 | -0.0094785 | 0.0041785 | 0.0098565 | 0.00019874 | 0.00049778 | -0.0026617 | -0.020172 | 0.016344 | 0.0036166 | 4.4788e-05 | -0.0043066 | -0.0018756 | -0.00097194 | -0.09613 | 0.23804 | -0.29755 | -0.1236 | 0.004578 | -0.14648 | -0.018311 | 0.28381 | 0.98419 | 0.52643 | 0.76904 | 0.74158 | 0.737 | 0.86975 | 122.1817 | -0.64545 | -1.0071 | 122.4838 | 122.4609 | 122.3328 | 0.27923 | 0.15106 | 123.0057 | 0.10071 | -0.11444 | 123.2208 | 123.349 | 123.2162 | 0.34332 | 0.21057 | 0.30212 | 0.17395 | 0.21515 | 0.24262 | 0.53558 | 0.45776 | 122.7173 | 123.4634 | -1.181 | -0.35706 | 122.3557 | 123.2483 | 122.3831 | 122.7631
2394.4844 | 123.3765 | -122.493 | 0.91095 | 0.0033567 | -0.0086239 | 0.0041785 | 0.0085749 | 0.0019077 | -0.0014248 | -0.00031193 | -0.044586 | 0.016985 | 0.0053256 | 0.0019674 | -0.005802 | 4.7018e-05 | -0.0011855 | -0.064087 | 0.23804 | -0.28381 | -0.16937 | -0.036621 | -0.1831 | -0.082397 | 0.21057 | 1.0071 | 0.49896 | 0.65918 | 0.62714 | 0.59052 | 0.70496 | 122.2092 | -0.67291 | -1.0803 | 122.4564 | 122.4106 | 122.3099 | 0.20142 | 0.10071 | 122.9919 | 0.09613 | -0.25177 | 123.1201 | 123.1979 | 123.0835 | 0.20599 | 0.091553 | 0.24719 | 0.11444 | 0.12817 | 0.16022 | 0.52185 | 0.50812 | 122.731 | 123.5001 | -1.1948 | -0.41199 | 122.3236 | 123.1522 | 122.4289 | 122.7036
2395.4844 | 123.4039 | -122.5159 | 0.9201 | -0.042419 | -0.0079831 | 0.0041785 | 0.0043023 | 0.0021213 | -0.00035682 | -0.00073913 | -0.041534 | 0.016771 | 0.004471 | -0.002305 | -0.0032386 | 4.7018e-05 | 0.0011643 | -0.10529 | 0.25635 | -0.3067 | -0.054932 | -0.013733 | -0.19684 | 0.004578 | 0.21973 | 1.0345 | 0.5127 | 0.67291 | 0.66376 | 0.60883 | 0.75073 | 122.2092 | -0.66376 | -0.97504 | 122.5021 | 122.5204 | 122.319 | 0.31128 | 0.10986 | 123.0286 | 0.11444 | -0.24719 | 123.1796 | 123.2666 | 123.1247 | 0.23804 | 0.096131 | 0.29297 | 0.25177 | 0.15106 | 0.16022 | 0.56305 | 0.52185 | 122.7722 | 123.5504 | -1.2268 | -0.40741 | 122.4609 | 123.1888 | 122.4106 | 122.7356
2396.4844 | 123.3719 | -122.4976 | 0.9201 | 0.026245 | -0.0073423 | 0.0048193 | 0.0083611 | 0.0019077 | -0.0014248 | -0.0020209 | -0.041534 | 0.016131 | 0.0048984 | 0.0051718 | -0.0036658 | -0.0023028 | 0.00052346 | -0.11444 | 0.23804 | -0.31128 | -0.21515 | -0.086975 | -0.19684 | -0.091553 | 0.14191 | 1.0254 | 0.49439 | 0.66834 | 0.64545 | 0.6134 | 0.73242 | 122.1863 | -0.68207 | -1.1353 | 122.4106 | 122.406 | 122.3007 | 0.21973 | 0.11444 | 122.9919 | 0.10529 | -0.25177 | 123.143 | 123.23 | 123.111 | 0.23804 | 0.11902 | 0.2243 | 0.09613 | 0.15106 | 0.17395 | 0.54932 | 0.53101 | 122.7356 | 123.5229 | -1.2314 | -0.42572 | 122.2824 | 123.1659 | 122.3831 | 122.6395
2397.5469 | 123.5046 | -122.4335 | 0.90637 | -0.088196 | -0.0081967 | 0.0058875 | 0.0090021 | 0.0023349 | 7.0582e-05 | -0.0011663 | -0.011017 | 0.014422 | 0.0014804 | 0.0036764 | -0.0032386 | -0.0018756 | -0.00011754 | -0.032043 | 0.20599 | -0.25635 | -0.054932 | 0.073242 | -0.059509 | 0.022888 | 0.36163 | 0.97961 | 0.55389 | 0.79193 | 0.79651 | 0.74616 | 0.87433 | 122.1771 | -0.70038 | -0.9613 | 122.5067 | 122.4564 | 122.374 | 0.27924 | 0.19684 | 122.9874 | 0.073242 | -0.11444 | 123.23 | 123.3078 | 123.1796 | 0.32044 | 0.19226 | 0.32959 | 0.20142 | 0.24262 | 0.23804 | 0.46234 | 0.42572 | 122.6395 | 123.4131 | -1.1627 | -0.35248 | 122.3785 | 123.2254 | 122.4014 | 122.7951
2398.4844 | 123.5092 | -122.4609 | 0.9201 | -0.027161 | -0.0088375 | 0.0018285 | 0.0087885 | 0.0012667 | 7.0582e-05 | 0.00032907 | 0.004242 | 0.01549 | 0.0038302 | -0.0020914 | -0.0036658 | -0.0018756 | -0.0016129 | -0.041199 | 0.21057 | -0.26093 | -0.07782 | 0.086975 | -0.082397 | 0.022888 | 0.34332 | 0.9613 | 0.53558 | 0.79651 | 0.78278 | 0.74158 | 0.87433 | 122.2 | -0.70953 | -0.99792 | 122.5479 | 122.4838 | 122.3785 | 0.28381 | 0.17853 | 122.9965 | 0.041199 | -0.1236 | 123.2437 | 123.3353 | 123.2025 | 0.33875 | 0.20599 | 0.3479 | 0.18311 | 0.24719 | 0.26093 | 0.4715 | 0.42572 | 122.6715 | 123.4222 | -1.181 | -0.38452 | 122.3831 | 123.2574 | 122.4197 | 122.8043
2399.4844 | 123.4772 | -122.5021 | 0.92468 | -0.019531 | -0.0081967 | 0.0043921 | 0.01007 | 0.0010531 | -0.00035682 | -0.00095273 | -0.056793 | 0.016558 | 0.0036166 | 0.0017538 | -0.0045202 | 0.00026062 | -0.0046035 | -0.086975 | 0.25177 | -0.27924 | -0.16022 | -0.013733 | -0.16479 | -0.054932 | 0.30212 | 1.0025 | 0.52185 | 0.73242 | 0.74158 | 0.67749 | 0.79193 | 122.2229 | -0.67291 | -1.0849 | 122.4884 | 122.4472 | 122.3373 | 0.2243 | 0.11444 | 123.024 | 0.077819 | -0.19226 | 123.2437 | 123.2941 | 123.1796 | 0.27008 | 0.15564 | 0.2655 | 0.11902 | 0.21973 | 0.21057 | 0.53101 | 0.48065 | 122.7539 | 123.5046 | -1.2039 | -0.40283 | 122.3419 | 123.2346 | 122.4152 | 122.8043
2400.5469 | 123.4268 | -122.5021 | 0.92926 | 0.0033567 | -0.0079831 | 0.0033239 | 0.0094293 | -0.00022866 | 0.0011386 | -0.00073913 | -0.023224 | 0.016131 | 0.003403 | -0.0020914 | -0.0043066 | -0.0023028 | -0.00075834 | -0.059509 | 0.25635 | -0.29755 | -0.16479 | -0.045776 | -0.15106 | -0.041199 | 0.23804 | 1.0162 | 0.5127 | 0.68207 | 0.6958 | 0.6546 | 0.76446 | 122.2046 | -0.67291 | -1.0941 | 122.4564 | 122.4609 | 122.3511 | 0.25635 | 0.14648 | 123.0148 | 0.086975 | -0.24719 | 123.1979 | 123.2666 | 123.1567 | 0.25177 | 0.14191 | 0.25177 | 0.13275 | 0.18311 | 0.16937 | 0.55389 | 0.50354 | 122.7585 | 123.5184 | -1.2268 | -0.41656 | 122.3373 | 123.1842 | 122.4426 | 122.7402

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.5427 | 35.893 | 33.3631 | 33.5381
0.4573 | 35.8858 | 33.3611 | 33.5337
1.4573 | 35.8816 | 33.3638 | 33.5306
2.4573 | 36.0606 | 33.3472 | 33.5224
3.4573 | 36.9098 | 33.3552 | 33.5234
4.4573 | 38.5685 | 33.3507 | 33.5282
5.4573 | 40.9547 | 33.3501 | 33.5255
6.4573 | 43.9258 | 33.3435 | 33.5227
7.4573 | 47.365 | 33.3361 | 33.5233
8.4573 | 51.2093 | 33.3489 | 33.5235
9.4573 | 55.3517 | 33.3497 | 33.5151
10.4729 | 59.8011 | 33.3379 | 33.5176
11.4573 | 64.3906 | 33.3316 | 33.5213
12.4573 | 69.2388 | 33.3331 | 33.5133
13.4573 | 74.2109 | 33.3466 | 33.5177
14.4573 | 79.3193 | 33.3366 | 33.5247
15.4573 | 84.544 | 33.3294 | 33.5223
16.4573 | 89.9085 | 33.332 | 33.5189
17.4573 | 95.3758 | 33.3299 | 33.522
18.4573 | 100.9811 | 33.32 | 33.5269
19.4573 | 106.6829 | 33.3322 | 33.5358
20.4573 | 112.4267 | 33.3301 | 33.5389
21.4573 | 118.1881 | 33.3334 | 33.5464
22.4573 | 123.9723 | 33.3376 | 33.5477
23.4573 | 129.7834 | 33.3321 | 33.5647
24.4573 | 135.6496 | 33.3419 | 33.5785
25.4573 | 141.5747 | 33.3378 | 33.5906
26.4573 | 147.5009 | 33.3387 | 33.6095
27.4573 | 153.3151 | 33.3432 | 33.6279
28.4573 | 159.2108 | 33.3605 | 33.6522
29.4573 | 165.1626 | 33.3607 | 33.685
30.4573 | 171.0656 | 33.3727 | 33.7157
31.4573 | 176.9034 | 33.3807 | 33.7437
32.4573 | 182.7946 | 33.3886 | 33.7794
33.4573 | 188.8027 | 33.3979 | 33.8171
34.4573 | 194.667 | 33.4307 | 33.8583
35.4573 | 200.5007 | 33.4474 | 33.9035
36.4573 | 206.2958 | 33.4662 | 33.9467
37.4573 | 212.0962 | 33.4872 | 34.0115
38.4573 | 218.0181 | 33.5084 | 34.066
39.4573 | 223.9438 | 33.5365 | 34.129
40.4573 | 229.7599 | 33.576 | 34.195
41.4573 | 235.6352 | 33.5987 | 34.2683
42.4573 | 241.2878 | 33.636 | 34.3467
43.4573 | 247.1062 | 33.6712 | 34.4372
44.4573 | 252.8737 | 33.7306 | 34.5209
45.4573 | 258.6892 | 33.7769 | 34.6266
46.4573 | 264.4494 | 33.8208 | 34.7318
47.4573 | 270.0999 | 33.8802 | 34.8326
48.4573 | 275.6601 | 33.9516 | 34.9566
49.4573 | 281.1806 | 34.0093 | 35.0824
50.4573 | 286.5832 | 34.0794 | 35.2062
51.4573 | 291.5305 | 34.1421 | 35.3458
52.4573 | 296.0779 | 34.2289 | 35.4845
53.4573 | 300.2409 | 34.3031 | 35.637
54.4573 | 304.0841 | 34.3938 | 35.7961
55.4573 | 307.7676 | 34.4898 | 35.9696
56.4573 | 311.1977 | 34.5902 | 36.1415
57.4573 | 314.5586 | 34.6911 | 36.329
58.4573 | 317.6715 | 34.8072 | 36.5234
59.4573 | 320.348 | 34.9188 | 36.72
60.4573 | 322.7991 | 35.0424 | 36.9237
61.4573 | 325.1351 | 35.1699 | 37.1405
62.4573 | 327.1174 | 35.3105 | 37.3631
63.4573 | 328.847 | 35.4575 | 37.5999
64.4573 | 330.2613 | 35.6095 | 37.8301
65.4573 | 331.4704 | 35.7532 | 38.0934
66.4573 | 332.5027 | 35.9216 | 38.3465
67.4573 | 333.2894 | 36.0869 | 38.6068
68.5667 | 333.8911 | 36.2848 | 38.9057
69.551 | 334.2038 | 36.4606 | 39.1821
70.5042 | 334.4114 | 36.6396 | 39.4584
71.5198 | 334.5732 | 36.8459 | 39.7534
72.4729 | 334.7165 | 37.0315 | 40.0434
73.4573 | 334.7414 | 37.2395 | 40.3452
74.551 | 334.5783 | 37.4744 | 40.6773
75.4885 | 334.369 | 37.6902 | 40.9777
76.5198 | 334.3118 | 37.9251 | 41.3132
77.4573 | 334.1666 | 38.14 | 41.6136
78.4885 | 333.9621 | 38.3792 | 41.9586
79.4573 | 333.6287 | 38.615 | 42.2856
80.4573 | 333.1411 | 38.8605 | 42.6268
81.4573 | 332.7815 | 39.1249 | 42.9713
82.4573 | 332.44 | 39.3851 | 43.338
83.4573 | 332.0687 | 39.6584 | 43.6856
84.4573 | 331.6794 | 39.9186 | 44.0474
85.4573 | 331.2548 | 40.1806 | 44.4055
86.4573 | 330.9582 | 40.4581 | 44.7633
87.4573 | 330.673 | 40.756 | 45.1379
88.4573 | 330.2917 | 41.0551 | 45.502
89.4573 | 329.8822 | 41.3392 | 45.8784
90.4573 | 329.472 | 41.6413 | 46.2547
91.4573 | 329.0171 | 41.9312 | 46.6249
92.4573 | 328.5468 | 42.236 | 47.0093
93.4573 | 328.0964 | 42.526 | 47.3911
94.4573 | 327.6509 | 42.843 | 47.771
95.4573 | 327.2291 | 43.1589 | 48.1559
96.4573 | 326.8584 | 43.4958 | 48.5466
97.4573 | 326.3852 | 43.8175 | 48.9296
98.4573 | 325.9095 | 44.1282 | 49.3187
99.4573 | 325.585 | 44.4445 | 49.7029
100.4573 | 325.2173 | 44.777 | 50.0981
101.4573 | 324.8488 | 45.1053 | 50.4904
102.4573 | 324.562 | 45.432 | 50.8797
103.4573 | 324.2813 | 45.7657 | 51.2701
104.4573 | 323.9875 | 46.0939 | 51.6661
105.4573 | 323.6992 | 46.4351 | 52.0524
106.4573 | 323.498 | 46.7741 | 52.4505
107.4573 | 323.4046 | 47.104 | 52.8514
108.4573 | 323.2984 | 47.4456 | 53.2411
109.4573 | 323.1995 | 47.7866 | 53.6442
110.4573 | 323.2403 | 48.1152 | 54.036
111.4573 | 323.3457 | 48.4651 | 54.4242
112.4573 | 323.4041 | 48.8006 | 54.8177
113.4573 | 323.4875 | 49.1537 | 55.2124
114.4573 | 323.5457 | 49.4938 | 55.6006
115.4573 | 323.7903 | 49.8434 | 55.9932
116.4573 | 324.1173 | 50.1738 | 56.3818
117.4573 | 324.2694 | 50.546 | 56.7738
118.4573 | 324.4174 | 50.8859 | 57.1675
119.4573 | 324.6476 | 51.2371 | 57.5628
120.4573 | 324.9357 | 51.5919 | 57.95
121.4573 | 325.1373 | 51.9468 | 58.3396
122.4573 | 325.2735 | 52.2979 | 58.7238
123.4573 | 325.4283 | 52.6492 | 59.1199
124.4573 | 325.6837 | 53.0023 | 59.5101
125.4573 | 325.9546 | 53.3499 | 59.9018
126.4573 | 326.2182 | 53.7199 | 60.2835
127.4573 | 326.3857 | 54.0724 | 60.6797
128.4573 | 326.6058 | 54.4279 | 61.0617
129.4573 | 326.8634 | 54.7747 | 61.4559
130.4729 | 327.0037 | 55.1026 | 61.8437
131.4573 | 327.1006 | 55.495 | 62.2425
132.4573 | 327.2635 | 55.8427 | 62.6329
133.4573 | 327.5605 | 56.2 | 63.0121
134.4573 | 327.8153 | 56.5631 | 63.408
135.4573 | 327.98 | 56.9299 | 63.7959
136.4573 | 328.1167 | 57.2832 | 64.1856
137.4573 | 328.274 | 57.6281 | 64.5712
138.4573 | 328.5252 | 57.9976 | 64.9663
139.4573 | 328.6167 | 58.3652 | 65.3539
140.4573 | 328.5665 | 58.735 | 65.7476
141.4573 | 328.5243 | 59.092 | 66.1285
142.4573 | 328.7656 | 59.443 | 66.5166
143.4573 | 329.0226 | 59.8244 | 66.8983
144.4573 | 329.041 | 60.1835 | 67.2908
145.4573 | 329.0182 | 60.5616 | 67.6814
146.4573 | 329.1058 | 60.9179 | 68.0662
147.4573 | 329.1206 | 61.2977 | 68.453
148.4573 | 329.1525 | 61.6593 | 68.8407
149.4573 | 329.3931 | 62.028 | 69.2319
150.4573 | 329.5481 | 62.4034 | 69.6213
151.4573 | 329.5183 | 62.7803 | 69.9972
152.4573 | 329.5758 | 63.1537 | 70.3915
153.4573 | 329.6214 | 63.515 | 70.7826
154.4573 | 329.5397 | 63.902 | 71.1728
155.4573 | 329.5837 | 64.2726 | 71.5596
156.4573 | 329.6499 | 64.6392 | 71.9494
157.4573 | 329.7846 | 65.015 | 72.3357
158.4573 | 329.84 | 65.3801 | 72.7208
159.4573 | 329.7619 | 65.7618 | 73.1083
160.4573 | 329.7924 | 66.1388 | 73.4939
161.4573 | 329.8447 | 66.5034 | 73.8719
162.4573 | 329.9119 | 66.8684 | 74.2648
163.4573 | 330.0739 | 67.2399 | 74.6561
164.4573 | 330.1058 | 67.6229 | 75.0343
165.4573 | 330.044 | 68.0002 | 75.4125
166.4573 | 329.9833 | 68.37 | 75.7999
167.4573 | 330.061 | 68.7245 | 76.1825
168.4573 | 330.0838 | 69.1281 | 76.5627
169.4573 | 329.9854 | 69.5105 | 76.9454
170.4573 | 329.8797 | 69.8685 | 77.3242
171.4573 | 329.8006 | 70.2631 | 77.7041
172.4573 | 329.719 | 70.6385 | 78.0737
173.4573 | 329.605 | 71.0056 | 78.4593
174.4885 | 329.5001 | 71.4105 | 78.8516
175.4573 | 329.4531 | 71.7792 | 79.2146
176.4573 | 329.368 | 72.1612 | 79.5944
177.4573 | 329.3649 | 72.5376 | 79.9773
178.4573 | 329.327 | 72.9231 | 80.345
179.4573 | 329.2309 | 73.2973 | 80.7264
180.4573 | 329.211 | 73.6765 | 81.1017
181.4573 | 329.2338 | 74.0505 | 81.4789
182.4573 | 329.0788 | 74.4349 | 81.853
183.4573 | 329.0157 | 74.7945 | 82.227
184.4573 | 328.9419 | 75.174 | 82.5914
185.4573 | 328.8961 | 75.5552 | 82.9575
186.4573 | 328.7701 | 75.929 | 83.3311
187.4573 | 328.6672 | 76.2978 | 83.7017
188.4573 | 328.6654 | 76.6675 | 84.0669
189.4573 | 328.5694 | 77.0481 | 84.4254
190.4573 | 328.4925 | 77.4097 | 84.7925
191.4573 | 328.4719 | 77.7794 | 85.1537
192.4573 | 328.3957 | 78.1586 | 85.5156
193.4573 | 328.3964 | 78.5145 | 85.8773
194.4573 | 328.2176 | 78.8837 | 86.2463
195.4573 | 328.1016 | 79.2565 | 86.6063
196.4573 | 328.19 | 79.6213 | 86.9588
197.4573 | 328.2955 | 79.9994 | 87.3156
198.4573 | 328.2053 | 80.3517 | 87.6736
199.4573 | 328.2938 | 80.7184 | 88.0239
200.4573 | 328.2569 | 81.0883 | 88.3854
201.4573 | 328.2423 | 81.4521 | 88.7393
202.4573 | 328.1532 | 81.8126 | 89.0961
203.4573 | 328.1971 | 82.16 | 89.4479
204.4573 | 328.2047 | 82.5214 | 89.7919
205.4573 | 328.2357 | 82.8909 | 90.1508
206.4573 | 328.3049 | 83.2442 | 90.5058
207.4573 | 328.3855 | 83.6 | 90.8572
208.4573 | 328.4178 | 83.9485 | 91.2026
209.4573 | 328.4419 | 84.2999 | 91.549
210.4573 | 328.4808 | 84.658 | 91.8973
211.4573 | 328.5217 | 85.0007 | 92.2324
212.4573 | 328.51 | 85.3544 | 92.5849
213.4573 | 328.4411 | 85.7137 | 92.9291
214.4573 | 328.4197 | 86.0444 | 93.267
215.4573 | 328.4839 | 86.4006 | 93.6089
216.4573 | 328.4514 | 86.7485 | 93.9443
217.4573 | 328.4168 | 87.0916 | 94.2876
218.4573 | 328.4552 | 87.4469 | 94.6251
219.4573 | 328.396 | 87.7889 | 94.9531
220.4573 | 328.4842 | 88.1237 | 95.2918
221.4573 | 328.5519 | 88.4655 | 95.6252
222.4573 | 328.6151 | 88.8119 | 95.9555
223.4573 | 328.6061 | 89.154 | 96.2873
224.4573 | 328.6275 | 89.4771 | 96.6195
225.4573 | 328.6293 | 89.8263 | 96.9527
226.4573 | 328.6821 | 90.152 | 97.2786
227.4573 | 328.81 | 90.5032 | 97.6142
228.4573 | 328.9687 | 90.8359 | 97.9425
229.4573 | 328.9389 | 91.1693 | 98.2629
230.4573 | 328.9729 | 91.5118 | 98.5955
231.4573 | 329.0436 | 91.8347 | 98.9198
232.4573 | 329.1735 | 92.1577 | 99.2362
233.4573 | 329.1773 | 92.4816 | 99.5699
234.4573 | 329.1542 | 92.8122 | 99.9257
235.4573 | 329.1059 | 93.1502 | 100.2594
236.4573 | 329.1368 | 93.4721 | 100.5883
237.4573 | 329.2159 | 93.7821 | 100.9067
238.4573 | 329.2835 | 94.1218 | 101.227
239.4573 | 329.3737 | 94.4329 | 101.5382
240.4573 | 329.3918 | 94.7558 | 101.8557
241.4573 | 329.3825 | 95.0805 | 102.16
242.4573 | 329.4136 | 95.3926 | 102.478
243.4573 | 329.351 | 95.7083 | 102.7797
244.4573 | 329.3141 | 96.0305 | 103.0824
245.4573 | 329.294 | 96.3456 | 103.3841
246.4573 | 329.1845 | 96.6665 | 103.6854
247.4573 | 329.1386 | 96.9739 | 103.9883
248.4573 | 329.1079 | 97.2922 | 104.2842
249.4573 | 329.0827 | 97.6106 | 104.5979
250.4573 | 329.1279 | 97.915 | 104.8939
251.4573 | 329.1758 | 98.2171 | 105.1905
252.4573 | 329.1442 | 98.5224 | 105.4928
253.4573 | 329.0655 | 98.8415 | 105.789
254.4573 | 329.119 | 99.1493 | 106.0844
255.4573 | 329.0329 | 99.4602 | 106.3844
256.4573 | 328.9259 | 99.7663 | 106.6729
257.4573 | 328.9465 | 100.0914 | 106.975
258.4573 | 329.0053 | 100.3935 | 107.262
259.4573 | 329.0568 | 100.6933 | 107.5622
260.4573 | 329.1498 | 100.9952 | 107.8457
261.4573 | 329.1991 | 101.3044 | 108.1421
262.4573 | 329.2613 | 101.6164 | 108.431
263.4573 | 329.2646 | 101.9203 | 108.7189
264.4573 | 329.2471 | 102.2366 | 109.0048
265.4573 | 329.2546 | 102.5472 | 109.2985
266.4573 | 329.1934 | 102.853 | 109.5801
267.4573 | 329.0768 | 103.1542 | 109.8611
268.4573 | 329.0233 | 103.4753 | 110.1432
269.4573 | 328.9396 | 103.7726 | 110.4228
270.4573 | 329.0158 | 104.1062 | 110.7006
271.4573 | 329.0566 | 104.4246 | 110.9691
272.4573 | 329.0969 | 104.7441 | 111.2501
273.4573 | 329.0153 | 105.0602 | 111.5316
274.4573 | 329.0008 | 105.3627 | 111.8017
275.4573 | 328.9082 | 105.6687 | 112.0859
276.4573 | 328.8665 | 105.9645 | 112.3651
277.4573 | 328.7491 | 106.277 | 112.6388
278.4573 | 328.701 | 106.5858 | 112.9122
279.4573 | 328.5991 | 106.8882 | 113.1907
280.4573 | 328.6282 | 107.1961 | 113.463
281.4573 | 328.6569 | 107.5178 | 113.7521
282.4573 | 328.576 | 107.8402 | 114.0216
283.4573 | 328.5347 | 108.153 | 114.2927
284.4573 | 328.5707 | 108.4714 | 114.5768
285.4573 | 328.5541 | 108.7811 | 114.8526
286.4573 | 328.4762 | 109.1408 | 115.1371
287.4573 | 328.4889 | 109.5407 | 115.422
288.4573 | 328.4766 | 109.9357 | 115.6981
289.4573 | 328.5108 | 110.2866 | 115.9767
290.4573 | 328.5251 | 110.6415 | 116.2608
291.4573 | 328.4467 | 110.9772 | 116.5448
292.4573 | 328.3687 | 111.322 | 116.8302
293.4573 | 328.4169 | 111.6531 | 117.1142
294.4573 | 328.583 | 111.9976 | 117.4018
295.4573 | 328.7452 | 112.3314 | 117.6892
296.4573 | 328.7455 | 112.67 | 117.9752
297.4573 | 328.7366 | 112.987 | 118.2744
298.4573 | 328.6963 | 113.3348 | 118.5688
299.4573 | 328.6776 | 113.6632 | 118.8725
300.4573 | 328.6735 | 113.9915 | 119.1713
301.4573 | 328.6614 | 114.3301 | 119.4704
302.4573 | 328.7588 | 114.6762 | 119.7604
303.4573 | 328.8021 | 115.0109 | 120.0645
304.4573 | 328.847 | 115.3389 | 120.3615
305.4573 | 328.8837 | 115.6858 | 120.6544
306.4573 | 328.8816 | 116.0162 | 120.9487
307.4573 | 328.8539 | 116.3593 | 121.2436
308.4573 | 328.8551 | 116.6764 | 121.5492
309.4573 | 328.8745 | 117.0071 | 121.8473
310.4573 | 328.8412 | 117.3419 | 122.1463
311.4573 | 328.9493 | 117.6581 | 122.449
312.4573 | 329.0413 | 117.9776 | 122.7381
313.4573 | 329.1087 | 118.2842 | 123.0351
314.4573 | 329.0778 | 118.5158 | 123.3365
315.4573 | 329.18 | 118.7151 | 123.629
316.4573 | 329.1658 | 118.9473 | 123.9292
317.4573 | 329.1538 | 119.2065 | 124.2277
318.4573 | 329.0819 | 119.4678 | 124.5225
319.4573 | 329.0355 | 119.7475 | 124.8213
320.4573 | 329.01 | 120.0508 | 125.1148
321.4573 | 328.981 | 120.3477 | 125.414
322.4573 | 329.0423 | 120.6436 | 125.7153
323.4573 | 329.0702 | 120.9722 | 126.0132
324.4573 | 328.9476 | 121.291 | 126.3234
325.4573 | 328.9058 | 121.608 | 126.628
326.4573 | 328.8633 | 121.9046 | 126.9338
327.4573 | 328.857 | 122.1885 | 127.233
328.4573 | 328.8654 | 122.4954 | 127.549
329.4573 | 328.9072 | 122.8099 | 127.861
330.4573 | 328.9497 | 123.157 | 128.1767
331.4573 | 328.9422 | 123.5041 | 128.5079
332.4573 | 328.9113 | 123.8904 | 128.8336
333.4573 | 328.901 | 124.2521 | 129.1579
334.4573 | 328.9797 | 124.6239 | 129.4835
335.4573 | 329.0075 | 124.9842 | 129.8196
336.4573 | 328.834 | 125.3937 | 130.1468
337.4573 | 328.7943 | 125.7896 | 130.4718
338.4573 | 328.7159 | 126.1725 | 130.7982
339.4573 | 328.6341 | 126.5716 | 131.136
340.4573 | 328.6064 | 126.974 | 131.4608
341.4573 | 328.5064 | 127.3523 | 131.7981
342.4573 | 328.4578 | 127.7539 | 132.1228
343.4573 | 328.422 | 128.1475 | 132.4457
344.4573 | 328.4225 | 128.5204 | 132.7719
345.4573 | 328.2777 | 128.9013 | 133.098
346.4573 | 328.1955 | 129.3009 | 133.4201
347.4573 | 328.1657 | 129.6721 | 133.748
348.4573 | 328.1451 | 130.0538 | 134.0725
349.4573 | 328.1298 | 130.4224 | 134.3918
350.4573 | 328.1479 | 130.8024 | 134.7127
351.4573 | 328.2317 | 131.1707 | 135.0313
352.4573 | 328.1901 | 131.5442 | 135.3548
353.4573 | 328.1606 | 131.9161 | 135.6675
354.4573 | 328.1382 | 132.2715 | 135.9863
355.4573 | 328.1577 | 132.6403 | 136.3009
356.4573 | 328.19 | 132.9823 | 136.615
357.4573 | 328.0867 | 133.3442 | 136.9314
358.4573 | 328.0209 | 133.6942 | 137.2435
359.4573 | 327.9848 | 134.0173 | 137.5565
360.4573 | 327.8267 | 134.3504 | 137.8701
361.4573 | 327.8355 | 134.682 | 138.1981
362.4573 | 327.8934 | 135.0097 | 138.5024
363.5198 | 327.9797 | 135.3668 | 138.8326
364.4729 | 328.0435 | 135.6883 | 139.1317
365.4573 | 327.9714 | 136.0281 | 139.4313
366.4573 | 327.9744 | 136.3633 | 139.7384
367.4885 | 327.8984 | 136.7015 | 140.0546
368.4573 | 327.8863 | 137.0403 | 140.3546
369.4573 | 327.9287 | 137.3917 | 140.6641
370.4573 | 328.0253 | 137.7406 | 140.9627
371.4573 | 327.9912 | 138.0901 | 141.2743
372.4573 | 327.9486 | 138.4556 | 141.5779
373.4573 | 328.0079 | 138.8104 | 141.8827
374.4573 | 327.9517 | 139.1366 | 142.1748
375.4573 | 327.9731 | 139.4968 | 142.4733
376.4573 | 328.0614 | 139.864 | 142.7767
377.4573 | 328.1508 | 140.1983 | 143.0742
378.4573 | 328.3077 | 140.535 | 143.3781
379.4573 | 328.3509 | 140.861 | 143.6741
380.4573 | 328.3438 | 141.2017 | 143.9676
381.4573 | 328.3638 | 141.5259 | 144.2661
382.4573 | 328.4139 | 141.8786 | 144.5611
383.4573 | 328.4057 | 142.196 | 144.8529
384.4573 | 328.4492 | 142.5215 | 145.146
385.4573 | 328.3854 | 142.8469 | 145.4461
386.4573 | 328.4023 | 143.1678 | 145.7423
387.4573 | 328.4226 | 143.4833 | 146.0289
388.4573 | 328.5645 | 143.8029 | 146.3172
389.4573 | 328.7404 | 144.1341 | 146.6043
390.4573 | 328.7333 | 144.4366 | 146.8907
391.4573 | 328.6554 | 144.7565 | 147.1773
392.4573 | 328.592 | 145.0739 | 147.4542
393.4573 | 328.6398 | 145.4058 | 147.7464
394.4573 | 328.7164 | 145.7189 | 148.04
395.4573 | 328.7032 | 146.0392 | 148.3185
396.4573 | 328.6783 | 146.3447 | 148.5928
397.4573 | 328.6122 | 146.6655 | 148.8749
398.4573 | 328.6296 | 146.9755 | 149.1455
399.4573 | 328.6508 | 147.2879 | 149.4269
400.4573 | 328.7575 | 147.5973 | 149.6914
401.4573 | 328.7204 | 147.9173 | 149.9629
402.4573 | 328.62 | 148.241 | 150.2246
403.4573 | 328.7271 | 148.5493 | 150.492
404.4573 | 328.76 | 148.848 | 150.7457
405.4573 | 328.7587 | 149.1748 | 150.9997
406.4573 | 328.7732 | 149.4941 | 151.2501
407.4573 | 328.8332 | 149.7966 | 151.4912
408.4573 | 328.7324 | 150.1214 | 151.729
409.4573 | 328.5768 | 150.4252 | 151.9476
410.4573 | 328.5374 | 150.7009 | 152.1894
411.4573 | 328.4254 | 150.9375 | 152.4503
412.4573 | 328.4349 | 151.2504 | 152.6743
413.4573 | 328.4054 | 151.5401 | 152.9278
414.4573 | 328.3694 | 151.8288 | 153.1994
415.4573 | 328.4217 | 152.1376 | 153.4802
416.4573 | 328.4603 | 152.4275 | 153.7515
417.4573 | 328.5195 | 152.7351 | 154.0443
418.4573 | 328.521 | 153.0439 | 154.3182
419.4573 | 328.4607 | 153.3468 | 154.6063
420.4573 | 328.415 | 153.6434 | 154.8958
421.4573 | 328.2904 | 153.942 | 155.1796
422.4573 | 328.1355 | 154.2398 | 155.4671
423.4573 | 328.1146 | 154.5411 | 155.7605
424.4573 | 328.1571 | 154.8473 | 156.0573
425.4573 | 328.1575 | 155.1524 | 156.3647
426.4573 | 328.2588 | 155.4616 | 156.666
427.4573 | 328.3751 | 155.7524 | 156.937
428.4573 | 328.2354 | 156.0583 | 157.2373
429.4573 | 328.0687 | 156.3512 | 157.5186
430.4573 | 328.0022 | 156.6586 | 157.8059
431.4573 | 327.9914 | 156.9701 | 158.0869
432.4573 | 327.9701 | 157.3006 | 158.3538
433.4573 | 327.8736 | 157.7055 | 158.555
434.4573 | 328.0203 | 158.0195 | 158.8244
435.4573 | 328.0892 | 158.3245 | 159.107
436.4573 | 328.0555 | 158.6285 | 159.3799
437.4573 | 327.9488 | 158.9302 | 159.668
438.4573 | 327.9442 | 159.2354 | 159.9481
439.4573 | 327.8982 | 159.5327 | 160.2333
440.4573 | 327.8891 | 159.8383 | 160.5347
441.4573 | 327.8424 | 160.1342 | 160.8098
442.4573 | 327.8631 | 160.4229 | 161.0795
443.4573 | 327.9208 | 160.718 | 161.3469
444.4573 | 328.0252 | 161.0138 | 161.6171
445.4573 | 327.9727 | 161.2842 | 161.8858
446.4573 | 327.9572 | 161.6044 | 162.164
447.4573 | 327.9744 | 161.8992 | 162.4346
448.4573 | 328.0206 | 162.1917 | 162.702
449.4573 | 328.1175 | 162.4802 | 162.9829
450.4573 | 328.1927 | 162.7715 | 163.2531
451.4573 | 328.237 | 163.0583 | 163.535
452.4573 | 328.2827 | 163.3517 | 163.8308
453.4573 | 328.3627 | 163.627 | 164.1162
454.4573 | 328.4358 | 163.9209 | 164.4092
455.4573 | 328.3931 | 164.2044 | 164.6992
456.4573 | 328.2859 | 164.4793 | 164.9772
457.4573 | 328.1579 | 164.781 | 165.2497
458.4573 | 328.2282 | 165.0558 | 165.5324
459.4573 | 328.2499 | 165.3517 | 165.8153
460.4573 | 328.3197 | 165.6338 | 166.0872
461.4573 | 328.3576 | 165.9179 | 166.3673
462.4573 | 328.3446 | 166.1925 | 166.6406
463.4573 | 328.4527 | 166.4743 | 166.9191
464.4573 | 328.4543 | 166.7501 | 167.2087
465.4573 | 328.3892 | 167.0493 | 167.4901
466.4573 | 328.4492 | 167.3249 | 167.7622
467.4573 | 328.3465 | 167.6107 | 168.0426
468.4573 | 328.3341 | 167.8928 | 168.3178
469.4573 | 328.3598 | 168.1648 | 168.5801
470.4573 | 328.4996 | 168.4394 | 168.8416
471.4573 | 328.4563 | 168.7301 | 169.1076
472.4573 | 328.3771 | 168.9915 | 169.3779
473.4573 | 328.4368 | 169.2708 | 169.64
474.4573 | 328.4635 | 169.5487 | 169.9037
475.4573 | 328.5042 | 169.8257 | 170.1741
476.4573 | 328.4428 | 170.0978 | 170.44
477.4573 | 328.4087 | 170.3749 | 170.7284
478.4573 | 328.2417 | 170.6393 | 171.0007
479.4573 | 328.1271 | 170.9157 | 171.2788
480.4573 | 328.1101 | 171.1789 | 171.554
481.4573 | 328.0261 | 171.4576 | 171.8276
482.4573 | 328.0323 | 171.7262 | 172.0995
483.4573 | 328.1242 | 171.9887 | 172.3607
484.4573 | 328.1379 | 172.2681 | 172.6371
485.4573 | 328.1457 | 172.5249 | 172.919
486.4573 | 328.2125 | 172.793 | 173.1888
487.4573 | 328.2935 | 173.0654 | 173.4386
488.4573 | 328.1894 | 173.3343 | 173.688
489.4573 | 328.1509 | 173.5949 | 173.9538
490.4573 | 328.0923 | 173.8524 | 174.2036
491.4573 | 328.1716 | 174.1164 | 174.4695
492.4573 | 328.1593 | 174.3763 | 174.7406
493.4573 | 328.1765 | 174.6397 | 175.0146
494.4573 | 328.0976 | 174.9035 | 175.277
495.4573 | 328.1055 | 175.1586 | 175.534
496.4573 | 328.0704 | 175.4176 | 175.7966
497.4573 | 327.9801 | 175.6727 | 176.0451
498.4573 | 327.9382 | 175.9263 | 176.2951
499.4573 | 327.9176 | 176.1862 | 176.5558
500.4573 | 327.9019 | 176.4286 | 176.8204
501.4573 | 327.923 | 176.6933 | 177.0902
502.4573 | 327.8808 | 176.9683 | 177.3325
503.4573 | 327.9654 | 177.2217 | 177.573
504.4573 | 327.8769 | 177.4676 | 177.8264
505.4573 | 327.858 | 177.724 | 178.0928
506.4573 | 327.8686 | 177.9782 | 178.3411
507.4573 | 327.9329 | 178.2178 | 178.5285
508.4573 | 327.8521 | 178.4762 | 178.7224
509.4573 | 327.8765 | 178.7144 | 178.9482
510.4573 | 327.9478 | 178.9567 | 179.2015
511.4573 | 327.9425 | 179.2148 | 179.469
512.4573 | 327.8307 | 179.4637 | 179.7153
513.4573 | 327.792 | 179.7117 | 179.9925
514.4573 | 327.7881 | 179.9501 | 180.2689
515.4573 | 327.724 | 180.1937 | 180.5217
516.4573 | 327.7364 | 180.4423 | 180.7724
517.4573 | 327.704 | 180.6804 | 181.0245
518.4573 | 327.7811 | 180.9173 | 181.2722
519.4573 | 327.7855 | 181.1736 | 181.5159
520.4573 | 327.8123 | 181.3994 | 181.7574
521.4573 | 327.786 | 181.6489 | 181.9903
522.4573 | 327.869 | 181.8859 | 182.2288
523.4573 | 327.9189 | 182.1202 | 182.4729
524.4573 | 327.9052 | 182.3676 | 182.6998
525.4573 | 328.0219 | 182.5863 | 182.9349
526.4573 | 328.0252 | 182.8377 | 183.1613
527.4573 | 327.9704 | 183.0807 | 183.3774
528.4573 | 327.9542 | 183.3087 | 183.5916
529.4573 | 327.9929 | 183.5434 | 183.8057
530.4573 | 327.9606 | 183.7791 | 183.996
531.4573 | 327.8896 | 184.0204 | 184.1959
532.4573 | 327.9785 | 184.2422 | 184.3853
533.4573 | 328.0906 | 184.4785 | 184.5676
534.4573 | 328.1506 | 184.7115 | 184.755
535.4573 | 328.2383 | 184.9489 | 184.9662
536.4573 | 328.1993 | 185.1866 | 185.1893
537.4573 | 328.2662 | 185.4124 | 185.4037
538.4573 | 328.2213 | 185.6393 | 185.6347
539.4573 | 328.2364 | 185.8889 | 185.8459
540.4573 | 328.1749 | 186.1191 | 186.0646
541.4573 | 328.1175 | 186.3474 | 186.2825
542.4573 | 328.148 | 186.555 | 186.5114
543.4573 | 328.1997 | 186.8178 | 186.741
544.4573 | 328.116 | 187.0514 | 186.9793
545.4573 | 328.089 | 187.2714 | 187.1942
546.4573 | 328.0618 | 187.5153 | 187.4364
547.4573 | 328.1102 | 187.7347 | 187.667
548.4573 | 328.2453 | 187.9676 | 187.9102
549.4573 | 328.2969 | 188.1917 | 188.136
550.4573 | 328.3996 | 188.4147 | 188.3693
551.4573 | 328.3127 | 188.6501 | 188.5964
552.4573 | 328.3271 | 188.8531 | 188.8196
553.4573 | 328.3708 | 189.0943 | 189.0507
554.4573 | 328.4324 | 189.3057 | 189.2757
555.4573 | 328.4099 | 189.5404 | 189.5047
556.4573 | 328.3659 | 189.7656 | 189.7239
557.4573 | 328.3469 | 189.9814 | 189.9509
558.4573 | 328.3571 | 190.1961 | 190.1737
559.4573 | 328.3474 | 190.4211 | 190.3849
560.4573 | 328.3655 | 190.6392 | 190.6089
561.4573 | 328.3982 | 190.8669 | 190.8332
562.4573 | 328.3353 | 191.0806 | 191.0555
563.4573 | 328.3734 | 191.2943 | 191.2764
564.4573 | 328.3184 | 191.5076 | 191.5033
565.4573 | 328.3146 | 191.7283 | 191.7197
566.4573 | 328.3397 | 191.9371 | 191.9426
567.4573 | 328.2675 | 192.1588 | 192.1414
568.4573 | 328.2332 | 192.3769 | 192.3612
569.4573 | 328.1399 | 192.6021 | 192.5702
570.4573 | 328.0467 | 192.8009 | 192.7831
571.4573 | 327.9089 | 193.0215 | 192.9907
572.4573 | 327.7962 | 193.2438 | 193.1922
573.4573 | 327.7789 | 193.4427 | 193.4052
574.4573 | 327.7784 | 193.6475 | 193.6136
575.4573 | 327.9292 | 193.8491 | 193.824
576.4573 | 327.8798 | 194.0737 | 194.0312
577.4573 | 327.8465 | 194.2655 | 194.2379
578.4573 | 327.7967 | 194.4879 | 194.4564
579.4573 | 327.7426 | 194.7123 | 194.6627
580.4573 | 327.7868 | 194.9212 | 194.8754
581.4573 | 327.8021 | 195.121 | 195.0898
582.4573 | 327.8299 | 195.3328 | 195.2952
583.4573 | 327.8963 | 195.5389 | 195.5018
584.4573 | 327.96 | 195.7451 | 195.7085
585.4573 | 328.0048 | 195.9559 | 195.9041
586.4573 | 328.0672 | 196.1597 | 196.1198
587.4573 | 328.0936 | 196.372 | 196.329
588.4573 | 328.0596 | 196.5864 | 196.5294
589.4573 | 327.9803 | 196.7874 | 196.7517
590.4573 | 327.9825 | 196.9821 | 196.9585
591.4573 | 327.9891 | 197.1921 | 197.1585
592.4573 | 327.9038 | 197.4024 | 197.377
593.4573 | 327.7367 | 197.6099 | 197.5828
594.4573 | 327.674 | 197.8101 | 197.784
595.4573 | 327.6178 | 198.011 | 197.9966
596.4573 | 327.7152 | 198.2227 | 198.2066
597.4573 | 327.8162 | 198.4211 | 198.4141
598.4573 | 327.8986 | 198.6266 | 198.618
599.4573 | 327.9573 | 198.833 | 198.833
600.4573 | 328.0352 | 199.0396 | 199.0384
601.4573 | 328.0987 | 199.2321 | 199.2447
602.4573 | 328.1274 | 199.4332 | 199.4617
603.4573 | 328.1364 | 199.6273 | 199.6703
604.4573 | 328.1855 | 199.8328 | 199.8603
605.4573 | 328.2021 | 200.0321 | 200.0649
606.4573 | 328.1539 | 200.2207 | 200.2625
607.4573 | 328.0856 | 200.4285 | 200.4623
608.4573 | 327.9974 | 200.6222 | 200.6691
609.4573 | 327.8922 | 200.8088 | 200.875
610.4573 | 327.7279 | 201.0035 | 201.0773
611.4573 | 327.822 | 201.2036 | 201.2662
612.4573 | 327.8794 | 201.3866 | 201.467
613.4573 | 327.8998 | 201.5905 | 201.6807
614.4573 | 327.8734 | 201.7794 | 201.8767
615.4573 | 327.7635 | 201.9692 | 202.0684
616.4573 | 327.7399 | 202.1577 | 202.2436
617.4573 | 327.8323 | 202.3504 | 202.4413
618.4573 | 327.9023 | 202.5478 | 202.6294
619.4573 | 327.8399 | 202.7357 | 202.828
620.4573 | 327.7588 | 202.9161 | 203.0247
621.4573 | 327.7775 | 203.1023 | 203.1835
622.4573 | 327.7855 | 203.2944 | 203.364
623.4573 | 327.6885 | 203.4793 | 203.5238
624.4573 | 327.715 | 203.6689 | 203.7005
625.4573 | 327.7168 | 203.857 | 203.877
626.4573 | 327.752 | 204.0478 | 204.0428
627.4573 | 327.8457 | 204.2272 | 204.2122
628.4573 | 327.9667 | 204.3984 | 204.3891
629.4573 | 328.0273 | 204.595 | 204.5583
630.4573 | 328.0726 | 204.7771 | 204.7407
631.4573 | 328.0236 | 204.9725 | 204.9269
632.4573 | 327.8963 | 205.1559 | 205.1053
633.4573 | 327.969 | 205.3318 | 205.2883
634.4573 | 327.9717 | 205.5061 | 205.4689
635.4573 | 327.9773 | 205.7107 | 205.6494
636.4573 | 327.9929 | 205.8951 | 205.835
637.4573 | 327.9043 | 206.0749 | 206.0189
638.4573 | 327.8894 | 206.2609 | 206.2013
639.4573 | 327.812 | 206.4444 | 206.4038
640.4573 | 327.7512 | 206.642 | 206.5896
641.4573 | 327.6949 | 206.8023 | 206.7677
642.4573 | 327.8264 | 206.9866 | 206.9543
643.4573 | 327.9257 | 207.1719 | 207.1343
644.4573 | 327.9246 | 207.3415 | 207.3285
645.4573 | 327.8861 | 207.521 | 207.5035
646.4573 | 327.9722 | 207.6906 | 207.689
647.4573 | 327.9882 | 207.8912 | 207.8558
648.4573 | 327.9238 | 208.0545 | 208.0182
649.4573 | 327.9829 | 208.2289 | 208.1835
650.4573 | 327.9976 | 208.3947 | 208.3386
651.4573 | 328.0269 | 208.5747 | 208.4861
652.4573 | 327.9588 | 208.7589 | 208.6491
653.4573 | 327.9786 | 208.9345 | 208.8341
654.4573 | 328.0652 | 209.1001 | 209.0113
655.4573 | 328.0838 | 209.276 | 209.191
656.4573 | 328.1198 | 209.4658 | 209.3592
657.4573 | 328.1493 | 209.6296 | 209.5402
658.4573 | 328.096 | 209.8146 | 209.7023
659.4573 | 328.1002 | 209.9883 | 209.8708
660.4573 | 328.0197 | 210.1534 | 210.0368
661.4573 | 328.0422 | 210.3112 | 210.1971
662.4573 | 328.076 | 210.4967 | 210.3591
663.4573 | 328.1104 | 210.6749 | 210.5068
664.4573 | 328.1356 | 210.8419 | 210.5853
665.4573 | 328.1592 | 211.0157 | 210.7301
666.4573 | 328.2337 | 211.1865 | 210.9072
667.4573 | 328.1188 | 211.3524 | 211.0942
668.4573 | 327.9982 | 211.5216 | 211.263
669.4573 | 328.0186 | 211.6799 | 211.4289
670.4573 | 328.0355 | 211.8577 | 211.6072
671.4573 | 327.9914 | 212.0215 | 211.7788
672.4573 | 327.9625 | 212.1963 | 211.9471
673.4573 | 327.9002 | 212.3569 | 212.1087
674.4573 | 327.9062 | 212.5188 | 212.2775
675.4573 | 327.9669 | 212.6943 | 212.4439
676.4573 | 327.8581 | 212.8573 | 212.6179
677.4573 | 327.7991 | 213.0155 | 212.7863
678.4573 | 327.7683 | 213.1799 | 212.9536
679.4573 | 327.8708 | 213.3565 | 213.124
680.4573 | 327.8134 | 213.5194 | 213.2867
681.4573 | 327.8976 | 213.6841 | 213.456
682.4573 | 327.9292 | 213.8433 | 213.6257
683.4573 | 327.9276 | 214.0121 | 213.7919
684.4573 | 327.8981 | 214.1601 | 213.9497
685.4573 | 327.8612 | 214.2992 | 214.114
686.4573 | 327.8203 | 214.4943 | 214.2687
687.4573 | 327.7134 | 214.6574 | 214.4269
688.4573 | 327.7088 | 214.8204 | 214.5904
689.4573 | 327.7918 | 214.9775 | 214.7496
690.4573 | 327.8733 | 215.1418 | 214.9042
691.4573 | 327.8298 | 215.2965 | 215.0659
692.4573 | 327.7796 | 215.4639 | 215.2218
693.4573 | 327.7821 | 215.6135 | 215.3807
694.4573 | 327.839 | 215.7721 | 215.5301
695.4573 | 327.8247 | 215.939 | 215.6884
696.4573 | 327.8641 | 216.1007 | 215.8513
697.4573 | 327.9258 | 216.2606 | 216.0002
698.4573 | 327.8595 | 216.4239 | 216.1699
699.4573 | 327.8664 | 216.577 | 216.3197
700.4573 | 327.8807 | 216.7337 | 216.4652
701.4573 | 327.8172 | 216.8713 | 216.6171
702.4573 | 327.7685 | 217.0453 | 216.7679
703.4573 | 327.6784 | 217.1961 | 216.9116
704.4573 | 327.608 | 217.3505 | 217.0695
705.4573 | 327.7474 | 217.5009 | 217.2128
706.4573 | 327.7736 | 217.6489 | 217.3614
707.4573 | 327.8086 | 217.8087 | 217.5027
708.4573 | 327.8276 | 217.9637 | 217.6506
709.4573 | 327.9036 | 218.1086 | 217.7821
710.4573 | 327.9688 | 218.2717 | 217.9386
711.4573 | 327.9915 | 218.4117 | 218.0846
712.4573 | 327.9994 | 218.5672 | 218.2245
713.4573 | 328.0062 | 218.7169 | 218.3714
714.4573 | 328.0591 | 218.8831 | 218.5141
715.4573 | 328.1348 | 219.0266 | 218.6603
716.4573 | 328.1332 | 219.1809 | 218.8011
717.4573 | 328.1036 | 219.3255 | 218.9438
718.4573 | 328.0472 | 219.4772 | 219.0833
719.4573 | 327.9622 | 219.6222 | 219.2303
720.4573 | 327.9865 | 219.7801 | 219.3716
721.4573 | 328.0361 | 219.916 | 219.5031
722.4573 | 328.1068 | 220.0829 | 219.6474
723.4573 | 328.217 | 220.2312 | 219.7687
724.4573 | 328.2455 | 220.3737 | 219.9196
725.4573 | 328.2928 | 220.5189 | 220.0489
726.4573 | 328.465 | 220.6667 | 220.1841
727.4573 | 328.4594 | 220.8119 | 220.3298
728.4573 | 328.468 | 220.9547 | 220.4706
729.4573 | 328.6034 | 221.0717 | 220.6144
730.4573 | 328.6404 | 221.2277 | 220.751
731.4573 | 328.6742 | 221.3805 | 220.8905
732.4573 | 328.7179 | 221.5204 | 221.0191
733.4573 | 328.7359 | 221.6683 | 221.1469
734.4573 | 328.8288 | 221.8084 | 221.2851
735.4573 | 328.8566 | 221.9495 | 221.4089
736.4573 | 328.9236 | 222.0845 | 221.538
737.4573 | 328.7771 | 222.2188 | 221.6769
738.4573 | 328.7165 | 222.3694 | 221.8138
739.4573 | 328.7414 | 222.5139 | 221.9519
740.4573 | 328.8071 | 222.6498 | 222.085
741.4573 | 328.7723 | 222.7944 | 222.2242
742.4573 | 328.7307 | 222.9455 | 222.3642
743.4573 | 328.7308 | 223.0809 | 222.4902
744.4573 | 328.7738 | 223.2189 | 222.6234
745.4573 | 328.7301 | 223.3675 | 222.7498
746.4573 | 328.7133 | 223.4969 | 222.8713
747.4573 | 328.6522 | 223.6407 | 223.006
748.4573 | 328.573 | 223.7816 | 223.141
749.4573 | 328.5413 | 223.9195 | 223.2768
750.4573 | 328.6195 | 224.0519 | 223.4107
751.4573 | 328.6629 | 224.1992 | 223.5424
752.4573 | 328.6498 | 224.3321 | 223.6563
753.4573 | 328.744 | 224.4698 | 223.7877
754.4573 | 328.7743 | 224.6081 | 223.9066
755.4573 | 328.702 | 224.7532 | 224.0335
756.4573 | 328.6487 | 224.8824 | 224.1625
757.4573 | 328.6726 | 225.0294 | 224.2963
758.4573 | 328.6717 | 225.1679 | 224.4194
759.4573 | 328.7351 | 225.3003 | 224.5422
760.4573 | 328.8074 | 225.4355 | 224.6608
761.4573 | 328.8749 | 225.5773 | 224.8043
762.4573 | 328.8185 | 225.7232 | 224.9293
763.4573 | 328.7107 | 225.8535 | 225.0544
764.4573 | 328.6715 | 226.0073 | 225.189
765.4573 | 328.7069 | 226.1553 | 225.32
766.4573 | 328.7145 | 226.2886 | 225.45
767.4573 | 328.7085 | 226.4083 | 225.5738
768.4573 | 328.6882 | 226.5648 | 225.7067
769.4573 | 328.6046 | 226.6982 | 225.8331
770.4573 | 328.5492 | 226.8456 | 225.9821
771.4573 | 328.5292 | 226.9851 | 226.1077
772.4573 | 328.5715 | 227.1225 | 226.2409
773.4573 | 328.5618 | 227.2581 | 226.3747
774.4573 | 328.5977 | 227.3897 | 226.5058
775.4573 | 328.6273 | 227.5303 | 226.6427
776.4573 | 328.5941 | 227.6733 | 226.7728
777.4573 | 328.5616 | 227.8053 | 226.8991
778.4573 | 328.519 | 227.9476 | 227.033
779.4573 | 328.4435 | 228.0836 | 227.1603
780.4573 | 328.4862 | 228.2268 | 227.2948
781.4573 | 328.5033 | 228.3527 | 227.4231
782.4573 | 328.5206 | 228.4726 | 227.5499
783.4573 | 328.5386 | 228.6235 | 227.6735
784.4573 | 328.5771 | 228.7579 | 227.8072
785.4573 | 328.5388 | 228.8989 | 227.9109
786.4573 | 328.528 | 229.036 | 228.0262
787.4573 | 328.5424 | 229.1825 | 228.1482
788.4573 | 328.5369 | 229.3344 | 228.263
789.4573 | 328.3857 | 229.4733 | 228.3954
790.4573 | 328.4193 | 229.6093 | 228.5134
791.4573 | 328.3821 | 229.7495 | 228.6473
792.4573 | 328.2856 | 229.8934 | 228.7693
793.4573 | 328.2869 | 230.021 | 228.8924
794.4573 | 328.2155 | 230.135 | 229.0252
795.4573 | 328.2532 | 230.2907 | 229.1384
796.4573 | 328.27 | 230.4211 | 229.2492
797.4573 | 328.2612 | 230.5492 | 229.3774
798.4573 | 328.2104 | 230.6782 | 229.4925
799.4573 | 328.166 | 230.8027 | 229.6081
800.4573 | 328.1588 | 230.9255 | 229.7355
801.4573 | 328.1056 | 231.067 | 229.8581
802.4573 | 328.1509 | 231.1982 | 229.9747
803.4573 | 328.0448 | 231.3045 | 230.0898
804.4573 | 327.9375 | 231.4458 | 230.2004
805.4573 | 327.9245 | 231.5707 | 230.3186
806.4573 | 327.8788 | 231.6979 | 230.4333
807.4573 | 327.9027 | 231.8304 | 230.5503
808.4573 | 327.872 | 231.9479 | 230.6653
809.4573 | 327.8162 | 232.0813 | 230.7753
810.4573 | 327.9969 | 232.1942 | 230.8736
811.4573 | 328.0567 | 232.3378 | 230.9866
812.4573 | 328.1014 | 232.4585 | 231.0808
813.4573 | 328.0763 | 232.5792 | 231.1946
814.4573 | 328.0473 | 232.7088 | 231.3089
815.4573 | 328.0735 | 232.8379 | 231.4144
816.4573 | 328.1779 | 232.9627 | 231.5251
817.4573 | 328.323 | 233.0934 | 231.6386
818.4573 | 328.4183 | 233.2187 | 231.75
819.4573 | 328.4863 | 233.34 | 231.8544
820.4573 | 328.4721 | 233.4513 | 231.9594
821.4573 | 328.4674 | 233.5722 | 232.0663
822.4573 | 328.5454 | 233.701 | 232.1734
823.4573 | 328.659 | 233.8297 | 232.2877
824.4573 | 328.6455 | 233.9564 | 232.3996
825.4573 | 328.6505 | 234.0647 | 232.503
826.4573 | 328.6797 | 234.1893 | 232.6105
827.4573 | 328.662 | 234.3281 | 232.7159
828.4573 | 328.7182 | 234.4321 | 232.8173
829.4573 | 328.7249 | 234.5818 | 232.9196
830.4573 | 328.6917 | 234.7072 | 233.0317
831.4573 | 328.6139 | 234.8286 | 233.1315
832.4573 | 328.5746 | 234.9466 | 233.2333
833.4573 | 328.5377 | 235.0841 | 233.3291
834.4573 | 328.5304 | 235.2094 | 233.4242
835.4573 | 328.528 | 235.3336 | 233.522
836.4573 | 328.5114 | 235.4669 | 233.624
837.4573 | 328.4044 | 235.6166 | 233.7346
838.4573 | 328.3461 | 235.7472 | 233.8389
839.4573 | 328.3568 | 235.8704 | 233.9442
840.4573 | 328.3072 | 235.9916 | 234.0472
841.4573 | 328.3939 | 236.115 | 234.1476
842.4573 | 328.3169 | 236.2349 | 234.2496
843.4573 | 328.291 | 236.3563 | 234.3425
844.4573 | 328.1896 | 236.4887 | 234.4422
845.4573 | 328.0337 | 236.6007 | 234.5498
846.4573 | 327.9717 | 236.7291 | 234.643
847.4573 | 328.0368 | 236.8357 | 234.7463
848.4573 | 328.0068 | 236.9521 | 234.8435
849.4573 | 328.0511 | 237.083 | 234.9297
850.4573 | 328.0993 | 237.2073 | 235.0282
851.4573 | 328.1162 | 237.35 | 235.1276
852.4573 | 328.0156 | 237.4789 | 235.2084
853.4573 | 328.0629 | 237.595 | 235.3097
854.4573 | 328.1358 | 237.7221 | 235.4068
855.4573 | 328.1942 | 237.8084 | 235.4955
856.4573 | 328.2043 | 237.9201 | 235.5982
857.4573 | 328.2218 | 238.011 | 235.6988
858.4573 | 328.2851 | 238.0954 | 235.7828
859.4573 | 328.3052 | 238.1783 | 235.8778
860.4573 | 328.3044 | 238.2667 | 235.9684
861.4573 | 328.2905 | 238.3644 | 236.0601
862.4573 | 328.3312 | 238.4543 | 236.138
863.4573 | 328.2348 | 238.5277 | 236.2266
864.4573 | 328.1276 | 238.6219 | 236.3105
865.4573 | 328.2385 | 238.6931 | 236.4075
866.4573 | 328.3036 | 238.7809 | 236.4839
867.4573 | 328.3129 | 238.8972 | 236.5745
868.4573 | 328.3934 | 238.9776 | 236.6629
869.4573 | 328.3741 | 239.0663 | 236.7558
870.4573 | 328.35 | 239.1717 | 236.8421
871.4573 | 328.3146 | 239.2475 | 236.9314
872.4573 | 328.2324 | 239.3289 | 237.0166
873.4573 | 328.2212 | 239.4193 | 237.1041
874.4573 | 328.193 | 239.5085 | 237.1983
875.4573 | 328.2293 | 239.5892 | 237.2864
876.4573 | 328.2496 | 239.6683 | 237.3793
877.4573 | 328.2431 | 239.7328 | 237.4596
878.4573 | 328.2257 | 239.8096 | 237.5448
879.4573 | 328.1852 | 239.8905 | 237.6253
880.4573 | 328.1093 | 239.9732 | 237.7107
881.4573 | 328.0378 | 240.0516 | 237.7973
882.4573 | 328.0953 | 240.1188 | 237.8863
883.4573 | 328.1803 | 240.1932 | 237.9582
884.4573 | 328.2785 | 240.2815 | 238.0516
885.4573 | 328.2807 | 240.3681 | 238.1303
886.4573 | 328.2981 | 240.4271 | 238.2107
887.4573 | 328.2453 | 240.5012 | 238.3005
888.4573 | 328.217 | 240.6015 | 238.3844
889.4573 | 328.2036 | 240.6801 | 238.4631
890.4573 | 328.2536 | 240.755 | 238.5293
891.4573 | 328.2157 | 240.851 | 238.6117
892.4573 | 328.2238 | 240.9119 | 238.6887
893.4573 | 328.2253 | 240.995 | 238.7704
894.4573 | 328.2185 | 241.0551 | 238.8507
895.4573 | 328.2045 | 241.1339 | 238.9336
896.4573 | 328.2178 | 241.1752 | 239.0187
897.4573 | 328.2407 | 241.2206 | 239.105
898.4573 | 328.2805 | 241.2628 | 239.1865
899.4573 | 328.1631 | 241.3275 | 239.2652
900.4573 | 328.1716 | 241.3972 | 239.3447
901.4573 | 328.1473 | 241.4516 | 239.4126
902.4573 | 328.0868 | 241.5356 | 239.4839
903.4573 | 328.0433 | 241.5983 | 239.5695
904.4573 | 327.9758 | 241.6695 | 239.6431
905.4573 | 327.9853 | 241.7577 | 239.7172
906.4573 | 328.0518 | 241.8725 | 239.7884
907.4573 | 328.12 | 241.9501 | 239.8691
908.4573 | 328.0988 | 242.0389 | 239.9378
909.4573 | 328.161 | 242.1103 | 240.016
910.4573 | 328.175 | 242.1878 | 240.0827
911.4573 | 328.2137 | 242.2639 | 240.1549
912.4573 | 328.2298 | 242.3166 | 240.2275
913.4573 | 328.2219 | 242.3943 | 240.3041
914.4573 | 328.2634 | 242.4653 | 240.3698
915.4573 | 328.2566 | 242.5282 | 240.445
916.4573 | 328.2215 | 242.5987 | 240.5139
917.4573 | 328.1607 | 242.6659 | 240.5813
918.4573 | 328.192 | 242.7209 | 240.6491
919.4573 | 328.2638 | 242.7896 | 240.7275
920.4573 | 328.2456 | 242.8433 | 240.8006
921.4573 | 328.2234 | 242.9087 | 240.8694
922.4573 | 328.245 | 242.9692 | 240.93
923.4573 | 328.1673 | 243.0245 | 240.9963
924.4573 | 328.0218 | 243.0832 | 241.0662
925.4573 | 327.9285 | 243.1387 | 241.1344
926.4573 | 327.8924 | 243.2032 | 241.2079
927.4573 | 327.8961 | 243.2291 | 241.2694
928.4573 | 327.9488 | 243.26 | 241.3342
929.4573 | 327.9589 | 243.303 | 241.402
930.4573 | 328.0022 | 243.3639 | 241.4682
931.4573 | 327.9129 | 243.4062 | 241.5356
932.4573 | 327.7955 | 243.4528 | 241.5983
933.4573 | 327.7354 | 243.4978 | 241.6631
934.4573 | 327.7625 | 243.5577 | 241.7282
935.4573 | 327.711 | 243.6127 | 241.7807
936.4573 | 327.7185 | 243.6679 | 241.8552
937.4573 | 327.7922 | 243.7228 | 241.9166
938.4573 | 327.7519 | 243.7817 | 241.9779
939.4573 | 327.7559 | 243.8395 | 242.0475
940.4573 | 327.7891 | 243.8746 | 242.1089
941.4573 | 327.7405 | 243.9173 | 242.1693
942.4573 | 327.7397 | 243.984 | 242.2363
943.4573 | 327.7449 | 244.04 | 242.3008
944.4573 | 327.7663 | 244.0987 | 242.3659
945.4573 | 327.7155 | 244.1658 | 242.4225
946.4573 | 327.6985 | 244.2231 | 242.4898
947.4573 | 327.8017 | 244.2788 | 242.5471
948.4573 | 327.8263 | 244.3508 | 242.6187
949.4573 | 327.9069 | 244.3969 | 242.6759
950.4573 | 327.8703 | 244.4567 | 242.7396
951.4573 | 327.8043 | 244.5079 | 242.8026
952.4573 | 327.7861 | 244.5851 | 242.8619
953.4573 | 327.8835 | 244.624 | 242.9319
954.4573 | 327.8472 | 244.6876 | 242.9911
955.4573 | 327.9248 | 244.7398 | 243.0481
956.4573 | 327.9745 | 244.8001 | 243.1079
957.4573 | 327.9555 | 244.8431 | 243.1578
958.4573 | 327.9789 | 244.907 | 243.223
959.4573 | 327.9685 | 244.9393 | 243.2776
960.4573 | 327.9721 | 245.0074 | 243.3342
961.4573 | 327.9919 | 245.0579 | 243.3874
962.4573 | 327.9297 | 245.1024 | 243.4448
963.4573 | 327.8464 | 245.1551 | 243.4983
964.4573 | 327.8727 | 245.2098 | 243.5577
965.4573 | 327.8973 | 245.2639 | 243.6126
966.4573 | 327.943 | 245.3292 | 243.6701
967.4573 | 328.03 | 245.369 | 243.7189
968.4573 | 327.9956 | 245.4217 | 243.7682
969.4573 | 327.9674 | 245.4632 | 243.8269
970.4573 | 328.0239 | 245.5054 | 243.8825
971.4573 | 328.0976 | 245.5603 | 243.9363
972.4573 | 328.1069 | 245.5895 | 243.9902
973.4573 | 328.1144 | 245.6355 | 244.0345
974.4573 | 328.2591 | 245.6754 | 244.094
975.4573 | 328.3554 | 245.7292 | 244.1436
976.4573 | 328.453 | 245.7794 | 244.187
977.4573 | 328.6071 | 245.822 | 244.2481
978.4573 | 328.557 | 245.8713 | 244.2969
979.4573 | 328.5263 | 245.9167 | 244.3479
980.4573 | 328.5899 | 245.9688 | 244.3917
981.4573 | 328.6633 | 245.998 | 244.4493
982.4573 | 328.795 | 246.0391 | 244.4961
983.4573 | 328.8124 | 246.0831 | 244.5498
984.4573 | 328.8471 | 246.1373 | 244.5894
985.4573 | 328.8003 | 246.1692 | 244.6406
986.4573 | 328.8097 | 246.2157 | 244.6913
987.4573 | 328.8342 | 246.2583 | 244.7401
988.4573 | 328.7676 | 246.29 | 244.7945
989.4573 | 328.7731 | 246.3338 | 244.8413
990.4573 | 328.7098 | 246.3684 | 244.8886
991.4573 | 328.7225 | 246.4087 | 244.9414
992.4573 | 328.594 | 246.4488 | 244.9891
993.4573 | 328.463 | 246.4798 | 245.0429
994.4573 | 328.4092 | 246.5143 | 245.093
995.4573 | 328.3273 | 246.5591 | 245.1392
996.4573 | 328.294 | 246.6017 | 245.1902
997.4573 | 328.2368 | 246.644 | 245.2396
998.4573 | 328.1743 | 246.6842 | 245.2958
999.4573 | 328.2148 | 246.7132 | 245.3552
1000.4573 | 328.2206 | 246.7382 | 245.4085
1001.4729 | 328.237 | 246.7879 | 245.4758
1002.4573 | 328.2564 | 246.8257 | 245.5301
1003.4573 | 328.2122 | 246.8593 | 245.5961
1004.4573 | 328.1738 | 246.8822 | 245.6642
1005.4573 | 328.262 | 246.914 | 245.7202
1006.4573 | 328.3211 | 246.937 | 245.7892
1007.4573 | 328.3488 | 246.9567 | 245.8388
1008.4573 | 328.2756 | 246.986 | 245.8954
1009.4573 | 328.2995 | 247.0014 | 245.9426
1010.4573 | 328.3444 | 247.0241 | 245.9986
1011.4573 | 328.3496 | 247.0602 | 246.0479
1012.4573 | 328.38 | 247.0826 | 246.0961
1013.4573 | 328.4213 | 247.102 | 246.1426
1014.4573 | 328.3918 | 247.13 | 246.1945
1015.4573 | 328.3602 | 247.1537 | 246.2401
1016.4573 | 328.3853 | 247.2047 | 246.2874
1017.4573 | 328.3124 | 247.2252 | 246.3398
1018.4573 | 328.3289 | 247.2469 | 246.3827
1019.4573 | 328.3098 | 247.2929 | 246.4327
1020.4573 | 328.3118 | 247.3185 | 246.4797
1021.4573 | 328.2597 | 247.369 | 246.5284
1022.4573 | 328.1313 | 247.4053 | 246.5687
1023.4573 | 328.0446 | 247.4416 | 246.6139
1024.4573 | 327.953 | 247.4754 | 246.6594
1025.4573 | 327.9388 | 247.501 | 246.6903
1026.4573 | 328.0419 | 247.5526 | 246.7301
1027.4573 | 328.1094 | 247.5904 | 246.7708
1028.4573 | 328.1167 | 247.619 | 246.8172
1029.4573 | 328.1204 | 247.6612 | 246.8721
1030.4573 | 328.1563 | 247.7053 | 246.9085
1031.4573 | 328.1418 | 247.7427 | 246.9466
1032.4573 | 328.121 | 247.7742 | 246.9868
1033.4573 | 328.1176 | 247.8136 | 247.0288
1034.4573 | 328.1639 | 247.8637 | 247.062
1035.4573 | 328.1867 | 247.8883 | 247.0984
1036.4573 | 328.0843 | 247.9185 | 247.134
1037.4573 | 328.0109 | 247.9561 | 247.173
1038.4573 | 327.9978 | 248.0004 | 247.2117
1039.4573 | 327.9883 | 248.0362 | 247.2523
1040.4573 | 328.0789 | 248.0653 | 247.291
1041.4573 | 328.0668 | 248.1055 | 247.3314
1042.4573 | 328.1351 | 248.1449 | 247.3717
1043.4573 | 328.1917 | 248.176 | 247.4137
1044.4573 | 328.1128 | 248.2171 | 247.4494
1045.4573 | 328.0904 | 248.2458 | 247.4943
1046.4573 | 328.0335 | 248.2855 | 247.5291
1047.4573 | 328.04 | 248.3223 | 247.5598
1048.4573 | 328.0192 | 248.3594 | 247.5995
1049.4573 | 327.988 | 248.3914 | 247.6447
1050.4573 | 328.0486 | 248.4289 | 247.6746
1051.4573 | 328.1457 | 248.4626 | 247.7128
1052.4573 | 328.1996 | 248.5011 | 247.7525
1053.4573 | 328.1473 | 248.55 | 247.7908
1054.4573 | 328.1803 | 248.5812 | 247.8345
1055.4573 | 328.1454 | 248.6259 | 247.8767
1056.4573 | 328.046 | 248.6624 | 247.9053
1057.4573 | 328.0221 | 248.6928 | 247.9405
1058.4573 | 328.1732 | 248.7278 | 247.9887
1059.4573 | 328.2278 | 248.7761 | 248.0279
1060.4573 | 328.2207 | 248.8239 | 248.0693
1061.4573 | 328.0979 | 248.8497 | 248.1027
1062.4573 | 327.9446 | 248.8994 | 248.1418
1063.4573 | 327.8317 | 248.9342 | 248.1747
1064.4573 | 327.8091 | 248.9565 | 248.2185
1065.4573 | 327.7719 | 249.0074 | 248.2508
1066.4573 | 327.7379 | 249.033 | 248.2858
1067.4573 | 327.7628 | 249.062 | 248.3597
1068.4573 | 327.7742 | 249.1103 | 248.3996
1069.4573 | 327.7565 | 249.143 | 248.435
1070.4573 | 327.7763 | 249.1756 | 248.4729
1071.4573 | 327.7836 | 249.2158 | 248.507
1072.4573 | 327.8201 | 249.2463 | 248.533
1073.4573 | 327.8627 | 249.2841 | 248.5772
1074.4573 | 327.8554 | 249.3239 | 248.6071
1075.4573 | 327.9076 | 249.3547 | 248.6386
1076.4573 | 327.9046 | 249.3944 | 248.6737
1077.4573 | 327.9091 | 249.4265 | 248.7088
1078.4573 | 327.9501 | 249.4469 | 248.7424
1079.4573 | 328.0527 | 249.485 | 248.7728
1080.4573 | 328.0571 | 249.5143 | 248.8197
1081.4573 | 328.026 | 249.5474 | 248.8411
1082.4573 | 328.129 | 249.5958 | 248.8724
1083.4573 | 328.1346 | 249.6219 | 248.9076
1084.4573 | 328.159 | 249.63 | 248.9417
1085.4573 | 328.166 | 249.6686 | 248.9808
1086.4573 | 328.2323 | 249.7107 | 249.0112
1087.4573 | 328.2694 | 249.7437 | 249.0475
1088.4573 | 328.288 | 249.7734 | 249.0814
1089.4573 | 328.3335 | 249.8035 | 249.1228
1090.4573 | 328.3693 | 249.8219 | 249.157
1091.4573 | 328.3664 | 249.8711 | 249.1895
1092.4573 | 328.3168 | 249.9139 | 249.2259
1093.4573 | 328.3062 | 249.944 | 249.2508
1094.4573 | 328.3099 | 249.9569 | 249.3002
1095.4573 | 328.2334 | 250.0091 | 249.3351
1096.4573 | 328.2541 | 250.0424 | 249.3653
1097.4573 | 328.3685 | 250.0727 | 249.3982
1098.4573 | 328.4056 | 250.1107 | 249.4328
1099.4573 | 328.345 | 250.1544 | 249.4694
1100.4573 | 328.2782 | 250.1825 | 249.4987
1101.4573 | 328.2577 | 250.2274 | 249.5288
1102.4573 | 328.317 | 250.2561 | 249.5653
1103.4573 | 328.3446 | 250.2837 | 249.5964
1104.4573 | 328.3933 | 250.322 | 249.6301
1105.4573 | 328.3673 | 250.3609 | 249.6542
1106.4573 | 328.3433 | 250.3896 | 249.6888
1107.4573 | 328.3986 | 250.4325 | 249.7227
1108.4573 | 328.4531 | 250.4563 | 249.7557
1109.4573 | 328.4044 | 250.4833 | 249.7864
1110.4573 | 328.3561 | 250.5334 | 249.8108
1111.4573 | 328.3241 | 250.5658 | 249.8331
1112.4573 | 328.3326 | 250.5979 | 249.8763
1113.4573 | 328.4192 | 250.6293 | 249.9048
1114.4573 | 328.3931 | 250.6706 | 249.9295
1115.4573 | 328.4315 | 250.6948 | 249.9697
1116.4573 | 328.5391 | 250.7331 | 250.0023
1117.4573 | 328.5991 | 250.777 | 250.0249
1118.4573 | 328.6172 | 250.7996 | 250.0644
1119.4573 | 328.6241 | 250.8413 | 250.0853
1120.4573 | 328.597 | 250.8694 | 250.1138
1121.4573 | 328.5408 | 250.9061 | 250.1466
1122.4573 | 328.4644 | 250.9423 | 250.1798
1123.4573 | 328.3908 | 250.9787 | 250.207
1124.4573 | 328.3945 | 251.011 | 250.2372
1125.4573 | 328.3804 | 251.0311 | 250.2639
1126.4573 | 328.3471 | 251.0744 | 250.296
1127.4573 | 328.4274 | 251.1179 | 250.3292
1128.4573 | 328.5432 | 251.1509 | 250.3573
1129.4573 | 328.485 | 251.1813 | 250.3843
1130.4573 | 328.4556 | 251.2221 | 250.4162
1131.4573 | 328.4298 | 251.2568 | 250.4405
1132.4573 | 328.3897 | 251.2934 | 250.4709
1133.4573 | 328.4486 | 251.3109 | 250.5028
1134.4573 | 328.4422 | 251.3492 | 250.5306
1135.4573 | 328.3945 | 251.3769 | 250.5594
1136.4573 | 328.3642 | 251.4191 | 250.5946
1137.4573 | 328.4029 | 251.4497 | 250.6252
1138.4573 | 328.3307 | 251.483 | 250.6545
1139.4573 | 328.2207 | 251.522 | 250.6844
1140.4573 | 328.1138 | 251.5494 | 250.7127
1141.4573 | 328.1417 | 251.587 | 250.7433
1142.4573 | 328.0244 | 251.6069 | 250.7675
1143.4573 | 327.9106 | 251.6382 | 250.7981
1144.4573 | 327.8765 | 251.6692 | 250.8303
1145.4573 | 327.8246 | 251.7077 | 250.8547
1146.4573 | 327.7561 | 251.7308 | 250.8806
1147.4573 | 327.7002 | 251.7505 | 250.9114
1148.4573 | 327.6872 | 251.8029 | 250.9361
1149.4573 | 327.6691 | 251.8334 | 250.9624
1150.4573 | 327.6375 | 251.8615 | 251.0116
1151.4573 | 327.6778 | 251.8782 | 251.0456
1152.4573 | 327.5938 | 251.9295 | 251.0723
1153.4573 | 327.6205 | 251.9556 | 251.1006
1154.4573 | 327.6327 | 251.9878 | 251.1323
1155.4573 | 327.6913 | 252.0141 | 251.1596
1156.4573 | 327.6788 | 252.035 | 251.1906
1157.4573 | 327.6953 | 252.0638 | 251.2199
1158.4573 | 327.6713 | 252.0993 | 251.2472
1159.4573 | 327.6289 | 252.1255 | 251.2741
1160.4573 | 327.6083 | 252.1524 | 251.2797
1161.4573 | 327.7525 | 252.1905 | 251.307
1162.4573 | 327.7556 | 252.2098 | 251.3287
1163.4573 | 327.8417 | 252.2433 | 251.3585
1164.4573 | 327.8087 | 252.271 | 251.3809
1165.4573 | 327.7934 | 252.3026 | 251.4102
1166.4573 | 327.8022 | 252.3385 | 251.2797
1167.4573 | 327.811 | 252.3656 | 251.3149
1168.4573 | 327.8554 | 252.4044 | 251.3279
1169.4573 | 327.9173 | 252.4241 | 251.3492
1170.4573 | 327.9171 | 252.469 | 251.3831
1171.4573 | 327.9755 | 252.4884 | 251.4067
1172.4573 | 328.0229 | 252.5149 | 251.4349
1173.4573 | 328.0654 | 252.5366 | 251.4697
1174.4573 | 328.1908 | 252.5622 | 251.5118
1175.4573 | 328.2218 | 252.5914 | 251.5475
1176.4573 | 328.1482 | 252.6277 | 251.5777
1177.4573 | 328.0972 | 252.6611 | 251.6034
1178.4573 | 328.115 | 252.6833 | 251.5806
1179.4573 | 328.0977 | 252.705 | 251.6024
1180.4573 | 328.0641 | 252.7472 | 251.6326
1181.4573 | 328.0664 | 252.7665 | 251.6583
1182.4573 | 328.0785 | 252.781 | 251.6791
1183.4573 | 328.0621 | 252.8054 | 251.7166
1184.4573 | 328.0624 | 252.839 | 251.738
1185.4573 | 327.8604 | 252.8593 | 251.7687
1186.4573 | 327.8008 | 252.872 | 251.7943
1187.4573 | 327.8008 | 252.896 | 251.83
1188.4573 | 327.7193 | 252.9387 | 251.847
1189.4573 | 327.6617 | 252.9611 | 251.8804
1190.4573 | 327.6825 | 252.9764 | 251.9047
1191.4573 | 327.7606 | 252.9997 | 251.9355
1192.4573 | 327.8735 | 253.0159 | 251.9591
1193.4573 | 327.8601 | 253.0545 | 251.9914
1194.4573 | 327.7927 | 253.0736 | 252.0305
1195.4573 | 327.7639 | 253.1086 | 252.0524
1196.4573 | 327.7211 | 253.1284 | 252.081
1197.4573 | 327.6978 | 253.1468 | 252.106
1198.4573 | 327.6998 | 253.1774 | 252.1372
1199.4573 | 327.7358 | 253.1967 | 252.1546
1200.4573 | 327.6108 | 253.2168 | 252.1831
1201.4573 | 327.6077 | 253.2468 | 252.2068
1202.4573 | 327.5764 | 253.2804 | 252.2289
1203.4573 | 327.6138 | 253.3024 | 252.2538
1204.4573 | 327.5684 | 253.3168 | 252.2839
1205.4573 | 327.5655 | 253.3387 | 252.3062
1206.4573 | 327.5393 | 253.367 | 252.3438
1207.4573 | 327.5406 | 253.4024 | 252.3636
1208.4573 | 327.6216 | 253.4177 | 252.3884
1209.4573 | 327.6113 | 253.4428 | 252.409
1210.4573 | 327.5676 | 253.4696 | 252.4349
1211.4573 | 327.4938 | 253.4902 | 252.5
1212.4573 | 327.3983 | 253.497 | 252.5286
1213.4573 | 327.4131 | 253.5473 | 252.5452
1214.4573 | 327.4519 | 253.559 | 252.5676
1215.4573 | 327.471 | 253.5847 | 252.5931
1216.4573 | 327.5817 | 253.61 | 252.6162
1217.4573 | 327.6661 | 253.6315 | 252.6391
1218.4573 | 327.6743 | 253.6573 | 252.6583
1219.4573 | 327.6124 | 253.6778 | 252.6793
1220.4573 | 327.559 | 253.7012 | 252.7018
1221.4573 | 327.5915 | 253.707 | 252.7209
1222.4573 | 327.6517 | 253.7385 | 252.7397
1223.4573 | 327.6321 | 253.7655 | 252.7007
1224.4573 | 327.5922 | 253.7844 | 252.7337
1225.4573 | 327.592 | 253.8061 | 252.7606
1226.4573 | 327.6365 | 253.8323 | 252.7802
1227.4573 | 327.6887 | 253.8353 | 252.8704
1228.4573 | 327.6804 | 253.855 | 252.8931
1229.4573 | 327.666 | 253.8875 | 252.9249
1230.4573 | 327.6852 | 253.9094 | 252.9334
1231.4573 | 327.7566 | 253.9281 | 252.9407
1232.4573 | 327.8379 | 253.9423 | 252.954
1233.4573 | 327.822 | 253.9763 | 252.9184
1234.4573 | 327.7404 | 253.9886 | 252.944
1235.4573 | 327.7607 | 254.0194 | 252.9709
1236.4573 | 327.7313 | 254.0157 | 252.9927
1237.4573 | 327.6786 | 254.0569 | 253.0143
1238.4573 | 327.6432 | 254.0878 | 253.0389
1239.4573 | 327.5943 | 254.1076 | 253.0711
1240.4573 | 327.5059 | 254.1261 | 253.0961
1241.4573 | 327.5053 | 254.1463 | 253.1208
1242.4573 | 327.5787 | 254.1681 | 253.1471
1243.4573 | 327.5723 | 254.1948 | 253.163
1244.4573 | 327.5804 | 254.2136 | 253.1854
1245.4573 | 327.6217 | 254.244 | 253.206
1246.4573 | 327.6809 | 254.2569 | 253.2308
1247.4573 | 327.6909 | 254.2901 | 253.2584
1248.4573 | 327.7075 | 254.2973 | 253.2853
1249.4573 | 327.7263 | 254.3284 | 253.3117
1250.4573 | 327.7249 | 254.3431 | 253.3304
1251.4573 | 327.6794 | 254.3713 | 253.3572
1252.4573 | 327.6286 | 254.3862 | 253.3707
1253.4573 | 327.6541 | 254.4173 | 253.3918
1254.4573 | 327.6745 | 254.432 | 253.4313
1255.4573 | 327.7543 | 254.4486 | 253.4551
1256.4573 | 327.7674 | 254.4731 | 253.4626
1257.4573 | 327.7221 | 254.5017 | 253.4898
1258.4573 | 327.6692 | 254.5317 | 253.5053
1259.4573 | 327.7669 | 254.5369 | 253.5271
1260.4573 | 327.7879 | 254.5573 | 253.5452
1261.4573 | 327.719 | 254.5685 | 253.5617
1262.4573 | 327.7058 | 254.5837 | 253.5829
1263.4573 | 327.69 | 254.6033 | 253.5919
1264.4573 | 327.7128 | 254.6267 | 253.6083
1265.4573 | 327.751 | 254.6566 | 253.6307
1266.4573 | 327.8366 | 254.6734 | 253.6391
1267.4573 | 327.924 | 254.6883 | 253.6575
1268.4573 | 327.8932 | 254.709 | 253.6822
1269.4573 | 327.9432 | 254.7215 | 253.6973
1270.4573 | 327.9742 | 254.745 | 253.7159
1271.4573 | 327.9948 | 254.7761 | 253.7339
1272.4573 | 328.0093 | 254.791 | 253.7608
1273.4573 | 327.9614 | 254.8078 | 253.7987
1274.4573 | 327.9099 | 254.8176 | 253.8244
1275.4573 | 327.9003 | 254.8244 | 253.8942
1276.4573 | 327.9042 | 254.8488 | 253.9394
1277.4573 | 327.9474 | 254.849 | 253.9584
1278.4573 | 327.9275 | 254.879 | 253.9829
1279.4573 | 327.8675 | 254.8998 | 254.008
1280.4573 | 327.8588 | 254.9163 | 254.0247
1281.4573 | 327.8281 | 254.9234 | 254.0293
1282.4573 | 327.8543 | 254.9519 | 254.0712
1283.4573 | 327.888 | 254.9553 | 254.0956
1284.4573 | 327.9758 | 254.9692 | 254.1294
1285.4573 | 328.0459 | 254.994 | 254.1428
1286.4573 | 328.0444 | 255.0117 | 254.1494
1287.4573 | 328.0304 | 255.0195 | 254.1743
1288.4573 | 327.9693 | 255.0686 | 254.1895
1289.4573 | 328.0312 | 255.0839 | 254.2025
1290.4573 | 328.0828 | 255.1039 | 254.2169
1291.4573 | 328.1389 | 255.119 | 254.2217
1292.4573 | 328.1234 | 255.1424 | 254.2411
1293.4573 | 328.1057 | 255.1488 | 254.2484
1294.4573 | 328.018 | 255.1824 | 254.2771
1295.4573 | 327.9226 | 255.1948 | 254.2916
1296.4573 | 327.8301 | 255.2109 | 254.3049
1297.4573 | 327.8704 | 255.2319 | 254.3337
1298.4573 | 327.8272 | 255.2502 | 254.3455
1299.4573 | 327.837 | 255.2567 | 254.3548
1300.4573 | 327.8004 | 255.2892 | 254.3737
1301.4573 | 327.762 | 255.291 | 254.3909
1302.4573 | 327.6632 | 255.3249 | 254.4127
1303.4573 | 327.6783 | 255.3322 | 254.4317
1304.4573 | 327.6672 | 255.3461 | 254.4468
1305.4573 | 327.6697 | 255.3712 | 254.4742
1306.4573 | 327.5917 | 255.396 | 254.4925
1307.4573 | 327.5173 | 255.4098 | 254.5136
1308.4573 | 327.4559 | 255.4219 | 254.5203
1309.4573 | 327.4754 | 255.4415 | 254.5374
1310.4573 | 327.4586 | 255.4611 | 254.5473
1311.4573 | 327.5148 | 255.4748 | 254.5648
1312.4573 | 327.5263 | 255.4846 | 254.5863
1313.4573 | 327.46 | 255.5083 | 254.5966
1314.4573 | 327.4507 | 255.5179 | 254.626
1315.4573 | 327.519 | 255.5367 | 254.6349
1316.4573 | 327.4972 | 255.5544 | 254.6636
1317.4573 | 327.4093 | 255.5646 | 254.6609
1318.4573 | 327.4371 | 255.5779 | 254.6778
1319.4573 | 327.4537 | 255.6084 | 254.6949
1320.4573 | 327.4347 | 255.6153 | 254.7011
1321.4573 | 327.2839 | 255.6365 | 254.7233
1322.4573 | 327.2948 | 255.6453 | 254.7316
1323.4573 | 327.3259 | 255.6624 | 254.7392
1324.4573 | 327.2543 | 255.6903 | 254.756
1325.4573 | 327.3115 | 255.6978 | 254.7654
1326.4573 | 327.2603 | 255.7168 | 254.7762
1327.4573 | 327.3625 | 255.7261 | 254.7671
1328.4573 | 327.3795 | 255.7487 | 254.7931
1329.4573 | 327.4897 | 255.7562 | 254.8104
1330.4573 | 327.6358 | 255.7652 | 254.8141
1331.4573 | 327.671 | 255.7815 | 254.7956
1332.4573 | 327.6948 | 255.7964 | 254.8158
1333.4573 | 327.7348 | 255.8088 | 254.8303
1334.4573 | 327.7653 | 255.8253 | 254.8461
1335.4573 | 327.9285 | 255.8352 | 254.857
1336.4573 | 328.0991 | 255.8515 | 254.8798
1337.4573 | 328.1309 | 255.8678 | 254.8906
1338.4573 | 328.1224 | 255.8826 | 254.9066
1339.4573 | 328.1313 | 255.9061 | 254.9214
1340.4573 | 327.9858 | 255.9201 | 254.9356
1341.4573 | 327.8384 | 255.9241 | 254.9516
1342.4573 | 327.6346 | 255.949 | 254.9619
1343.4573 | 327.3375 | 255.9555 | 254.9764
1344.4573 | 327.0644 | 255.9767 | 254.9927
1345.4573 | 326.8552 | 255.9777 | 255.0124
1346.4573 | 326.5007 | 256.0002 | 255.0268
1347.4573 | 326.0935 | 256.0208 | 255.042
1348.4573 | 325.7513 | 256.0366 | 255.0637
1349.4573 | 325.3349 | 256.025 | 255.0933
1350.4573 | 324.8805 | 256.0559 | 255.063
1351.4573 | 324.498 | 256.0709 | 255.0776
1352.4573 | 324.1361 | 256.0926 | 255.0902
1353.4573 | 323.8246 | 256.0925 | 255.1065
1354.4573 | 323.5993 | 256.1198 | 255.115
1355.4573 | 323.2655 | 256.1404 | 255.1256
1356.4573 | 322.813 | 256.1567 | 255.1426
1357.4573 | 322.378 | 256.1596 | 255.1692
1358.4573 | 321.9726 | 256.178 | 255.1796
1359.4573 | 321.5509 | 256.1829 | 255.2018
1360.4573 | 321.0573 | 256.2127 | 255.2076
1361.4573 | 320.523 | 256.2196 | 255.2262
1362.4573 | 320.1762 | 256.2353 | 255.2477
1363.4573 | 319.7627 | 256.2525 | 255.2672
1364.4573 | 319.3436 | 256.2665 | 255.2766
1365.4573 | 318.916 | 256.2716 | 255.2976
1366.4573 | 318.495 | 256.2841 | 255.3164
1367.4573 | 318.1373 | 256.2913 | 255.3344
1368.4573 | 317.6685 | 256.3119 | 255.3449
1369.4573 | 317.2803 | 256.3308 | 255.3608
1370.4573 | 316.8873 | 256.3288 | 255.3672
1371.4573 | 316.5289 | 256.3424 | 255.3787
1372.4573 | 316.1663 | 256.3558 | 255.3919
1373.4573 | 315.8172 | 256.3744 | 255.3976
1374.4573 | 315.5117 | 256.3749 | 255.4101
1375.4573 | 314.9823 | 256.3884 | 255.4229
1376.4573 | 314.5785 | 256.4097 | 255.4287
1377.4573 | 314.1841 | 256.3999 | 255.4304
1378.4573 | 313.8591 | 256.4204 | 255.4441
1379.4573 | 313.4511 | 256.4393 | 255.445
1380.4573 | 313.0039 | 256.4462 | 255.4505
1381.4573 | 312.5291 | 256.4418 | 255.4731
1382.4573 | 312.1074 | 256.4663 | 255.4833
1383.4573 | 311.6834 | 256.4557 | 255.4907
1384.4573 | 311.2079 | 256.4726 | 255.4908
1385.4573 | 310.6457 | 256.4723 | 255.4877
1386.4573 | 310.1598 | 256.4825 | 255.4903
1387.4573 | 309.7459 | 256.4827 | 255.5049
1388.4573 | 309.3287 | 256.4847 | 255.4934
1389.4573 | 308.9049 | 256.4752 | 255.5025
1390.4573 | 308.4152 | 256.4788 | 255.4981
1391.4573 | 307.9481 | 256.4864 | 255.4954
1392.4573 | 307.6286 | 256.4915 | 255.4956
1393.4573 | 307.2715 | 256.4911 | 255.5015
1394.4573 | 306.9642 | 256.4831 | 255.528
1395.4573 | 306.5297 | 256.474 | 255.5167
1396.4573 | 306.0876 | 256.4771 | 255.5103
1397.4573 | 305.5696 | 256.4791 | 255.505
1398.4573 | 305.0607 | 256.4739 | 255.4946
1399.4573 | 304.6858 | 256.4825 | 255.4871
1400.4573 | 304.2641 | 256.4687 | 255.4779
1401.4573 | 303.8564 | 256.4556 | 255.4651
1402.4573 | 303.5308 | 256.444 | 255.443
1403.4573 | 303.1766 | 256.437 | 255.49
1404.4573 | 302.8071 | 256.4345 | 255.5174
1405.4573 | 302.4178 | 256.4226 | 255.5016
1406.4573 | 301.9781 | 256.4109 | 255.4891
1407.4573 | 301.4833 | 256.386 | 255.4771
1408.4573 | 301.0477 | 256.3936 | 255.4513
1409.4573 | 300.5729 | 256.3942 | 255.439
1410.4573 | 300.149 | 256.3746 | 255.4178
1411.4573 | 299.7231 | 256.3486 | 255.3786
1412.4573 | 299.3398 | 256.3442 | 255.3231
1413.4573 | 298.8682 | 256.3318 | 255.3059
1414.4573 | 298.4289 | 256.3073 | 255.2923
1415.4573 | 297.995 | 256.2889 | 255.267
1416.4573 | 297.6296 | 256.2869 | 255.2357
1417.4573 | 297.2506 | 256.2584 | 255.2044
1418.4573 | 296.7223 | 256.2374 | 255.1721
1419.4573 | 296.2696 | 256.2068 | 255.1495
1420.4573 | 295.7978 | 256.1883 | 255.1171
1421.4573 | 295.433 | 256.1726 | 255.0867
1422.4573 | 295.0453 | 256.142 | 255.0312
1423.4573 | 294.7093 | 256.1072 | 255.002
1424.4573 | 294.3473 | 256.0959 | 254.9734
1425.4573 | 293.9783 | 256.0635 | 254.9379
1426.4573 | 293.4777 | 256.032 | 254.9137
1427.4573 | 292.9677 | 255.9908 | 254.8737
1428.4573 | 292.5352 | 255.974 | 254.8426
1429.4573 | 292.1582 | 255.9341 | 254.798
1430.4573 | 291.8661 | 255.9104 | 254.7625
1431.4573 | 291.5149 | 255.877 | 254.7343
1432.4573 | 291.1298 | 255.8435 | 254.7026
1433.4573 | 290.7119 | 255.8011 | 254.6694
1434.4573 | 290.3498 | 255.7801 | 254.6265
1435.4573 | 289.9114 | 255.7475 | 254.6056
1436.4573 | 289.4818 | 255.6867 | 254.5998
1437.4573 | 289.1703 | 255.664 | 254.564
1438.4573 | 288.7612 | 255.62 | 254.5216
1439.4573 | 288.3831 | 255.5818 | 254.4817
1440.4573 | 288.0331 | 255.5483 | 254.4374
1441.4573 | 287.658 | 255.4944 | 254.4048
1442.4573 | 287.217 | 255.4584 | 254.3599
1443.4573 | 286.7818 | 255.4228 | 254.3002
1444.4573 | 286.402 | 255.3725 | 254.2135
1445.4573 | 285.9955 | 255.3334 | 254.1737
1446.4573 | 285.6289 | 255.29 | 254.1279
1447.4573 | 285.2658 | 255.2347 | 254.0812
1448.4573 | 284.9193 | 255.2068 | 254.0295
1449.4573 | 284.5539 | 255.1643 | 253.9801
1450.4573 | 284.2012 | 255.1153 | 253.9258
1451.4573 | 283.8436 | 255.0581 | 253.8695
1452.4573 | 283.4099 | 255.013 | 253.8194
1453.4573 | 283.0515 | 254.9625 | 253.7776
1454.4573 | 282.6863 | 254.8963 | 253.7429
1455.4573 | 282.3497 | 254.8523 | 253.704
1456.4573 | 281.9338 | 254.8073 | 253.6213
1457.4573 | 281.5183 | 254.7588 | 253.5807
1458.4573 | 281.1146 | 254.7142 | 253.5057
1459.4573 | 280.6864 | 254.6639 | 253.4619
1460.4573 | 280.3078 | 254.5964 | 253.4219
1461.4573 | 279.9868 | 254.5375 | 253.3638
1462.4573 | 279.5752 | 254.4885 | 253.3037
1463.4573 | 279.2048 | 254.4197 | 253.2466
1464.4573 | 278.8467 | 254.3686 | 253.1795
1465.4573 | 278.5091 | 254.3107 | 253.1365
1466.4573 | 278.0712 | 254.2517 | 253.0818
1467.4573 | 277.6829 | 254.1978 | 252.9798
1468.4573 | 277.3312 | 254.1346 | 252.9172
1469.4573 | 276.9545 | 254.064 | 252.8449
1470.4573 | 276.6025 | 254.0184 | 252.7832
1471.4573 | 276.2711 | 253.9522 | 252.7153
1472.4573 | 275.9188 | 253.8828 | 252.6487
1473.4573 | 275.6193 | 253.8077 | 252.5902
1474.4573 | 275.2959 | 253.7539 | 252.5143
1475.4573 | 274.9199 | 253.6702 | 252.4865
1476.4573 | 274.5241 | 253.5999 | 252.3975
1477.4573 | 274.1604 | 253.5333 | 252.3432
1478.4573 | 273.7735 | 253.4512 | 252.2545
1479.4573 | 273.4934 | 253.3824 | 252.1777
1480.4573 | 273.1389 | 253.3122 | 252.0983
1481.4573 | 272.7806 | 253.249 | 252.0252
1482.4573 | 272.4162 | 253.1751 | 251.9823
1483.4573 | 272.013 | 253.0912 | 251.9077
1484.4573 | 271.642 | 253.01 | 251.8276
1485.4573 | 271.209 | 252.9497 | 251.7257
1486.4573 | 270.7752 | 252.8736 | 251.6465
1487.4573 | 270.3419 | 252.7916 | 251.569
1488.4573 | 270 | 252.729 | 251.4885
1489.4573 | 269.5805 | 252.6413 | 251.4059
1490.4573 | 268.907 | 252.5592 | 251.3256
1491.4573 | 268.8529 | 252.4797 | 251.2423
1492.4573 | 268.5531 | 252.3908 | 251.162
1493.4573 | 268.2536 | 252.3291 | 251.1027
1494.4573 | 267.8812 | 252.2427 | 251.0179
1495.4573 | 267.5078 | 252.1555 | 250.9322
1496.4573 | 267.2018 | 252.0738 | 250.8451
1497.4573 | 266.8286 | 251.977 | 250.7595
1498.4573 | 266.4153 | 251.9013 | 250.6652
1499.4573 | 266.0206 | 251.8183 | 250.577
1500.4573 | 265.6612 | 251.7246 | 250.4781
1501.4573 | 265.3592 | 251.639 | 250.3941
1502.4573 | 264.9154 | 251.5547 | 250.3036
1503.4573 | 264.5073 | 251.4652 | 250.2152
1504.4573 | 264.2162 | 251.3824 | 250.1279
1505.4573 | 263.9082 | 251.2818 | 250.0332
1506.4573 | 263.606 | 251.2003 | 249.937
1507.4573 | 263.3294 | 251.112 | 249.8433
1508.5823 | 262.9293 | 250.998 | 249.7447
1509.4573 | 262.6239 | 250.9302 | 249.6677
1510.4573 | 262.25 | 250.8333 | 249.5694
1511.5042 | 261.9047 | 250.7403 | 249.4749
1512.551 | 261.5637 | 250.6526 | 249.3716
1513.4573 | 261.274 | 250.5635 | 249.2914
1514.4573 | 260.9032 | 250.4723 | 249.1896
1515.4573 | 260.5637 | 250.3735 | 249.0942
1516.4729 | 260.2647 | 250.2945 | 248.994
1517.4573 | 259.8878 | 250.1941 | 248.8966
1518.4573 | 259.5093 | 250.0949 | 248.7952
1519.4573 | 259.1756 | 249.9985 | 248.7007
1520.4573 | 258.8012 | 249.897 | 248.6019
1521.4573 | 258.5038 | 249.7993 | 248.4969
1522.4573 | 258.1651 | 249.6957 | 248.3955
1523.4573 | 257.8702 | 249.5821 | 248.2941
1524.4573 | 257.5255 | 249.4938 | 248.1923
1525.4573 | 257.1564 | 249.3859 | 248.0747
1526.4573 | 256.8101 | 249.2948 | 247.9859
1527.4573 | 256.5058 | 249.1818 | 247.8757
1528.4573 | 256.1878 | 249.0621 | 247.7712
1529.4573 | 255.8551 | 248.9749 | 247.66
1530.4573 | 255.5169 | 248.859 | 247.562
1531.4573 | 255.1799 | 248.728 | 247.4495
1532.4573 | 254.8653 | 248.6468 | 247.3349
1533.4573 | 254.5962 | 248.5564 | 247.1991
1534.4573 | 254.321 | 248.4353 | 247.0932
1535.4573 | 254.0649 | 248.3311 | 246.9822
1536.4573 | 253.7458 | 248.2332 | 246.8717
1537.4573 | 253.405 | 248.1107 | 246.7524
1538.4573 | 253.015 | 247.9989 | 246.634
1539.4573 | 252.6321 | 247.8971 | 246.5307
1540.4573 | 252.2898 | 247.773 | 246.4136
1541.4573 | 252.0021 | 247.6686 | 246.3049
1542.4573 | 251.713 | 247.5601 | 246.1892
1543.4573 | 251.3481 | 247.4396 | 246.0755
1544.4573 | 251.0289 | 247.3384 | 245.9634
1545.4573 | 250.6794 | 247.2151 | 245.8457
1546.4573 | 250.3434 | 247.1 | 245.7361
1547.4573 | 250.0135 | 246.9909 | 245.6204
1548.4573 | 249.6443 | 246.8634 | 245.4906
1549.4573 | 249.3246 | 246.7576 | 245.3782
1550.4573 | 248.9794 | 246.6399 | 245.2633
1551.4573 | 248.6427 | 246.5188 | 245.1463
1552.4573 | 248.3358 | 246.4002 | 245.0232
1553.4573 | 248.037 | 246.292 | 244.9039
1554.4573 | 247.8186 | 246.1634 | 244.7878
1555.4573 | 247.4903 | 246.0561 | 244.6626
1556.4573 | 247.1786 | 245.9345 | 244.5497
1557.4573 | 246.806 | 245.8171 | 244.4279
1558.4573 | 246.4591 | 245.6979 | 244.304
1559.4573 | 246.1648 | 245.5733 | 244.1858
1560.4573 | 245.899 | 245.4364 | 244.058
1561.4573 | 245.6628 | 245.3257 | 243.9355
1562.4573 | 245.4162 | 245.1927 | 243.8172
1563.4573 | 245.0931 | 245.081 | 243.6895
1564.4573 | 244.8018 | 244.9468 | 243.5714
1565.4573 | 244.4552 | 244.8297 | 243.4429
1566.4573 | 244.1174 | 244.6961 | 243.3181
1567.4573 | 243.805 | 244.5818 | 243.1937
1568.4573 | 243.5469 | 244.4455 | 243.0737
1569.4573 | 243.2211 | 244.3155 | 242.9719
1570.4573 | 242.8842 | 244.2086 | 242.8442
1571.4573 | 242.5647 | 244.0744 | 242.7205
1572.4573 | 242.2979 | 243.9455 | 242.5934
1573.4573 | 242.049 | 243.8208 | 242.4684
1574.4573 | 241.7558 | 243.6817 | 242.3372
1575.4573 | 241.4596 | 243.5588 | 242.2071
1576.4573 | 241.095 | 243.4214 | 242.0758
1577.4573 | 240.7705 | 243.3039 | 241.9467
1578.4573 | 240.5046 | 243.1733 | 241.8163
1579.4573 | 240.2257 | 243.041 | 241.6898
1580.4573 | 239.9242 | 242.9063 | 241.5594
1581.4573 | 239.5898 | 242.7747 | 241.4249
1582.4573 | 239.2329 | 242.6453 | 241.3003
1583.4573 | 238.9294 | 242.5197 | 241.1619
1584.4573 | 238.6844 | 242.3815 | 241.0305
1585.4573 | 238.3677 | 242.2564 | 240.8943
1586.4573 | 238.068 | 242.1237 | 240.7647
1587.4573 | 237.7954 | 241.9907 | 240.6364
1588.4573 | 237.5073 | 241.8524 | 240.4985
1589.4573 | 237.1552 | 241.7142 | 240.364
1590.4573 | 236.8829 | 241.584 | 240.2287
1591.4573 | 236.6545 | 241.4524 | 240.0928
1592.4573 | 236.3806 | 241.3272 | 239.96
1593.4573 | 236.0947 | 241.1737 | 239.8174
1594.4573 | 235.8524 | 241.0489 | 239.6902
1595.4573 | 235.5616 | 240.9137 | 239.5507
1596.4573 | 235.257 | 240.7715 | 239.4135
1597.4573 | 234.9259 | 240.632 | 239.2716
1598.4573 | 234.6419 | 240.4934 | 239.1326
1599.4573 | 234.3933 | 240.346 | 238.9906
1600.4573 | 234.1274 | 240.2045 | 238.8521
1601.4573 | 233.815 | 240.0675 | 238.706
1602.4573 | 233.5295 | 239.9131 | 238.5643
1603.4573 | 233.2939 | 239.7683 | 238.4217
1604.4573 | 233.0286 | 239.6262 | 238.2829
1605.4573 | 232.7776 | 239.4949 | 238.1302
1606.4573 | 232.4822 | 239.3459 | 237.9886
1607.4573 | 232.1833 | 239.1886 | 237.8447
1608.4573 | 231.9858 | 239.0441 | 237.6944
1609.4573 | 231.7203 | 238.9024 | 237.5522
1610.4573 | 231.5064 | 238.7616 | 237.4101
1611.4573 | 231.2274 | 238.6126 | 237.2603
1612.4573 | 230.9012 | 238.4683 | 237.1178
1613.4573 | 230.5073 | 238.3233 | 236.9727
1614.4573 | 230.2021 | 238.159 | 236.822
1615.4573 | 229.8939 | 238.0326 | 236.6745
1616.4573 | 229.5934 | 237.8917 | 236.5305
1617.4573 | 229.3053 | 237.743 | 236.3864
1618.4573 | 228.9969 | 237.5888 | 236.2361
1619.4573 | 228.6896 | 237.4401 | 236.0883
1620.4573 | 228.4073 | 237.2931 | 235.924
1621.4573 | 228.1881 | 237.1377 | 235.7673
1622.4573 | 227.9111 | 237.0094 | 235.6105
1623.4573 | 227.5741 | 236.8583 | 235.4606
1624.4573 | 227.2927 | 236.7082 | 235.3134
1625.4573 | 227.0142 | 236.5638 | 235.1689
1626.4573 | 226.7781 | 236.4133 | 235.0131
1627.4573 | 226.4977 | 236.2575 | 234.8636
1628.4573 | 226.1798 | 236.115 | 234.7148
1629.4573 | 225.911 | 235.9588 | 234.5824
1630.4573 | 225.6118 | 235.8032 | 234.4295
1631.4573 | 225.3688 | 235.6406 | 234.2872
1632.4573 | 225.1338 | 235.4942 | 234.1414
1633.4573 | 224.9284 | 235.3516 | 233.9909
1634.4573 | 224.7246 | 235.2053 | 233.8364
1635.4573 | 224.52 | 235.0492 | 233.6854
1636.4573 | 224.3414 | 234.8934 | 233.531
1637.4573 | 224.4087 | 234.7417 | 233.3867
1638.4573 | 225.0985 | 234.5888 | 233.2271
1639.4573 | 226.7087 | 234.4416 | 233.0732
1640.4573 | 229.028 | 234.2837 | 232.9233
1641.4573 | 231.9673 | 234.1277 | 232.7719
1642.4573 | 235.3653 | 233.9732 | 232.6094
1643.4573 | 239.0023 | 233.8172 | 232.4609
1644.4573 | 242.8874 | 233.6541 | 232.3112
1645.4573 | 247.0386 | 233.5054 | 232.1577
1646.4573 | 251.4468 | 233.353 | 232
1647.4573 | 255.9998 | 233.1972 | 231.8488
1648.4573 | 260.6448 | 233.0447 | 231.6998
1649.4573 | 265.4119 | 232.8859 | 231.5487
1650.4573 | 270.1883 | 232.7271 | 231.3933
1651.4573 | 275.0361 | 232.5649 | 231.2481
1652.4573 | 279.7035 | 232.4261 | 231.0985
1653.4573 | 284.1517 | 232.266 | 230.9575
1654.4573 | 288.2619 | 232.1185 | 230.8092
1655.4573 | 292.1709 | 231.9718 | 230.6589
1656.4573 | 295.9465 | 231.8202 | 230.5194
1657.5823 | 300.0572 | 231.6538 | 230.349
1658.4573 | 303.2365 | 231.5163 | 230.2234
1659.4573 | 306.8529 | 231.3646 | 230.092
1660.4573 | 310.3004 | 231.211 | 229.9563
1661.4573 | 313.6107 | 231.0895 | 229.8295
1662.4573 | 316.6791 | 230.9528 | 229.6911
1663.4573 | 319.5247 | 230.8158 | 229.5644
1664.4573 | 322.1203 | 230.683 | 229.4486
1665.4573 | 324.4354 | 230.5548 | 229.329
1666.4573 | 326.3794 | 230.424 | 229.2114
1667.4573 | 328.0718 | 230.2909 | 229.1031
1668.4573 | 329.4922 | 230.1786 | 228.9881
1669.4573 | 330.6545 | 230.0633 | 228.8877
1670.4573 | 331.4688 | 229.9387 | 228.7939
1671.4573 | 332.2303 | 229.8323 | 228.6885
1672.4573 | 332.7331 | 229.7235 | 228.5919
1673.4573 | 333.0983 | 229.623 | 228.4978
1674.4573 | 333.4036 | 229.5245 | 228.4238
1675.4573 | 333.5185 | 229.435 | 228.3426
1676.4573 | 333.5262 | 229.3548 | 228.2611
1677.4573 | 333.5404 | 229.2583 | 228.184
1678.4573 | 333.4407 | 229.1687 | 228.1095
1679.4573 | 333.3217 | 229.108 | 228.04
1680.4573 | 333.1551 | 229.0328 | 227.9813
1681.4573 | 332.9384 | 228.9677 | 227.9215
1682.4573 | 332.7453 | 228.904 | 227.8669
1683.4573 | 332.4801 | 228.8404 | 227.8125
1684.4573 | 332.1657 | 228.7812 | 227.7653
1685.4573 | 331.8991 | 228.7251 | 227.7124
1686.4573 | 331.6166 | 228.6896 | 227.6699
1687.4573 | 331.3524 | 228.6226 | 227.6347
1688.4573 | 330.899 | 228.5834 | 227.5879
1689.4573 | 330.5483 | 228.5427 | 227.5554
1690.4573 | 330.1128 | 228.513 | 227.5302
1691.4573 | 329.5856 | 228.4788 | 227.503
1692.4885 | 329.1685 | 228.4627 | 227.4716
1693.551 | 328.8156 | 228.4326 | 227.4519
1694.4729 | 328.508 | 228.4095 | 227.4347
1695.4573 | 328.208 | 228.4003 | 227.4149
1696.4729 | 327.785 | 228.3688 | 227.4051
1697.4885 | 327.2619 | 228.366 | 227.3967
1698.4573 | 326.8073 | 228.3497 | 227.3867
1699.4573 | 326.4782 | 228.3454 | 227.3802
1700.4573 | 326.193 | 228.3379 | 227.3817
1701.4573 | 326.0609 | 228.334 | 227.3724
1702.4573 | 325.904 | 228.3439 | 227.379
1703.4573 | 325.7249 | 228.3527 | 227.3788
1704.4573 | 325.4503 | 228.3453 | 227.3835
1705.4573 | 325.2082 | 228.3618 | 227.3917
1706.4573 | 325.0937 | 228.3802 | 227.3966
1707.4573 | 324.9107 | 228.3841 | 227.415
1708.4573 | 324.6309 | 228.4062 | 227.4172
1709.4573 | 324.4223 | 228.4233 | 227.4338
1710.4573 | 324.4332 | 228.433 | 227.4514
1711.4573 | 324.4747 | 228.4523 | 227.4713
1712.4573 | 324.4387 | 228.4753 | 227.4849
1713.4573 | 324.4325 | 228.4911 | 227.5144
1714.4573 | 324.456 | 228.5246 | 227.5368
1715.4573 | 324.4356 | 228.5304 | 227.5596
1716.4573 | 324.4825 | 228.5755 | 227.5887
1717.4573 | 324.6118 | 228.5981 | 227.6158
1718.4573 | 324.7189 | 228.6294 | 227.6431
1719.4573 | 324.8192 | 228.6362 | 227.6776
1720.4573 | 324.8631 | 228.6783 | 227.704
1721.4573 | 325.0451 | 228.7249 | 227.7348
1722.4573 | 325.0926 | 228.7519 | 227.7723
1723.4573 | 325.2572 | 228.7905 | 227.8087
1724.4573 | 325.5117 | 228.8392 | 227.8421
1725.4573 | 325.7863 | 228.8684 | 227.8794
1726.4573 | 325.9525 | 228.9073 | 227.9097
1727.4573 | 325.9963 | 228.9437 | 227.9481
1728.4573 | 326.1334 | 228.9866 | 227.99
1729.4573 | 326.3182 | 229.021 | 228.0284
1730.4573 | 326.5117 | 229.0658 | 228.0641
1731.4573 | 326.7045 | 229.1022 | 228.1031
1732.4573 | 326.8392 | 229.1458 | 228.149
1733.4573 | 326.9767 | 229.1919 | 228.1918
1734.4573 | 327.0878 | 229.236 | 228.233
1735.4573 | 327.2448 | 229.2861 | 228.2883
1736.4573 | 327.2936 | 229.3272 | 228.3336
1737.4573 | 327.4201 | 229.3738 | 228.3746
1738.4573 | 327.5164 | 229.4342 | 228.4264
1739.4573 | 327.6169 | 229.4732 | 228.4745
1740.4573 | 327.7381 | 229.5132 | 228.5266
1741.4573 | 327.8894 | 229.5734 | 228.5778
1742.4573 | 328.0111 | 229.6309 | 228.6296
1743.4573 | 328.0934 | 229.6644 | 228.6896
1744.4573 | 328.254 | 229.7341 | 228.7358
1745.4573 | 328.3683 | 229.7761 | 228.7853
1746.4573 | 328.4201 | 229.8499 | 228.8353
1747.4573 | 328.4771 | 229.8971 | 228.8969
1748.4573 | 328.5001 | 229.9523 | 228.9555
1749.4573 | 328.6114 | 230.0158 | 229.015
1750.4573 | 328.7045 | 230.0561 | 229.0714
1751.4573 | 328.7409 | 230.1275 | 229.1242
1752.4573 | 328.7983 | 230.1761 | 229.1843
1753.4573 | 328.7638 | 230.2303 | 229.245
1754.4573 | 328.7406 | 230.2914 | 229.3049
1755.4573 | 328.6634 | 230.351 | 229.3679
1756.4573 | 328.6003 | 230.4085 | 229.4308
1757.4573 | 328.6107 | 230.4568 | 229.486
1758.4573 | 328.6892 | 230.5275 | 229.5466
1759.4573 | 328.7099 | 230.5783 | 229.6004
1760.4573 | 328.6205 | 230.6332 | 229.6643
1761.4573 | 328.5723 | 230.7057 | 229.73
1762.4573 | 328.4758 | 230.7666 | 229.7848
1763.4573 | 328.4915 | 230.8314 | 229.8496
1764.4573 | 328.4994 | 230.8808 | 229.9151
1765.4573 | 328.552 | 230.96 | 229.9809
1766.4573 | 328.5492 | 231.0148 | 230.0495
1767.4573 | 328.4932 | 231.0907 | 230.1169
1768.4573 | 328.5335 | 231.1353 | 230.1809
1769.4573 | 328.5108 | 231.1806 | 230.2368
1770.4573 | 328.4245 | 231.2682 | 230.3051
1771.4573 | 328.3547 | 231.336 | 230.3703
1772.4573 | 328.3943 | 231.4017 | 230.4343
1773.4573 | 328.3951 | 231.4806 | 230.5029
1774.4573 | 328.3851 | 231.5312 | 230.5696
1775.4573 | 328.362 | 231.6024 | 230.635
1776.4573 | 328.3618 | 231.6797 | 230.6947
1777.4573 | 328.4104 | 231.7452 | 230.7631
1778.4573 | 328.4148 | 231.8162 | 230.8328
1779.4573 | 328.4471 | 231.8597 | 230.8964
1780.4573 | 328.5312 | 231.9344 | 230.97
1781.4573 | 328.5204 | 232.0065 | 231.0347
1782.4573 | 328.4718 | 232.0677 | 231.1024
1783.4573 | 328.4702 | 232.1462 | 231.1691
1784.4573 | 328.4643 | 232.2224 | 231.2427
1785.4573 | 328.4351 | 232.2826 | 231.3091
1786.4573 | 328.3896 | 232.3673 | 231.3822
1787.4573 | 328.3245 | 232.4283 | 231.4471
1788.4573 | 328.3552 | 232.4973 | 231.5165
1789.4573 | 328.337 | 232.5768 | 231.5876
1790.4573 | 328.3073 | 232.6514 | 231.6601
1791.4573 | 328.287 | 232.7227 | 231.7262
1792.4573 | 328.2703 | 232.7923 | 231.7961
1793.4573 | 328.2927 | 232.8655 | 231.8662
1794.4573 | 328.297 | 232.9382 | 231.9399
1795.4573 | 328.3417 | 233.0119 | 232.0071
1796.4573 | 328.2528 | 233.0697 | 232.0757
1797.4573 | 328.1962 | 233.1455 | 232.1445
1798.4573 | 328.1782 | 233.2253 | 232.2196
1799.4573 | 328.047 | 233.2876 | 232.2878
1800.4573 | 328.0077 | 233.3653 | 232.3613
1801.4573 | 327.9103 | 233.444 | 232.4578
1802.4573 | 327.7809 | 233.5107 | 232.5075
1803.4573 | 327.7486 | 233.5872 | 232.6022
1804.4573 | 327.7875 | 233.6542 | 232.6737
1805.4573 | 327.9241 | 233.7314 | 232.7446
1806.4573 | 327.931 | 233.8149 | 232.7908
1807.4573 | 327.8913 | 233.8813 | 232.8549
1808.4573 | 327.7846 | 233.9414 | 232.921
1809.4573 | 327.7744 | 234.0181 | 233.0019
1810.4573 | 327.8779 | 234.0906 | 233.0726
1811.4573 | 327.9472 | 234.1659 | 233.1432
1812.4573 | 328.0328 | 234.2186 | 233.2158
1813.4573 | 328.0651 | 234.2804 | 233.2783
1814.4573 | 328.1035 | 234.3716 | 233.3497
1815.4573 | 328.0964 | 234.4312 | 233.4268
1816.4573 | 328.1572 | 234.5119 | 233.4914
1817.4573 | 328.1413 | 234.571 | 233.5733
1818.4573 | 328.1098 | 234.6452 | 233.6331
1819.4573 | 328.0352 | 234.7032 | 233.7063
1820.4573 | 327.9417 | 234.7902 | 233.7765
1821.4573 | 327.8696 | 234.8597 | 233.8508
1822.4573 | 327.901 | 234.9489 | 233.9261
1823.4573 | 327.9074 | 235.014 | 233.9957
1824.4573 | 327.9196 | 235.1075 | 234.0609
1825.4573 | 327.9736 | 235.1663 | 234.133
1826.4573 | 327.9478 | 235.2424 | 234.202
1827.4573 | 327.9763 | 235.3234 | 234.2765
1828.4573 | 327.9147 | 235.3988 | 234.3452
1829.4573 | 327.8994 | 235.4533 | 234.4187
1830.4573 | 327.8224 | 235.5361 | 234.486
1831.4573 | 327.8179 | 235.6087 | 234.5671
1832.4573 | 327.7958 | 235.6658 | 234.6419
1833.4573 | 327.7885 | 235.7446 | 234.7146
1834.4573 | 327.8678 | 235.8189 | 234.7751
1835.4573 | 327.8974 | 235.8808 | 234.8481
1836.4573 | 327.8689 | 235.9552 | 234.9225
1837.4573 | 327.8958 | 236.0205 | 234.9904
1838.4573 | 327.9027 | 236.1075 | 235.0633
1839.4573 | 328.0176 | 236.1609 | 235.1467
1840.4573 | 328.0638 | 236.2276 | 235.2165
1841.4573 | 328.0346 | 236.3043 | 235.2888
1842.4573 | 327.9998 | 236.3638 | 235.3514
1843.4573 | 328.0131 | 236.4532 | 235.4307
1844.4573 | 327.9774 | 236.5057 | 235.4967
1845.4573 | 327.9015 | 236.5962 | 235.5803
1846.4573 | 327.8496 | 236.6631 | 235.6751
1847.4573 | 327.9058 | 236.7208 | 235.7557
1848.4573 | 327.9244 | 236.8133 | 235.8275
1849.4573 | 327.9991 | 236.8765 | 235.9037
1850.4573 | 328.0186 | 236.9412 | 235.9786
1851.4573 | 327.9938 | 237.0134 | 236.0489
1852.4573 | 327.8974 | 237.0884 | 236.1134
1853.4573 | 327.8207 | 237.143 | 236.1942
1854.4573 | 327.7727 | 237.2158 | 236.2646
1855.4573 | 327.838 | 237.3024 | 236.3271
1856.4573 | 327.8742 | 237.3619 | 236.3861
1857.4573 | 327.843 | 237.4277 | 236.4427
1858.4573 | 327.8145 | 237.4943 | 236.5133
1859.4573 | 327.8733 | 237.5585 | 236.575
1860.4573 | 327.9512 | 237.6226 | 236.628
1861.4573 | 328.0014 | 237.7063 | 236.6889
1862.4573 | 327.9697 | 237.7651 | 236.7557
1863.4573 | 327.9583 | 237.8312 | 236.8193
1864.4573 | 328.0022 | 237.8953 | 236.8855
1865.4573 | 328.0714 | 237.9655 | 236.9586
1866.4573 | 328.1238 | 238.0283 | 237.0209
1867.4573 | 328.1328 | 238.0999 | 237.0973
1868.4573 | 328.136 | 238.1689 | 237.1654
1869.4573 | 328.1144 | 238.2354 | 237.243
1870.4573 | 328.1523 | 238.3197 | 237.3221
1871.4573 | 328.2157 | 238.3812 | 237.3931
1872.4573 | 328.3297 | 238.4496 | 237.4738
1873.4573 | 328.3794 | 238.52 | 237.5725
1874.4573 | 328.3621 | 238.5871 | 237.6364
1875.4573 | 328.4373 | 238.6582 | 237.6929
1876.4729 | 328.5274 | 238.722 | 237.7588
1877.4573 | 328.5291 | 238.7864 | 237.8427
1878.4573 | 328.5008 | 238.8532 | 237.9196
1879.4573 | 328.5057 | 238.9344 | 237.9912
1880.4573 | 328.473 | 238.9874 | 238.1024
1881.4573 | 328.5305 | 239.064 | 238.1934
1882.4573 | 328.5402 | 239.1244 | 238.2496
1883.4573 | 328.5562 | 239.1905 | 238.3165
1884.4573 | 328.4864 | 239.2576 | 238.3688
1885.4573 | 328.468 | 239.3344 | 238.4079
1886.4573 | 328.4354 | 239.3939 | 238.4832
1887.4573 | 328.41 | 239.4536 | 238.5323
1888.4573 | 328.4776 | 239.5206 | 238.5152
1889.4573 | 328.4365 | 239.5879 | 238.5724
1890.4573 | 328.3251 | 239.6529 | 238.6463
1891.4573 | 328.3413 | 239.7274 | 238.7172
1892.4573 | 328.3245 | 239.8077 | 238.8147
1893.4573 | 328.296 | 239.8556 | 238.9138
1894.4573 | 328.2778 | 239.92 | 238.9847
1895.4573 | 328.2089 | 239.9938 | 239.0515
1896.4573 | 328.1446 | 240.046 | 239.1181
1897.4573 | 328.0921 | 240.1162 | 239.1381
1898.4573 | 328.0351 | 240.1873 | 239.2079
1899.4573 | 327.9672 | 240.2546 | 239.2686
1900.4573 | 327.9334 | 240.316 | 239.3308
1901.4573 | 327.9357 | 240.3885 | 239.3941
1902.4573 | 327.8876 | 240.4347 | 239.4547
1903.4573 | 327.8586 | 240.5102 | 239.5423
1904.4573 | 327.94 | 240.5826 | 239.611
1905.4573 | 327.9598 | 240.6487 | 239.6709
1906.4573 | 327.856 | 240.7237 | 239.7396
1907.4573 | 327.8751 | 240.7707 | 239.7951
1908.4573 | 327.8857 | 240.8434 | 239.8594
1909.4573 | 327.8685 | 240.9064 | 240.0051
1910.4573 | 327.8973 | 240.9705 | 240.0931
1911.4573 | 327.9523 | 241.032 | 240.1765
1912.4573 | 327.9 | 241.1105 | 240.2406
1913.4573 | 327.8633 | 241.1755 | 240.3179
1914.4573 | 327.8485 | 241.2363 | 240.3479
1915.4573 | 327.7766 | 241.3136 | 240.4115
1916.4573 | 327.8342 | 241.3748 | 240.4631
1917.4573 | 327.8752 | 241.4523 | 240.5302
1918.4573 | 327.8884 | 241.5067 | 240.6104
1919.4573 | 327.9963 | 241.5642 | 240.6764
1920.4573 | 327.9667 | 241.6291 | 240.7361
1921.4573 | 327.9851 | 241.7023 | 240.7946
1922.4573 | 327.9915 | 241.7556 | 240.8488
1923.4573 | 327.9075 | 241.8215 | 240.906
1924.4573 | 327.9148 | 241.8931 | 240.9567
1925.4573 | 327.9862 | 241.9618 | 241.0169
1926.4573 | 328.055 | 242.0077 | 241.073
1927.4573 | 328.0221 | 242.074 | 241.1297
1928.4573 | 328.0593 | 242.1251 | 241.1897
1929.4573 | 328.0729 | 242.1958 | 241.2733
1930.4573 | 328.1473 | 242.2424 | 241.3542
1931.4573 | 328.1952 | 242.3059 | 241.4171
1932.4573 | 328.2323 | 242.363 | 241.4911
1933.4573 | 328.2107 | 242.4255 | 241.5645
1934.4573 | 328.2336 | 242.4976 | 241.6324
1935.4573 | 328.3027 | 242.5567 | 241.6821
1936.4573 | 328.3777 | 242.618 | 241.7406
1937.4573 | 328.2714 | 242.6772 | 241.7954
1938.4573 | 328.2996 | 242.7332 | 241.849
1939.4573 | 328.3491 | 242.7958 | 241.9052
1940.4573 | 328.4154 | 242.8443 | 241.9755
1941.4573 | 328.3736 | 242.9061 | 242.0437
1942.4573 | 328.3247 | 242.9754 | 242.1255
1943.4573 | 328.3059 | 243.0342 | 242.1895
1944.4573 | 328.2935 | 243.0889 | 242.2444
1945.4573 | 328.2934 | 243.1551 | 242.2302
1946.4573 | 328.4103 | 243.2195 | 242.2898
1947.4573 | 328.5862 | 243.2739 | 242.348
1948.4573 | 328.6283 | 243.3373 | 242.4185
1949.4573 | 328.614 | 243.4045 | 242.4681
1950.4573 | 328.6401 | 243.4535 | 242.5366
1951.4573 | 328.6377 | 243.5277 | 242.5899
1952.4573 | 328.6287 | 243.5831 | 242.6548
1953.4573 | 328.6214 | 243.65 | 242.706
1954.4573 | 328.5926 | 243.704 | 242.7647
1955.4573 | 328.6001 | 243.7767 | 242.8292
1956.4573 | 328.532 | 243.8366 | 242.9461
1957.4573 | 328.5454 | 243.9003 | 242.947
1958.4573 | 328.5319 | 243.959 | 243.0022
1959.4573 | 328.4545 | 244.0117 | 243.1107
1960.4573 | 328.3581 | 244.0713 | 243.1734
1961.4573 | 328.259 | 244.1361 | 243.2372
1962.4573 | 328.2464 | 244.1896 | 243.2957
1963.4573 | 328.2515 | 244.2453 | 243.3496
1964.4573 | 328.2593 | 244.3188 | 243.4079
1965.4573 | 328.2794 | 244.3818 | 243.4678
1966.4573 | 328.2394 | 244.4256 | 243.5158
1967.4573 | 328.1358 | 244.5014 | 243.5771
1968.4573 | 328.0749 | 244.5571 | 243.6405
1969.4573 | 327.9969 | 244.621 | 243.7052
1970.4573 | 327.9784 | 244.6814 | 243.7529
1971.4573 | 327.8697 | 244.7388 | 243.7793
1972.4573 | 327.7034 | 244.8075 | 243.8368
1973.4573 | 327.6045 | 244.8692 | 243.8877
1974.4573 | 327.6257 | 244.9181 | 243.9484
1975.4885 | 327.6023 | 244.9844 | 244.0086
1976.4573 | 327.5499 | 245.0445 | 244.0621
1977.4573 | 327.4768 | 245.1004 | 244.1174
1978.4573 | 327.4359 | 245.1567 | 244.1729
1979.4573 | 327.3822 | 245.212 | 244.2321
1980.4573 | 327.3056 | 245.2773 | 244.3184
1981.4573 | 327.3891 | 245.3384 | 244.3719
1982.4573 | 327.4547 | 245.3939 | 244.3882
1983.4573 | 327.4836 | 245.449 | 244.4374
1984.4573 | 327.4226 | 245.5091 | 244.4804
1985.4573 | 327.39 | 245.5691 | 244.5146
1986.4573 | 327.4144 | 245.6167 | 244.5608
1987.4573 | 327.3439 | 245.7033 | 244.6103
1988.4573 | 327.383 | 245.7501 | 244.6614
1989.4573 | 327.4406 | 245.8061 | 244.7052
1990.4573 | 327.3891 | 245.8619 | 244.7514
1991.4573 | 327.3642 | 245.9137 | 244.8234
1992.4573 | 327.3615 | 245.9675 | 244.8671
1993.4573 | 327.2693 | 246.0279 | 244.9075
1994.4573 | 327.3884 | 246.0774 | 244.9787
1995.4573 | 327.4494 | 246.1348 | 244.9889
1996.4729 | 327.472 | 246.1846 | 245.0364
1997.4573 | 327.4591 | 246.2383 | 245.084
1998.4573 | 327.4488 | 246.2885 | 245.141
1999.4573 | 327.4745 | 246.35 | 245.1974
2000.4573 | 327.6114 | 246.3936 | 245.2584
2001.4573 | 327.7284 | 246.4529 | 245.2996
2002.4573 | 327.8459 | 246.5038 | 245.3572
2003.4573 | 328.0046 | 246.5379 | 245.3981
2004.4573 | 328.0322 | 246.593 | 245.4735
2005.4573 | 328.0963 | 246.6488 | 245.5382
2006.4573 | 328.1064 | 246.7231 | 245.5954
2007.4573 | 328.0072 | 246.7554 | 245.666
2008.4573 | 328.0917 | 246.8062 | 245.711
2009.4573 | 328.1927 | 246.8586 | 245.7611
2010.4573 | 328.2953 | 246.9121 | 245.831
2011.4573 | 328.385 | 246.955 | 245.862
2012.4573 | 328.423 | 247.0212 | 245.9399
2013.4573 | 328.452 | 247.0738 | 245.9474
2014.4573 | 328.5391 | 247.1089 | 245.9722
2015.4573 | 328.4409 | 247.158 | 246.0084
2016.4573 | 328.5105 | 247.2207 | 246.0517
2017.4573 | 328.5212 | 247.2738 | 246.0926
2018.4573 | 328.5161 | 247.329 | 246.1436
2019.4573 | 328.5284 | 247.3765 | 246.1808
2020.4573 | 328.5244 | 247.4203 | 246.2328
2021.4573 | 328.6205 | 247.4691 | 246.2786
2022.4573 | 328.7038 | 247.5015 | 246.3658
2023.4573 | 328.7318 | 247.5564 | 246.4367
2024.4573 | 328.7311 | 247.6275 | 246.4958
2025.4573 | 328.7103 | 247.6641 | 246.5534
2026.4573 | 328.6271 | 247.7369 | 246.6004
2027.4573 | 328.5773 | 247.7906 | 246.6546
2028.4573 | 328.5232 | 247.8597 | 246.7052
2029.4573 | 328.4917 | 247.9001 | 246.7564
2030.4573 | 328.4666 | 247.9532 | 246.8013
2031.4573 | 328.4761 | 248.0098 | 246.8446
2032.4573 | 328.5365 | 248.0481 | 246.8927
2033.4573 | 328.5448 | 248.1055 | 246.9415
2034.4573 | 328.4867 | 248.1663 | 246.9807
2035.4573 | 328.5107 | 248.2235 | 247.0302
2036.4573 | 328.4953 | 248.286 | 247.0678
2037.4573 | 328.5043 | 248.333 | 247.1209
2038.4573 | 328.5466 | 248.3851 | 247.1592
2039.4573 | 328.4932 | 248.446 | 247.2129
2040.4573 | 328.4352 | 248.5106 | 247.2552
2041.4573 | 328.4754 | 248.5679 | 247.3043
2042.4573 | 328.5353 | 248.6126 | 247.3489
2043.4573 | 328.5422 | 248.6656 | 247.3927
2044.4573 | 328.4413 | 248.7108 | 247.4389
2045.4573 | 328.4384 | 248.7635 | 247.4881
2046.4573 | 328.494 | 248.7878 | 247.5453
2047.4573 | 328.4495 | 248.8653 | 247.5487
2048.4573 | 328.508 | 248.9042 | 247.5765
2049.4573 | 328.5261 | 248.963 | 247.6471
2050.4573 | 328.3863 | 248.9983 | 247.736
2051.4573 | 328.1933 | 249.0483 | 247.7513
2052.4573 | 328.1639 | 249.1147 | 247.7585
2053.4573 | 328.1713 | 249.1508 | 247.8501
2054.4573 | 328.1028 | 249.1968 | 247.8985
2055.4573 | 328.0314 | 249.225 | 247.9473
2056.4573 | 327.9785 | 249.284 | 247.9895
2057.4573 | 327.9397 | 249.3248 | 248.0303
2058.4573 | 327.8856 | 249.378 | 248.0847
2059.4573 | 327.9832 | 249.4335 | 248.132
2060.4573 | 327.9148 | 249.4804 | 248.1827
2061.4573 | 327.9159 | 249.5384 | 248.1738
2062.4573 | 328.0367 | 249.5731 | 248.2254
2063.4573 | 328.0668 | 249.6373 | 248.2732
2064.4573 | 328.0435 | 249.6852 | 248.3142
2065.4573 | 328.0217 | 249.7398 | 248.3578
2066.4573 | 328.1053 | 249.773 | 248.4095
2067.4573 | 328.1464 | 249.8282 | 248.4643
2068.4573 | 328.1125 | 249.8598 | 248.5051
2069.4573 | 328.1013 | 249.9255 | 248.5456
2070.4573 | 328.1313 | 249.9679 | 248.5896
2071.4573 | 328.1147 | 249.9954 | 248.6394
2072.4573 | 328.0972 | 250.0452 | 248.6828
2073.4573 | 328.0241 | 250.0933 | 248.7263
2074.4573 | 328.0826 | 250.1404 | 248.765
2075.4573 | 328.1438 | 250.1861 | 248.8043
2076.4573 | 328.0877 | 250.2347 | 248.8413
2077.4573 | 328.035 | 250.2723 | 248.8827
2078.4573 | 328.0069 | 250.3281 | 248.9223
2079.4573 | 327.9638 | 250.3738 | 248.9678
2080.4573 | 328.0189 | 250.4119 | 249.0019
2081.4573 | 328.1308 | 250.4524 | 249.0507
2082.4573 | 328.1547 | 250.4843 | 249.0878
2083.4573 | 328.0931 | 250.5309 | 249.1365
2084.4573 | 328.1135 | 250.5718 | 249.18
2085.4573 | 328.1959 | 250.6098 | 249.2241
2086.4573 | 328.1841 | 250.6645 | 249.2681
2087.4573 | 328.1071 | 250.7045 | 249.3045
2088.4573 | 328.0071 | 250.748 | 249.3401
2089.4573 | 327.9677 | 250.78 | 249.3851
2090.4573 | 327.9088 | 250.8166 | 249.4242
2091.4573 | 327.9326 | 250.876 | 249.4605
2092.4573 | 327.9493 | 250.9266 | 249.5015
2093.4573 | 327.932 | 250.9659 | 249.5424
2094.4573 | 327.9448 | 251.0203 | 249.5814
2095.4573 | 328.0142 | 251.055 | 249.6142
2096.4573 | 328.0364 | 251.1017 | 249.6579
2097.4573 | 328.0009 | 251.1461 | 249.697
2098.4573 | 328.0393 | 251.1872 | 249.7377
2099.4573 | 327.9972 | 251.2241 | 249.8025
2100.4573 | 327.8934 | 251.2677 | 249.8449
2101.4573 | 327.8297 | 251.3035 | 249.8942
2102.4573 | 327.7797 | 251.348 | 249.892
2103.4573 | 327.7711 | 251.3906 | 249.9351
2104.4573 | 327.7327 | 251.4311 | 249.9777
2105.4573 | 327.7314 | 251.4572 | 250.0052
2106.4573 | 327.7933 | 251.4989 | 250.0489
2107.4573 | 327.8468 | 251.5432 | 250.0857
2108.4573 | 327.8954 | 251.5942 | 250.1261
2109.4573 | 327.8981 | 251.617 | 250.1623
2110.4573 | 327.8427 | 251.6644 | 250.2002
2111.4573 | 327.8866 | 251.7064 | 250.268
2112.4729 | 327.8529 | 251.734 | 250.3104
2113.4573 | 327.8715 | 251.773 | 250.355
2114.4573 | 327.923 | 251.8165 | 250.3984
2115.4573 | 327.9935 | 251.8561 | 250.4368
2116.4573 | 328.0724 | 251.8791 | 250.4772
2117.4573 | 328.0981 | 251.9198 | 250.5104
2118.4573 | 328.0025 | 251.959 | 250.5465
2119.4573 | 328.0524 | 251.9971 | 250.5782
2120.4573 | 328.1601 | 252.0354 | 250.6076
2121.4573 | 328.178 | 252.0797 | 250.6404
2122.4573 | 328.2394 | 252.102 | 250.6423
2123.4573 | 328.1669 | 252.1266 | 250.7077
2124.4573 | 328.1421 | 252.1627 | 250.7389
2125.4573 | 328.1726 | 252.1911 | 250.7803
2126.4573 | 328.0294 | 252.2359 | 250.812
2127.4573 | 328.0072 | 252.2505 | 250.849
2128.4573 | 328.0274 | 252.3065 | 250.879
2129.4573 | 328.0786 | 252.3499 | 250.9214
2130.4573 | 328.1862 | 252.3879 | 250.9183
2131.4573 | 328.3228 | 252.4223 | 250.9577
2132.4573 | 328.3658 | 252.4727 | 250.9851
2133.4573 | 328.4323 | 252.5064 | 251.0259
2134.4573 | 328.4486 | 252.5317 | 251.0798
2135.4573 | 328.4244 | 252.5727 | 251.088
2136.4573 | 328.4652 | 252.5956 | 251.1376
2137.4573 | 328.4838 | 252.6379 | 251.1764
2138.4573 | 328.4961 | 252.6841 | 251.2138
2139.4573 | 328.4543 | 252.7213 | 251.2391
2140.4573 | 328.3869 | 252.7559 | 251.2718
2141.4573 | 328.3717 | 252.7871 | 251.3106
2142.4729 | 328.4559 | 252.8104 | 251.3451
2143.4573 | 328.4508 | 252.8585 | 251.3789
2144.4573 | 328.3614 | 252.9001 | 251.4199
2145.4573 | 328.3692 | 252.9297 | 251.4507
2146.4573 | 328.2249 | 252.945 | 251.4802
2147.4573 | 328.1799 | 252.9726 | 251.5084
2148.4573 | 328.2095 | 253.0064 | 251.5448
2149.4573 | 328.1505 | 253.027 | 251.5752
2150.4573 | 328.1899 | 253.0684 | 251.6061
2151.4573 | 328.1268 | 253.1111 | 251.6402
2152.4573 | 328.1335 | 253.1488 | 251.689
2153.4573 | 328.0338 | 253.176 | 251.7058
2154.4573 | 328.0163 | 253.214 | 251.737
2155.4573 | 327.9987 | 253.2439 | 251.7681
2156.4573 | 328.0857 | 253.2784 | 251.8039
2157.4573 | 328.2016 | 253.3161 | 251.8067
2158.4573 | 328.2511 | 253.3638 | 251.8464
2159.4573 | 328.2892 | 253.3776 | 251.9031
2160.4573 | 328.2974 | 253.4124 | 251.9431
2161.4573 | 328.2246 | 253.4527 | 251.997
2162.4573 | 328.1551 | 253.4745 | 252.0371
2163.4573 | 328.1448 | 253.4978 | 252.067
2164.4573 | 328.2433 | 253.5374 | 252.0951
2165.4573 | 328.3271 | 253.5628 | 252.1325
2166.4573 | 328.3431 | 253.5965 | 252.1302
2167.4573 | 328.3711 | 253.6108 | 252.1695
2168.4573 | 328.3644 | 253.6647 | 252.2322
2169.4573 | 328.3675 | 253.6943 | 252.2594
2170.4573 | 328.4079 | 253.7297 | 252.274
2171.4573 | 328.444 | 253.7598 | 252.2945
2172.4573 | 328.578 | 253.8025 | 252.3509
2173.4573 | 328.5665 | 253.8301 | 252.3876
2174.4573 | 328.4876 | 253.8553 | 252.4245
2175.4573 | 328.4754 | 253.8904 | 252.4495
2176.4573 | 328.5034 | 253.9246 | 252.4848
2177.4573 | 328.4752 | 253.9564 | 252.5093
2178.4573 | 328.4708 | 253.9869 | 252.5495
2179.4573 | 328.3864 | 254.0196 | 252.5688
2180.4573 | 328.3433 | 254.0451 | 252.5852
2181.4573 | 328.376 | 254.0736 | 252.6266
2182.4573 | 328.3393 | 254.1053 | 252.647
2183.4573 | 328.3329 | 254.1322 | 252.682
2184.4573 | 328.2765 | 254.1764 | 252.7063
2185.4573 | 328.1769 | 254.1843 | 252.7383
2186.4573 | 328.3311 | 254.2131 | 252.7626
2187.4573 | 328.3666 | 254.2364 | 252.79
2188.4573 | 328.3441 | 254.2778 | 252.8367
2189.4573 | 328.3377 | 254.3094 | 252.8487
2190.4573 | 328.3297 | 254.3303 | 252.8802
2191.4573 | 328.3181 | 254.3641 | 252.9103
2192.4573 | 328.283 | 254.3975 | 252.9374
2193.4573 | 328.3103 | 254.4199 | 252.9687
2194.4573 | 328.3287 | 254.4425 | 252.9948
2195.4573 | 328.1826 | 254.4632 | 253.0275
2196.4573 | 328.2017 | 254.4996 | 253.0245
2197.4573 | 328.2073 | 254.5224 | 253.049
2198.4573 | 328.1708 | 254.5438 | 253.0753
2199.4573 | 328.1293 | 254.5717 | 253.1067
2200.4573 | 328.1426 | 254.6089 | 253.1327
2201.4573 | 328.1643 | 254.6431 | 253.1908
2202.4573 | 328.1428 | 254.6675 | 253.2263
2203.4573 | 328.1539 | 254.6999 | 253.2557
2204.4573 | 328.1331 | 254.7408 | 253.2894
2205.4573 | 328.1367 | 254.7451 | 253.3229
2206.4573 | 328.0335 | 254.7947 | 253.3534
2207.4573 | 328.0346 | 254.8232 | 253.3793
2208.4573 | 328.0231 | 254.8538 | 253.4054
2209.4573 | 328.0375 | 254.8773 | 253.4013
2210.4573 | 328.0517 | 254.9109 | 253.426
2211.4573 | 328.1162 | 254.9248 | 253.4569
2212.4573 | 328.0836 | 254.9449 | 253.4844
2213.4573 | 328.1068 | 254.9908 | 253.5081
2214.4573 | 328.1171 | 255.003 | 253.5367
2215.4573 | 328.102 | 255.0431 | 253.5762
2216.4573 | 327.967 | 255.0502 | 253.6003
2217.4573 | 327.9282 | 255.0911 | 253.6321
2218.4573 | 327.9677 | 255.1287 | 253.6745
2219.4573 | 327.962 | 255.1525 | 253.6964
2220.4573 | 328.04 | 255.1678 | 253.7621
2221.4573 | 328.1152 | 255.2097 | 253.7574
2222.4573 | 328.0377 | 255.2332 | 253.8123
2223.4573 | 328.0027 | 255.2718 | 253.8461
2224.4573 | 327.9494 | 255.2919 | 253.8221
2225.4573 | 327.8981 | 255.3358 | 253.8466
2226.4573 | 327.9211 | 255.3637 | 253.8722
2227.4573 | 327.8768 | 255.3882 | 253.9023
2228.4573 | 327.7747 | 255.4168 | 253.9242
2229.4573 | 327.6958 | 255.4358 | 253.946
2230.4573 | 327.5611 | 255.4531 | 253.9649
2231.4573 | 327.4805 | 255.4869 | 253.9999
2232.4573 | 327.3988 | 255.5188 | 254.026
2233.4573 | 327.2619 | 255.5468 | 254.0446
2234.4573 | 327.193 | 255.5682 | 254.0681
2235.4573 | 327.1649 | 255.5973 | 254.0938
2236.4729 | 327.1883 | 255.6384 | 254.1202
2237.4573 | 327.1176 | 255.6502 | 254.1481
2238.4573 | 327.1496 | 255.67 | 254.1696
2239.4573 | 327.1653 | 255.687 | 254.1945
2240.4573 | 327.1979 | 255.719 | 254.2203
2241.4573 | 327.2428 | 255.7447 | 254.2497
2242.4573 | 327.3402 | 255.7725 | 254.2754
2243.4573 | 327.3078 | 255.7948 | 254.3003
2244.4573 | 327.288 | 255.8154 | 254.3247
2245.4573 | 327.2383 | 255.8304 | 254.349
2246.4573 | 327.2244 | 255.863 | 254.4222
2247.4573 | 327.2273 | 255.8912 | 254.4493
2248.4573 | 327.2523 | 255.8978 | 254.4811
2249.4573 | 327.2107 | 255.9247 | 254.5071
2250.4573 | 327.2219 | 255.9634 | 254.5161
2251.4573 | 327.3205 | 255.9927 | 254.5573
2252.4573 | 327.3907 | 256.0106 | 254.5228
2253.4573 | 327.4577 | 256.04 | 254.5407
2254.4573 | 327.4614 | 256.0522 | 254.5638
2255.4573 | 327.4975 | 256.0853 | 254.5901
2256.4573 | 327.5275 | 256.0997 | 254.6106
2257.4573 | 327.5939 | 256.1396 | 254.626
2258.4573 | 327.5924 | 256.1594 | 254.661
2259.4573 | 327.65 | 256.1845 | 254.6866
2260.4573 | 327.7797 | 256.1874 | 254.747
2261.4573 | 327.8771 | 256.217 | 254.8097
2262.4573 | 327.9642 | 256.2307 | 254.8201
2263.4573 | 328.0298 | 256.2527 | 254.8124
2264.4573 | 327.926 | 256.2835 | 254.8282
2265.4573 | 327.9387 | 256.294 | 254.8401
2266.4573 | 327.9179 | 256.3114 | 254.8613
2267.4573 | 327.9401 | 256.3299 | 254.9196
2268.4573 | 327.9628 | 256.3576 | 254.8944
2269.4573 | 328.0566 | 256.3715 | 254.9134
2270.4573 | 328.1143 | 256.3883 | 254.931
2271.4573 | 328.1016 | 256.4058 | 254.9523
2272.4573 | 328.1697 | 256.4295 | 254.9725
2273.4573 | 328.2529 | 256.4477 | 254.982
2274.4573 | 328.3998 | 256.4836 | 255.0046
2275.4573 | 328.3828 | 256.5044 | 255.0205
2276.4573 | 328.3812 | 256.5183 | 255.0524
2277.4573 | 328.2901 | 256.5416 | 255.0652
2278.4573 | 328.2707 | 256.5643 | 255.0856
2279.4573 | 328.3218 | 256.5773 | 255.1047
2280.4573 | 328.3488 | 256.6174 | 255.1497
2281.4573 | 328.4536 | 256.6052 | 255.1953
2282.4573 | 328.4522 | 256.6402 | 255.2118
2283.4573 | 328.474 | 256.6594 | 255.1904
2284.4573 | 328.4585 | 256.6819 | 255.2143
2285.4573 | 328.3749 | 256.7099 | 255.2444
2286.4573 | 328.3809 | 256.7389 | 255.2653
2287.4573 | 328.341 | 256.7465 | 255.2848
2288.4573 | 328.2696 | 256.782 | 255.3128
2289.4573 | 328.2871 | 256.8056 | 255.324
2290.4573 | 328.2731 | 256.8156 | 255.3446
2291.4573 | 328.2013 | 256.8377 | 255.3699
2292.4573 | 328.0791 | 256.8572 | 255.4019
2293.4573 | 328.0815 | 256.8842 | 255.4282
2294.4573 | 328.0341 | 256.9146 | 255.4917
2295.4573 | 328.0793 | 256.9541 | 255.5138
2296.4573 | 328.0062 | 256.9787 | 255.5441
2297.4573 | 327.8819 | 256.9974 | 255.5581
2298.4573 | 327.836 | 257.0205 | 255.5796
2299.4573 | 327.7269 | 257.0412 | 255.6073
2300.4573 | 327.711 | 257.0561 | 255.6288
2301.4573 | 327.5751 | 257.0865 | 255.6491
2302.4573 | 327.5082 | 257.0891 | 255.6677
2303.4573 | 327.4808 | 257.1226 | 255.681
2304.4573 | 327.4976 | 257.1458 | 255.7155
2305.4573 | 327.518 | 257.1677 | 255.7374
2306.4573 | 327.6069 | 257.1897 | 255.7588
2307.4573 | 327.7095 | 257.1914 | 255.7354
2308.4573 | 327.7522 | 257.2052 | 255.7537
2309.4573 | 327.7491 | 257.2409 | 255.7669
2310.4573 | 327.7277 | 257.2583 | 255.7992
2311.4573 | 327.6603 | 257.283 | 255.8219
2312.4573 | 327.722 | 257.3067 | 255.839
2313.4573 | 327.7118 | 257.3275 | 255.8613
2314.4573 | 327.7434 | 257.3391 | 255.9314
2315.4573 | 327.8074 | 257.3688 | 255.9442
2316.4573 | 327.8215 | 257.3752 | 255.9675
2317.4573 | 327.853 | 257.4042 | 256.0169
2318.4573 | 327.8783 | 257.412 | 256.0633
2319.4573 | 327.8867 | 257.4248 | 256.0742
2320.4573 | 327.9234 | 257.4434 | 256.0942
2321.4573 | 327.8111 | 257.4546 | 256.0276
2322.4573 | 327.7889 | 257.4767 | 256.0389
2323.4573 | 327.8315 | 257.5032 | 256.054
2324.4573 | 327.8679 | 257.5158 | 256.0757
2325.4573 | 327.8025 | 257.5471 | 256.0963
2326.4573 | 327.8568 | 257.5673 | 256.11
2327.4573 | 327.9699 | 257.6021 | 256.1373
2328.4573 | 328.0312 | 257.6095 | 256.1544
2329.4573 | 327.9717 | 257.6272 | 256.1717
2330.4573 | 328.0707 | 257.6376 | 256.1957
2331.4573 | 328.1246 | 257.6665 | 256.2127
2332.4573 | 328.0989 | 257.6811 | 256.2629
2333.4573 | 328.0639 | 257.6843 | 256.2582
2334.4573 | 328.0312 | 257.7156 | 256.3399
2335.4573 | 328.0139 | 257.7305 | 256.2931
2336.4573 | 328.0516 | 257.7466 | 256.3284
2337.4573 | 327.9566 | 257.7719 | 256.4122
2338.4573 | 328.1086 | 257.7807 | 256.4306
2339.4573 | 328.1068 | 257.8164 | 256.4527
2340.4573 | 328.0672 | 257.8398 | 256.4612
2341.4573 | 328.111 | 257.8378 | 256.4809
2342.4573 | 328.1506 | 257.8583 | 256.4271
2343.4573 | 328.1457 | 257.8924 | 256.4546
2344.4573 | 328.2397 | 257.9073 | 256.4698
2345.4573 | 328.2462 | 257.9368 | 256.4839
2346.4573 | 328.1147 | 257.9544 | 256.4994
2347.4573 | 328.0839 | 257.9782 | 256.5131
2348.4573 | 328.1626 | 258.007 | 256.5371
2349.4573 | 328.3077 | 258.0148 | 256.5578
2350.4573 | 328.3482 | 257.8783 | 256.4836
2351.4573 | 328.4043 | 258.0634 | 256.5743
2352.4573 | 328.5756 | 258.0692 | 256.5907
2353.4573 | 328.6557 | 258.0983 | 256.6118
2354.4573 | 328.6205 | 258.103 | 256.6299
2355.4573 | 328.6519 | 258.142 | 256.6527
2356.4573 | 328.6432 | 258.1631 | 256.6729
2357.4573 | 328.7027 | 258.1757 | 256.6829
2358.4573 | 328.6551 | 258.1973 | 256.7074
2359.4573 | 328.5332 | 258.2096 | 256.7222
2360.4573 | 328.4869 | 258.2548 | 256.7361
2361.4573 | 328.4915 | 258.2551 | 256.7505
2362.4573 | 328.4593 | 258.273 | 256.7632
2363.4573 | 328.3355 | 258.2944 | 256.7858
2364.4573 | 328.2743 | 258.3024 | 256.8058
2365.4573 | 328.3435 | 258.3132 | 256.8196
2366.4573 | 328.364 | 258.3272 | 256.8356
2367.4573 | 328.3213 | 258.35 | 256.8567
2368.4573 | 328.2333 | 258.3671 | 256.8769
2369.4573 | 328.1717 | 258.381 | 256.8941
2370.4573 | 328.0662 | 258.3964 | 256.9228
2371.4573 | 328.0274 | 258.4183 | 256.9416
2372.4573 | 327.9458 | 258.4401 | 256.9597
2373.4573 | 327.9161 | 258.4467 | 256.9792
2374.4573 | 327.8818 | 258.4771 | 257.0024
2375.4573 | 327.8342 | 258.486 | 257.0176
2376.4573 | 327.7735 | 258.508 | 257.0421
2377.4573 | 327.8275 | 258.5344 | 257.0621
2378.4573 | 327.8888 | 258.556 | 257.0905
2379.4573 | 327.9087 | 258.568 | 257.1111
2380.4573 | 327.9609 | 258.5963 | 257.1294
2381.4573 | 327.9946 | 258.6241 | 257.1413
2382.4573 | 327.9709 | 258.6281 | 257.1605
2383.4573 | 327.9842 | 258.6458 | 257.1747
2384.4573 | 327.9638 | 258.6596 | 257.1931
2385.4573 | 327.9416 | 258.6866 | 257.2162
2386.4573 | 327.878 | 258.7069 | 257.2286
2387.4573 | 327.9022 | 258.7224 | 257.2528
2388.4573 | 327.9373 | 258.736 | 257.2608
2389.4573 | 327.9657 | 258.7645 | 257.2848
2390.4573 | 327.9856 | 258.7847 | 257.2938
2391.4573 | 327.9874 | 258.7995 | 257.3073
2392.4573 | 327.9358 | 258.8155 | 257.3305
2393.4573 | 327.9488 | 258.8322 | 257.3435
2394.4573 | 327.9179 | 258.8382 | 257.3661
2395.4573 | 327.8893 | 258.8687 | 257.3826
2396.4573 | 327.8187 | 258.8711 | 257.4083
2397.4573 | 327.8198 | 258.8977 | 257.4175
2398.4573 | 327.7923 | 258.9229 | 257.4494
2399.4573 | 327.8279 | 258.9215 | 257.4585
2400.4573 | 327.7828 | 258.9514 | 257.4754