## Test Conditions
DESIREE-FIRE Penlight Test Number 17-qualification - Circuit Simulator Data Only
Test Date: | July-30-2009 | Fill in these fields - B7 and B11, time offsets for the fire time and temperature time, is critical to data processing. The rest are info only.
Nominal Test start time: | 10:38
SCDU DAQ start time | 10:38
Fire Ignition time: | 10:42
Fire time offset | 220 | This is the time in seconds after the DAQ was started that the fire was ignited
Penlight DAQ Start Time | 10:37
Fire Ignition time: | 10:42
Temp data offset | 255 | This is the time in seconds after the Penlight data logger was activated and Penlight was turned on.
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
SCDU 1 | Kerite FR-III 3c |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC25 in the Temperature Data File
Circuit Simulator Configurations and connections:
Note: Template opens with default conditions, update if alternate wiring configuration is used. |  | Circuit #1 | Circuit#2 | Circuit #3 | Circuit #4
| CPT Size: | 100 VA
| CPT Grounding: | NOT Grounded
| General Config. | Generic MOV
| Cable Type | Kerite
| Wiring Config: | MOV - source centered
| Circuit Path 1: | Switch Closed: Energized source. Conductor 1
| Circuit Path 2: | Switch open: not connected
| Circuit Path 3: | Switch open: not connected
| Circuit Path 4: | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation). Not used
| Circuit Path 5: | Active Target: Connected to Motor Starter and connected to Red conductor. Conductor 2
| Circuit Path 6: | Active Target: Connected to Motor Starter and connected to Wht/Blk conductor. Conductor 3
| Circuit Path 7: | switch open - no connection
| Circuit Path 8: | switch open - no connection
| Circuit Path 9: | switch open - no connection
A Note on Data Conversion and Accuracy:
Each of the voltage and current transducers used produces a 4-20mA signal which is routed through 477ohm precision resistors converting the signal to a nominal 2-10 VDC signal. This DC voltage signal was monitored using a National Instruments PCI-6071E data aquisition (DAQ) card. These data as recorded are presented in the "Raw Test Data" worksheet. The raw data were converted to actual values as shown on the "Converted Test Data" worksheet. The conversion is based on the fact that the 4-20 mA signal corresponds to a full scale reading on the voltage transducers of 0-300 VAC and on the current transducers of 0-5A. Nominal zero point readings for each transducer were taken in a separate test run in order to establish more accurately the zero points for current and voltage measurement. The Zero Point values are provided, and the full run is documented in a separate data file (see 'Zero Points' worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Circuit Fault Summary
Summary of Circuit Faulting Behavior for all Tested Circuits
Circuit 1 | The 3c Kerite FR-III was used for Circuit 1. The initial temperature was set to 375C for 20 minutes, at which it was increased to 400C. Ten minutes later, the temperature was increased to 435C. Nine minutes later, the temperature was increased to 470C. Bubbling was observed; however, the cable did not ignite. After 47 minutes, the circuit failed to ground.
Circuit 2 | Circuit 2 was not used in this test.
Circuit 3 | Circuit 3 was not used in this test.
Circuit 4 | Circuit 4 was not used in this test.
Note: | Update this worksheet with a summary of faulting behavior for each circuit e.g.: - what was mode of first failure, - what was time of first failure, - was a spurious actuation observed, - how long did spurious actuation persist, - when did fuse blow.

## Circuit 1 Faulting
Summary of Observed Faulting Behavior for Circuit #1
Time (s) | Event | Discussion
2769 | Short to ground | At this time, the circuit voltage shorted to ground
Summary observations
The initial temperature was set to 375C for 20 minutes, at which it was increased to 400C. Ten minutes later, the temperature was increased to 435C. Nine minutes later, the temperature was increased to 470C. Bubbling was observed; however, the cable did not ignite. After 47 minutes, the circuit failed to ground.

## Converted Data C1
Fire Time (s) | C1 V1 | C1 A1 | C1 V2 | C1 A2 | C1 V3 | C1 A3 | C1 V4 | C1 A4 | C1 V5 | C1 A5 | C1 V6 | C1 A6 | C1 V7 | C1 A7 | C1 V8 | C1 A8
-10 | 128.9006 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-9.8 | 128.9006 | 0.0073551 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-9.6 | 128.9006 | 0.0057559 | 0.29387 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
-9.4 | 128.9006 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-9.2 | 128.8046 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.003271 | -0.0036512 | 0.0035139
-9 | 128.9006 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
-8.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-8.6 | 128.9966 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.003271 | -0.0036512 | 0.0035139
-8.4 | 128.9006 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
-8.2 | 128.8046 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.003271 | -0.0036512 | 0.0035139
-8 | 128.9006 | 0.0073551 | 0.10193 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.28424 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
-7.8 | 128.9006 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-7.6 | 128.9006 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-7.4 | 128.9006 | 0.0057559 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.18729 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.19792 | 0.003271 | -0.0036512 | 0.0035139
-7.2 | 128.9006 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.37923 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-7 | 128.9966 | 0.0057559 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0019147
-6.8 | 128.9966 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
-6.6 | 128.9006 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
-6.4 | 128.9006 | 0.0057559 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.18829 | 0.0035139
-6.2 | 128.9006 | 0.0057559 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
-6 | 128.9006 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-5.8 | 128.9966 | 0.0073551 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
-5.6 | 128.9006 | 0.0057559 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.003271 | -0.0036512 | 0.0035139
-5.4 | 128.9006 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.28424 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
-5.2 | 128.9006 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-5 | 128.9006 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-4.8 | 128.9966 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
-4.6 | 128.9966 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
-4.4 | 128.9006 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-4.2 | 128.9966 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0019147
-4 | 128.9966 | 0.0073551 | 0.10193 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-3.8 | 128.9966 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.099642 | 0.0051138
-3.6 | 128.9006 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.003271 | -0.0036512 | 0.0035139
-3.4 | 128.9006 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-3.2 | 128.9006 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
-3 | 128.9006 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-2.8 | 128.9966 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.003271 | -0.0036512 | 0.0035139
-2.6 | 128.9006 | 0.0057559 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
-2.4 | 128.9006 | 0.0057559 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
-2.2 | 128.9006 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
-2 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-1.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.19792 | 0.0048701 | -0.0036512 | 0.0019147
-1.6 | 128.8046 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-1.4 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.19792 | 0.0048701 | -0.0036512 | 0.0035139
-1.2 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
-1 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
-0.8 | 127.557 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | -0.0013064 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-0.6 | 127.749 | 0.0057559 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-0.4 | 127.9409 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
-0.2 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
0 | 128.0369 | 0.0057559 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
0.2 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
0.4 | 128.3248 | 0.0057559 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
0.6 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | -0.0013064 | 0.38986 | 0.0048701 | -0.0036512 | 0.0019147
0.8 | 127.8449 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
1 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.28424 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
1.2 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
1.4 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.003271 | -0.0036512 | 0.0035139
1.6 | 128.1329 | 0.0073551 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.18829 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
1.8 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | -0.0013064 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
2.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
2.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | -0.0013064 | 0.29387 | 0.003271 | -0.0036512 | 0.0035139
2.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
2.8 | 128.5167 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | -0.0013064 | 0.29387 | 0.003271 | -0.0036512 | 0.0035139
3 | 128.5167 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.57213 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
3.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
3.4 | 128.6127 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
3.6 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.19792 | 0.0048701 | -0.0036512 | 0.0035139
3.8 | 128.7087 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
4 | 128.6127 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
4.2 | 128.6127 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
4.4 | 128.6127 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
4.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.28424 | 0.0018926 | 0.38986 | 0.003271 | -0.0036512 | 0.0051138
4.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
5 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.003271 | -0.0036512 | 0.0035139
5.2 | 128.7087 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
5.4 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
5.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
5.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
6 | 128.6127 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
6.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
6.4 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
6.6 | 128.7087 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
6.8 | 128.8046 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.18729 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
7 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
7.2 | 128.7087 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | -0.0013064 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
7.4 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
7.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
7.8 | 128.7087 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
8 | 128.7087 | 0.0057559 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
8.2 | 128.7087 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
8.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
8.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
8.8 | 128.6127 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
9 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
9.2 | 128.5167 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
9.4 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
9.6 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
9.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
10 | 128.5167 | 0.0057559 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
10.2 | 128.6127 | 0.0073551 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
10.4 | 128.7087 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.18729 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
10.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
10.8 | 128.5167 | 0.0073551 | 0.29387 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
11 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
11.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
11.4 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
11.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
11.8 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
12 | 128.6127 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
12.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
12.4 | 128.4208 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
12.6 | 128.5167 | 0.0073551 | 0.29387 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
12.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
13 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
13.2 | 128.5167 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
13.4 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.006713
13.6 | 128.5167 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
13.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
14 | 128.5167 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
14.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
14.4 | 128.5167 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
14.6 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
14.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
15 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
15.2 | 128.4208 | 0.0057559 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
15.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.23811 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
15.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
15.8 | 128.4208 | 0.0073551 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
16 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
16.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0035139
16.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
16.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
16.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
17 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
17.2 | 128.5167 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
17.4 | 128.4208 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
17.6 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
17.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
18 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
18.2 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
18.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
18.6 | 128.4208 | 0.0057559 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
18.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
19 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
19.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
19.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
19.6 | 128.5167 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
19.8 | 128.4208 | 0.0057559 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0035139
20 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
20.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
20.4 | 128.4208 | 0.0057559 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
20.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
20.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.006713
21 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
21.2 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
21.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
21.6 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
21.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
22 | 128.5167 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
22.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
22.4 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
22.6 | 128.5167 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
22.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
23 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
23.2 | 128.4208 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
23.4 | 128.4208 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
23.6 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
23.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
24 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
24.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
24.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
24.6 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
24.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
25 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
25.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
25.4 | 128.5167 | 0.0057559 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
25.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
25.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
26 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
26.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
26.4 | 128.4208 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
26.6 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
26.8 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
27 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
27.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
27.4 | 128.4208 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
27.6 | 128.5167 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
27.8 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
28 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
28.2 | 128.4208 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
28.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
28.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
28.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
29 | 128.5167 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
29.2 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
29.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
29.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
29.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
30 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
30.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
30.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
30.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
30.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.5818 | 0.0048701 | 0.0923 | 0.0051138
31 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
31.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
31.4 | 128.4208 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
31.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
31.8 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
32 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
32.2 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
32.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
32.6 | 128.2288 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
32.8 | 128.3248 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
33 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
33.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
33.4 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
33.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.00012733 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
33.8 | 128.1329 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
34 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.18729 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
34.2 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
34.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
34.6 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
34.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
35 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
35.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
35.4 | 128.4208 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
35.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
35.8 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
36 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
36.2 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
36.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
36.6 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
36.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
37 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
37.2 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
37.4 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
37.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
37.8 | 128.2288 | 0.0073551 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
38 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.00012733 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
38.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
38.4 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
38.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | -0.0013064 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
38.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
39 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
39.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.38916 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.28424 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
39.4 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
39.6 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
39.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
40 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
40.2 | 128.3248 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
40.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
40.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
40.8 | 128.3248 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
41 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.19792 | 0.00647 | 0.0923 | 0.0035139
41.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
41.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
41.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
41.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
42 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
42.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.19792 | 0.0048701 | 0.0923 | 0.0035139
42.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
42.6 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.48581 | 0.0048701 | -0.0036512 | 0.0035139
42.8 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
43 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
43.2 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
43.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
43.6 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
43.8 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
44 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
44.2 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
44.4 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
44.6 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
44.8 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
45 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
45.2 | 128.2288 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
45.4 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
45.6 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
45.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
46 | 128.3248 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
46.2 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | -0.0036512 | 0.0051138
46.4 | 128.3248 | 0.010554 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
46.6 | 128.2288 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.28424 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
46.8 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
47 | 128.3248 | 0.0089549 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
47.2 | 128.3248 | 0.010554 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
47.4 | 128.3248 | 0.010554 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
47.6 | 128.3248 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.099642 | 0.0051138
47.8 | 128.3248 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
48 | 128.2288 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
48.2 | 128.3248 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.28424 | 0.0051138
48.4 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.0035139
48.6 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
48.8 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
49 | 128.4208 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | -0.0013064 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
49.2 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.18829 | 0.0051138
49.4 | 128.4208 | 0.010554 | 0.10193 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
49.6 | 128.3248 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
49.8 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
50 | 128.3248 | 0.013753 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
50.2 | 128.3248 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
50.4 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
50.6 | 128.3248 | 0.015352 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0019147
50.8 | 128.4208 | 0.018551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
51 | 128.4208 | 0.018551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0080692 | -0.0036512 | 0.0035139
51.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
51.4 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
51.6 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
51.8 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
52 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
52.2 | 128.4208 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
52.4 | 128.4208 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
52.6 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
52.8 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
53 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
53.2 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
53.4 | 128.4208 | 0.013753 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
53.6 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.5818 | 0.003271 | 0.0923 | 0.0035139
53.8 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
54 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.10127 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
54.2 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
54.4 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.18829 | 0.0035139
54.6 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
54.8 | 128.6127 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.18729 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
55 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0080692 | -0.0036512 | 0.0035139
55.2 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
55.4 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
55.6 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
55.8 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
56 | 128.8046 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
56.2 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
56.4 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
56.6 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
56.8 | 128.7087 | 0.013753 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
57 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
57.2 | 128.7087 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
57.4 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
57.6 | 128.7087 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
57.8 | 128.7087 | 0.013753 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
58 | 128.7087 | 0.013753 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
58.2 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
58.4 | 128.7087 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | -0.0014725 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
58.6 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
58.8 | 128.5167 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
59 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
59.2 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
59.4 | 129.1885 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.00647 | 0.0923 | 0.0051138
59.6 | 129.6683 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
59.8 | 128.9006 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
60 | 128.7087 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
60.2 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
60.4 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
60.6 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
60.8 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
61 | 128.5167 | 0.018551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
61.2 | 128.3248 | 0.020151 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
61.4 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
61.6 | 128.3248 | 0.024949 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.006713
61.8 | 128.3248 | 0.015352 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
62 | 128.4208 | 0.015352 | 0.19792 | 0.0047816 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0035139
62.2 | 128.4208 | 0.015352 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
62.4 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
62.6 | 128.4208 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
62.8 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0019147
63 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
63.2 | 128.3248 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
63.4 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
63.6 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.28424 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
63.8 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
64 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
64.2 | 128.3248 | 0.013753 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
64.4 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
64.6 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
64.8 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
65 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
65.2 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.19792 | 0.00647 | -0.0036512 | 0.0035139
65.4 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
65.6 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
65.8 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
66 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.003271 | 0.0923 | 0.0035139
66.2 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
66.4 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
66.6 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
66.8 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
67 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
67.2 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
67.4 | 128.1329 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.006713
67.6 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
67.8 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
68 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
68.2 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
68.4 | 128.3248 | 0.015352 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
68.6 | 128.3248 | 0.010554 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
68.8 | 128.9006 | 0.02175 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0097238 | 0.47618 | 0.0050916 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
69 | 128.5167 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
69.2 | 128.5167 | 0.010554 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.28424 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
69.4 | 128.5167 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
69.6 | 128.5167 | 0.010554 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
69.8 | 128.5167 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
70 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
70.2 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.003271 | 0.0923 | 0.0035139
70.4 | 128.5167 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
70.6 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
70.8 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.003271 | 0.0923 | 0.0035139
71 | 128.5167 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
71.2 | 128.4208 | 0.010554 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
71.4 | 128.4208 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
71.6 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.38916 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
71.8 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.23811 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.003271 | 0.0923 | 0.0035139
72 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
72.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
72.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.28424 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
72.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
72.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
73 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.66813 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
73.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
73.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
73.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
73.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
74 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
74.2 | 128.4208 | 0.010554 | 0.10193 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
74.4 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
74.6 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
74.8 | 128.4208 | 0.0089549 | -0.089975 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
75 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
75.2 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
75.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
75.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
75.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
76 | 128.5167 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
76.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
76.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
76.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
76.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
77 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
77.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
77.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
77.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
77.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
78 | 128.4208 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
78.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
78.4 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
78.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
78.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0049255 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
79 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
79.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
79.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
79.6 | 128.4208 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
79.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
80 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
80.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
80.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
80.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
80.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
81 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0035139
81.2 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
81.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0019147
81.6 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
81.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.099642 | 0.0051138
82 | 128.5167 | 0.0057559 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
82.2 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
82.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
82.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
82.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
83 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
83.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
83.4 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
83.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
83.8 | 128.6127 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
84 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
84.2 | 128.5167 | 0.012154 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
84.4 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0019147
84.6 | 128.5167 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
84.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.099642 | 0.0035139
85 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
85.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0019147
85.4 | 128.6127 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.19792 | 0.0048701 | 0.0923 | 0.0035139
85.6 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0080692 | -0.0036512 | 0.0035139
85.8 | 128.5167 | 0.0073551 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
86 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
86.2 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
86.4 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0035139
86.6 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
86.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
87 | 128.6127 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
87.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
87.4 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
87.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
87.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
88 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
88.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
88.4 | 128.6127 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
88.6 | 128.6127 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
88.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
89 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | -0.0013064 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
89.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
89.4 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
89.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
89.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
90 | 128.7087 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
90.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
90.4 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
90.6 | 128.6127 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
90.8 | 128.7087 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
91 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
91.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
91.4 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
91.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
91.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
92 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
92.2 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
92.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
92.6 | 128.7087 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
92.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.18729 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
93 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
93.2 | 128.7087 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | -0.0014725 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
93.4 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
93.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
93.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
94 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
94.2 | 127.653 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
94.4 | 127.4611 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
94.6 | 127.8449 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
94.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
95 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0080692 | -0.0036512 | 0.0035139
95.2 | 128.5167 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
95.4 | 128.6127 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
95.6 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
95.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
96 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.19792 | 0.00647 | -0.0036512 | 0.0035139
96.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
96.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
96.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.19792 | 0.00647 | 0.0923 | 0.0035139
96.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
97 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
97.2 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
97.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.57213 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0019147
97.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
97.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
98 | 128.8046 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
98.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
98.4 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
98.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
98.8 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
99 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
99.2 | 128.7087 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.099642 | 0.0051138
99.4 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
99.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
99.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
100 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
100.2 | 128.7087 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
100.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
100.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
100.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0035139
101 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
101.2 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
101.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
101.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
101.8 | 128.7087 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
102 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
102.2 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
102.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
102.6 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
102.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
103 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
103.2 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.006713
103.4 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
103.6 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
103.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
104 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
104.2 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
104.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
104.6 | 128.7087 | 0.0057559 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.19792 | 0.00647 | 0.0923 | 0.0035139
104.8 | 128.8046 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
105 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
105.2 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
105.4 | 128.7087 | 0.0073551 | 0.29387 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
105.6 | 128.8046 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
105.8 | 128.8046 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
106 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
106.2 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
106.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0019147
106.6 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
106.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0035139
107 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
107.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
107.4 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
107.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
107.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
108 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
108.2 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
108.4 | 128.8046 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
108.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
108.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
109 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
109.2 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
109.4 | 128.8046 | 0.0073551 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0035139
109.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0019147
109.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.10127 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
110 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
110.2 | 128.9006 | 0.0057559 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
110.4 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
110.6 | 128.8046 | 0.0089549 | 0.29387 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
110.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
111 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
111.2 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
111.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.003271 | 0.0923 | 0.0035139
111.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
111.8 | 128.8046 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
112 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
112.2 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
112.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0035139
112.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
112.8 | 128.8046 | 0.0089549 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
113 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
113.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
113.4 | 128.8046 | 0.0057559 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
113.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
113.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
114 | 128.8046 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
114.2 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
114.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
114.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
114.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
115 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
115.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
115.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
115.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
115.8 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
116 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
116.2 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
116.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0019147
116.6 | 128.7087 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
116.8 | 128.8046 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
117 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
117.2 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
117.4 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
117.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
117.8 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
118 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
118.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
118.4 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
118.6 | 128.8046 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
118.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
119 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
119.2 | 128.7087 | 0.0057559 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
119.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
119.6 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
119.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
120 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
120.2 | 128.7087 | 0.0073551 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
120.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
120.6 | 128.8046 | 0.0073551 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
120.8 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
121 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
121.2 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
121.4 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
121.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
121.8 | 128.8046 | 0.0057559 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
122 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
122.2 | 128.8046 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.003271 | 0.0923 | 0.0051138
122.4 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
122.6 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
122.8 | 128.8046 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
123 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
123.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
123.4 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
123.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
123.8 | 128.8046 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
124 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
124.2 | 128.7087 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
124.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
124.6 | 128.8046 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
124.8 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
125 | 128.8046 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
125.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
125.4 | 128.8046 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
125.6 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
125.8 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
126 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
126.2 | 128.8046 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
126.4 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
126.6 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
126.8 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
127 | 128.7087 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
127.2 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
127.4 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.28424 | 0.0051138
127.6 | 128.7087 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
127.8 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
128 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
128.2 | 128.8046 | 0.015352 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
128.4 | 128.9006 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.006713
128.6 | 128.9006 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
128.8 | 128.9006 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
129 | 128.8046 | 0.013753 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
129.2 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
129.4 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
129.6 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
129.8 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
130 | 128.6127 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
130.2 | 128.5167 | 0.016952 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
130.4 | 128.6127 | 0.018551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
130.6 | 128.9006 | 0.02335 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
130.8 | 128.8046 | 0.02175 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
131 | 128.7087 | 0.020151 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
131.2 | 128.7087 | 0.02175 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
131.4 | 128.6127 | 0.02335 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
131.6 | 128.6127 | 0.028148 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
131.8 | 128.6127 | 0.026549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
132 | 128.6127 | 0.031347 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.38019 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.006713
132.2 | 128.6127 | 0.024949 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
132.4 | 129.3804 | 0.05214 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
132.6 | 128.9966 | 0.026549 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0097238 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
132.8 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.011324 | 0.57213 | 0.0082906 | 0.38986 | 0.00647 | 0.18829 | 0.006713
133 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.47618 | 0.013089 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
133.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
133.4 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0081246 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
133.6 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
133.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.011324 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.006713
134 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.016122 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
134.2 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0098898 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
134.4 | 128.7087 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
134.6 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
134.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.006713
135 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.0923 | 0.006713
135.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
135.4 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
135.6 | 128.6127 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
135.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
136 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
136.2 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
136.4 | 128.6127 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.00060315 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
136.6 | 128.6127 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
136.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
137 | 128.6127 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
137.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
137.4 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
137.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
137.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
138 | 128.6127 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0002934 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
138.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
138.4 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
138.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
138.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
139 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
139.2 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
139.4 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
139.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
139.8 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
140 | 128.6127 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
140.2 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
140.4 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.006713
140.6 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
140.8 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
141 | 128.5167 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
141.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
141.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
141.6 | 128.6127 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
141.8 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
142 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
142.2 | 128.6127 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
142.4 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
142.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.00647 | 0.0923 | 0.006713
142.8 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
143 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
143.2 | 128.6127 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
143.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
143.6 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
143.8 | 128.6127 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
144 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
144.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
144.4 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
144.6 | 128.5167 | 0.0073551 | 0.10193 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
144.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
145 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
145.2 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
145.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
145.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
145.8 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
146 | 128.5167 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
146.2 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
146.4 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
146.6 | 128.5167 | 0.0057559 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
146.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.009669 | 0.0923 | 0.0051138
147 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
147.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
147.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
147.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
147.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
148 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
148.2 | 128.4208 | 0.0089549 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
148.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
148.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
148.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
149 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
149.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
149.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
149.6 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
149.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
150 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
150.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
150.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
150.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
150.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
151 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
151.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
151.4 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
151.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
151.8 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
152 | 128.4208 | 0.010554 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
152.2 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
152.4 | 128.3248 | 0.013753 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
152.6 | 128.4208 | 0.016952 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
152.8 | 128.3248 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
153 | 128.5167 | 0.018551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
153.2 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
153.4 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.66813 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
153.6 | 128.4208 | 0.0089549 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | -0.0036512 | 0.0051138
153.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
154 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
154.2 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 1.6612e-05 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
154.4 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
154.6 | 128.4208 | 0.010554 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
154.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
155 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
155.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
155.4 | 128.4208 | 0.010554 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0035139
155.6 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
155.8 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
156 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
156.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
156.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
156.6 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
156.8 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
157 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
157.2 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
157.4 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
157.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
157.8 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
158 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
158.2 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
158.4 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
158.6 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | -0.0036512 | 0.0035139
158.8 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
159 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
159.2 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
159.4 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
159.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
159.8 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
160 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
160.2 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
160.4 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
160.6 | 128.4208 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
160.8 | 128.3248 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
161 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
161.2 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
161.4 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
161.6 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.28424 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
161.8 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
162 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
162.2 | 128.4208 | 0.012154 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
162.4 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
162.6 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
162.8 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | -0.0013064 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
163 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
163.2 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
163.4 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
163.6 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0083128
163.8 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
164 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0035139
164.2 | 128.4208 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
164.4 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
164.6 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
164.8 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
165 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
165.2 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
165.4 | 128.4208 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
165.6 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
165.8 | 128.4208 | 0.013753 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
166 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.18729 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
166.2 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
166.4 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.003271 | 0.0923 | 0.006713
166.6 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
166.8 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.006713
167 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
167.2 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
167.4 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
167.6 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
167.8 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
168 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
168.2 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
168.4 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
168.6 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
168.8 | 128.6127 | 0.013753 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
169 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
169.2 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.006713
169.4 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
169.6 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
169.8 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
170 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
170.2 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
170.4 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
170.6 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
170.8 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
171 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
171.2 | 128.5167 | 0.013753 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.18829 | 0.0051138
171.4 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
171.6 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
171.8 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
172 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
172.2 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
172.4 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
172.6 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
172.8 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
173 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
173.2 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
173.4 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
173.6 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
173.8 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
174 | 128.6127 | 0.012154 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
174.2 | 128.7087 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.28424 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
174.4 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
174.6 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
174.8 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
175 | 128.8046 | 0.031347 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
175.2 | 128.6127 | 0.02335 | 0.38986 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
175.4 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
175.6 | 128.7087 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
175.8 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
176 | 128.8046 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
176.2 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
176.4 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
176.6 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
176.8 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.0923 | 0.0051138
177 | 128.7087 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
177.2 | 128.8046 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
177.4 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
177.6 | 128.9006 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
177.8 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
178 | 128.9006 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
178.2 | 128.9966 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
178.4 | 129.1885 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
178.6 | 129.8603 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
178.8 | 130.1482 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
179 | 129.3804 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
179.2 | 129.1885 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
179.4 | 128.9966 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
179.6 | 129.0925 | 0.016952 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
179.8 | 128.9966 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
180 | 128.9006 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
180.2 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
180.4 | 128.8046 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
180.6 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
180.8 | 128.8046 | 0.015352 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
181 | 128.8046 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
181.2 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
181.4 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
181.6 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
181.8 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.0923 | 0.006713
182 | 128.8046 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
182.2 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
182.4 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
182.6 | 128.9006 | 0.016952 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.009669 | 0.0923 | 0.0051138
182.8 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
183 | 128.7087 | 0.015352 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
183.2 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
183.4 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
183.6 | 128.9006 | 0.015352 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
183.8 | 128.8046 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
184 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
184.2 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
184.4 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
184.6 | 128.8046 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0035139
184.8 | 128.8046 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
185 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
185.2 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
185.4 | 128.8046 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
185.6 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
185.8 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
186 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
186.2 | 128.8046 | 0.013753 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
186.4 | 128.8046 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
186.6 | 128.8046 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
186.8 | 128.8046 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
187 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
187.2 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
187.4 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
187.6 | 128.8046 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
187.8 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
188 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
188.2 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
188.4 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
188.6 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
188.8 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
189 | 128.9006 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
189.2 | 128.8046 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
189.4 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
189.6 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
189.8 | 128.7087 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
190 | 128.8046 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
190.2 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
190.4 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
190.6 | 128.7087 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
190.8 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
191 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
191.2 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
191.4 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
191.6 | 128.7087 | 0.016952 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
191.8 | 128.8046 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
192 | 128.6127 | 0.020151 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
192.2 | 128.8046 | 0.024949 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
192.4 | 128.8046 | 0.024949 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
192.6 | 128.7087 | 0.018551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0019147
192.8 | 128.1329 | 0.024949 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
193 | 128.8046 | 0.034546 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
193.2 | 129.0925 | 0.05054 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
193.4 | 128.7087 | 0.026549 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.012923 | 0.57213 | 0.013089 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
193.6 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.01149 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
193.8 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.47618 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
194 | 128.7087 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0066908 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
194.2 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
194.4 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
194.6 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0002934 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
194.8 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
195 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
195.2 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
195.4 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
195.6 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
195.8 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.18829 | 0.0051138
196 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
196.2 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
196.4 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
196.6 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
196.8 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
197 | 128.7087 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.0048701 | -0.0036512 | 0.0051138
197.2 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
197.4 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
197.6 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
197.8 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
198 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
198.2 | 128.6127 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
198.4 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.003271 | 0.0923 | 0.0051138
198.6 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
198.8 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
199 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
199.2 | 128.6127 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
199.4 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
199.6 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
199.8 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
200 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
200.2 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
200.4 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.23811 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
200.6 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
200.8 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
201 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | -0.0036512 | 0.0051138
201.2 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
201.4 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
201.6 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
201.8 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.099642 | 0.0051138
202 | 128.6127 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
202.2 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
202.4 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
202.6 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
202.8 | 128.5167 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
203 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
203.2 | 128.6127 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
203.4 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
203.6 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
203.8 | 128.5167 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
204 | 128.5167 | 0.012154 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
204.2 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
204.4 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
204.6 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
204.8 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
205 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
205.2 | 128.6127 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
205.4 | 128.5167 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
205.6 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
205.8 | 128.5167 | 0.012154 | 0.10193 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
206 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
206.2 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0019147
206.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
206.6 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
206.8 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
207 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
207.2 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
207.4 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
207.6 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
207.8 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.28424 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
208 | 128.5167 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
208.2 | 128.4208 | 0.010554 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
208.4 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
208.6 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
208.8 | 128.4208 | 0.010554 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
209 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
209.2 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
209.4 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
209.6 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
209.8 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
210 | 128.4208 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
210.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
210.4 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
210.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
210.8 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
211 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
211.2 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
211.4 | 128.5167 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
211.6 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
211.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.57118 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
212 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
212.2 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
212.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
212.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
212.8 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
213 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
213.2 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
213.4 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
213.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
213.8 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
214 | 128.5167 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
214.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
214.4 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
214.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
214.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
215 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
215.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
215.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
215.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
215.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
216 | 128.5167 | 0.0089549 | 0.29387 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
216.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
216.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
216.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
216.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
217 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
217.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
217.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
217.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
217.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
218 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
218.2 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
218.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
218.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
218.8 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
219 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
219.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
219.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
219.6 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
219.8 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | -0.0036512 | 0.0051138
220 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
220.2 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
220.4 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
220.6 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
220.8 | 128.2288 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
221 | 128.3248 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
221.2 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
221.4 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
221.6 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
221.8 | 128.3248 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
222 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
222.2 | 128.3248 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
222.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
222.6 | 128.4208 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
222.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
223 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
223.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
223.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
223.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
223.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
224 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
224.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
224.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
224.6 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
224.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
225 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
225.2 | 128.4208 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
225.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
225.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.0048701 | 0.0923 | 0.0051138
225.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
226 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
226.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
226.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
226.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
226.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
227 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
227.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
227.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
227.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
227.8 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
228 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
228.2 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
228.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
228.6 | 128.5167 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
228.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
229 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
229.2 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
229.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
229.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
229.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
230 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.10127 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
230.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
230.4 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.003271 | 0.0923 | 0.0051138
230.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
230.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
231 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
231.2 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
231.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
231.6 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
231.8 | 128.7087 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
232 | 128.7087 | 0.0057559 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
232.2 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
232.4 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
232.6 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0019147
232.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
233 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
233.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
233.4 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
233.6 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
233.8 | 127.9409 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
234 | 127.9409 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.28424 | 0.0051138
234.2 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
234.4 | 128.6127 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
234.6 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
234.8 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
235 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
235.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
235.4 | 128.8046 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
235.6 | 128.8046 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
235.8 | 128.8046 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
236 | 128.8046 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
236.2 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
236.4 | 128.8046 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
236.6 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
236.8 | 128.7087 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
237 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
237.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
237.4 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
237.6 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
237.8 | 128.6127 | 0.016952 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
238 | 128.5167 | 0.031347 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
238.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0098898 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
238.4 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.014522 | 0.57213 | 0.0082906 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
238.6 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
238.8 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
239 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
239.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
239.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
239.6 | 128.6127 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
239.8 | 128.6127 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
240 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
240.2 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
240.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
240.6 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
240.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
241 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
241.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
241.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
241.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
241.8 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
242 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
242.2 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
242.4 | 128.4208 | 0.0089549 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
242.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
242.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
243 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
243.2 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
243.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
243.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
243.8 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
244 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
244.2 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
244.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
244.6 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
244.8 | 128.3248 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
245 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
245.2 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
245.4 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
245.6 | 128.4208 | 0.018551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
245.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
246 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0081246 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
246.2 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
246.4 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
246.6 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
246.8 | 128.3248 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
247 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
247.2 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
247.4 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
247.6 | 128.3248 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
247.8 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
248 | 128.3248 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
248.2 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
248.4 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
248.6 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
248.8 | 128.4208 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
249 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
249.2 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
249.4 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
249.6 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
249.8 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
250 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
250.2 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
250.4 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
250.6 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
250.8 | 128.4208 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
251 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
251.2 | 128.4208 | 0.013753 | 0.19792 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
251.4 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
251.6 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
251.8 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
252 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
252.2 | 128.4208 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
252.4 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
252.6 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
252.8 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
253 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
253.2 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
253.4 | 128.5167 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
253.6 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.006713
253.8 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
254 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
254.2 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
254.4 | 128.6127 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
254.6 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
254.8 | 128.6127 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
255 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
255.2 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
255.4 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
255.6 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
255.8 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
256 | 128.6127 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
256.2 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
256.4 | 128.4208 | 0.02175 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
256.6 | 128.7087 | 0.031347 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
256.8 | 128.9006 | 0.039345 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
257 | 128.7087 | 0.015352 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
257.2 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
257.4 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
257.6 | 128.7087 | 0.013753 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
257.8 | 128.7087 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
258 | 128.7087 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
258.2 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
258.4 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
258.6 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
258.8 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
259 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.006713
259.2 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
259.4 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
259.6 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
259.8 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
260 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
260.2 | 128.9006 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
260.4 | 129.0925 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
260.6 | 129.6683 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
260.8 | 130.2441 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
261 | 129.5724 | 0.016952 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
261.2 | 129.0925 | 0.012154 | 0.38986 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.28424 | 0.0051138
261.4 | 129.0925 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0035139
261.6 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
261.8 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
262 | 128.9006 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
262.2 | 128.8046 | 0.015352 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
262.4 | 128.9006 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0002934 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
262.6 | 128.9006 | 0.016952 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
262.8 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.006713
263 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
263.2 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
263.4 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.00647 | 0.18829 | 0.006713
263.6 | 128.7087 | 0.015352 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
263.8 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
264 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
264.2 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.0048701 | 0.0923 | 0.0051138
264.4 | 128.9006 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
264.6 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
264.8 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
265 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
265.2 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
265.4 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
265.6 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
265.8 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
266 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
266.2 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
266.4 | 128.6127 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
266.6 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
266.8 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
267 | 128.6127 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
267.2 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
267.4 | 128.5167 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
267.6 | 128.7087 | 0.02335 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
267.8 | 128.7087 | 0.039345 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
268 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0098898 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
268.2 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
268.4 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
268.6 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
268.8 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
269 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
269.2 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
269.4 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
269.6 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
269.8 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
270 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
270.2 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
270.4 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
270.6 | 128.6127 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
270.8 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
271 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
271.2 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
271.4 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
271.6 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
271.8 | 128.3248 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
272 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.003271 | 0.0923 | 0.0051138
272.2 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
272.4 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
272.6 | 128.4208 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
272.8 | 128.4208 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
273 | 128.4208 | 0.010554 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
273.2 | 128.3248 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.00647 | 0.0923 | 0.0051138
273.4 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
273.6 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
273.8 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
274 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
274.2 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
274.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
274.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
274.8 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
275 | 128.3248 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
275.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
275.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
275.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
275.8 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
276 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
276.2 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
276.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
276.6 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
276.8 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
277 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.28424 | 0.0051138
277.2 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
277.4 | 128.4208 | 0.0057559 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
277.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
277.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
278 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
278.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
278.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
278.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
278.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.18829 | 0.0051138
279 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
279.2 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
279.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
279.6 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
279.8 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
280 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
280.2 | 128.6127 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
280.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
280.6 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
280.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
281 | 128.7087 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
281.2 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
281.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
281.6 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
281.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
282 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
282.2 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
282.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
282.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
282.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
283 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
283.2 | 127.749 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
283.4 | 127.9409 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
283.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
283.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
284 | 128.8046 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
284.2 | 128.8046 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
284.4 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
284.6 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
284.8 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
285 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
285.2 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
285.4 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
285.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
285.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
286 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
286.2 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
286.4 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.0923 | 0.0051138
286.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
286.8 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
287 | 128.6127 | 0.010554 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
287.2 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
287.4 | 128.5167 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
287.6 | 128.5167 | 0.024949 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
287.8 | 128.8046 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
288 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
288.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.01149 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
288.4 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
288.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
288.8 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
289 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
289.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
289.4 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
289.6 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
289.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
290 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
290.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
290.4 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
290.6 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
290.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
291 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
291.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
291.4 | 128.5167 | 0.0089549 | 0.10193 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0035139
291.6 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
291.8 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
292 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
292.2 | 128.5167 | 0.0073551 | 0.48581 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
292.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
292.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
292.8 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.38019 | 0.0051138
293 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
293.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
293.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
293.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
293.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
294 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.006713
294.2 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
294.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
294.6 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
294.8 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
295 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
295.2 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
295.4 | 128.3248 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
295.6 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
295.8 | 128.5167 | 0.018551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
296 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
296.2 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
296.4 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
296.6 | 128.3248 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
296.8 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0002934 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
297 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
297.2 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
297.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
297.6 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
297.8 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
298 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
298.2 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
298.4 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
298.6 | 128.4208 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
298.8 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
299 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
299.2 | 128.5167 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
299.4 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
299.6 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
299.8 | 128.5167 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
300 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
300.2 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
300.4 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
300.6 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
300.8 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
301 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
301.2 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
301.4 | 128.6127 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
301.6 | 128.5167 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
301.8 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
302 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
302.2 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
302.4 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
302.6 | 128.6127 | 0.024949 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
302.8 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
303 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.18829 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
303.2 | 128.8046 | 0.016952 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
303.4 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
303.6 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
303.8 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
304 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
304.2 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
304.4 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
304.6 | 128.9006 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.0051138
304.8 | 129.6683 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
305 | 129.6683 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
305.2 | 129.1885 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
305.4 | 128.9966 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
305.6 | 128.9006 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
305.8 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
306 | 128.8046 | 0.015352 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
306.2 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
306.4 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
306.6 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
306.8 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
307 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
307.2 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
307.4 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
307.6 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
307.8 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
308 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
308.2 | 128.8046 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
308.4 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0035139
308.6 | 128.8046 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
308.8 | 128.8046 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
309 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
309.2 | 128.7087 | 0.018551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
309.4 | 129.4764 | 0.042543 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.011324 | 0.57213 | 0.0066908 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
309.6 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.18729 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
309.8 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
310 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
310.2 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
310.4 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
310.6 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
310.8 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
311 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
311.2 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
311.4 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
311.6 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
311.8 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
312 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
312.2 | 128.6127 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.003271 | 0.18829 | 0.0051138
312.4 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
312.6 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
312.8 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
313 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
313.2 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
313.4 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
313.6 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
313.8 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
314 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
314.2 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
314.4 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
314.6 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
314.8 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
315 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
315.2 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
315.4 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
315.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
315.8 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
316 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
316.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
316.4 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
316.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
316.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
317 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
317.2 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
317.4 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
317.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
317.8 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
318 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
318.2 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
318.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
318.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
318.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
319 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
319.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.0051138
319.4 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
319.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
319.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
320 | 128.4208 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
320.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
320.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
320.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
320.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.003271 | 0.18829 | 0.0051138
321 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
321.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
321.4 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
321.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.006414 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
321.8 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
322 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
322.2 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
322.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
322.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
322.8 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
323 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
323.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
323.4 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
323.6 | 128.5167 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
323.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
324 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
324.2 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
324.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
324.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
324.8 | 128.6127 | 0.020151 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
325 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
325.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
325.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
325.6 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
325.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
326 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
326.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
326.4 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
326.6 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
326.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
327 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
327.2 | 128.5167 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0035139
327.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
327.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
327.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
328 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
328.2 | 128.8046 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
328.4 | 128.8046 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
328.6 | 128.8046 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
328.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
329 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
329.2 | 128.8046 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.57118 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.00647 | 0.0923 | 0.0051138
329.4 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
329.6 | 128.8046 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
329.8 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
330 | 128.7087 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
330.2 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
330.4 | 128.7087 | 0.020151 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.006713
330.6 | 128.8046 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.012923 | 0.57213 | 0.0098898 | 0.48581 | 0.00647 | 0.18829 | 0.006713
330.8 | 128.6127 | 0.0073551 | 0.29387 | 0.0015826 | 0.38916 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.016122 | 0.66813 | 0.0082906 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
331 | 128.6127 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
331.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
331.4 | 128.7087 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
331.6 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
331.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
332 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
332.2 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
332.4 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
332.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
332.8 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
333 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
333.2 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
333.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
333.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
333.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
334 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.00012733 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
334.2 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
334.4 | 128.5167 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
334.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
334.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
335 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
335.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
335.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
335.6 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
335.8 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
336 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
336.2 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
336.4 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.00647 | 0.0923 | 0.0035139
336.6 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0035139
336.8 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
337 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
337.2 | 128.5167 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
337.4 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
337.6 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
337.8 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
338 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
338.2 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
338.4 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
338.6 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
338.8 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
339 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.0051138
339.2 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
339.4 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.48515 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
339.6 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
339.8 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
340 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
340.2 | 128.5167 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
340.4 | 128.6127 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
340.6 | 128.6127 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
340.8 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
341 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
341.2 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
341.4 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
341.6 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
341.8 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
342 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
342.2 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
342.4 | 128.7087 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
342.6 | 128.7087 | 0.013753 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
342.8 | 128.7087 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
343 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
343.2 | 128.8046 | 0.032947 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
343.4 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
343.6 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
343.8 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
344 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
344.2 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
344.4 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
344.6 | 128.8046 | 0.016952 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
344.8 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
345 | 128.9966 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
345.2 | 129.1885 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
345.4 | 130.2441 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
345.6 | 129.4764 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
345.8 | 129.0925 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
346 | 128.9966 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
346.2 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
346.4 | 128.8046 | 0.015352 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
346.6 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
346.8 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
347 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
347.2 | 128.8046 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
347.4 | 128.8046 | 0.015352 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
347.6 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
347.8 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
348 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
348.2 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
348.4 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
348.6 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
348.8 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
349 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
349.2 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0035139
349.4 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
349.6 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
349.8 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
350 | 128.7087 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
350.2 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
350.4 | 128.9006 | 0.029748 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
350.6 | 128.9006 | 0.037745 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
350.8 | 129.0925 | 0.024949 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.012923 | 0.47618 | 0.0098898 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
351 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
351.2 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | -0.19559 | 0.0051138
351.4 | 128.7087 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
351.6 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
351.8 | 128.6127 | 0.013753 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
352 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
352.2 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
352.4 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
352.6 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
352.8 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
353 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
353.2 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
353.4 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
353.6 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
353.8 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
354 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
354.2 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
354.4 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
354.6 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
354.8 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
355 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
355.2 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
355.4 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
355.6 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
355.8 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
356 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
356.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
356.4 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
356.6 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
356.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
357 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
357.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
357.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
357.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
357.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
358 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
358.2 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
358.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
358.6 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
358.8 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
359 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0081246 | 0.47618 | 0.0066908 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
359.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
359.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
359.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
359.8 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
360 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
360.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
360.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
360.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
360.8 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
361 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
361.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
361.4 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
361.6 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
361.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
362 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
362.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
362.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
362.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
362.8 | 128.5167 | 0.0073551 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
363 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
363.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.006713
363.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
363.6 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
363.8 | 128.6127 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
364 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0002934 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
364.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
364.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
364.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
364.8 | 128.6127 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
365 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
365.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
365.4 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
365.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
365.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
366 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
366.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
366.4 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
366.6 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
366.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
367 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
367.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
367.4 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
367.6 | 128.6127 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
367.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.57118 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
368 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
368.2 | 128.8046 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
368.4 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
368.6 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
368.8 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
369 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
369.2 | 127.4611 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
369.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
369.6 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
369.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
370 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.19792 | 0.00647 | 0.0923 | 0.0051138
370.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
370.4 | 128.8046 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
370.6 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
370.8 | 128.8046 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
371 | 128.8046 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
371.2 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
371.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
371.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
371.8 | 128.8046 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
372 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
372.2 | 128.8046 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
372.4 | 128.8046 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
372.6 | 128.8046 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
372.8 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
373 | 128.7087 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
373.2 | 128.6127 | 0.02335 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
373.4 | 128.8046 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0097238 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
373.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.014522 | 0.57213 | 0.0082906 | 0.48581 | 0.00647 | 0.0923 | 0.006713
373.8 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
374 | 128.7087 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
374.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
374.4 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
374.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
374.8 | 128.6127 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
375 | 128.5167 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
375.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
375.4 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
375.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
375.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
376 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
376.2 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
376.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
376.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
376.8 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.006713
377 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
377.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
377.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
377.6 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
377.8 | 128.4208 | 0.010554 | 0.10193 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
378 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
378.2 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
378.4 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
378.6 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
378.8 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
379 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
379.2 | 128.5167 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
379.4 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
379.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.10127 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
379.8 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
380 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
380.2 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
380.4 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
380.6 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
380.8 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
381 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
381.2 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
381.4 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
381.6 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
381.8 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
382 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
382.2 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
382.4 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
382.6 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
382.8 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
383 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
383.2 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
383.4 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
383.6 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
383.8 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
384 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
384.2 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
384.4 | 128.6127 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
384.6 | 128.7087 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
384.8 | 128.8046 | 0.020151 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
385 | 128.9966 | 0.040944 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
385.2 | 128.7087 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | -0.58044 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
385.4 | 128.8046 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
385.6 | 128.7087 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
385.8 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
386 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
386.2 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | -0.0036512 | 0.0051138
386.4 | 128.9006 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
386.6 | 129.9562 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
386.8 | 129.1885 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
387 | 128.9966 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
387.2 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.5818 | 0.00647 | 0.18829 | 0.0051138
387.4 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
387.6 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
387.8 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
388 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
388.2 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
388.4 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
388.6 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
388.8 | 128.8046 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
389 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
389.2 | 128.8046 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
389.4 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.28424 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
389.6 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
389.8 | 128.8046 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
390 | 128.9006 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
390.2 | 128.9006 | 0.026549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
390.4 | 128.9006 | 0.029748 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.012923 | 0.66813 | 0.0098898 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
390.6 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
390.8 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
391 | 128.6127 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
391.2 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
391.4 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
391.6 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.57118 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
391.8 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
392 | 128.6127 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
392.2 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
392.4 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
392.6 | 128.6127 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
392.8 | 128.6127 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | -0.0036512 | 0.0051138
393 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
393.2 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
393.4 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
393.6 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
393.8 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
394 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
394.2 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
394.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
394.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
394.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
395 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
395.2 | 128.5167 | 0.0073551 | 0.38986 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
395.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
395.6 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
395.8 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.00647 | 0.0923 | 0.006713
396 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0081246 | 0.47618 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
396.2 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
396.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
396.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
396.8 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
397 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
397.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
397.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.76408 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
397.6 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
397.8 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
398 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
398.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
398.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.57118 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
398.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
398.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
399 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
399.2 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
399.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
399.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
399.8 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
400 | 128.5167 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
400.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
400.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
400.6 | 128.6127 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
400.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
401 | 128.6127 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
401.2 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
401.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
401.6 | 128.6127 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
401.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
402 | 128.7087 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
402.2 | 128.6127 | 0.020151 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
402.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
402.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0081246 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
402.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
403 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
403.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
403.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
403.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
403.8 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
404 | 128.7087 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
404.2 | 128.7087 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
404.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
404.6 | 128.1329 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
404.8 | 127.557 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
405 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
405.2 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
405.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0050916 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
405.6 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
405.8 | 128.9006 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.0923 | 0.0051138
406 | 128.8046 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
406.2 | 128.8046 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
406.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
406.6 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
406.8 | 128.8046 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
407 | 128.8046 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
407.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
407.4 | 128.8046 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
407.6 | 128.8046 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
407.8 | 128.8046 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
408 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
408.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
408.4 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
408.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
408.8 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
409 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
409.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
409.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
409.6 | 128.6127 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
409.8 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
410 | 128.5167 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
410.2 | 128.6127 | 0.020151 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
410.4 | 128.9006 | 0.039345 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
410.6 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.01149 | 0.48581 | 0.00647 | 0.18829 | 0.006713
410.8 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.011324 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
411 | 128.6127 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
411.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
411.4 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
411.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
411.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
412 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
412.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
412.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
412.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
412.8 | 128.6127 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
413 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
413.2 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
413.4 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
413.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
413.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
414 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
414.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
414.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
414.6 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
414.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
415 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
415.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
415.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
415.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
415.8 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
416 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
416.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
416.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
416.6 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
416.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
417 | 128.5167 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
417.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
417.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
417.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
417.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
418 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
418.2 | 128.5167 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
418.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
418.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
418.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
419 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
419.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
419.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
419.6 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
419.8 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
420 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
420.2 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
420.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
420.6 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.29387 | 0.00647 | 0.18829 | 0.006713
420.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
421 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
421.2 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
421.4 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
421.6 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
421.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.48515 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
422 | 128.3248 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
422.2 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
422.4 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
422.6 | 128.4208 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
422.8 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
423 | 128.5167 | 0.016952 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
423.2 | 128.3248 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
423.4 | 128.4208 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
423.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
423.8 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
424 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
424.2 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
424.4 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
424.6 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
424.8 | 128.3248 | 0.010554 | 0.19792 | 0.0031824 | 0.38916 | 0.006414 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
425 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.0923 | 0.0051138
425.2 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
425.4 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | -0.0036512 | 0.006713
425.6 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
425.8 | 128.3248 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
426 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
426.2 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
426.4 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
426.6 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
426.8 | 128.4208 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
427 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
427.2 | 128.5167 | 0.012154 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
427.4 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
427.6 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
427.8 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
428 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
428.2 | 128.4208 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
428.4 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
428.6 | 128.5167 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
428.8 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
429 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
429.2 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
429.4 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
429.6 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
429.8 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
430 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
430.2 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
430.4 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
430.6 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
430.8 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
431 | 128.5167 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | -0.0036512 | 0.006713
431.2 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
431.4 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
431.6 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
431.8 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
432 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
432.2 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0002934 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
432.4 | 128.6127 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
432.6 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
432.8 | 128.7087 | 0.013753 | 0.29387 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
433 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
433.2 | 128.7087 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
433.4 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0083128
433.6 | 128.6127 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
433.8 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
434 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
434.2 | 128.5167 | 0.024949 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
434.4 | 129.0925 | 0.039345 | 0.10193 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
434.6 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
434.8 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
435 | 128.8046 | 0.015352 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
435.2 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
435.4 | 128.8046 | 0.015352 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
435.6 | 128.7087 | 0.015352 | 0.29387 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
435.8 | 128.8046 | 0.016952 | 0.10193 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.71795 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.38019 | 0.0051138
436 | 128.8046 | 0.015352 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
436.2 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
436.4 | 128.8046 | 0.016952 | 0.38986 | 0.0015826 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
436.6 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
436.8 | 128.9006 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
437 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
437.2 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
437.4 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
437.6 | 129.1885 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
437.8 | 129.8603 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
438 | 129.7643 | 0.016952 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
438.2 | 129.1885 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
438.4 | 128.9966 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.009912
438.6 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
438.8 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
439 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
439.2 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
439.4 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.76408 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
439.6 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
439.8 | 128.8046 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.38019 | 0.0051138
440 | 128.8046 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0083128
440.2 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
440.4 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
440.6 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
440.8 | 128.9006 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
441 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
441.2 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
441.4 | 128.9006 | 0.015352 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
441.6 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
441.8 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
442 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
442.2 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
442.4 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
442.6 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
442.8 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
443 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
443.2 | 128.9006 | 0.02335 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
443.4 | 128.6127 | 0.028148 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
443.6 | 128.7087 | 0.026549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0097238 | 0.57213 | 0.0098898 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
443.8 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
444 | 128.7087 | 0.015352 | 0.29387 | 0.0015826 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
444.2 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
444.4 | 128.7087 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
444.6 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
444.8 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
445 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
445.2 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
445.4 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
445.6 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
445.8 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
446 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
446.2 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
446.4 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
446.6 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
446.8 | 128.7087 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
447 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
447.2 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
447.4 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
447.6 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
447.8 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
448 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
448.2 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
448.4 | 128.5167 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
448.6 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
448.8 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
449 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
449.2 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
449.4 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
449.6 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
449.8 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
450 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
450.2 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
450.4 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
450.6 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
450.8 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
451 | 128.5167 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
451.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
451.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
451.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
451.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
452 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
452.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | -0.0036512 | 0.0051138
452.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
452.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
452.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
453 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
453.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
453.4 | 128.5167 | 0.012154 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
453.6 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
453.8 | 128.2288 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
454 | 128.3248 | 0.013753 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
454.2 | 128.7087 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
454.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
454.6 | 128.3248 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
454.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
455 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
455.2 | 128.3248 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
455.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
455.6 | 128.5167 | 0.0073551 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
455.8 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
456 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
456.2 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
456.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
456.6 | 128.5167 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
456.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
457 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
457.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
457.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
457.6 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
457.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
458 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
458.2 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
458.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
458.6 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
458.8 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
459 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
459.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
459.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
459.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
459.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
460 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
460.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
460.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
460.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
460.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
461 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
461.2 | 128.5167 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
461.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
461.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
461.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
462 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
462.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
462.4 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
462.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
462.8 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
463 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
463.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
463.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
463.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
463.8 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
464 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
464.2 | 128.7087 | 0.020151 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
464.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
464.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
464.8 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
465 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.57118 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
465.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
465.4 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
465.6 | 128.7087 | 0.0073551 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
465.8 | 128.7087 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
466 | 128.6127 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
466.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
466.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
466.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.5818 | 0.00647 | 0.0923 | 0.0051138
466.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0035139
467 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
467.2 | 128.6127 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
467.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
467.6 | 127.653 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
467.8 | 127.557 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
468 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
468.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
468.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
468.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
468.8 | 128.6127 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
469 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
469.2 | 128.7087 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
469.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
469.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
469.8 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
470 | 128.6127 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
470.2 | 128.6127 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
470.4 | 128.8046 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
470.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
470.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
471 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
471.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
471.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
471.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
471.8 | 128.7087 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
472 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
472.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
472.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
472.6 | 128.6127 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
472.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
473 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
473.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
473.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
473.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
473.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
474 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
474.2 | 128.6127 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
474.4 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
474.6 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
474.8 | 128.5167 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
475 | 128.8046 | 0.02175 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
475.2 | 128.6127 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
475.4 | 128.9006 | 0.036146 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
475.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
475.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
476 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
476.2 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.014522 | 0.66813 | 0.0098898 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
476.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.013089 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
476.6 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
476.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
477 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
477.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
477.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.71795 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
477.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
477.8 | 128.5167 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
478 | 128.6127 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
478.2 | 128.5167 | 0.0073551 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
478.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
478.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
478.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
479 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
479.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
479.4 | 128.6127 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
479.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
479.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
480 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
480.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
480.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
480.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
480.8 | 128.5167 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
481 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
481.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
481.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
481.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
481.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
482 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
482.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0083128
482.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
482.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
482.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.18829 | 0.006713
483 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
483.2 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
483.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
483.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
483.8 | 128.4208 | 0.0057559 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
484 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
484.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
484.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
484.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
484.8 | 128.4208 | 0.0073551 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
485 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.011268 | 0.18829 | 0.006713
485.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.38019 | 0.006713
485.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.38019 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
485.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
485.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
486 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
486.2 | 128.5167 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
486.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
486.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
486.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
487 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
487.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
487.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
487.6 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
487.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
488 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
488.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
488.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
488.6 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
488.8 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
489 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
489.2 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
489.4 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
489.6 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
489.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
490 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
490.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.006713
490.4 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
490.6 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
490.8 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
491 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
491.2 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
491.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.006713
491.6 | 128.3248 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
491.8 | 128.3248 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
492 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
492.2 | 128.2288 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
492.4 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0098898 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
492.6 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
492.8 | 128.3248 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
493 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
493.2 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
493.4 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
493.6 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
493.8 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
494 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
494.2 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
494.4 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
494.6 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
494.8 | 128.3248 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
495 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
495.2 | 128.3248 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
495.4 | 128.3248 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
495.6 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
495.8 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
496 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
496.2 | 128.3248 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.5818 | 0.00647 | 0.18829 | 0.0051138
496.4 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
496.6 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
496.8 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
497 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
497.2 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
497.4 | 128.3248 | 0.013753 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
497.6 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
497.8 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
498 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
498.2 | 128.3248 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
498.4 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
498.6 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
498.8 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
499 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
499.2 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
499.4 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
499.6 | 128.4208 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
499.8 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
500 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
500.2 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
500.4 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
500.6 | 128.4208 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
500.8 | 128.5167 | 0.013753 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
501 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
501.2 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
501.4 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
501.6 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
501.8 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
502 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
502.2 | 128.6127 | 0.028148 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
502.4 | 128.6127 | 0.015352 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.28424 | 0.006713
502.6 | 128.6127 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
502.8 | 128.6127 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
503 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
503.2 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
503.4 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
503.6 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.57118 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
503.8 | 128.6127 | 0.016952 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
504 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
504.2 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
504.4 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
504.6 | 128.6127 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
504.8 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
505 | 128.8046 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
505.2 | 129.1885 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
505.4 | 130.0522 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
505.6 | 129.4764 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
505.8 | 128.9006 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
506 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
506.2 | 128.8046 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
506.4 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
506.6 | 128.7087 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
506.8 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
507 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
507.2 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
507.4 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
507.6 | 128.7087 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
507.8 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
508 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
508.2 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
508.4 | 128.7087 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
508.6 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
508.8 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
509 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
509.2 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
509.4 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
509.6 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
509.8 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
510 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.0051138
510.2 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
510.4 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
510.6 | 128.5167 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
510.8 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
511 | 128.6127 | 0.02175 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
511.2 | 128.7087 | 0.042543 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
511.4 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0082906 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
511.6 | 128.4208 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
511.8 | 128.5167 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
512 | 128.5167 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
512.2 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
512.4 | 128.4208 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
512.6 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | 0.0923 | 0.0051138
512.8 | 128.4208 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
513 | 128.4208 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
513.2 | 128.3248 | 0.013753 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
513.4 | 128.4208 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
513.6 | 128.4208 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
513.8 | 128.4208 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
514 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
514.2 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
514.4 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
514.6 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
514.8 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
515 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
515.2 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
515.4 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
515.6 | 128.3248 | 0.012154 | 0.48581 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
515.8 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
516 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
516.2 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
516.4 | 128.3248 | 0.012154 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
516.6 | 128.2288 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
516.8 | 128.2288 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.006713
517 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
517.2 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
517.4 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
517.6 | 128.2288 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
517.8 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
518 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
518.2 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
518.4 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
518.6 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
518.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
519 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
519.2 | 128.1329 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
519.4 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
519.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
519.8 | 128.2288 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
520 | 128.2288 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
520.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
520.4 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
520.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
520.8 | 128.3248 | 0.012154 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
521 | 128.2288 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
521.2 | 128.2288 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
521.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
521.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
521.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
522 | 128.2288 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
522.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
522.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
522.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
522.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
523 | 128.2288 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
523.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
523.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
523.6 | 128.1329 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
523.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
524 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
524.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
524.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
524.6 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
524.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
525 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
525.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
525.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
525.6 | 128.3248 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
525.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
526 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
526.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
526.4 | 128.3248 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
526.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
526.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
527 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
527.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
527.4 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
527.6 | 128.4208 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
527.8 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
528 | 128.1329 | 0.0089549 | 0.38986 | 0.0031824 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
528.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0081246 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
528.4 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
528.6 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
528.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
529 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
529.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
529.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
529.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
529.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
530 | 128.5167 | 0.0073551 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.33406 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
530.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
530.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
530.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
530.8 | 127.4611 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
531 | 127.749 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
531.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
531.4 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
531.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
531.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
532 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
532.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
532.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
532.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
532.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
533 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
533.2 | 128.5167 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
533.4 | 128.5167 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
533.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
533.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
534 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
534.2 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
534.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
534.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
534.8 | 128.5167 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
535 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
535.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
535.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
535.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
535.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
536 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
536.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
536.4 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
536.6 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
536.8 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
537 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
537.2 | 128.5167 | 0.020151 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
537.4 | 128.6127 | 0.02335 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
537.6 | 128.8046 | 0.039345 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
537.8 | 128.7087 | 0.024949 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
538 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0098898 | 0.48581 | 0.00647 | 0.18829 | 0.006713
538.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.011324 | 0.47618 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
538.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.014522 | 0.66813 | 0.0098898 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
538.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
538.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
539 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
539.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
539.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
539.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
539.8 | 128.4208 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
540 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
540.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
540.4 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
540.6 | 128.4208 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
540.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0015826 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
541 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
541.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
541.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
541.6 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
541.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
542 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
542.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
542.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
542.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
542.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
543 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
543.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
543.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
543.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
543.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0086004 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
544 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
544.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
544.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
544.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
544.8 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
545 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
545.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
545.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
545.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
545.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
546 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
546.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
546.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
546.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.006713
546.8 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
547 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
547.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
547.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
547.6 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
547.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
548 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
548.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.28424 | 0.006713
548.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0083128
548.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
548.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
549 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
549.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
549.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
549.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
549.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.28424 | 0.006713
550 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
550.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
550.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
550.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.28424 | 0.006713
550.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
551 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
551.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
551.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
551.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
551.8 | 128.3248 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
552 | 128.4208 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
552.2 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.67775 | 0.00647 | 0.18829 | 0.006713
552.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
552.6 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
552.8 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
553 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
553.2 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
553.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
553.6 | 128.4208 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
553.8 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
554 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
554.2 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
554.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
554.6 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
554.8 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
555 | 128.4208 | 0.013753 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
555.2 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
555.4 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
555.6 | 128.4208 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
555.8 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
556 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
556.2 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.23811 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
556.4 | 128.2288 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
556.6 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
556.8 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
557 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
557.2 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
557.4 | 128.3248 | 0.012154 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
557.6 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
557.8 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
558 | 128.4208 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
558.2 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
558.4 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0083128
558.6 | 128.4208 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
558.8 | 128.4208 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
559 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.76408 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
559.2 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
559.4 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
559.6 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
559.8 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
560 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
560.2 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
560.4 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.011268 | 0.18829 | 0.006713
560.6 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
560.8 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
561 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
561.2 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.006713
561.4 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
561.6 | 128.5167 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
561.8 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
562 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
562.2 | 128.5167 | 0.015352 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
562.4 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
562.6 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
562.8 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
563 | 128.5167 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
563.2 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
563.4 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
563.6 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
563.8 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
564 | 128.6127 | 0.013753 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
564.2 | 128.6127 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
564.4 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
564.6 | 128.4208 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
564.8 | 128.8046 | 0.039345 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
565 | 128.7087 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
565.2 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
565.4 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
565.6 | 128.5167 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.66813 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
565.8 | 128.5167 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
566 | 128.6127 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
566.2 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
566.4 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
566.6 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.48515 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
566.8 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
567 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
567.2 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
567.4 | 128.8046 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.0083128
567.6 | 129.2844 | 0.016952 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
567.8 | 130.1482 | 0.020151 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
568 | 129.3804 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
568.2 | 128.9006 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
568.4 | 128.9006 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
568.6 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
568.8 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
569 | 128.8046 | 0.016952 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
569.2 | 128.7087 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
569.4 | 128.7087 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
569.6 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
569.8 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
570 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
570.2 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
570.4 | 128.7087 | 0.016952 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
570.6 | 128.6127 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
570.8 | 128.7087 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
571 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
571.2 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
571.4 | 128.6127 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
571.6 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
571.8 | 128.7087 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
572 | 128.7087 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
572.2 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
572.4 | 128.7087 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
572.6 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
572.8 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.0923 | 0.006713
573 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
573.2 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
573.4 | 128.6127 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
573.6 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
573.8 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
574 | 128.6127 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
574.2 | 128.6127 | 0.012154 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
574.4 | 128.6127 | 0.013753 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
574.6 | 128.5167 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.38019 | 0.0051138
574.8 | 128.5167 | 0.020151 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
575 | 128.6127 | 0.02175 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0081246 | 0.47618 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
575.2 | 128.6127 | 0.029748 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
575.4 | 128.9966 | 0.045742 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.012923 | 0.57213 | 0.0082906 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
575.6 | 128.6127 | 0.024949 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.011324 | 0.57213 | 0.01149 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
575.8 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
576 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
576.2 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
576.4 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
576.6 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
576.8 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
577 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
577.2 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
577.4 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
577.6 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
577.8 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
578 | 128.4208 | 0.012154 | 0.29387 | 0.0015826 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
578.2 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0035139
578.4 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
578.6 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
578.8 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
579 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
579.2 | 128.5167 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
579.4 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
579.6 | 128.4208 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
579.8 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
580 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
580.2 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
580.4 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
580.6 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
580.8 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
581 | 128.4208 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
581.2 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
581.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
581.6 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
581.8 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
582 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
582.2 | 128.5167 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
582.4 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
582.6 | 128.4208 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
582.8 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
583 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
583.2 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
583.4 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
583.6 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
583.8 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
584 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
584.2 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
584.4 | 128.4208 | 0.013753 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
584.6 | 128.4208 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
584.8 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
585 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
585.2 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
585.4 | 128.3248 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
585.6 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
585.8 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
586 | 128.4208 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
586.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.28424 | 0.006713
586.4 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
586.6 | 128.4208 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
586.8 | 128.5167 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
587 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
587.2 | 128.4208 | 0.010554 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0083128
587.4 | 128.4208 | 0.012154 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
587.6 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
587.8 | 128.3248 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
588 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
588.2 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
588.4 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
588.6 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
588.8 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
589 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
589.2 | 128.2288 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
589.4 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
589.6 | 128.4208 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
589.8 | 128.3248 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
590 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
590.2 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
590.4 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
590.6 | 128.3248 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
590.8 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
591 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
591.2 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
591.4 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
591.6 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
591.8 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
592 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
592.2 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
592.4 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
592.6 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
592.8 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
593 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
593.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
593.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
593.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
593.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
594 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
594.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
594.4 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
594.6 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
594.8 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
595 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
595.2 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
595.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
595.6 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.5818 | 0.00647 | 0.18829 | 0.006713
595.8 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
596 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
596.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
596.4 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
596.6 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
596.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
597 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
597.2 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
597.4 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
597.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
597.8 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
598 | 128.3248 | 0.010554 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
598.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
598.4 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
598.6 | 128.3248 | 0.010554 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
598.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
599 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
599.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
599.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
599.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | 0.28424 | 0.006713
599.8 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
600 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
600.2 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
600.4 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
600.6 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
600.8 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
601 | 128.3248 | 0.010554 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
601.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
601.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
601.6 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
601.8 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
602 | 128.2288 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
602.2 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
602.4 | 128.2288 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
602.6 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
602.8 | 128.1329 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
603 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
603.2 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
603.4 | 128.6127 | 0.016952 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
603.6 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
603.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0081246 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
604 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0081246 | 0.47618 | 0.0082906 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
604.2 | 128.3248 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
604.4 | 128.3248 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | -0.1006 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
604.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
604.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
605 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
605.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
605.4 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
605.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0080139 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
605.8 | 128.2288 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
606 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
606.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
606.4 | 128.3248 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
606.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
606.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
607 | 128.2288 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
607.2 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
607.4 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
607.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
607.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
608 | 128.2288 | 0.0089549 | 0.29387 | 0.0015826 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
608.2 | 128.2288 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
608.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
608.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
608.8 | 128.2288 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
609 | 128.2288 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
609.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
609.4 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
609.6 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
609.8 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
610 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
610.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
610.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
610.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
610.8 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
611 | 128.3248 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | 0.28424 | 0.006713
611.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
611.4 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
611.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
611.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
612 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0035139
612.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
612.4 | 128.3248 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
612.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
612.8 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
613 | 128.3248 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
613.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
613.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
613.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
613.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
614 | 128.3248 | 0.0073551 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
614.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
614.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
614.6 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
614.8 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
615 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
615.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
615.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
615.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0080139 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
615.8 | 128.3248 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
616 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
616.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
616.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
616.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
616.8 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
617 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
617.2 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
617.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
617.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
617.8 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
618 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
618.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
618.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
618.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
618.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
619 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
619.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
619.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
619.6 | 128.4208 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
619.8 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
620 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
620.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
620.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
620.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
620.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
621 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
621.2 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
621.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
621.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
621.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
622 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
622.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
622.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
622.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
622.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
623 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
623.2 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
623.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
623.6 | 128.4208 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
623.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
624 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
624.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
624.4 | 128.5167 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
624.6 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
624.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
625 | 128.4208 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
625.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
625.4 | 128.5167 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
625.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
625.8 | 128.4208 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
626 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
626.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
626.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
626.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
626.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
627 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
627.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
627.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
627.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
627.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
628 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
628.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
628.4 | 128.5167 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
628.6 | 128.5167 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
628.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
629 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
629.2 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
629.4 | 128.5167 | 0.0073551 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
629.6 | 128.5167 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
629.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
630 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
630.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
630.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
630.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
630.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
631 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
631.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
631.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
631.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
631.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
632 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
632.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
632.4 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
632.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
632.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
633 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
633.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.66713 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
633.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
633.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
633.8 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | -0.0036512 | 0.0051138
634 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
634.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
634.4 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
634.6 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
634.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
635 | 128.5167 | 0.010554 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
635.2 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.006713
635.4 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
635.6 | 128.7087 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0051138
635.8 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.006713
636 | 128.4208 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
636.2 | 128.5167 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
636.4 | 128.4208 | 0.015352 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
636.6 | 128.5167 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
636.8 | 128.7087 | 0.02175 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
637 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
637.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
637.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
637.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
637.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
638 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
638.2 | 128.3248 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
638.4 | 128.6127 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
638.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
638.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
639 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
639.2 | 128.6127 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
639.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
639.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
639.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
640 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
640.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
640.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
640.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
640.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
641 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
641.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
641.4 | 128.6127 | 0.0073551 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
641.6 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
641.8 | 128.6127 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
642 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
642.2 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0086004 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
642.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
642.6 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
642.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
643 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
643.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
643.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
643.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
643.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
644 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
644.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
644.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
644.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
644.8 | 128.5167 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
645 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
645.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
645.4 | 128.7087 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
645.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
645.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
646 | 128.7087 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
646.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
646.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
646.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
646.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
647 | 128.7087 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
647.2 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
647.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
647.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
647.8 | 128.6127 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
648 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
648.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
648.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
648.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
648.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
649 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
649.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
649.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
649.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
649.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
650 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.38019 | 0.0051138
650.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
650.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
650.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
650.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
651 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
651.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
651.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
651.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
651.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
652 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
652.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
652.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
652.6 | 128.1329 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
652.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
653 | 127.749 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
653.2 | 127.2692 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
653.4 | 127.3651 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
653.6 | 127.4611 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
653.8 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
654 | 128.2288 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
654.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
654.4 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
654.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
654.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
655 | 128.4208 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
655.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
655.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
655.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
655.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
656 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
656.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
656.4 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
656.6 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
656.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
657 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
657.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
657.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
657.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
657.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
658 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
658.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
658.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
658.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
658.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
659 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
659.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
659.4 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
659.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
659.8 | 128.6127 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
660 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
660.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
660.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
660.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
660.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
661 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.28424 | 0.0051138
661.2 | 128.7087 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
661.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
661.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
661.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
662 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
662.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
662.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
662.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
662.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
663 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
663.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
663.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
663.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
663.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
664 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
664.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
664.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
664.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
664.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
665 | 128.6127 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
665.2 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
665.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
665.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
665.8 | 128.7087 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
666 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
666.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
666.4 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
666.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
666.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
667 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
667.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
667.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
667.6 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
667.8 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
668 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
668.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
668.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
668.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
668.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
669 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
669.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
669.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
669.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
669.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
670 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
670.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
670.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
670.6 | 128.6127 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
670.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
671 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
671.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
671.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
671.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
671.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
672 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
672.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
672.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
672.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
672.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
673 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
673.2 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
673.4 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
673.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
673.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
674 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
674.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
674.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
674.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
674.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
675 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
675.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
675.4 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
675.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
675.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
676 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
676.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
676.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
676.6 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
676.8 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
677 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
677.2 | 128.6127 | 0.0073551 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
677.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
677.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
677.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
678 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
678.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
678.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
678.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
678.8 | 128.6127 | 0.0073551 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
679 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
679.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
679.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
679.6 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
679.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
680 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
680.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
680.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.28424 | 0.0051138
680.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
680.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
681 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
681.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
681.4 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
681.6 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
681.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
682 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
682.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
682.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
682.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
682.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
683 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
683.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
683.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
683.6 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
683.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
684 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
684.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
684.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
684.6 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
684.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
685 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
685.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
685.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
685.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
685.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
686 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
686.2 | 128.6127 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
686.4 | 128.6127 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
686.6 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
686.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
687 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
687.2 | 128.5167 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.006713
687.4 | 128.8046 | 0.02175 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
687.6 | 128.4208 | 0.024949 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
687.8 | 128.8046 | 0.036146 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
688 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0097238 | 0.47618 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
688.2 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.011324 | 0.57213 | 0.01149 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
688.4 | 128.2288 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0098898 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
688.6 | 128.5167 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
688.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.012923 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
689 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.01149 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
689.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0098898 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
689.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
689.6 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
689.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.0923 | 0.006713
690 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
690.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
690.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
690.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
690.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
691 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
691.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
691.4 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
691.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
691.8 | 128.6127 | 0.0089549 | 0.48581 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
692 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
692.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
692.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
692.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
692.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
693 | 128.6127 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
693.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
693.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
693.6 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
693.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
694 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
694.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
694.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
694.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
694.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
695 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
695.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
695.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
695.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
695.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
696 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
696.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
696.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
696.6 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
696.8 | 128.7087 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
697 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
697.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
697.4 | 128.6127 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
697.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
697.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
698 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
698.2 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
698.4 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
698.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
698.8 | 128.7087 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
699 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
699.2 | 128.7087 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
699.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
699.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
699.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
700 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
700.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
700.4 | 128.6127 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
700.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
700.8 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
701 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
701.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
701.4 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
701.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
701.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
702 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
702.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
702.4 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
702.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
702.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
703 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
703.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
703.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
703.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
703.8 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
704 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
704.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
704.4 | 128.6127 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
704.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
704.8 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
705 | 128.6127 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
705.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
705.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
705.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
705.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
706 | 128.7087 | 0.010554 | 0.48581 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
706.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
706.4 | 128.6127 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
706.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
706.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
707 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
707.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
707.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
707.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
707.8 | 128.6127 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
708 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
708.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
708.4 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.0923 | 0.006713
708.6 | 128.6127 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
708.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.006713
709 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
709.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
709.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
709.6 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0051138
709.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
710 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
710.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
710.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
710.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
710.8 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
711 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
711.2 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
711.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
711.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
711.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
712 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
712.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
712.4 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
712.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
712.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
713 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
713.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
713.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
713.6 | 128.6127 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
713.8 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
714 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
714.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
714.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
714.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
714.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
715 | 128.6127 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
715.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
715.4 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
715.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
715.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
716 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
716.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
716.4 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
716.6 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
716.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
717 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
717.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
717.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
717.6 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
717.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
718 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
718.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
718.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
718.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
718.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
719 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
719.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
719.4 | 128.6127 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
719.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
719.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
720 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
720.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
720.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
720.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
720.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
721 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
721.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
721.4 | 128.7087 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
721.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
721.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
722 | 128.6127 | 0.010554 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
722.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
722.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
722.6 | 128.7087 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
722.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
723 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
723.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
723.4 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
723.6 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
723.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
724 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
724.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
724.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
724.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
724.8 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
725 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
725.2 | 128.5167 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
725.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
725.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
725.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
726 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
726.2 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
726.4 | 128.7087 | 0.010554 | 0.38986 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
726.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
726.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
727 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
727.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
727.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
727.6 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
727.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
728 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
728.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
728.4 | 128.8046 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
728.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
728.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
729 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
729.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
729.4 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
729.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
729.8 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
730 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
730.2 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
730.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.014522 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
730.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.01149 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
730.8 | 128.8046 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.012923 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
731 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0097238 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
731.2 | 128.7087 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
731.4 | 128.2288 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.01149 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
731.6 | 128.4208 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.01149 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
731.8 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.012923 | 0.57213 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
732 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.012923 | 0.66813 | 0.0098898 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
732.2 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0097238 | 0.57213 | 0.0098898 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
732.4 | 129.2844 | 0.047342 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
732.6 | 129.1885 | 0.044143 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
732.8 | 128.7087 | 0.034546 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
733 | 128.7087 | 0.034546 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
733.2 | 128.6127 | 0.028148 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
733.4 | 128.6127 | 0.02175 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
733.6 | 128.8046 | 0.020151 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
733.8 | 128.9006 | 0.024949 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
734 | 128.9006 | 0.02175 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
734.2 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
734.4 | 128.8046 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
734.6 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
734.8 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
735 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
735.2 | 128.9966 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
735.4 | 128.8046 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
735.6 | 128.8046 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
735.8 | 128.8046 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
736 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
736.2 | 128.9006 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
736.4 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
736.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
736.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.0083128
737 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
737.2 | 128.8046 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
737.4 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
737.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
737.8 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
738 | 128.8046 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
738.2 | 128.9006 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
738.4 | 128.8046 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
738.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
738.8 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
739 | 128.8046 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
739.2 | 128.9006 | 0.0089549 | 0.29387 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
739.4 | 128.8046 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
739.6 | 128.8046 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
739.8 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
740 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
740.2 | 128.8046 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
740.4 | 128.9006 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
740.6 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
740.8 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
741 | 128.8046 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
741.2 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.011268 | 0.18829 | 0.006713
741.4 | 128.9006 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
741.6 | 128.9966 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
741.8 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
742 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
742.2 | 128.9006 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
742.4 | 128.9006 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
742.6 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
742.8 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
743 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
743.2 | 128.9006 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
743.4 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
743.6 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
743.8 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
744 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
744.2 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
744.4 | 128.9006 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
744.6 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
744.8 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
745 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
745.2 | 128.8046 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
745.4 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
745.6 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
745.8 | 128.9006 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
746 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
746.2 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
746.4 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
746.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
746.8 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
747 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
747.2 | 128.8046 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
747.4 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
747.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
747.8 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
748 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
748.2 | 128.8046 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
748.4 | 128.9006 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
748.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
748.8 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
749 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
749.2 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
749.4 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
749.6 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
749.8 | 128.9006 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
750 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
750.2 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
750.4 | 128.9966 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
750.6 | 128.9006 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
750.8 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
751 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
751.2 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
751.4 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
751.6 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
751.8 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
752 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
752.2 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
752.4 | 128.9006 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
752.6 | 128.8046 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
752.8 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
753 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
753.2 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
753.4 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
753.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
753.8 | 128.9006 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
754 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
754.2 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
754.4 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
754.6 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
754.8 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
755 | 128.9006 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
755.2 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
755.4 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
755.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
755.8 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
756 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
756.2 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
756.4 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
756.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
756.8 | 128.9006 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
757 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
757.2 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
757.4 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
757.6 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
757.8 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
758 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
758.2 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
758.4 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
758.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
758.8 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
759 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
759.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
759.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
759.6 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
759.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
760 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
760.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.0083128
760.4 | 128.3248 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
760.6 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
760.8 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
761 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
761.2 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
761.4 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
761.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
761.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
762 | 128.8046 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
762.2 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
762.4 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
762.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
762.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
763 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
763.2 | 128.8046 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
763.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
763.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
763.8 | 128.8046 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
764 | 128.8046 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
764.2 | 128.8046 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
764.4 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
764.6 | 128.9006 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
764.8 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
765 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
765.2 | 128.8046 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.006713
765.4 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
765.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.0923 | 0.006713
765.8 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
766 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
766.2 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.47618 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
766.4 | 128.9006 | 0.024949 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
766.6 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
766.8 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
767 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
767.2 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
767.4 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
767.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
767.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
768 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
768.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
768.4 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
768.6 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
768.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
769 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
769.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
769.4 | 128.6127 | 0.010554 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
769.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
769.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
770 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
770.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
770.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
770.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
770.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
771 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
771.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
771.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
771.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.006713
771.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
772 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
772.2 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
772.4 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
772.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
772.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
773 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
773.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
773.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
773.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
773.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
774 | 128.5167 | 0.0089549 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
774.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
774.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
774.6 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
774.8 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
775 | 128.5167 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
775.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
775.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
775.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
775.8 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
776 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
776.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
776.4 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
776.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
776.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
777 | 128.4208 | 0.010554 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
777.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.28424 | 0.006713
777.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
777.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
777.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
778 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
778.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
778.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
778.6 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
778.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
779 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
779.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
779.4 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
779.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
779.8 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
780 | 128.4208 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
780.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
780.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
780.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
780.8 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
781 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
781.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
781.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
781.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
781.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
782 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
782.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
782.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
782.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
782.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
783 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
783.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
783.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.006713
783.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
783.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
784 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
784.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
784.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
784.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
784.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
785 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
785.2 | 128.4208 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
785.4 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
785.6 | 128.4208 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
785.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
786 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
786.2 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
786.4 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
786.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
786.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
787 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
787.2 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
787.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
787.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
787.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
788 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
788.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
788.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
788.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
788.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
789 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
789.2 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
789.4 | 128.3248 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
789.6 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
789.8 | 128.4208 | 0.013753 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
790 | 128.3248 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
790.2 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
790.4 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
790.6 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
790.8 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
791 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
791.2 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
791.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
791.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
791.8 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.19722 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
792 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
792.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
792.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
792.6 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
792.8 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
793 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
793.2 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
793.4 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
793.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
793.8 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
794 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
794.2 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
794.4 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
794.6 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
794.8 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
795 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
795.2 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
795.4 | 128.4208 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
795.6 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
795.8 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
796 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
796.2 | 128.5167 | 0.012154 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
796.4 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
796.6 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
796.8 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
797 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
797.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
797.4 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
797.6 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
797.8 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
798 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
798.2 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
798.4 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
798.6 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
798.8 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
799 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
799.2 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
799.4 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
799.6 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
799.8 | 128.5167 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
800 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
800.2 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
800.4 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
800.6 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
800.8 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
801 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
801.2 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
801.4 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
801.6 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
801.8 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
802 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
802.2 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
802.4 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
802.6 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
802.8 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
803 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
803.2 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
803.4 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
803.6 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
803.8 | 128.4208 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
804 | 128.7087 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
804.2 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
804.4 | 128.5167 | 0.013753 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
804.6 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
804.8 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
805 | 128.4208 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
805.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
805.4 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
805.6 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
805.8 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
806 | 128.5167 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
806.2 | 128.5167 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
806.4 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
806.6 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
806.8 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
807 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
807.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
807.4 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
807.6 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
807.8 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
808 | 128.4208 | 0.012154 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
808.2 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
808.4 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
808.6 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
808.8 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
809 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
809.2 | 128.5167 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
809.4 | 128.4208 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
809.6 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
809.8 | 128.5167 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
810 | 128.4208 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
810.2 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
810.4 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
810.6 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
810.8 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.18829 | 0.006713
811 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
811.2 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
811.4 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
811.6 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
811.8 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
812 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
812.2 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
812.4 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
812.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
812.8 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
813 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
813.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
813.4 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
813.6 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
813.8 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
814 | 128.4208 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
814.2 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
814.4 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
814.6 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
814.8 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
815 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
815.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
815.4 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
815.6 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
815.8 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
816 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
816.2 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
816.4 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
816.6 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
816.8 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
817 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
817.2 | 128.5167 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
817.4 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
817.6 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
817.8 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
818 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
818.2 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
818.4 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
818.6 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
818.8 | 128.7087 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.00647 | 0.18829 | 0.006713
819 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
819.2 | 128.5167 | 0.012154 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
819.4 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
819.6 | 128.4208 | 0.013753 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
819.8 | 128.3248 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
820 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
820.2 | 128.6127 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
820.4 | 128.9006 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
820.6 | 128.8046 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
820.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
821 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0098898 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
821.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
821.4 | 128.5167 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
821.6 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
821.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
822 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
822.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
822.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0080139 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
822.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
822.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
823 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
823.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
823.4 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
823.6 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
823.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
824 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
824.2 | 128.4208 | 0.0073551 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
824.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
824.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
824.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
825 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
825.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
825.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
825.6 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
825.8 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
826 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
826.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
826.4 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
826.6 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
826.8 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
827 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
827.2 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
827.4 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
827.6 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
827.8 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.0923 | 0.006713
828 | 128.4208 | 0.0089549 | 0.38986 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
828.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
828.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
828.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
828.8 | 128.4208 | 0.010554 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
829 | 128.4208 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
829.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
829.4 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
829.6 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
829.8 | 128.4208 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
830 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
830.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
830.4 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
830.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
830.8 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
831 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
831.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
831.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
831.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
831.8 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
832 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
832.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
832.4 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
832.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
832.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
833 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
833.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
833.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
833.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
833.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
834 | 128.5167 | 0.0089549 | 0.29387 | 0.0079807 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
834.2 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
834.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
834.6 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
834.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
835 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
835.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.28424 | 0.006713
835.4 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
835.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
835.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
836 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.0083128
836.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
836.4 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
836.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
836.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
837 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
837.2 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
837.4 | 128.4208 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
837.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
837.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
838 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
838.2 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
838.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
838.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
838.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
839 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
839.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.5811 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
839.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
839.6 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
839.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
840 | 128.5167 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
840.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
840.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
840.6 | 128.5167 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
840.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
841 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
841.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
841.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
841.6 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
841.8 | 128.5167 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
842 | 128.5167 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
842.2 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
842.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
842.6 | 128.5167 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
842.8 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
843 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
843.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
843.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
843.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.0051138
843.8 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.18829 | 0.006713
844 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
844.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
844.4 | 128.2288 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
844.6 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
844.8 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
845 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
845.2 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
845.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
845.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
845.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
846 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
846.2 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
846.4 | 128.5167 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
846.6 | 128.2288 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
846.8 | 128.3248 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.006713
847 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
847.2 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
847.4 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
847.6 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
847.8 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
848 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
848.2 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
848.4 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
848.6 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
848.8 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.009912
849 | 128.5167 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
849.2 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
849.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
849.6 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
849.8 | 128.4208 | 0.010554 | 0.29387 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
850 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
850.2 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
850.4 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
850.6 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
850.8 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
851 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
851.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
851.4 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.38019 | 0.006713
851.6 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
851.8 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
852 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
852.2 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
852.4 | 128.5167 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
852.6 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
852.8 | 128.4208 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
853 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
853.2 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
853.4 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
853.6 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
853.8 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
854 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
854.2 | 128.5167 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
854.4 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
854.6 | 128.3248 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
854.8 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
855 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
855.2 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
855.4 | 128.6127 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
855.6 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
855.8 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
856 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.006713
856.2 | 128.5167 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
856.4 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
856.6 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
856.8 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
857 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
857.2 | 128.4208 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
857.4 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
857.6 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
857.8 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
858 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
858.2 | 128.5167 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
858.4 | 128.6127 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.009669 | 0.18829 | 0.006713
858.6 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
858.8 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
859 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
859.2 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
859.4 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
859.6 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
859.8 | 128.6127 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
860 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
860.2 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
860.4 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
860.6 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
860.8 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
861 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
861.2 | 128.6127 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
861.4 | 128.6127 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
861.6 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
861.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
862 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
862.2 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
862.4 | 128.6127 | 0.013753 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
862.6 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
862.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
863 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
863.2 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
863.4 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
863.6 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
863.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
864 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
864.2 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
864.4 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
864.6 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
864.8 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
865 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
865.2 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
865.4 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
865.6 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
865.8 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
866 | 128.7087 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
866.2 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
866.4 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
866.6 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
866.8 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
867 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
867.2 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.006713
867.4 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.006713
867.6 | 129.1885 | 0.044143 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.014522 | 0.66813 | 0.0098898 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
867.8 | 128.9006 | 0.029748 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.014522 | 0.57213 | 0.01149 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
868 | 129.2844 | 0.047342 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.012923 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
868.2 | 128.8046 | 0.039345 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
868.4 | 128.7087 | 0.031347 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
868.6 | 128.7087 | 0.032947 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
868.8 | 128.6127 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
869 | 128.9006 | 0.024949 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
869.2 | 128.9006 | 0.026549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
869.4 | 128.7087 | 0.02175 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
869.6 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
869.8 | 128.9006 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
870 | 128.9006 | 0.018551 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
870.2 | 128.8046 | 0.018551 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
870.4 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
870.6 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
870.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
871 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
871.2 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
871.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
871.6 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
871.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.006713
872 | 128.7087 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
872.2 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
872.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
872.6 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
872.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
873 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
873.2 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
873.4 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
873.6 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
873.8 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
874 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
874.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
874.4 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
874.6 | 128.7087 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
874.8 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
875 | 128.8046 | 0.013753 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
875.2 | 128.7087 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
875.4 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
875.6 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
875.8 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
876 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
876.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
876.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
876.6 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
876.8 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
877 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
877.2 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
877.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
877.6 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
877.8 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
878 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
878.2 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
878.4 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
878.6 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
878.8 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
879 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.18829 | 0.006713
879.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
879.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
879.6 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
879.8 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
880 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
880.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
880.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
880.6 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
880.8 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
881 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
881.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
881.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
881.6 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
881.8 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
882 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
882.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
882.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
882.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
882.8 | 128.7087 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
883 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
883.2 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
883.4 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
883.6 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
883.8 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
884 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
884.2 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
884.4 | 128.7087 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
884.6 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
884.8 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
885 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
885.2 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
885.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
885.6 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
885.8 | 128.8046 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
886 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
886.2 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
886.4 | 128.8046 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
886.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
886.8 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
887 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
887.2 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
887.4 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
887.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
887.8 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
888 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
888.2 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
888.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
888.6 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
888.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
889 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
889.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
889.4 | 128.7087 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
889.6 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
889.8 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
890 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
890.2 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
890.4 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
890.6 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
890.8 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
891 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
891.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
891.4 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
891.6 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
891.8 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
892 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
892.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
892.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
892.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
892.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
893 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
893.2 | 128.7087 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
893.4 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
893.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
893.8 | 128.7087 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
894 | 128.6127 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
894.2 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
894.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
894.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
894.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
895 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
895.2 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
895.4 | 128.7087 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
895.6 | 128.7087 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
895.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
896 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
896.2 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
896.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
896.6 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
896.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
897 | 128.8046 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
897.2 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
897.4 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
897.6 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
897.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
898 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
898.2 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
898.4 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
898.6 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
898.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
899 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
899.2 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0038022 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
899.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
899.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
899.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
900 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
900.2 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
900.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
900.6 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
900.8 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
901 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
901.2 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
901.4 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
901.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
901.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
902 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
902.2 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
902.4 | 128.7087 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
902.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
902.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
903 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
903.2 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
903.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
903.6 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
903.8 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
904 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
904.2 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
904.4 | 128.7087 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
904.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
904.8 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
905 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
905.2 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
905.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
905.6 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
905.8 | 128.8046 | 0.015352 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
906 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
906.2 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
906.4 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.0083128
906.6 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
906.8 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
907 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
907.2 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
907.4 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
907.6 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
907.8 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
908 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
908.2 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
908.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
908.6 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.006713
908.8 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
909 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
909.2 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
909.4 | 128.8046 | 0.013753 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
909.6 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
909.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
910 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
910.2 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
910.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
910.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
910.8 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
911 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
911.2 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
911.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.006713
911.6 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
911.8 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
912 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
912.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
912.4 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
912.6 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
912.8 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
913 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
913.2 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
913.4 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
913.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
913.8 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
914 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
914.2 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
914.4 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
914.6 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
914.8 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.006713
915 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
915.2 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
915.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
915.6 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
915.8 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
916 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
916.2 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
916.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
916.6 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
916.8 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
917 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
917.2 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
917.4 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
917.6 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
917.8 | 128.7087 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.009912
918 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
918.2 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
918.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
918.6 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
918.8 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
919 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
919.2 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
919.4 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
919.6 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
919.8 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
920 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
920.2 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
920.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
920.6 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
920.8 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
921 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
921.2 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
921.4 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
921.6 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.18829 | 0.006713
921.8 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.006713
922 | 128.9006 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
922.2 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
922.4 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
922.6 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
922.8 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
923 | 128.8046 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
923.2 | 128.7087 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
923.4 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
923.6 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
923.8 | 128.9006 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
924 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
924.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
924.4 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
924.6 | 128.9006 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
924.8 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
925 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
925.2 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
925.4 | 128.9006 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
925.6 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
925.8 | 128.9006 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
926 | 128.9006 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
926.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
926.4 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
926.6 | 128.9006 | 0.016952 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
926.8 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
927 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
927.2 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
927.4 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
927.6 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
927.8 | 128.8046 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
928 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
928.2 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
928.4 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
928.6 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
928.8 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
929 | 128.9006 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
929.2 | 128.9966 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
929.4 | 129.0925 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
929.6 | 129.6683 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
929.8 | 130.3401 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
930 | 129.6683 | 0.015352 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
930.2 | 129.4764 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
930.4 | 129.1885 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
930.6 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
930.8 | 128.9966 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
931 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
931.2 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
931.4 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
931.6 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
931.8 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
932 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
932.2 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
932.4 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
932.6 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
932.8 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
933 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
933.2 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
933.4 | 128.7087 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.006713
933.6 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
933.8 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
934 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
934.2 | 128.8046 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
934.4 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
934.6 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
934.8 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
935 | 128.8046 | 0.016952 | 0.29387 | 0.0079807 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
935.2 | 128.7087 | 0.020151 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
935.4 | 128.9006 | 0.031347 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.006713
935.6 | 128.8046 | 0.032947 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
935.8 | 128.3248 | 0.02175 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
936 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
936.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
936.4 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
936.6 | 128.7087 | 0.013753 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
936.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
937 | 128.7087 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
937.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
937.4 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
937.6 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
937.8 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
938 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
938.2 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
938.4 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
938.6 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
938.8 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
939 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
939.2 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
939.4 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
939.6 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
939.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
940 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
940.2 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
940.4 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
940.6 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
940.8 | 128.5167 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
941 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
941.2 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
941.4 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
941.6 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
941.8 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
942 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
942.2 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
942.4 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
942.6 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
942.8 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
943 | 128.6127 | 0.013753 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
943.2 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
943.4 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
943.6 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
943.8 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
944 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
944.2 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
944.4 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
944.6 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
944.8 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
945 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
945.2 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
945.4 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
945.6 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
945.8 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
946 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
946.2 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
946.4 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
946.6 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
946.8 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
947 | 128.5167 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
947.2 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
947.4 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
947.6 | 128.4208 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
947.8 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
948 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
948.2 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
948.4 | 128.6127 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
948.6 | 128.5167 | 0.015352 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
948.8 | 128.5167 | 0.013753 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
949 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
949.2 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
949.4 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
949.6 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
949.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
950 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
950.2 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
950.4 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
950.6 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
950.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
951 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
951.2 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
951.4 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
951.6 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
951.8 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
952 | 128.6127 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
952.2 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
952.4 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
952.6 | 128.5167 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
952.8 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
953 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
953.2 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
953.4 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
953.6 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
953.8 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
954 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
954.2 | 128.5167 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
954.4 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
954.6 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
954.8 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
955 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
955.2 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
955.4 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
955.6 | 128.4208 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
955.8 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.006713
956 | 128.5167 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.006713
956.2 | 128.2288 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
956.4 | 128.5167 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
956.6 | 128.6127 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
956.8 | 128.5167 | 0.018551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
957 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
957.2 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
957.4 | 128.6127 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
957.6 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
957.8 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
958 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
958.2 | 128.4208 | 0.012154 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
958.4 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.006713
958.6 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
958.8 | 128.3248 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
959 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
959.2 | 128.2288 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
959.4 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
959.6 | 128.2288 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
959.8 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
960 | 128.3248 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
960.2 | 128.2288 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
960.4 | 128.3248 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
960.6 | 128.2288 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
960.8 | 128.3248 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
961 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
961.2 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
961.4 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
961.6 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
961.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
962 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
962.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
962.4 | 128.5167 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
962.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
962.8 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
963 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
963.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
963.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
963.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
963.8 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
964 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
964.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
964.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
964.6 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
964.8 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
965 | 128.5167 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
965.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
965.4 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
965.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
965.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
966 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
966.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
966.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
966.6 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
966.8 | 128.5167 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
967 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
967.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
967.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
967.6 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
967.8 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
968 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
968.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
968.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
968.6 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
968.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
969 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
969.2 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
969.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
969.6 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
969.8 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.47618 | 0.006713
970 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
970.2 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
970.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
970.6 | 128.6127 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
970.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
971 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
971.2 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
971.4 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
971.6 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
971.8 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
972 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
972.2 | 128.6127 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
972.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
972.6 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
972.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
973 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
973.2 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
973.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0079807 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
973.6 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
973.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
974 | 128.6127 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
974.2 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
974.4 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
974.6 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
974.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
975 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
975.2 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
975.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
975.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
975.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
976 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
976.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
976.4 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
976.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
976.8 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
977 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
977.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
977.4 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
977.6 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
977.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
978 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
978.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
978.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
978.6 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
978.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
979 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
979.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
979.4 | 128.7087 | 0.010554 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.012923 | 0.66813 | 0.01149 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
979.6 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.00647 | 0.28424 | 0.0083128
979.8 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.012923 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
980 | 129.2844 | 0.040944 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
980.2 | 128.6127 | 0.026549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
980.4 | 128.9966 | 0.02335 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
980.6 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
980.8 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
981 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
981.2 | 128.9966 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
981.4 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
981.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
981.8 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
982 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
982.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
982.4 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
982.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
982.8 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
983 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
983.2 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
983.4 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
983.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
983.8 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
984 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.00647 | 0.28424 | 0.006713
984.2 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
984.4 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
984.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
984.8 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
985 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
985.2 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
985.4 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
985.6 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
985.8 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
986 | 128.8046 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
986.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
986.4 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
986.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
986.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
987 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
987.2 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
987.4 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
987.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
987.8 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
988 | 128.8046 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
988.2 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
988.4 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
988.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
988.8 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
989 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
989.2 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
989.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
989.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
989.8 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
990 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
990.2 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
990.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
990.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
990.8 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
991 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
991.2 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
991.4 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
991.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
991.8 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
992 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
992.2 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
992.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
992.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
992.8 | 129.0925 | 0.026549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
993 | 128.8046 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
993.2 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
993.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
993.6 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
993.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
994 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
994.2 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
994.4 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
994.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
994.8 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
995 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
995.2 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
995.4 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
995.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
995.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
996 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
996.2 | 128.7087 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
996.4 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
996.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
996.8 | 128.7087 | 0.010554 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
997 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
997.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
997.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
997.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
997.8 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
998 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
998.2 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
998.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
998.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
998.8 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
999 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
999.2 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
999.4 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
999.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
999.8 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1000 | 128.7087 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1000.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1000.4 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1000.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1000.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1001 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1001.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1001.4 | 128.6127 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.009912
1001.6 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
1001.8 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1002 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1002.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1002.4 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1002.6 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1002.8 | 128.6127 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1003 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1003.2 | 128.6127 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1003.4 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1003.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1003.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1004 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1004.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1004.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1004.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1004.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1005 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1005.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1005.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1005.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1005.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1006 | 128.5167 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1006.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1006.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1006.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1006.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1007 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1007.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1007.4 | 128.6127 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1007.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1007.8 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1008 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1008.2 | 128.6127 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0016718 | 0.28424 | 0.0083128
1008.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1008.6 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0097238 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1008.8 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1009 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1009.2 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1009.4 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1009.6 | 128.6127 | 0.012154 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1009.8 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1010 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1010.2 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1010.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1010.6 | 128.5167 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1010.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1011 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1011.2 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1011.4 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1011.6 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1011.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1012 | 128.7087 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.38019 | 0.0051138
1012.2 | 128.6127 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1012.4 | 128.6127 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1012.6 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1012.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1013 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1013.2 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1013.4 | 128.6127 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1013.6 | 128.7087 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1013.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1014 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1014.2 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1014.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1014.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1014.8 | 128.7087 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.006713
1015 | 128.8046 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1015.2 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1015.4 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1015.6 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1015.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1016 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1016.2 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1016.4 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1016.6 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1016.8 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1017 | 128.8046 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1017.2 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
1017.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1017.6 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.014688 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1017.8 | 128.9966 | 0.042543 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1018 | 128.8046 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.006713
1018.2 | 128.9966 | 0.02335 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1018.4 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1018.6 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1018.8 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1019 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1019.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1019.4 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1019.6 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1019.8 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1020 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1020.2 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1020.4 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1020.6 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1020.8 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1021 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1021.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1021.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1021.6 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1021.8 | 128.9006 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1022 | 128.9006 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1022.2 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1022.4 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1022.6 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1022.8 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1023 | 128.9006 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1023.2 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1023.4 | 128.9966 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1023.6 | 128.9966 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1023.8 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1024 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1024.2 | 128.9966 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1024.4 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1024.6 | 128.9966 | 0.016952 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1024.8 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1025 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1025.2 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1025.4 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1025.6 | 129.0925 | 0.018551 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1025.8 | 129.0925 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1026 | 129.2844 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1026.2 | 129.3804 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1026.4 | 129.7643 | 0.02175 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1026.6 | 129.9562 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1026.8 | 129.5724 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1027 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1027.2 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1027.4 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1027.6 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1027.8 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1028 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1028.2 | 128.9006 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1028.4 | 128.9966 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1028.6 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1028.8 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1029 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1029.2 | 128.9966 | 0.016952 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1029.4 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1029.6 | 128.9006 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1029.8 | 128.8046 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1030 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1030.2 | 128.9006 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1030.4 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1030.6 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0022023 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1030.8 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1031 | 128.8046 | 0.029748 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1031.2 | 128.6127 | 0.02335 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1031.4 | 128.8046 | 0.016952 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1031.6 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1031.8 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1032 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1032.2 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1032.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1032.6 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1032.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1033 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1033.2 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1033.4 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1033.6 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1033.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1034 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1034.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1034.4 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1034.6 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1034.8 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1035 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1035.2 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1035.4 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1035.6 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1035.8 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1036 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1036.2 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1036.4 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1036.6 | 128.7087 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1036.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1037 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1037.2 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1037.4 | 128.6127 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1037.6 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1037.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1038 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1038.2 | 128.5167 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1038.4 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1038.6 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1038.8 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1039 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1039.2 | 128.6127 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1039.4 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1039.6 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1039.8 | 128.4208 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1040 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.5811 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1040.2 | 128.7087 | 0.02175 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1040.4 | 128.6127 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1040.6 | 128.6127 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1040.8 | 128.6127 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1041 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
1041.2 | 128.5167 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1041.4 | 128.5167 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1041.6 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1041.8 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1042 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1042.2 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1042.4 | 128.5167 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
1042.6 | 128.6127 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1042.8 | 128.5167 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1043 | 128.5167 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1043.2 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1043.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1043.6 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1043.8 | 128.5167 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0102 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1044 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1044.2 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1044.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1044.6 | 128.6127 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1044.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1045 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1045.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1045.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1045.6 | 128.6127 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1045.8 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1046 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1046.2 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1046.4 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1046.6 | 128.7087 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1046.8 | 128.7087 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1047 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1047.2 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1047.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1047.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1047.8 | 128.8046 | 0.010554 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1048 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1048.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1048.4 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1048.6 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1048.8 | 129.4764 | 0.05054 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1049 | 128.9966 | 0.02335 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1049.2 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1049.4 | 128.8046 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1049.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1049.8 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1050 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1050.2 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1050.4 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1050.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1050.8 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1051 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1051.2 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1051.4 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1051.6 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1051.8 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
1052 | 129.0925 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1052.2 | 129.0925 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1052.4 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1052.6 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1052.8 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1053 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1053.2 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1053.4 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1053.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1053.8 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1054 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1054.2 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1054.4 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1054.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1054.8 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1055 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1055.2 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1055.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1055.6 | 129.1885 | 0.024949 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1055.8 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1056 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
1056.2 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1056.4 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1056.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1056.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1057 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1057.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1057.4 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1057.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1057.8 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1058 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1058.2 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1058.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1058.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1058.8 | 128.7087 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1059 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1059.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1059.4 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1059.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1059.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1060 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1060.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.011511
1060.4 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1060.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1060.8 | 128.7087 | 0.010554 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1061 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1061.2 | 128.7087 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1061.4 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1061.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0098898 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1061.8 | 128.9006 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1062 | 128.8046 | 0.013753 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1062.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1062.4 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1062.6 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1062.8 | 128.6127 | 0.010554 | 0.48581 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1063 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1063.2 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1063.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1063.6 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.5811 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1063.8 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1064 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1064.2 | 128.8046 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1064.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1064.6 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1064.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1065 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1065.2 | 128.8046 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1065.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1065.6 | 128.8046 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.18829 | 0.0083128
1065.8 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1066 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1066.2 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1066.4 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1066.6 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
1066.8 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
1067 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1067.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1067.4 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1067.6 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1067.8 | 128.9966 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1068 | 128.9966 | 0.015352 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1068.2 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1068.4 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1068.6 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1068.8 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1069 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1069.2 | 129.6683 | 0.044143 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.012923 | 0.66813 | 0.0098898 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1069.4 | 128.7087 | 0.02175 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1069.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1069.8 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1070 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1070.2 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1070.4 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1070.6 | 129.0925 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1070.8 | 129.0925 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1071 | 129.0925 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1071.2 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1071.4 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1071.6 | 129.1885 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1071.8 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1072 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1072.2 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1072.4 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1072.6 | 129.1885 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1072.8 | 129.0925 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.18829 | 0.006713
1073 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1073.2 | 129.1885 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1073.4 | 129.2844 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1073.6 | 129.3804 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.00647 | 0.38019 | 0.0083128
1073.8 | 129.4764 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1074 | 130.4361 | 0.018551 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1074.2 | 129.6683 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1074.4 | 129.2844 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1074.6 | 129.1885 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1074.8 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1075 | 129.0925 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1075.2 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1075.4 | 128.9966 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1075.6 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1075.8 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0034924 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1076 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1076.2 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1076.4 | 129.0925 | 0.018551 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.47618 | 0.006713
1076.6 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1076.8 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1077 | 128.9966 | 0.032947 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1077.2 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1077.4 | 129.0925 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1077.6 | 129.0925 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1077.8 | 128.9966 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1078 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1078.2 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1078.4 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.5811 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1078.6 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1078.8 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1079 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1079.2 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1079.4 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1079.6 | 128.9006 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1079.8 | 128.9006 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1080 | 128.9006 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1080.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1080.4 | 128.9006 | 0.015352 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1080.6 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1080.8 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1081 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1081.2 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1081.4 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1081.6 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1081.8 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1082 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1082.2 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1082.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1082.6 | 128.9006 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1082.8 | 128.9006 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1083 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1083.2 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1083.4 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1083.6 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1083.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1084 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1084.2 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1084.4 | 128.7087 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1084.6 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1084.8 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.47618 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1085 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1085.2 | 128.9966 | 0.020151 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1085.4 | 128.9006 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1085.6 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1085.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1086 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1086.2 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1086.4 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1086.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1086.8 | 128.9966 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1087 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1087.2 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1087.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1087.6 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1087.8 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1088 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1088.2 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1088.4 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1088.6 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1088.8 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1089 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
1089.2 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1089.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1089.6 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1089.8 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1090 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1090.2 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1090.4 | 128.9966 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1090.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1090.8 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1091 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1091.2 | 128.9006 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1091.4 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1091.6 | 129.0925 | 0.039345 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1091.8 | 128.9966 | 0.02175 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1092 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1092.2 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1092.4 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1092.6 | 129.0925 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1092.8 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1093 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1093.2 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1093.4 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1093.6 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1093.8 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1094 | 129.0925 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1094.2 | 129.0925 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1094.4 | 128.9966 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1094.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1094.8 | 128.3248 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1095 | 128.5167 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1095.2 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1095.4 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1095.6 | 128.9966 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1095.8 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
1096 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1096.2 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1096.4 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1096.6 | 128.7087 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1096.8 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1097 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1097.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1097.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1097.6 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1097.8 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1098 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1098.2 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1098.4 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1098.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1098.8 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1099 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1099.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1099.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1099.6 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1099.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1100 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1100.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1100.4 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1100.6 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1100.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1101 | 128.6127 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1101.2 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1101.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1101.6 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1101.8 | 128.7087 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1102 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1102.2 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1102.4 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1102.6 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1102.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1103 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1103.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1103.4 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1103.6 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1103.8 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1104 | 128.7087 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.18829 | 0.0083128
1104.2 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1104.4 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1104.6 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1104.8 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1105 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1105.2 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1105.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1105.6 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1105.8 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1106 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1106.2 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1106.4 | 128.8046 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1106.6 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
1106.8 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1107 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1107.2 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1107.4 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1107.6 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1107.8 | 128.9966 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1108 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1108.2 | 129.2844 | 0.045742 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1108.4 | 129.1885 | 0.028148 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1108.6 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1108.8 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1109 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1109.2 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1109.4 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1109.6 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1109.8 | 129.0925 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1110 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1110.2 | 129.0925 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.47618 | 0.0083128
1110.4 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1110.6 | 128.9966 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1110.8 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1111 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1111.2 | 129.0925 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.47618 | 0.006713
1111.4 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1111.6 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1111.8 | 129.1885 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1112 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1112.2 | 129.2844 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1112.4 | 129.3804 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1112.6 | 130.4361 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1112.8 | 129.2844 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1113 | 128.9966 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1113.2 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1113.4 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1113.6 | 128.9966 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1113.8 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1114 | 128.9966 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1114.2 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1114.4 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1114.6 | 128.9966 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1114.8 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1115 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1115.2 | 128.9966 | 0.031347 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1115.4 | 129.0925 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1115.6 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1115.8 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1116 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1116.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1116.4 | 128.9006 | 0.013753 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.47618 | 0.0083128
1116.6 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1116.8 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1117 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1117.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1117.4 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1117.6 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.18829 | 0.0083128
1117.8 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1118 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1118.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1118.4 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1118.6 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1118.8 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1119 | 128.8046 | 0.015352 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1119.2 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1119.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1119.6 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1119.8 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1120 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1120.2 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1120.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1120.6 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1120.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1121 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1121.2 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1121.4 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1121.6 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1121.8 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1122 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1122.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1122.4 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1122.6 | 127.3651 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1122.8 | 127.3651 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1123 | 128.3248 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1123.2 | 128.6127 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1123.4 | 128.6127 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1123.6 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1123.8 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1124 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1124.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1124.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1124.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1124.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1125 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1125.2 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1125.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1125.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1125.8 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1126 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1126.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1126.4 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1126.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1126.8 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1127 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1127.2 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1127.4 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1127.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1127.8 | 128.7087 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1128 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1128.2 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1128.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1128.6 | 129.5724 | 0.047342 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1128.8 | 128.9006 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1129 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1129.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1129.4 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1129.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1129.8 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1130 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1130.2 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1130.4 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1130.6 | 128.9006 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1130.8 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1131 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1131.2 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1131.4 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1131.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1131.8 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1132 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1132.2 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1132.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1132.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1132.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1133 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1133.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1133.4 | 128.9006 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1133.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1133.8 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1134 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1134.2 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1134.4 | 128.8046 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1134.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.006713
1134.8 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1135 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1135.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1135.4 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1135.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1135.8 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1136 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0038022 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1136.2 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1136.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1136.6 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1136.8 | 128.7087 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1137 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1137.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1137.4 | 128.7087 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1137.6 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1137.8 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1138 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1138.2 | 128.7087 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1138.4 | 128.7087 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1138.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1138.8 | 128.7087 | 0.0089549 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1139 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1139.2 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1139.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1139.6 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1139.8 | 128.6127 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1140 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1140.2 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1140.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1140.6 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1140.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1141 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1141.2 | 128.5167 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1141.4 | 128.6127 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1141.6 | 128.6127 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1141.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1142 | 128.5167 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1142.2 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1142.4 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1142.6 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1142.8 | 128.7087 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1143 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1143.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1143.4 | 128.7087 | 0.010554 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1143.6 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1143.8 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.011268 | 0.28424 | 0.0083128
1144 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1144.2 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1144.4 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1144.6 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1144.8 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1145 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1145.2 | 128.7087 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1145.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1145.6 | 128.8046 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1145.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1146 | 128.8046 | 0.012154 | 0.58176 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1146.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1146.4 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1146.6 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1146.8 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1147 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1147.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1147.4 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1147.6 | 128.9966 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1147.8 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1148 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1148.2 | 128.9966 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1148.4 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1148.6 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1148.8 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1149 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1149.2 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1149.4 | 129.0925 | 0.015352 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1149.6 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1149.8 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.014998 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1150 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.014688 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1150.2 | 129.0925 | 0.037745 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1150.4 | 129.1885 | 0.028148 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1150.6 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1150.8 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1151 | 129.0925 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1151.2 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1151.4 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1151.6 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1151.8 | 129.0925 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1152 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1152.2 | 129.0925 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1152.4 | 129.0925 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1152.6 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1152.8 | 129.0925 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1153 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1153.2 | 129.0925 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1153.4 | 129.0925 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1153.6 | 129.0925 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1153.8 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1154 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1154.2 | 129.1885 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1154.4 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1154.6 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1154.8 | 129.2844 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1155 | 129.3804 | 0.018551 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1155.2 | 129.3804 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1155.4 | 130.3401 | 0.018551 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1155.6 | 129.7643 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1155.8 | 129.2844 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1156 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1156.2 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.00647 | 0.28424 | 0.0083128
1156.4 | 129.1885 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1156.6 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1156.8 | 129.1885 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
1157 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1157.2 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1157.4 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1157.6 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1157.8 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1158 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0002934 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1158.2 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1158.4 | 129.3804 | 0.042543 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1158.6 | 128.9006 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1158.8 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1159 | 128.9966 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1159.2 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1159.4 | 128.9966 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1159.6 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1159.8 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1160 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1160.2 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1160.4 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1160.6 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1160.8 | 128.9006 | 0.013753 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1161 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1161.2 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1161.4 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1161.6 | 128.8046 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
1161.8 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1162 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1162.2 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1162.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1162.6 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1162.8 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1163 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1163.2 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1163.4 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1163.6 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1163.8 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1164 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1164.2 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1164.4 | 128.8046 | 0.015352 | 0.48581 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1164.6 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1164.8 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1165 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1165.2 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1165.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0051138
1165.6 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1165.8 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1166 | 128.7087 | 0.012154 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1166.2 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1166.4 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1166.6 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1166.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1167 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1167.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0098898 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1167.4 | 128.3248 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1167.6 | 128.9006 | 0.024949 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1167.8 | 128.8046 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.47618 | 0.006713
1168 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1168.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1168.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1168.6 | 128.9006 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1168.8 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1169 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1169.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1169.4 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1169.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1169.8 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1170 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1170.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1170.4 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1170.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1170.8 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1171 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1171.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1171.4 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1171.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1171.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1172 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1172.2 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1172.4 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1172.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.7737 | 0.009669 | 0.28424 | 0.0083128
1172.8 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1173 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1173.2 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1173.4 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1173.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1173.8 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1174 | 129.0925 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1174.2 | 129.0925 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.013089 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1174.4 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.012923 | 0.66813 | 0.01149 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1174.6 | 129.0925 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1174.8 | 129.1885 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1175 | 129.1885 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1175.2 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1175.4 | 129.0925 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1175.6 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1175.8 | 129.1885 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1176 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1176.2 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1176.4 | 129.1885 | 0.0089549 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1176.6 | 129.1885 | 0.010554 | 0.48581 | 0.0031824 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0051138
1176.8 | 129.0925 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1177 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
1177.2 | 128.9966 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1177.4 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1177.6 | 128.3248 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1177.8 | 129.0925 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1178 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
1178.2 | 129.0925 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1178.4 | 129.0925 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1178.6 | 129.0925 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1178.8 | 129.0925 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.0923 | 0.0083128
1179 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | -0.0029056 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1179.2 | 128.9966 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1179.4 | 129.0925 | 0.02175 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1179.6 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1179.8 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1180 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1180.2 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1180.4 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1180.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1180.8 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1181 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1181.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1181.4 | 128.9006 | 0.0089549 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1181.6 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1181.8 | 128.9006 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1182 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1182.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1182.4 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1182.6 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1182.8 | 128.8046 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1183 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1183.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1183.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1183.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1183.8 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1184 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1184.2 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.66713 | 0.0054014 | 0.526 | 0.011324 | 0.66813 | 0.0098898 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1184.4 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1184.6 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1184.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1185 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0038022 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1185.2 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1185.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1185.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1185.8 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1186 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1186.2 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1186.4 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1186.6 | 128.9006 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1186.8 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1187 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1187.2 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1187.4 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1187.6 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1187.8 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1188 | 128.9966 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1188.2 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1188.4 | 129.0925 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1188.6 | 128.9966 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1188.8 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1189 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1189.2 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1189.4 | 129.0925 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1189.6 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.016288 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1189.8 | 128.9006 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1190 | 128.9966 | 0.02175 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1190.2 | 129.0925 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1190.4 | 129.0925 | 0.015352 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1190.6 | 129.1885 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1190.8 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1191 | 129.1885 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1191.2 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1191.4 | 129.1885 | 0.016952 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1191.6 | 129.1885 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1191.8 | 129.1885 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1192 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1192.2 | 129.2844 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1192.4 | 129.2844 | 0.016952 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1192.6 | 129.1885 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1192.8 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1193 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1193.2 | 129.2844 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1193.4 | 129.2844 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1193.6 | 129.3804 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1193.8 | 129.4764 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.18829 | 0.0083128
1194 | 130.4361 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1194.2 | 129.7643 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1194.4 | 129.2844 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1194.6 | 129.2844 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1194.8 | 129.1885 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1195 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1195.2 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1195.4 | 129.2844 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1195.6 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1195.8 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1196 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1196.2 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1196.4 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1196.6 | 128.9966 | 0.028148 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1196.8 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1197 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1197.2 | 129.0925 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1197.4 | 129.0925 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1197.6 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1197.8 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1198 | 128.9966 | 0.015352 | 0.48581 | 0.0047816 | 0.5811 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1198.2 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1198.4 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1198.6 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.00647 | 0.47618 | 0.0083128
1198.8 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1199 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1199.2 | 128.9006 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1199.4 | 128.9966 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1199.6 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
1199.8 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1200 | 128.9966 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1200.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1200.4 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1200.6 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1200.8 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1201 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1201.2 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1201.4 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1201.6 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1201.8 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1202 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1202.2 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1202.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1202.6 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1202.8 | 128.8046 | 0.013753 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1203 | 128.9966 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1203.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1203.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1203.6 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1203.8 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1204 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1204.2 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1204.4 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1204.6 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.011268 | 0.28424 | 0.0083128
1204.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1205 | 128.9006 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1205.2 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1205.4 | 128.8046 | 0.013753 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1205.6 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1205.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1206 | 128.8046 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1206.2 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1206.4 | 128.8046 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1206.6 | 128.9006 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1206.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1207 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1207.2 | 128.7087 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.011511
1207.4 | 128.8046 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1207.6 | 128.8046 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1207.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1208 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1208.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1208.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1208.6 | 128.9006 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1208.8 | 128.8046 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1209 | 128.8046 | 0.015352 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1209.2 | 128.8046 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1209.4 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1209.6 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1209.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1210 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1210.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1210.4 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1210.6 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1210.8 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1211 | 128.7087 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1211.2 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1211.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1211.6 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.8139 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1211.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1212 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1212.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1212.4 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1212.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1212.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1213 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1213.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1213.4 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1213.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1213.8 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1214 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1214.2 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1214.4 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1214.6 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1214.8 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1215 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1215.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1215.4 | 128.9006 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1215.6 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1215.8 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1216 | 128.8046 | 0.0073551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1216.2 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1216.4 | 128.8046 | 0.010554 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1216.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1216.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1217 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1217.2 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1217.4 | 128.9966 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1217.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1217.8 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1218 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1218.2 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1218.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1218.6 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1218.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1219 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1219.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1219.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1219.6 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1219.8 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1220 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1220.2 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1220.4 | 129.0925 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.016288 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1220.6 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1220.8 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1221 | 128.9966 | 0.029748 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1221.2 | 129.0925 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1221.4 | 129.0925 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1221.6 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1221.8 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1222 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1222.2 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1222.4 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1222.6 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1222.8 | 129.0925 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1223 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1223.2 | 129.0925 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1223.4 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1223.6 | 129.0925 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1223.8 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1224 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1224.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1224.4 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1224.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1224.8 | 129.0925 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1225 | 129.0925 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1225.2 | 128.9966 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.006713
1225.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1225.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1225.8 | 128.7087 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1226 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1226.2 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1226.4 | 128.5167 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1226.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1226.8 | 128.9966 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1227 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1227.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1227.4 | 129.1885 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1227.6 | 129.0925 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1227.8 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1228 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1228.2 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1228.4 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1228.6 | 129.0925 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1228.8 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1229 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1229.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1229.4 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1229.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1229.8 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1230 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1230.2 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1230.4 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1230.6 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1230.8 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1231 | 128.9006 | 0.02335 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1231.2 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.00647 | 0.38019 | 0.006713
1231.4 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1231.6 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1231.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1232 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1232.2 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1232.4 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1232.6 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1232.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1233 | 128.9006 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1233.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1233.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.01149 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1233.6 | 128.3248 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1233.8 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1234 | 128.4208 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1234.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1234.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1234.6 | 128.5167 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1234.8 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1235 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1235.2 | 128.6127 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1235.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1235.6 | 128.6127 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1235.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1236 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1236.2 | 128.7087 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1236.4 | 128.7087 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1236.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1236.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1237 | 128.7087 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1237.2 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1237.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1237.6 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1237.8 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1238 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1238.2 | 128.7087 | 0.016952 | 0.38986 | 0.0079807 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1238.4 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1238.6 | 128.5167 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1238.8 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1239 | 128.4208 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1239.2 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1239.4 | 128.3248 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1239.6 | 128.3248 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1239.8 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1240 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1240.2 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1240.4 | 128.4208 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1240.6 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1240.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1241 | 128.4208 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1241.2 | 128.4208 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1241.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1241.6 | 128.3248 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1241.8 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1242 | 128.4208 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1242.2 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1242.4 | 128.4208 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1242.6 | 128.5167 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1242.8 | 128.6127 | 0.0089549 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1243 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1243.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1243.4 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1243.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1243.8 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1244 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1244.2 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1244.4 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1244.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1244.8 | 128.6127 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1245 | 128.7087 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1245.2 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1245.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1245.6 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1245.8 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1246 | 128.8046 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1246.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1246.4 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1246.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1246.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1247 | 128.7087 | 0.013753 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1247.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1247.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1247.6 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1247.8 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1248 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1248.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1248.4 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1248.6 | 128.7087 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1248.8 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1249 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1249.2 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1249.4 | 128.7087 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1249.6 | 128.8046 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1249.8 | 128.6127 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1250 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1250.2 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1250.4 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1250.6 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1250.8 | 128.7087 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1251 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1251.2 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1251.4 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1251.6 | 128.8046 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1251.8 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1252 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1252.2 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1252.4 | 128.7087 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1252.6 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1252.8 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1253 | 128.8046 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1253.2 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1253.4 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0038022 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1253.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1253.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1254 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.009912
1254.2 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1254.4 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1254.6 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1254.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.009912
1255 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1255.2 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1255.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1255.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1255.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1256 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1256.2 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1256.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1256.6 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1256.8 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1257 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1257.2 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1257.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1257.6 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1257.8 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1258 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1258.2 | 128.8046 | 0.013753 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1258.4 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1258.6 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1258.8 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1259 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1259.2 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1259.4 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1259.6 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1259.8 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1260 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1260.2 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1260.4 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
1260.6 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1260.8 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1261 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1261.2 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1261.4 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1261.6 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1261.8 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1262 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1262.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1262.4 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1262.6 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1262.8 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1263 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1263.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1263.4 | 128.9006 | 0.015352 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1263.6 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1263.8 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1264 | 128.9006 | 0.015352 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1264.2 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.009912
1264.4 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1264.6 | 128.9966 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1264.8 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1265 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1265.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1265.4 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1265.6 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1265.8 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1266 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1266.2 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1266.4 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1266.6 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1266.8 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1267 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1267.2 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1267.4 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1267.6 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1267.8 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1268 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1268.2 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1268.4 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1268.6 | 129.0925 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1268.8 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1269 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1269.2 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1269.4 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1269.6 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.01149 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1269.8 | 129.2844 | 0.040944 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1270 | 128.8046 | 0.020151 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1270.2 | 129.1885 | 0.026549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1270.4 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1270.6 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1270.8 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1271 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1271.2 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1271.4 | 129.0925 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1271.6 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1271.8 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1272 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1272.2 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1272.4 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1272.6 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1272.8 | 129.0925 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1273 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1273.2 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1273.4 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1273.6 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1273.8 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1274 | 129.2844 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1274.2 | 129.2844 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1274.4 | 129.3804 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1274.6 | 129.4764 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1274.8 | 129.7643 | 0.020151 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1275 | 130.3401 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1275.2 | 129.8603 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1275.4 | 129.3804 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1275.6 | 129.1885 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1275.8 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1276 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1276.2 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1276.4 | 129.0925 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1276.6 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1276.8 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1277 | 129.0925 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1277.2 | 129.1885 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1277.4 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1277.6 | 129.0925 | 0.016952 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1277.8 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1278 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1278.2 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1278.4 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1278.6 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1278.8 | 128.9966 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1279 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1279.2 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1279.4 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1279.6 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1279.8 | 129.1885 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1280 | 128.9966 | 0.034546 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1280.2 | 128.6127 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1280.4 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1280.6 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1280.8 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1281 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1281.2 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1281.4 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1281.6 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1281.8 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1282 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1282.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1282.4 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1282.6 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1282.8 | 128.8046 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1283 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1283.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1283.4 | 128.8046 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1283.6 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1283.8 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1284 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1284.2 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1284.4 | 128.8046 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1284.6 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1284.8 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1285 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1285.2 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1285.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1285.6 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1285.8 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1286 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1286.2 | 128.9966 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1286.4 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1286.6 | 128.9006 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1286.8 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1287 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1287.2 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1287.4 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1287.6 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1287.8 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1288 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1288.2 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1288.4 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1288.6 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1288.8 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1289 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1289.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1289.4 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1289.6 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1289.8 | 128.9006 | 0.015352 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1290 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1290.2 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1290.4 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1290.6 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1290.8 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1291 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1291.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1291.4 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1291.6 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1291.8 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1292 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1292.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1292.4 | 128.9006 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1292.6 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1292.8 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1293 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1293.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1293.4 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1293.6 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1293.8 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1294 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1294.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1294.4 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1294.6 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1294.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1295 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1295.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1295.4 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1295.6 | 128.9006 | 0.013753 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1295.8 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1296 | 128.9006 | 0.015352 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1296.2 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1296.4 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1296.6 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1296.8 | 128.9006 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1297 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1297.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1297.4 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1297.6 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1297.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1298 | 128.9006 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1298.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0102 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1298.4 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1298.6 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1298.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1299 | 128.8046 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.47618 | 0.006713
1299.2 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1299.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1299.6 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1299.8 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1300 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1300.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1300.4 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1300.6 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.29321 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1300.8 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
1301 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1301.2 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1301.4 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1301.6 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1301.8 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1302 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1302.2 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1302.4 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1302.6 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1302.8 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1303 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1303.2 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1303.4 | 128.8046 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1303.6 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1303.8 | 128.9006 | 0.013753 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1304 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1304.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1304.4 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1304.6 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1304.8 | 128.9006 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1305 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1305.2 | 128.7087 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1305.4 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1305.6 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1305.8 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1306 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1306.2 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1306.4 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.012867 | 0.28424 | 0.006713
1306.6 | 128.9006 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1306.8 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1307 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1307.2 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1307.4 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1307.6 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1307.8 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0098898 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1308 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1308.2 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1308.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1308.6 | 128.9966 | 0.02175 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1308.8 | 128.9966 | 0.026549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1309 | 128.8046 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1309.2 | 129.0925 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1309.4 | 128.8046 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1309.6 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1309.8 | 128.9006 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1310 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1310.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1310.4 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1310.6 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1310.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1311 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1311.2 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1311.4 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1311.6 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1311.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1312 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1312.2 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1312.4 | 128.9006 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1312.6 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1312.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1313 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1313.2 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1313.4 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1313.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1313.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1314 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1314.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1314.4 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1314.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1314.8 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1315 | 128.9006 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1315.2 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1315.4 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1315.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1315.8 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1316 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1316.2 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1316.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1316.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.011268 | 0.28424 | 0.0083128
1316.8 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1317 | 128.8046 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1317.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1317.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1317.6 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1317.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1318 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1318.2 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1318.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1318.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1318.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1319 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1319.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1319.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1319.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1319.8 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1320 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1320.2 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1320.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1320.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1320.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1321 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1321.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1321.4 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1321.6 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1321.8 | 128.9006 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1322 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1322.2 | 128.9006 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1322.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1322.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1322.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1323 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1323.2 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1323.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1323.6 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1323.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1324 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1324.2 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1324.4 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1324.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1324.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1325 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1325.2 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1325.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1325.6 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1325.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1326 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1326.2 | 128.9966 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1326.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1326.6 | 128.9006 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1326.8 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1327 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1327.2 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1327.4 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1327.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1327.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1328 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1328.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1328.4 | 129.0925 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1328.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1328.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1329 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1329.2 | 128.9966 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1329.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1329.6 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1329.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1330 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1330.2 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1330.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1330.6 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1330.8 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1331 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1331.2 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1331.4 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1331.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1331.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1332 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1332.2 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1332.4 | 129.0925 | 0.010554 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1332.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1332.8 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.7737 | 0.009669 | 0.28424 | 0.009912
1333 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1333.2 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1333.4 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1333.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1333.8 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1334 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.016288 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1334.2 | 129.0925 | 0.010554 | 0.38986 | 0.01118 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.016122 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1334.4 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1334.6 | 128.3248 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.01149 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1334.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.71795 | 0.012923 | 0.66813 | 0.013089 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1335 | 129.4764 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.012923 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1335.2 | 129.6683 | 0.05054 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1335.4 | 128.9006 | 0.031347 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1335.6 | 128.9006 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1335.8 | 129.1885 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1336 | 129.1885 | 0.02335 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1336.2 | 129.1885 | 0.02335 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1336.4 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1336.6 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1336.8 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1337 | 129.0925 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1337.2 | 129.1885 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1337.4 | 129.1885 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1337.6 | 129.0925 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
1337.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1338 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1338.2 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1338.4 | 129.1885 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1338.6 | 129.1885 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1338.8 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1339 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1339.2 | 129.1885 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1339.4 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1339.6 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.009912
1339.8 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1340 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1340.2 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1340.4 | 129.0925 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1340.6 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1340.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1341 | 129.0925 | 0.0089549 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1341.2 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1341.4 | 129.1885 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1341.6 | 129.1885 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1341.8 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1342 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1342.2 | 129.1885 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1342.4 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1342.6 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1342.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1343 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1343.2 | 128.9966 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1343.4 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1343.6 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1343.8 | 129.0925 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1344 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1344.2 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1344.4 | 129.0925 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1344.6 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1344.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1345 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1345.2 | 129.1885 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1345.4 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1345.6 | 129.1885 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1345.8 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1346 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1346.2 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1346.4 | 129.1885 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1346.6 | 129.1885 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1346.8 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1347 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1347.2 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1347.4 | 129.1885 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1347.6 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1347.8 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1348 | 129.0925 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1348.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1348.4 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
1348.6 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1348.8 | 129.0925 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1349 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1349.2 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1349.4 | 129.0925 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1349.6 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1349.8 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1350 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1350.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1350.4 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1350.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1350.8 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1351 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0051138
1351.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1351.4 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.011268 | 0.28424 | 0.0083128
1351.6 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1351.8 | 128.8046 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1352 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1352.2 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1352.4 | 128.7087 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1352.6 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1352.8 | 128.7087 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1353 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1353.2 | 128.1329 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1353.4 | 128.0369 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1353.6 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1353.8 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1354 | 128.2288 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1354.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1354.4 | 128.8046 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1354.6 | 128.8046 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1354.8 | 129.0925 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1355 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1355.2 | 129.1885 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1355.4 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1355.6 | 129.0925 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1355.8 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1356 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1356.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1356.4 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1356.6 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1356.8 | 129.1885 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1357 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1357.2 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1357.4 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1357.6 | 129.0925 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1357.8 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1358 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1358.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1358.4 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1358.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1358.8 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1359 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1359.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0019147
1359.4 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1359.6 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1359.8 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.18829 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1360 | 129.0925 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1360.2 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1360.4 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1360.6 | 129.0925 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1360.8 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1361 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1361.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1361.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1361.6 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1361.8 | 129.2844 | 0.02335 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1362 | 129.2844 | 0.028148 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1362.2 | 129.3804 | 0.024949 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1362.4 | 128.9966 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1362.6 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1362.8 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1363 | 128.9006 | 0.015352 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1363.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1363.4 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1363.6 | 128.9966 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1363.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1364 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1364.2 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1364.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1364.6 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1364.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1365 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1365.2 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1365.4 | 128.9966 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1365.6 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1365.8 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1366 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1366.2 | 129.0925 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1366.4 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1366.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1366.8 | 128.9966 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1367 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1367.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1367.4 | 128.9006 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1367.6 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1367.8 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1368 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1368.2 | 128.9006 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1368.4 | 128.9966 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1368.6 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1368.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1369 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1369.2 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1369.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1369.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1369.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1370 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1370.2 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1370.4 | 128.9966 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1370.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1370.8 | 128.9966 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1371 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1371.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1371.4 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1371.6 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1371.8 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1372 | 128.9966 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1372.2 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1372.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0097238 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1372.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1372.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1373 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1373.2 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1373.4 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1373.6 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1373.8 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1374 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1374.2 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1374.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1374.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1374.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1375 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1375.2 | 128.9006 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1375.4 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1375.6 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1375.8 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1376 | 128.9966 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1376.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1376.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1376.6 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1376.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1377 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1377.2 | 128.9966 | 0.0089549 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1377.4 | 128.9006 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1377.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1377.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1378 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1378.2 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1378.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1378.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1378.8 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.47618 | 0.0083128
1379 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1379.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1379.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1379.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1379.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1380 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1380.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1380.4 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1380.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1380.8 | 128.9006 | 0.010554 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1381 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1381.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1381.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1381.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1381.8 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1382 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1382.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1382.4 | 128.7087 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1382.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1382.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1383 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1383.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1383.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1383.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1383.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1384 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1384.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1384.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1384.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1384.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1385 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.013111
1385.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1385.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1385.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1385.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1386 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.29321 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1386.2 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1386.4 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1386.6 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1386.8 | 128.7087 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1387 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1387.2 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1387.4 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1387.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1387.8 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1388 | 128.8046 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1388.2 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1388.4 | 128.8046 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1388.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1388.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1389 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1389.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1389.4 | 128.9006 | 0.012154 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1389.6 | 128.9006 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1389.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1390 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1390.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1390.4 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1390.6 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1390.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1391 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.009912
1391.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1391.4 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1391.6 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1391.8 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1392 | 128.9006 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1392.2 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1392.4 | 128.8046 | 0.013753 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1392.6 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1392.8 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1393 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1393.2 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1393.4 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1393.6 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1393.8 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1394 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1394.2 | 128.9966 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1394.4 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1394.6 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1394.8 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1395 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1395.2 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.43001 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1395.4 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1395.6 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1395.8 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1396 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1396.2 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1396.4 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1396.6 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1396.8 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1397 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1397.2 | 128.9966 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1397.4 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1397.6 | 128.9006 | 0.013753 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1397.8 | 129.0925 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1398 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1398.2 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1398.4 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1398.6 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1398.8 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1399 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1399.2 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1399.4 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1399.6 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.38019 | 0.0083128
1399.8 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1400 | 129.0925 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1400.2 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1400.4 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1400.6 | 129.0925 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1400.8 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1401 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1401.2 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1401.4 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1401.6 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1401.8 | 129.1885 | 0.026549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.014522 | 0.76408 | 0.013089 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1402 | 129.0925 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1402.2 | 128.9006 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1402.4 | 129.0925 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1402.6 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1402.8 | 129.0925 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1403 | 129.1885 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1403.2 | 129.1885 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1403.4 | 129.1885 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1403.6 | 129.1885 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1403.8 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1404 | 129.1885 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1404.2 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1404.4 | 129.1885 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1404.6 | 129.1885 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1404.8 | 129.1885 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1405 | 129.1885 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1405.2 | 129.1885 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1405.4 | 129.2844 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1405.6 | 129.2844 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1405.8 | 129.1885 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1406 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1406.2 | 129.1885 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1406.4 | 129.1885 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1406.6 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1406.8 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1407 | 129.2844 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1407.2 | 129.2844 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1407.4 | 129.2844 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1407.6 | 129.2844 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1407.8 | 129.2844 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1408 | 129.2844 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1408.2 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1408.4 | 129.2844 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1408.6 | 129.2844 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1408.8 | 129.1885 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1409 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1409.2 | 129.1885 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1409.4 | 129.2844 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1409.6 | 129.2844 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1409.8 | 129.2844 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1410 | 129.3804 | 0.016952 | 0.38986 | 0.0063808 | 0.5811 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1410.2 | 129.4764 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1410.4 | 129.5724 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1410.6 | 129.4764 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1410.8 | 129.6683 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1411 | 130.2441 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1411.2 | 130.628 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1411.4 | 129.8603 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1411.6 | 129.4764 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1411.8 | 129.2844 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1412 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1412.2 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1412.4 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1412.6 | 129.1885 | 0.018551 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1412.8 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1413 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1413.2 | 129.1885 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.28424 | 0.009912
1413.4 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1413.6 | 129.1885 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1413.8 | 129.2844 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1414 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1414.2 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1414.4 | 129.1885 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1414.6 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1414.8 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1415 | 129.1885 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1415.2 | 129.2844 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1415.4 | 129.1885 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1415.6 | 129.1885 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1415.8 | 129.2844 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1416 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1416.2 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
1416.4 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1416.6 | 129.1885 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1416.8 | 129.1885 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1417 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1417.2 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1417.4 | 129.1885 | 0.018551 | 0.29387 | 0.0063808 | 0.48515 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1417.6 | 129.1885 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1417.8 | 129.2844 | 0.039345 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1418 | 129.1885 | 0.031347 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1418.2 | 128.9966 | 0.028148 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.38019 | 0.0083128
1418.4 | 128.8046 | 0.02335 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1418.6 | 129.0925 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1418.8 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1419 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1419.2 | 129.0925 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1419.4 | 129.0925 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1419.6 | 129.0925 | 0.013753 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1419.8 | 129.0925 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1420 | 129.0925 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1420.2 | 129.0925 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1420.4 | 129.0925 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1420.6 | 129.0925 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1420.8 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1421 | 129.0925 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1421.2 | 129.1885 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1421.4 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1421.6 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1421.8 | 129.1885 | 0.015352 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1422 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1422.2 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1422.4 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1422.6 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1422.8 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1423 | 129.0925 | 0.016952 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1423.2 | 129.0925 | 0.015352 | 0.48581 | 0.0095798 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1423.4 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1423.6 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1423.8 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1424 | 128.9966 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1424.2 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1424.4 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1424.6 | 129.0925 | 0.015352 | 0.29387 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1424.8 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1425 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1425.2 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1425.4 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1425.6 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1425.8 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1426 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1426.2 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1426.4 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1426.6 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1426.8 | 128.9966 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
1427 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1427.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1427.4 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1427.6 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1427.8 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1428 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1428.2 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1428.4 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1428.6 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1428.8 | 129.0925 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1429 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1429.2 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1429.4 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1429.6 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1429.8 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1430 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1430.2 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1430.4 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1430.6 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1430.8 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1431 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1431.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1431.4 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1431.6 | 128.9966 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1431.8 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1432 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1432.2 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.18829 | 0.0083128
1432.4 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1432.6 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1432.8 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1433 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1433.2 | 128.9966 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1433.4 | 129.1885 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1433.6 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1433.8 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1434 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1434.2 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1434.4 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1434.6 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1434.8 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1435 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1435.2 | 128.9966 | 0.015352 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1435.4 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1435.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1435.8 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1436 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1436.2 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1436.4 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1436.6 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1436.8 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1437 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1437.2 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1437.4 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1437.6 | 128.9966 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1437.8 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1438 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1438.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1438.4 | 129.0925 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1438.6 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1438.8 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1439 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1439.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1439.4 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1439.6 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1439.8 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1440 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1440.2 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1440.4 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1440.6 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1440.8 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1441 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1441.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1441.4 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1441.6 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1441.8 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.011268 | 0.38019 | 0.0083128
1442 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1442.2 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1442.4 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1442.6 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1442.8 | 128.9966 | 0.013753 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1443 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1443.2 | 128.9966 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1443.4 | 128.9006 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1443.6 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1443.8 | 128.9966 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1444 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1444.2 | 128.9966 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1444.4 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1444.6 | 128.9006 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1444.8 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1445 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1445.2 | 128.8046 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1445.4 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1445.6 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1445.8 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1446 | 128.8046 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1446.2 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1446.4 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1446.6 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.7737 | 0.009669 | 0.28424 | 0.0083128
1446.8 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1447 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1447.2 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1447.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1447.6 | 128.8046 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1447.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
1448 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1448.2 | 128.9966 | 0.026549 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1448.4 | 128.7087 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1448.6 | 129.0925 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1448.8 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1449 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1449.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1449.4 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1449.6 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1449.8 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1450 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1450.2 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1450.4 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1450.6 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1450.8 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1451 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1451.2 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1451.4 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1451.6 | 128.9966 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1451.8 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1452 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1452.2 | 128.8046 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1452.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1452.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1452.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1453 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1453.2 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1453.4 | 128.8046 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1453.6 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1453.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1454 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1454.2 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1454.4 | 128.9966 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1454.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1454.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1455 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1455.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1455.4 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1455.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1455.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1456 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1456.2 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1456.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1456.6 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1456.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1457 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1457.2 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1457.4 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1457.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1457.8 | 128.9966 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1458 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1458.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1458.4 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1458.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1458.8 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1459 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1459.2 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1459.4 | 129.0925 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
1459.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1459.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1460 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1460.2 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.8139 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1460.4 | 129.0925 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1460.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1460.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1461 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.016122 | 0.76408 | 0.013089 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1461.2 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1461.4 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.014522 | 0.66813 | 0.013089 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1461.6 | 129.6683 | 0.05054 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1461.8 | 128.9966 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1462 | 129.3804 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1462.2 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1462.4 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1462.6 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1462.8 | 129.1885 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1463 | 129.1885 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1463.2 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1463.4 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1463.6 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1463.8 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1464 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1464.2 | 129.2844 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1464.4 | 129.2844 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1464.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1464.8 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1465 | 129.1885 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1465.2 | 129.1885 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1465.4 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1465.6 | 129.1885 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.00647 | 0.38019 | 0.0083128
1465.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1466 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1466.2 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1466.4 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1466.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1466.8 | 129.1885 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1467 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1467.2 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1467.4 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1467.6 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1467.8 | 129.1885 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1468 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1468.2 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1468.4 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1468.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.7737 | 0.0080692 | 0.28424 | 0.0083128
1468.8 | 129.1885 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1469 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1469.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1469.4 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1469.6 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1469.8 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1470 | 128.9006 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1470.2 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1470.4 | 128.3248 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1470.6 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1470.8 | 128.1329 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1471 | 128.4208 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1471.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1471.4 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1471.6 | 129.0925 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1471.8 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1472 | 129.0925 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.0923 | 0.0083128
1472.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1472.4 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1472.6 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1472.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1473 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1473.2 | 129.0925 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1473.4 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1473.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1473.8 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1474 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1474.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1474.4 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1474.6 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1474.8 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1475 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1475.2 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1475.4 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1475.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1475.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1476 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1476.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1476.4 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1476.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1476.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1477 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1477.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1477.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1477.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1477.8 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1478 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1478.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1478.4 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.01149 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1478.6 | 128.9966 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1478.8 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1479 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1479.2 | 129.0925 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1479.4 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1479.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1479.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1480 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1480.2 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1480.4 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1480.6 | 129.2844 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1480.8 | 129.0925 | 0.026549 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1481 | 129.0925 | 0.028148 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1481.2 | 128.9966 | 0.020151 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1481.4 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1481.6 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1481.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1482 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1482.2 | 129.0925 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1482.4 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1482.6 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1482.8 | 129.0925 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1483 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1483.2 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1483.4 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1483.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1483.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1484 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1484.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1484.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1484.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1484.8 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1485 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1485.2 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1485.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1485.6 | 128.9006 | 0.012154 | 0.38986 | 0.0095798 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1485.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1486 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1486.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1486.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1486.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1486.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1487 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1487.2 | 128.9966 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1487.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.011511
1487.6 | 128.9006 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1487.8 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1488 | 128.9006 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1488.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1488.4 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1488.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1488.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1489 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1489.2 | 128.9006 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1489.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1489.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1489.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1490 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1490.2 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1490.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1490.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1490.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1491 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1491.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1491.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.7737 | 0.0080692 | 0.28424 | 0.0083128
1491.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1491.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1492 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1492.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1492.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0033264 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1492.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1492.8 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1493 | 128.7087 | 0.010554 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1493.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1493.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1493.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1493.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1494 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1494.2 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1494.4 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1494.6 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1494.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.00647 | 0.38019 | 0.0083128
1495 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1495.2 | 128.8046 | 0.012154 | 0.38986 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1495.4 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1495.6 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1495.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.29321 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1496 | 128.8046 | 0.012154 | 0.29387 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1496.2 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1496.4 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1496.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1496.8 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1497 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1497.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1497.4 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1497.6 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0054014 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1497.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1498 | 128.9006 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1498.2 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1498.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1498.6 | 128.9006 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1498.8 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1499 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1499.2 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1499.4 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1499.6 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1499.8 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1500 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1500.2 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1500.4 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1500.6 | 128.9966 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1500.8 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1501 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1501.2 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1501.4 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1501.6 | 129.0925 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1501.8 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1502 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1502.2 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1502.4 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1502.6 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1502.8 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1503 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1503.2 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1503.4 | 129.7643 | 0.05214 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.8139 | 0.014522 | 0.76408 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1503.6 | 128.9006 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1503.8 | 129.0925 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0102 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1504 | 129.1885 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1504.2 | 129.1885 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1504.4 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1504.6 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1504.8 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1505 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1505.2 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1505.4 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1505.6 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1505.8 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1506 | 129.1885 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1506.2 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1506.4 | 129.2844 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1506.6 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1506.8 | 129.1885 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1507 | 129.2844 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.011268 | 0.28424 | 0.009912
1507.2 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1507.4 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1507.6 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1507.8 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1508 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1508.2 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1508.4 | 129.1885 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1508.6 | 129.3804 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1508.8 | 129.4764 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1509 | 129.4764 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1509.2 | 130.2441 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1509.4 | 129.9562 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1509.6 | 129.4764 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1509.8 | 129.1885 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1510 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1510.2 | 129.1885 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1510.4 | 129.1885 | 0.018551 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1510.6 | 129.0925 | 0.016952 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1510.8 | 129.0925 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1511 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1511.2 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1511.4 | 129.0925 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1511.6 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1511.8 | 129.0925 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1512 | 129.3804 | 0.040944 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1512.2 | 129.0925 | 0.036146 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1512.4 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1512.6 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1512.8 | 129.0925 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1513 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1513.2 | 129.0925 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1513.4 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.47618 | 0.006713
1513.6 | 129.0925 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1513.8 | 128.9966 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1514 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1514.2 | 128.9966 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1514.4 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1514.6 | 128.9966 | 0.016952 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1514.8 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1515 | 128.9966 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1515.2 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1515.4 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1515.6 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1515.8 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1516 | 128.9966 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1516.2 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1516.4 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1516.6 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1516.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1517 | 128.9966 | 0.015352 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1517.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1517.4 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1517.6 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1517.8 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1518 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1518.2 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1518.4 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1518.6 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1518.8 | 128.9006 | 0.015352 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1519 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1519.2 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1519.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1519.6 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1519.8 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1520 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.009912
1520.2 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1520.4 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1520.6 | 128.9006 | 0.013753 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1520.8 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1521 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1521.2 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1521.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1521.6 | 128.8046 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1521.8 | 128.9006 | 0.013753 | 0.38986 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1522 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1522.2 | 128.8046 | 0.013753 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1522.4 | 128.8046 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1522.6 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1522.8 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1523 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1523.2 | 128.8046 | 0.013753 | 0.29387 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1523.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1523.6 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1523.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1524 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1524.2 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.01149 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1524.4 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1524.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1524.8 | 128.9006 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1525 | 128.9006 | 0.02175 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1525.2 | 128.9006 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1525.4 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1525.6 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1525.8 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.47618 | 0.0083128
1526 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1526.2 | 128.7087 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.011511
1526.4 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1526.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1526.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1527 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1527.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1527.4 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1527.6 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1527.8 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1528 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1528.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1528.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1528.6 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1528.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1529 | 128.8046 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1529.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1529.4 | 128.8046 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1529.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1529.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.18829 | 0.0083128
1530 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1530.2 | 128.8046 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1530.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1530.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1530.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1531 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1531.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1531.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1531.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1531.8 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1532 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1532.2 | 128.9006 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1532.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1532.6 | 128.9966 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1532.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1533 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1533.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1533.4 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1533.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1533.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1534 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1534.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1534.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1534.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1534.8 | 128.9966 | 0.010554 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1535 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1535.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1535.4 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1535.6 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1535.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1536 | 129.0925 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1536.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1536.4 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1536.6 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1536.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1537 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1537.2 | 128.9966 | 0.010554 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1537.4 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1537.6 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1537.8 | 129.0925 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.016122 | 0.76408 | 0.01149 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
1538 | 129.0925 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1538.2 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1538.4 | 129.0925 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.014522 | 0.66813 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1538.6 | 129.1885 | 0.040944 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1538.8 | 128.9006 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1539 | 129.1885 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1539.2 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1539.4 | 129.1885 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1539.6 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1539.8 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1540 | 129.0925 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1540.2 | 129.0925 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1540.4 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1540.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1540.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1541 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1541.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1541.4 | 129.0925 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1541.6 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1541.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1542 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1542.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1542.4 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1542.6 | 129.0925 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1542.8 | 129.1885 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1543 | 129.1885 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1543.2 | 129.0925 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1543.4 | 129.0925 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1543.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1543.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1544 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1544.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1544.4 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1544.6 | 129.1885 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1544.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1545 | 129.1885 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1545.2 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1545.4 | 129.1885 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1545.6 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1545.8 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1546 | 129.1885 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1546.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1546.4 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1546.6 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1546.8 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1547 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1547.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1547.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1547.6 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1547.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.47618 | 0.0083128
1548 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1548.2 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1548.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1548.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1548.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1549 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1549.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1549.4 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1549.6 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1549.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1550 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1550.2 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1550.4 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1550.6 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1550.8 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1551 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1551.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1551.4 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1551.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1551.8 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
1552 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1552.2 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1552.4 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1552.6 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1552.8 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1553 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1553.2 | 129.3804 | 0.028148 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1553.4 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1553.6 | 129.1885 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1553.8 | 129.1885 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1554 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1554.2 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1554.4 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1554.6 | 129.0925 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1554.8 | 129.0925 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1555 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1555.2 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1555.4 | 129.0925 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1555.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1555.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1556 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.67705 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1556.2 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1556.4 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1556.6 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1556.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1557 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1557.2 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1557.4 | 129.0925 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1557.6 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1557.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1558 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1558.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1558.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1558.6 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1558.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1559 | 128.9006 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1559.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1559.4 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1559.6 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1559.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1560 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1560.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1560.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1560.6 | 128.9006 | 0.010554 | 0.38986 | 0.0079807 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1560.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1561 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1561.2 | 128.9006 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1561.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1561.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1561.8 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1562 | 128.9006 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1562.2 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1562.4 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1562.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1562.8 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1563 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1563.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1563.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.009912
1563.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1563.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1564 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1564.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1564.4 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1564.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1564.8 | 128.9006 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1565 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1565.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1565.4 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1565.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1565.8 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1566 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1566.2 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1566.4 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1566.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1566.8 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1567 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1567.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1567.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1567.6 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1567.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1568 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1568.2 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1568.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1568.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1568.8 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.38019 | 0.0083128
1569 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1569.2 | 128.9966 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1569.4 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1569.6 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1569.8 | 128.9966 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1570 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1570.2 | 129.0925 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1570.4 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1570.6 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1570.8 | 128.9966 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1571 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1571.2 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1571.4 | 128.9966 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1571.6 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1571.8 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1572 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1572.2 | 128.9966 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1572.4 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1572.6 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1572.8 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1573 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1573.2 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1573.4 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1573.6 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1573.8 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1574 | 129.0925 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1574.2 | 129.6683 | 0.026549 | 0.38986 | 0.0079807 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.016122 | 0.76408 | 0.013089 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1574.4 | 128.8046 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1574.6 | 129.2844 | 0.029748 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1574.8 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1575 | 129.1885 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1575.2 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1575.4 | 129.1885 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1575.6 | 129.1885 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1575.8 | 129.1885 | 0.016952 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1576 | 129.1885 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1576.2 | 129.1885 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1576.4 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1576.6 | 129.2844 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1576.8 | 129.2844 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1577 | 129.2844 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1577.2 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1577.4 | 129.2844 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1577.6 | 129.2844 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1577.8 | 129.2844 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1578 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1578.2 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1578.4 | 129.2844 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1578.6 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1578.8 | 129.3804 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.006713
1579 | 129.4764 | 0.016952 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1579.2 | 129.4764 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1579.4 | 130.532 | 0.018551 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1579.6 | 129.7643 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1579.8 | 129.3804 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1580 | 129.2844 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1580.2 | 129.2844 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1580.4 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1580.6 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1580.8 | 129.1885 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1581 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1581.2 | 129.0925 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1581.4 | 129.0925 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1581.6 | 129.1885 | 0.037745 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1581.8 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1582 | 128.9966 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1582.2 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1582.4 | 128.9966 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1582.6 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1582.8 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1583 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1583.2 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1583.4 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1583.6 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1583.8 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1584 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1584.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.28424 | 0.006713
1584.4 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1584.6 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1584.8 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1585 | 128.9966 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1585.2 | 128.9006 | 0.016952 | 0.29387 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1585.4 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.28424 | 0.0083128
1585.6 | 128.9006 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1585.8 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1586 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1586.2 | 128.9006 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1586.4 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1586.6 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1586.8 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1587 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1587.2 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1587.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1587.6 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1587.8 | 128.9006 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1588 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1588.2 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1588.4 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1588.6 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1588.8 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1589 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1589.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1589.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1589.6 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.012867 | 0.28424 | 0.0083128
1589.8 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1590 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1590.2 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1590.4 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1590.6 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1590.8 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1591 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1591.2 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1591.4 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.47618 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1591.6 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1591.8 | 128.9966 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1592 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1592.2 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1592.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1592.6 | 128.8046 | 0.015352 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1592.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1593 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1593.2 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1593.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1593.6 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1593.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1594 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1594.2 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1594.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1594.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1594.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1595 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1595.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1595.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1595.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1595.8 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1596 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1596.2 | 128.8046 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1596.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1596.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1596.8 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1597 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1597.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1597.4 | 128.8046 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1597.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1597.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1598 | 128.8046 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1598.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1598.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1598.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1598.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1599 | 128.9006 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1599.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1599.4 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1599.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1599.8 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1600 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1600.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1600.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1600.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1600.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1601 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1601.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1601.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1601.6 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1601.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
1602 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1602.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1602.4 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1602.6 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1602.8 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1603 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1603.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1603.4 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1603.6 | 128.9966 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1603.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1604 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1604.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1604.4 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1604.6 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1604.8 | 128.9966 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.009912
1605 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1605.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1605.4 | 129.0925 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.012923 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1605.6 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.016122 | 0.76408 | 0.014688 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1605.8 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.014522 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1606 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.01149 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1606.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.013089 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1606.4 | 129.6683 | 0.048941 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1606.6 | 128.9966 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1606.8 | 129.0925 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1607 | 129.2844 | 0.02335 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1607.2 | 129.1885 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1607.4 | 129.1885 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1607.6 | 129.0925 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1607.8 | 129.1885 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1608 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1608.2 | 129.0925 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1608.4 | 129.1885 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1608.6 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1608.8 | 129.1885 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1609 | 129.2844 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1609.2 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1609.4 | 129.1885 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1609.6 | 129.1885 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1609.8 | 129.1885 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1610 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1610.2 | 129.1885 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1610.4 | 129.1885 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1610.6 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
1610.8 | 129.1885 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1611 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1611.2 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1611.4 | 129.1885 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1611.6 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1611.8 | 129.0925 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1612 | 129.0925 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1612.2 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1612.4 | 129.1885 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1612.6 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1612.8 | 129.1885 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1613 | 129.1885 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1613.2 | 129.1885 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1613.4 | 129.1885 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1613.6 | 129.1885 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1613.8 | 129.1885 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1614 | 129.0925 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1614.2 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1614.4 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1614.6 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1614.8 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1615 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1615.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1615.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1615.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1615.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1616 | 128.3248 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1616.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1616.4 | 128.0369 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1616.6 | 128.2288 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1616.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1617 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1617.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1617.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1617.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1617.8 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1618 | 129.1885 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1618.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1618.4 | 129.0925 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1618.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1618.8 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1619 | 129.0925 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1619.2 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1619.4 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1619.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1619.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1620 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1620.2 | 129.0925 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1620.4 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1620.6 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1620.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1621 | 129.0925 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1621.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1621.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1621.6 | 129.1885 | 0.020151 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1621.8 | 129.1885 | 0.042543 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1622 | 128.8046 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1622.2 | 129.1885 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1622.4 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1622.6 | 128.9006 | 0.013753 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1622.8 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1623 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1623.2 | 128.9966 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1623.4 | 129.0925 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1623.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1623.8 | 128.9966 | 0.012154 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1624 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.009912
1624.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1624.4 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1624.6 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1624.8 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1625 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1625.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1625.4 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1625.6 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1625.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1626 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1626.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1626.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1626.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1626.8 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1627 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1627.2 | 128.9006 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1627.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1627.6 | 128.9006 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1627.8 | 128.9006 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1628 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1628.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1628.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1628.6 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1628.8 | 128.9006 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1629 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1629.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1629.4 | 128.8046 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1629.6 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1629.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
1630 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1630.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1630.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1630.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1630.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1631 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1631.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1631.4 | 128.8046 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1631.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1631.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1632 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1632.2 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1632.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1632.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1632.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1633 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1633.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1633.4 | 128.8046 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1633.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1633.8 | 129.1885 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1634 | 128.4208 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1634.2 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1634.4 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1634.6 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1634.8 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1635 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1635.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1635.4 | 128.8046 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.006713
1635.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1635.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1636 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.012867 | 0.28424 | 0.0083128
1636.2 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1636.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1636.6 | 128.5167 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1636.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1637 | 128.6127 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1637.2 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1637.4 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1637.6 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1637.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1638 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1638.2 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1638.4 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1638.6 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1638.8 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1639 | 128.8046 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.57213 | 0.0083128
1639.2 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1639.4 | 128.8046 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1639.6 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1639.8 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.011213 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1640 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1640.2 | 128.8046 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1640.4 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1640.6 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.18829 | 0.0083128
1640.8 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1641 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1641.2 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1641.4 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1641.6 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1641.8 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1642 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1642.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1642.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1642.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1642.8 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1643 | 128.9006 | 0.015352 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1643.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1643.4 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1643.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1643.8 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1644 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1644.2 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1644.4 | 128.9966 | 0.016952 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1644.6 | 129.3804 | 0.05214 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.014522 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1644.8 | 128.9006 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1645 | 129.2844 | 0.039345 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1645.2 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1645.4 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1645.6 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1645.8 | 128.9966 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1646 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1646.2 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1646.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1646.6 | 128.9966 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1646.8 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1647 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1647.2 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1647.4 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1647.6 | 129.0925 | 0.018551 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.011511
1647.8 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1648 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1648.2 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1648.4 | 129.0925 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1648.6 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1648.8 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1649 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1649.2 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1649.4 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.011511
1649.6 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.009669 | 0.28424 | 0.009912
1649.8 | 129.2844 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.006713
1650 | 129.3804 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1650.2 | 129.3804 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1650.4 | 130.2441 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1650.6 | 129.4764 | 0.018551 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1650.8 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
1651 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1651.2 | 128.9966 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1651.4 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1651.6 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1651.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1652 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1652.2 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1652.4 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1652.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1652.8 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1653 | 128.9006 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1653.2 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1653.4 | 129.0925 | 0.045742 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1653.6 | 128.7087 | 0.02175 | 0.38986 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1653.8 | 129.1885 | 0.034546 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1654 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1654.2 | 128.9006 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1654.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1654.6 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1654.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1655 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1655.2 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1655.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1655.6 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1655.8 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1656 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1656.2 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1656.4 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1656.6 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1656.8 | 128.8046 | 0.016952 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1657 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1657.2 | 128.7087 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1657.4 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1657.6 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1657.8 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1658 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1658.2 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1658.4 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1658.6 | 128.6127 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1658.8 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1659 | 128.7087 | 0.016952 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1659.2 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1659.4 | 128.6127 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1659.6 | 128.6127 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1659.8 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1660 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1660.2 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1660.4 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1660.6 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1660.8 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1661 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1661.2 | 128.6127 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1661.4 | 128.5167 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1661.6 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1661.8 | 128.7087 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1662 | 128.6127 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1662.2 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1662.4 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1662.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1662.8 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1663 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1663.2 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1663.4 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1663.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1663.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1664 | 128.6127 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1664.2 | 128.6127 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1664.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
1664.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1664.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1665 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1665.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1665.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1665.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1665.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1666 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1666.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1666.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1666.6 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1666.8 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1667 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1667.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1667.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1667.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1667.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1668 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1668.2 | 128.8046 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1668.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1668.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1668.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1669 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.017721 | 0.76408 | 0.01149 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1669.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0097238 | 0.76408 | 0.016288 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1669.4 | 129.4764 | 0.053739 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1669.6 | 128.6127 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1669.8 | 128.9966 | 0.031347 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1670 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1670.2 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.28424 | 0.0083128
1670.4 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1670.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1670.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1671 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1671.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1671.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1671.6 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1671.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1672 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1672.2 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1672.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1672.6 | 128.8046 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1672.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1673 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1673.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1673.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1673.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1673.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
1674 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1674.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1674.4 | 128.9006 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1674.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1674.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1675 | 128.8046 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1675.2 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1675.4 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1675.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1675.8 | 128.3248 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1676 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1676.2 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1676.4 | 128.2288 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1676.6 | 128.7087 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1676.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1677 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1677.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1677.4 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1677.6 | 128.8046 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1677.8 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1678 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1678.2 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1678.4 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1678.6 | 128.8046 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1678.8 | 128.8046 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1679 | 128.9006 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1679.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1679.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.012867 | 0.28424 | 0.009912
1679.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.18829 | 0.009912
1679.8 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1680 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1680.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1680.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1680.6 | 128.5167 | 0.012154 | 0.29387 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1680.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1681 | 129.0925 | 0.040944 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1681.2 | 128.6127 | 0.026549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1681.4 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1681.6 | 128.9006 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1681.8 | 128.8046 | 0.02175 | 0.48581 | 0.0063808 | 0.67705 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1682 | 128.6127 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1682.2 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1682.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1682.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1682.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1683 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1683.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1683.4 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1683.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1683.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.009912
1684 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1684.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1684.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1684.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1684.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1685 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1685.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1685.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1685.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1685.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1686 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1686.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1686.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1686.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1686.8 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1687 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1687.2 | 128.8046 | 0.012154 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1687.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1687.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1687.8 | 128.7087 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1688 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1688.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1688.4 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1688.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1688.8 | 128.7087 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1689 | 128.7087 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1689.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1689.4 | 128.7087 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1689.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1689.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1690 | 128.7087 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1690.2 | 128.7087 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1690.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1690.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1690.8 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1691 | 128.6127 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1691.2 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1691.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.37923 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1691.6 | 128.7087 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1691.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1692 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1692.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1692.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1692.6 | 128.7087 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1692.8 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1693 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1693.2 | 128.7087 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1693.4 | 128.6127 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1693.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1693.8 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1694 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.86003 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1694.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1694.4 | 128.6127 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1694.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1694.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1695 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1695.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1695.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1695.6 | 128.6127 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1695.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1696 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1696.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1696.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1696.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1696.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1697 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1697.2 | 128.6127 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1697.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1697.6 | 128.6127 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1697.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1698 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1698.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1698.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1698.6 | 128.5167 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1698.8 | 128.6127 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1699 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1699.2 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1699.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1699.6 | 128.6127 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1699.8 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1700 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1700.2 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1700.4 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1700.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1700.8 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1701 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1701.2 | 128.6127 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1701.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1701.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1701.8 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1702 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1702.2 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1702.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.006713
1702.6 | 128.6127 | 0.0089549 | 0.38986 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1702.8 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1703 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1703.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1703.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1703.6 | 128.6127 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1703.8 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1704 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1704.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1704.4 | 128.6127 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1704.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1704.8 | 128.6127 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1705 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1705.2 | 128.6127 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1705.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1705.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1705.8 | 128.6127 | 0.012154 | 0.29387 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1706 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1706.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1706.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1706.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1706.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1707 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1707.2 | 128.6127 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1707.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1707.6 | 128.6127 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1707.8 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1708 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1708.2 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1708.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1708.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1708.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1709 | 128.6127 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1709.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1709.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1709.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1709.8 | 128.6127 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1710 | 128.7087 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1710.2 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1710.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1710.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1710.8 | 128.6127 | 0.010554 | 0.38986 | 0.0079807 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1711 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1711.2 | 128.6127 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1711.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1711.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1711.8 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1712 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1712.2 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1712.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.37923 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1712.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.01149 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1712.8 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.57213 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1713 | 128.6127 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.01149 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1713.2 | 128.6127 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1713.4 | 128.9966 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1713.6 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1713.8 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1714 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1714.2 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1714.4 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1714.6 | 128.6127 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1714.8 | 128.6127 | 0.013753 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1715 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1715.2 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1715.4 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1715.6 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.37923 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1715.8 | 128.6127 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1716 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1716.2 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1716.4 | 128.6127 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1716.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1716.8 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1717 | 128.6127 | 0.012154 | 0.38986 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1717.2 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1717.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1717.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1717.8 | 128.6127 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1718 | 128.6127 | 0.012154 | 0.38986 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1718.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1718.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1718.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1718.8 | 128.6127 | 0.012154 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1719 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1719.2 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1719.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1719.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1719.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1720 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1720.2 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1720.4 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1720.6 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1720.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1721 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1721.2 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.37923 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1721.4 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1721.6 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1721.8 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.28424 | 0.009912
1722 | 128.5167 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1722.2 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1722.4 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1722.6 | 128.5167 | 0.013753 | 0.38986 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1722.8 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1723 | 128.6127 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1723.2 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1723.4 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1723.6 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1723.8 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1724 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1724.2 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1724.4 | 128.6127 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1724.6 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1724.8 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1725 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1725.2 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1725.4 | 128.6127 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1725.6 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1725.8 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1726 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1726.2 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1726.4 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1726.6 | 128.6127 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1726.8 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1727 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1727.2 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1727.4 | 128.6127 | 0.013753 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1727.6 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1727.8 | 128.7087 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1728 | 128.7087 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1728.2 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1728.4 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1728.6 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1728.8 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1729 | 128.7087 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1729.2 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1729.4 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1729.6 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1729.8 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1730 | 128.7087 | 0.016952 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1730.2 | 128.7087 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1730.4 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1730.6 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1730.8 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1731 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.47618 | 0.0083128
1731.2 | 128.7087 | 0.015352 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1731.4 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1731.6 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1731.8 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1732 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1732.2 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1732.4 | 128.6127 | 0.016952 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1732.6 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1732.8 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1733 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1733.2 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1733.4 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1733.6 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1733.8 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1734 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1734.2 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1734.4 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1734.6 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1734.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1735 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1735.2 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1735.4 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1735.6 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1735.8 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1736 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1736.2 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1736.4 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1736.6 | 128.9006 | 0.016952 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1736.8 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1737 | 128.9006 | 0.016952 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1737.2 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1737.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1737.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1737.8 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1738 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1738.2 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1738.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1738.6 | 128.8046 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1738.8 | 128.9966 | 0.016952 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1739 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1739.2 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1739.4 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1739.6 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1739.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1740 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1740.2 | 128.9006 | 0.016952 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1740.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1740.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1740.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1741 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1741.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1741.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1741.6 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1741.8 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1742 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1742.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1742.4 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1742.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1742.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1743 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1743.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1743.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1743.6 | 128.8046 | 0.015352 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1743.8 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1744 | 128.9006 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1744.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1744.4 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1744.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1744.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1745 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1745.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1745.4 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1745.6 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1745.8 | 128.9006 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1746 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.020865 | 0.28424 | 0.0083128
1746.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1746.4 | 128.8046 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1746.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.66813 | 0.0083128
1746.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.006713
1747 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1747.2 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1747.4 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1747.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1747.8 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1748 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1748.2 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1748.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1748.6 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1748.8 | 128.8046 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1749 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1749.2 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1749.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1749.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1749.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1750 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1750.2 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.01149 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1750.4 | 128.9006 | 0.016952 | 0.48581 | 0.0031824 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.76408 | 0.01149 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1750.6 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.019487 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1750.8 | 129.0925 | 0.024949 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.019321 | 0.76408 | 0.016288 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1751 | 129.3804 | 0.031347 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.37923 | 0.0086004 | 0.71795 | 0.02092 | 0.76408 | 0.016288 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1751.2 | 129.2844 | 0.053739 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.016122 | 0.66813 | 0.013089 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1751.4 | 129.2844 | 0.05054 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.014522 | 0.76408 | 0.01149 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1751.6 | 128.9006 | 0.034546 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.012923 | 0.66813 | 0.0098898 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1751.8 | 128.3248 | 0.029748 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.76408 | 0.013089 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1752 | 128.6127 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.66813 | 0.01149 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1752.2 | 129.2844 | 0.044143 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1752.4 | 129.1885 | 0.047342 | 0.38986 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1752.6 | 128.9006 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1752.8 | 128.9966 | 0.037745 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1753 | 128.7087 | 0.026549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1753.2 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1753.4 | 129.0925 | 0.024949 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1753.6 | 129.0925 | 0.026549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1753.8 | 128.9966 | 0.026549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1754 | 128.9966 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1754.2 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1754.4 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1754.6 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1754.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1755 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1755.2 | 128.9966 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1755.4 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1755.6 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1755.8 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1756 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1756.2 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1756.4 | 129.0925 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1756.6 | 129.0925 | 0.016952 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1756.8 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1757 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1757.2 | 129.0925 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1757.4 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1757.6 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1757.8 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1758 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1758.2 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1758.4 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1758.6 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1758.8 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1759 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1759.2 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1759.4 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1759.6 | 128.9966 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1759.8 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1760 | 129.0925 | 0.018551 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1760.2 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1760.4 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1760.6 | 129.0925 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1760.8 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
1761 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1761.2 | 129.0925 | 0.018551 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1761.4 | 129.0925 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1761.6 | 129.1885 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1761.8 | 129.0925 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.86003 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1762 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1762.2 | 129.1885 | 0.018551 | 0.48581 | 0.0095798 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1762.4 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1762.6 | 129.2844 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1762.8 | 129.3804 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1763 | 129.3804 | 0.018551 | 0.38986 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1763.2 | 129.7643 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1763.4 | 130.2441 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.006713
1763.6 | 130.532 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1763.8 | 129.4764 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.0083128
1764 | 129.2844 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1764.2 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.011799 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1764.4 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1764.6 | 129.0925 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1764.8 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1765 | 128.9966 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1765.2 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1765.4 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1765.6 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1765.8 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1766 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1766.2 | 128.9966 | 0.018551 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1766.4 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1766.6 | 128.9966 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1766.8 | 128.9006 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1767 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.85907 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1767.2 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.011511
1767.4 | 129.1885 | 0.047342 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1767.6 | 128.9006 | 0.032947 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1767.8 | 128.9006 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1768 | 129.1885 | 0.034546 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1768.2 | 128.9006 | 0.016952 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1768.4 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1768.6 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1768.8 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1769 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1769.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1769.4 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1769.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1769.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1770 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1770.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1770.4 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1770.6 | 128.8046 | 0.016952 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1770.8 | 128.8046 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1771 | 128.7087 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1771.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1771.4 | 128.8046 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1771.6 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1771.8 | 128.7087 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1772 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1772.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1772.4 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1772.6 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1772.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1773 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1773.2 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1773.4 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1773.6 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1773.8 | 128.7087 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1774 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1774.2 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1774.4 | 128.7087 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1774.6 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1774.8 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1775 | 128.7087 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1775.2 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1775.4 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1775.6 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1775.8 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1776 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1776.2 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1776.4 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1776.6 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1776.8 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1777 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1777.2 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1777.4 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1777.6 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1777.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1778 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1778.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1778.4 | 128.2288 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1778.6 | 128.8046 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.0048148 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1778.8 | 128.6127 | 0.026549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1779 | 128.7087 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1779.2 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1779.4 | 128.4208 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1779.6 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1779.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1780 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1780.2 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1780.4 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1780.6 | 128.6127 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1780.8 | 128.5167 | 0.012154 | 0.38986 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1781 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1781.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1781.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1781.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1781.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1782 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1782.2 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1782.4 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1782.6 | 128.5167 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1782.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1783 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1783.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1783.4 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1783.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.28424 | 0.0083128
1783.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1784 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1784.2 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1784.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1784.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1784.8 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1785 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1785.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1785.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1785.6 | 128.7087 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1785.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1786 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
1786.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1786.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1786.6 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1786.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1787 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
1787.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1787.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1787.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1787.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1788 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1788.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1788.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1788.6 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1788.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1789 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1789.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1789.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1789.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1789.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
1790 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1790.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1790.4 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.016288 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1790.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.016122 | 0.66813 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1790.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.012923 | 0.76408 | 0.017887 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1791 | 129.4764 | 0.063336 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1791.2 | 128.7087 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1791.4 | 129.0925 | 0.037745 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1791.6 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1791.8 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1792 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1792.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1792.4 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1792.6 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1792.8 | 128.8046 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1793 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1793.2 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1793.4 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1793.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1793.8 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1794 | 128.9006 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1794.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1794.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1794.6 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1794.8 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1795 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1795.2 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1795.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1795.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1795.8 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1796 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1796.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1796.4 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1796.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1796.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1797 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1797.2 | 128.7087 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1797.4 | 128.6127 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1797.6 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1797.8 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1798 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1798.2 | 127.3651 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1798.4 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1798.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1798.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1799 | 128.9006 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1799.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1799.4 | 128.8046 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1799.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1799.8 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1800 | 128.9006 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1800.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1800.4 | 128.8046 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1800.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1800.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1801 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1801.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1801.4 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1801.6 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1801.8 | 128.8046 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1802 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.76308 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1802.2 | 128.9966 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1802.4 | 128.5167 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1802.6 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1802.8 | 128.7087 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.012867 | 0.28424 | 0.006713
1803 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
1803.2 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1803.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1803.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1803.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1804 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1804.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1804.4 | 128.6127 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1804.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1804.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1805 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1805.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1805.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1805.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1805.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1806 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1806.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1806.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1806.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1806.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.7737 | 0.009669 | 0.28424 | 0.0083128
1807 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1807.2 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1807.4 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1807.6 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.009669 | 0.38019 | 0.0083128
1807.8 | 128.6127 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1808 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1808.2 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1808.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1808.6 | 128.5167 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1808.8 | 128.6127 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1809 | 128.5167 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1809.2 | 128.6127 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1809.4 | 128.5167 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1809.6 | 128.5167 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1809.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1810 | 128.6127 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1810.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1810.4 | 128.5167 | 0.010554 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1810.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1810.8 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1811 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1811.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1811.4 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1811.6 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1811.8 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1812 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1812.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1812.4 | 128.6127 | 0.0089549 | 0.48581 | 0.0095798 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.47618 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1812.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1812.8 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1813 | 128.5167 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1813.2 | 128.5167 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1813.4 | 128.5167 | 0.016952 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1813.6 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
1813.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1814 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1814.2 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1814.4 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1814.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1814.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1815 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1815.2 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1815.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.011213 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1815.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1815.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1816 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1816.2 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.00647 | 0.38019 | 0.009912
1816.4 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1816.6 | 128.7087 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1816.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1817 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1817.2 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1817.4 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1817.6 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.009912
1817.8 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1818 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1818.2 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1818.4 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1818.6 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1818.8 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1819 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1819.2 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1819.4 | 128.9006 | 0.015352 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1819.6 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1819.8 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1820 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1820.2 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1820.4 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1820.6 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1820.8 | 128.7087 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1821 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1821.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1821.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1821.6 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1821.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1822 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1822.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1822.4 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1822.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1822.8 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1823 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1823.2 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1823.4 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.76408 | 0.013089 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1823.6 | 128.9006 | 0.028148 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.014522 | 0.76408 | 0.017887 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1823.8 | 128.7087 | 0.029748 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.013089 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1824 | 129.2844 | 0.037745 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.86003 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1824.2 | 128.6127 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1824.4 | 129.1885 | 0.026549 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1824.6 | 129.0925 | 0.015352 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1824.8 | 129.0925 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1825 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1825.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1825.4 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1825.6 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1825.8 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1826 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1826.2 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1826.4 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1826.6 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1826.8 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1827 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.18829 | 0.009912
1827.2 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1827.4 | 129.0925 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1827.6 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1827.8 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1828 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1828.2 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1828.4 | 129.0925 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1828.6 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1828.8 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1829 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1829.2 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1829.4 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1829.6 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1829.8 | 129.1885 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1830 | 129.2844 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1830.2 | 129.3804 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1830.4 | 129.4764 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1830.6 | 129.6683 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1830.8 | 130.532 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1831 | 129.6683 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1831.2 | 129.4764 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1831.4 | 129.1885 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1831.6 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1831.8 | 129.0925 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1832 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1832.2 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1832.4 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1832.6 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1832.8 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1833 | 128.9966 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1833.2 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1833.4 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1833.6 | 128.9966 | 0.020151 | 0.38986 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1833.8 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.013089 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1834 | 129.0925 | 0.05054 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1834.2 | 128.4208 | 0.028148 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1834.4 | 129.0925 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1834.6 | 128.9966 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1834.8 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1835 | 128.9966 | 0.02335 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
1835.2 | 128.9966 | 0.015352 | 0.38986 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.47618 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1835.4 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1835.6 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1835.8 | 128.5167 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1836 | 128.2288 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1836.2 | 128.4208 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1836.4 | 128.4208 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1836.6 | 128.4208 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1836.8 | 128.5167 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1837 | 128.4208 | 0.018551 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1837.2 | 128.5167 | 0.015352 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1837.4 | 128.5167 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1837.6 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1837.8 | 128.6127 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1838 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1838.2 | 128.6127 | 0.016952 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1838.4 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1838.6 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1838.8 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1839 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1839.2 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1839.4 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1839.6 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1839.8 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1840 | 128.5167 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1840.2 | 128.5167 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1840.4 | 128.4208 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1840.6 | 128.3248 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1840.8 | 128.4208 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1841 | 128.3248 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1841.2 | 128.3248 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1841.4 | 128.3248 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1841.6 | 128.3248 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1841.8 | 128.3248 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1842 | 128.3248 | 0.018551 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1842.2 | 128.4208 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1842.4 | 128.3248 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1842.6 | 128.3248 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1842.8 | 128.3248 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1843 | 128.3248 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1843.2 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1843.4 | 128.3248 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1843.6 | 128.3248 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1843.8 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1844 | 128.3248 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1844.2 | 128.2288 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1844.4 | 128.3248 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.57213 | 0.0083128
1844.6 | 128.2288 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1844.8 | 128.2288 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1845 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1845.2 | 128.3248 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1845.4 | 128.5167 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1845.6 | 128.4208 | 0.013753 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1845.8 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1846 | 128.5167 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1846.2 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1846.4 | 128.6127 | 0.015352 | 0.38986 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1846.6 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1846.8 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1847 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.57213 | 0.0083128
1847.2 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1847.4 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.0083128
1847.6 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1847.8 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1848 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1848.2 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1848.4 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1848.6 | 128.7087 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1848.8 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1849 | 128.7087 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1849.2 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1849.4 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1849.6 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1849.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1850 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1850.2 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1850.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1850.6 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1850.8 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1851 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1851.2 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1851.4 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1851.6 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1851.8 | 128.7087 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1852 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1852.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1852.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1852.6 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1852.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1853 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1853.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1853.4 | 128.7087 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1853.6 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1853.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.7737 | 0.009669 | 0.38019 | 0.009912
1854 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1854.2 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.012867 | 0.28424 | 0.009912
1854.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1854.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1854.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1855 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1855.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1855.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1855.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1855.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1856 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1856.2 | 128.7087 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1856.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1856.6 | 128.7087 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1856.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1857 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1857.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1857.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1857.6 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1857.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1858 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1858.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1858.4 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1858.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1858.8 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1859 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
1859.2 | 128.8046 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1859.4 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1859.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1859.8 | 128.9006 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1860 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1860.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1860.4 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1860.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1860.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1861 | 128.8046 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1861.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1861.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1861.6 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1861.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1862 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1862.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1862.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1862.6 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1862.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
1863 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1863.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1863.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
1863.6 | 128.8046 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1863.8 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1864 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1864.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.006713
1864.4 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1864.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1864.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1865 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.009912
1865.2 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1865.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1865.6 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1865.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1866 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1866.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1866.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.67705 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1866.6 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1866.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1867 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1867.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1867.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1867.6 | 128.9006 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1867.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.017887 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1868 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.02092 | 0.76408 | 0.013089 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1868.2 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.014522 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1868.4 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.019487 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1868.6 | 129.0925 | 0.026549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.016122 | 0.66813 | 0.013089 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1868.8 | 129.1885 | 0.026549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.017721 | 0.76408 | 0.013089 | 0.67775 | 0.012867 | 0.38019 | 0.0083128
1869 | 129.5724 | 0.064936 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1869.2 | 128.6127 | 0.036146 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.01149 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1869.4 | 128.9966 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1869.6 | 129.0925 | 0.029748 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1869.8 | 129.0925 | 0.037745 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1870 | 128.8046 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1870.2 | 128.8046 | 0.02175 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1870.4 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1870.6 | 129.0925 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1870.8 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1871 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.28424 | 0.009912
1871.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1871.4 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1871.6 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1871.8 | 128.9966 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1872 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1872.2 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1872.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.011213 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1872.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1872.8 | 128.9966 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1873 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1873.2 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1873.4 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1873.6 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1873.8 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1874 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1874.2 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1874.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1874.6 | 128.9966 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1874.8 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1875 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1875.2 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1875.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1875.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1875.8 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1876 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1876.2 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1876.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1876.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1876.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1877 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1877.2 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1877.4 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1877.6 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1877.8 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1878 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1878.2 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1878.4 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1878.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
1878.8 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1879 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1879.2 | 128.9966 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1879.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1879.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1879.8 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1880 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1880.2 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1880.4 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1880.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
1880.8 | 128.9006 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1881 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1881.2 | 128.9966 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1881.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1881.6 | 128.9006 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.57213 | 0.0083128
1881.8 | 128.9006 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1882 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1882.2 | 128.9966 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1882.4 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1882.6 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1882.8 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1883 | 128.9966 | 0.010554 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1883.2 | 128.9966 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1883.4 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1883.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
1883.8 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1884 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1884.2 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1884.4 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1884.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1884.8 | 128.9966 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1885 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1885.2 | 128.9006 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1885.4 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1885.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1885.8 | 128.9966 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1886 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1886.2 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1886.4 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1886.6 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1886.8 | 128.9006 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1887 | 128.9006 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1887.2 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
1887.4 | 128.9006 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1887.6 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1887.8 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1888 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1888.2 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1888.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1888.6 | 128.8046 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1888.8 | 128.8046 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.011511
1889 | 128.9006 | 0.028148 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1889.2 | 129.0925 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1889.4 | 129.2844 | 0.040944 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1889.6 | 128.7087 | 0.026549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1889.8 | 128.7087 | 0.028148 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1890 | 128.6127 | 0.039345 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1890.2 | 128.6127 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1890.4 | 128.7087 | 0.036146 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1890.6 | 128.6127 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1890.8 | 128.8046 | 0.048941 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.47618 | 0.009912
1891 | 128.9966 | 0.055339 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1891.2 | 128.9966 | 0.05214 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.012923 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1891.4 | 129.4764 | 0.063336 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1891.6 | 129.5724 | 0.064936 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.012923 | 0.66813 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1891.8 | 129.3804 | 0.047342 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.016122 | 0.76408 | 0.013089 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1892 | 129.0925 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.019321 | 0.76408 | 0.013089 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1892.2 | 129.1885 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.019321 | 0.76408 | 0.014688 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1892.4 | 129.0925 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.02092 | 0.76408 | 0.016288 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1892.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.017721 | 0.76408 | 0.019487 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1892.8 | 128.4208 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.019487 | 0.5818 | 0.011268 | 0.38019 | 0.011511
1893 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.76408 | 0.019487 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1893.2 | 128.6127 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.019487 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
1893.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1893.6 | 128.8046 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.012923 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1893.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.67705 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.014522 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1894 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.8139 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1894.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.02092 | 0.76408 | 0.013089 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1894.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.02092 | 0.86003 | 0.016288 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1894.6 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.017887 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
1894.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.016122 | 0.76408 | 0.016288 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1895 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1895.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.013399 | 0.71795 | 0.0081246 | 0.66813 | 0.01149 | 0.7737 | 0.011268 | 0.47618 | 0.0083128
1895.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.7737 | 0.009669 | 0.47618 | 0.009912
1895.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1895.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.38019 | 0.009912
1896 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1896.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1896.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1896.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.47618 | 0.009912
1896.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.009669 | 0.47618 | 0.009912
1897 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1897.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1897.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1897.6 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1897.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1898 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1898.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1898.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1898.6 | 128.8046 | 0.010554 | 0.38986 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1898.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
1899 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
1899.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1899.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1899.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1899.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1900 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1900.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1900.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1900.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1900.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1901 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1901.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1901.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1901.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1901.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1902 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1902.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1902.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1902.6 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1902.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1903 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1903.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
1903.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1903.6 | 128.8046 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1903.8 | 128.8046 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1904 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1904.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1904.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1904.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.009669 | 0.38019 | 0.009912
1904.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1905 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1905.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1905.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1905.6 | 128.8046 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1905.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1906 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1906.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
1906.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1906.6 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1906.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1907 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1907.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1907.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1907.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1907.8 | 128.8046 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1908 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1908.2 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1908.4 | 128.9006 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1908.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1908.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1909 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
1909.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1909.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1909.6 | 128.8046 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1909.8 | 128.8046 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1910 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1910.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1910.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1910.6 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1910.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1911 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1911.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1911.4 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1911.6 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1911.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1912 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1912.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.009669 | 0.47618 | 0.009912
1912.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1912.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1912.8 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1913 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1913.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
1913.4 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1913.6 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1913.8 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1914 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1914.2 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1914.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1914.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.0083128
1914.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1915 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1915.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1915.4 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1915.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1915.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1916 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1916.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1916.4 | 128.8046 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1916.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1916.8 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1917 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1917.2 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1917.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1917.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1917.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1918 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1918.2 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
1918.4 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1918.6 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1918.8 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1919 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1919.2 | 128.8046 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1919.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1919.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1919.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1920 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1920.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1920.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1920.6 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.96565 | 0.011268 | 0.38019 | 0.009912
1920.8 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1921 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1921.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1921.4 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1921.6 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1921.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
1922 | 128.9966 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1922.2 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1922.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.86003 | 0.016288 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1922.6 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.016288 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1922.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1923 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.86003 | 0.017887 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
1923.2 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.86003 | 0.016288 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1923.4 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.86003 | 0.017887 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1923.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.017721 | 0.76408 | 0.014688 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1923.8 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.02092 | 0.76408 | 0.016288 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1924 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.86003 | 0.016288 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1924.2 | 128.9006 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.017721 | 0.76408 | 0.013089 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1924.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.019321 | 0.86003 | 0.014688 | 0.67775 | 0.009669 | 0.47618 | 0.009912
1924.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.76308 | 0.0086004 | 0.8139 | 0.017721 | 0.76408 | 0.013089 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1924.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.019321 | 0.76408 | 0.013089 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1925 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.02092 | 0.76408 | 0.014688 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1925.2 | 128.9006 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.017721 | 0.86003 | 0.013089 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1925.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.02092 | 0.76408 | 0.013089 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1925.6 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.016122 | 0.76408 | 0.013089 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1925.8 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1926 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.014522 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1926.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.012923 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1926.4 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1926.6 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1926.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.017887 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1927 | 128.3248 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.019487 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1927.2 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.017887 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1927.4 | 128.2288 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.019487 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1927.6 | 128.1329 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.011324 | 0.66813 | 0.014688 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1927.8 | 128.6127 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.016288 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1928 | 128.8046 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1928.2 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.011511
1928.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.017887 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1928.6 | 128.2288 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.019487 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1928.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.016288 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1929 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.016288 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1929.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1929.4 | 128.1329 | 0.010554 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.019487 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1929.6 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.019487 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1929.8 | 128.3248 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.017887 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1930 | 128.2288 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.019487 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1930.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.016122 | 0.76408 | 0.017887 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1930.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.012923 | 0.86003 | 0.017887 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1930.6 | 129.0925 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.019321 | 0.76408 | 0.014688 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1930.8 | 129.0925 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.019321 | 0.76408 | 0.014688 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1931 | 129.2844 | 0.037745 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.016122 | 0.76408 | 0.013089 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1931.2 | 129.1885 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.017721 | 0.76408 | 0.013089 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1931.4 | 129.2844 | 0.037745 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.017721 | 0.76408 | 0.013089 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1931.6 | 129.5724 | 0.058538 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.014522 | 0.76408 | 0.01149 | 0.67775 | 0.009669 | 0.47618 | 0.009912
1931.8 | 129.1885 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.017721 | 0.76408 | 0.013089 | 0.7737 | 0.011268 | 0.38019 | 0.0083128
1932 | 129.6683 | 0.064936 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.012923 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.011511
1932.2 | 129.5724 | 0.058538 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1932.4 | 129.6683 | 0.063336 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.014522 | 0.76408 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1932.6 | 129.3804 | 0.05054 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1932.8 | 129.5724 | 0.064936 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1933 | 129.1885 | 0.055339 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1933.2 | 128.6127 | 0.040944 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1933.4 | 128.6127 | 0.037745 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1933.6 | 128.5167 | 0.037745 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1933.8 | 128.6127 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
1934 | 128.7087 | 0.028148 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1934.2 | 128.9966 | 0.029748 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1934.4 | 128.9006 | 0.02335 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.86003 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1934.6 | 129.1885 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1934.8 | 128.9006 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1935 | 128.9966 | 0.036146 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1935.2 | 128.7087 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
1935.4 | 128.7087 | 0.02335 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1935.6 | 128.8046 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1935.8 | 128.7087 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1936 | 128.7087 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1936.2 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.011511
1936.4 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1936.6 | 128.9966 | 0.020151 | 0.48581 | 0.0095798 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.011511
1936.8 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1937 | 128.9966 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
1937.2 | 128.9006 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1937.4 | 128.9966 | 0.013753 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1937.6 | 128.9966 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1937.8 | 128.9006 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1938 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1938.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1938.4 | 128.9966 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.009912
1938.6 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1938.8 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1939 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1939.2 | 128.9006 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1939.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1939.6 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1939.8 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1940 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1940.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1940.4 | 128.9006 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1940.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1940.8 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1941 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1941.2 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1941.4 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1941.6 | 128.9966 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1941.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1942 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1942.2 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1942.4 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1942.6 | 128.9006 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.011511
1942.8 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1943 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1943.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
1943.4 | 128.9006 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1943.6 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1943.8 | 128.9006 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1944 | 128.8046 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1944.2 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1944.4 | 128.7087 | 0.015352 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.011511
1944.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1944.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1945 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1945.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1945.4 | 128.6127 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1945.6 | 128.8046 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1945.8 | 129.1885 | 0.039345 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1946 | 129.0925 | 0.036146 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.011511
1946.2 | 128.7087 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1946.4 | 128.6127 | 0.040944 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1946.6 | 129.4764 | 0.058538 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1946.8 | 129.0925 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.017721 | 0.76408 | 0.014688 | 0.67775 | 0.009669 | 0.47618 | 0.009912
1947 | 128.8046 | 0.012154 | 0.67775 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.017721 | 0.76408 | 0.016288 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1947.2 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.017887 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1947.4 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.014522 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1947.6 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.016122 | 0.76408 | 0.013089 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1947.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.86003 | 0.017887 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1948 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1948.2 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1948.4 | 128.8046 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1948.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1948.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1949 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1949.2 | 128.8046 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1949.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1949.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1949.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1950 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1950.2 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
1950.4 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1950.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1950.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1951 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1951.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1951.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1951.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1951.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1952 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1952.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1952.4 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1952.6 | 128.7087 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1952.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1953 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1953.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1953.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1953.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1953.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1954 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1954.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1954.4 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1954.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1954.8 | 128.7087 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1955 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1955.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1955.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1955.6 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1955.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1956 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1956.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1956.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1956.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1956.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1957 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1957.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1957.4 | 128.7087 | 0.010554 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1957.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1957.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1958 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1958.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1958.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1958.6 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1958.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1959 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1959.2 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1959.4 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1959.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1959.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1960 | 128.7087 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1960.2 | 128.7087 | 0.010554 | 0.38986 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1960.4 | 128.7087 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1960.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1960.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1961 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1961.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1961.4 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1961.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1961.8 | 128.7087 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1962 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1962.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1962.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1962.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1962.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1963 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1963.2 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
1963.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.86003 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1963.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1963.8 | 128.7087 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1964 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1964.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1964.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1964.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1964.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1965 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1965.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1965.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1965.6 | 128.6127 | 0.012154 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1965.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1966 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
1966.2 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1966.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1966.6 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1966.8 | 128.6127 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1967 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1967.2 | 128.7087 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1967.4 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1967.6 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1967.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1968 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1968.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1968.4 | 128.6127 | 0.013753 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1968.6 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1968.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1969 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1969.2 | 128.6127 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1969.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1969.6 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.57213 | 0.009912
1969.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1970 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1970.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1970.4 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1970.6 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1970.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1971 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1971.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1971.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1971.6 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1971.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1972 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1972.2 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1972.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1972.6 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1972.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1973 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1973.2 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1973.4 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1973.6 | 128.7087 | 0.013753 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1973.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1974 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1974.2 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1974.4 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1974.6 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1974.8 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1975 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1975.2 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1975.4 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1975.6 | 128.7087 | 0.024949 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1975.8 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1976 | 128.5167 | 0.026549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1976.2 | 128.9006 | 0.034546 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1976.4 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.57213 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1976.6 | 127.9409 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1976.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
1977 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1977.2 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.57213 | 0.013089 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1977.4 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1977.6 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1977.8 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1978 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1978.2 | 128.6127 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1978.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1978.6 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1978.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1979 | 128.6127 | 0.013753 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1979.2 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1979.4 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
1979.6 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1979.8 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1980 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1980.2 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1980.4 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1980.6 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1980.8 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1981 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1981.2 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1981.4 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1981.6 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1981.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1982 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1982.2 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1982.4 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1982.6 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1982.8 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1983 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1983.2 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1983.4 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1983.6 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1983.8 | 128.6127 | 0.016952 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1984 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1984.2 | 128.7087 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
1984.4 | 128.7087 | 0.015352 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1984.6 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1984.8 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1985 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
1985.2 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1985.4 | 128.7087 | 0.016952 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1985.6 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1985.8 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1986 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1986.2 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1986.4 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1986.6 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1986.8 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1987 | 128.7087 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1987.2 | 128.8046 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1987.4 | 128.8046 | 0.018551 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1987.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1987.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1988 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1988.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1988.4 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1988.6 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.012867 | 0.28424 | 0.009912
1988.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.67705 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1989 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1989.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1989.4 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1989.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1989.8 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1990 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1990.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1990.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1990.6 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.38019 | 0.009912
1990.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1991 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1991.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1991.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1991.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1991.8 | 128.8046 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1992 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1992.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.011213 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1992.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1992.6 | 128.9006 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1992.8 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.57213 | 0.0083128
1993 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1993.2 | 128.9006 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1993.4 | 128.9006 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1993.6 | 128.8046 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1993.8 | 129.0925 | 0.032947 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.01149 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1994 | 128.9006 | 0.02335 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1994.2 | 128.4208 | 0.026549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1994.4 | 128.9006 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1994.6 | 129.1885 | 0.039345 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.66813 | 0.013089 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1994.8 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1995 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1995.2 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1995.4 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1995.6 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1995.8 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1996 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1996.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1996.4 | 128.9966 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.0080692 | 0.47618 | 0.0083128
1996.6 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1996.8 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1997 | 129.0925 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1997.2 | 128.9966 | 0.018551 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
1997.4 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1997.6 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1997.8 | 128.9966 | 0.018551 | 0.58176 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1998 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1998.2 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1998.4 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1998.6 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1998.8 | 129.2844 | 0.02175 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1999 | 129.7643 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1999.2 | 130.3401 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1999.4 | 130.0522 | 0.02175 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1999.6 | 129.3804 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1999.8 | 129.3804 | 0.018551 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2000 | 129.2844 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2000.2 | 129.2844 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2000.4 | 129.0925 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2000.6 | 129.0925 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2000.8 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2001 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2001.2 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2001.4 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2001.6 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2001.8 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2002 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2002.2 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
2002.4 | 129.0925 | 0.018551 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2002.6 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2002.8 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2003 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2003.2 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2003.4 | 128.9966 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2003.6 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2003.8 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2004 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2004.2 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2004.4 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2004.6 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2004.8 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2005 | 128.9966 | 0.016952 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2005.2 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2005.4 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2005.6 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2005.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2006 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2006.2 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2006.4 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2006.6 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2006.8 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
2007 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2007.2 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
2007.4 | 128.9006 | 0.015352 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2007.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2007.8 | 128.9966 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2008 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2008.2 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2008.4 | 128.9006 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
2008.6 | 129.0925 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2008.8 | 128.9006 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2009 | 128.6127 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2009.2 | 129.0925 | 0.044143 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2009.4 | 129.1885 | 0.045742 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2009.6 | 128.6127 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.014522 | 0.86003 | 0.01149 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2009.8 | 128.4208 | 0.034546 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.012923 | 0.66813 | 0.01149 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2010 | 129.2844 | 0.053739 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.016122 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2010.2 | 129.3804 | 0.031347 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.02092 | 0.76408 | 0.016288 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2010.4 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.011324 | 0.76408 | 0.017887 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2010.6 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.01149 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2010.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2011 | 128.7087 | 0.015352 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2011.2 | 128.6127 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.33406 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2011.4 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2011.6 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2011.8 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
2012 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2012.2 | 128.6127 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
2012.4 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2012.6 | 128.6127 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
2012.8 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2013 | 128.6127 | 0.016952 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
2013.2 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2013.4 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2013.6 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2013.8 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2014 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2014.2 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2014.4 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2014.6 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2014.8 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2015 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2015.2 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2015.4 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2015.6 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2015.8 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2016 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2016.2 | 128.6127 | 0.016952 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2016.4 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2016.6 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2016.8 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2017 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2017.2 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2017.4 | 128.6127 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2017.6 | 128.5167 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2017.8 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2018 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2018.2 | 128.5167 | 0.015352 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2018.4 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
2018.6 | 128.5167 | 0.018551 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2018.8 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2019 | 128.5167 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
2019.2 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2019.4 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2019.6 | 128.2288 | 0.013753 | 0.48581 | 0.0063808 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2019.8 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2020 | 128.3248 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2020.2 | 128.4208 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2020.4 | 128.3248 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2020.6 | 128.3248 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2020.8 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2021 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2021.2 | 128.3248 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2021.4 | 128.3248 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2021.6 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
2021.8 | 128.2288 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2022 | 128.3248 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2022.2 | 128.3248 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2022.4 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2022.6 | 128.2288 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2022.8 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2023 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2023.2 | 128.3248 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2023.4 | 128.4208 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
2023.6 | 128.4208 | 0.015352 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2023.8 | 128.4208 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2024 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2024.2 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2024.4 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2024.6 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2024.8 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2025 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2025.2 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2025.4 | 128.5167 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2025.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2025.8 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2026 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2026.2 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2026.4 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2026.6 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2026.8 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2027 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.18829 | 0.009912
2027.2 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2027.4 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
2027.6 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2027.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2028 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2028.2 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2028.4 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2028.6 | 128.5167 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2028.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2029 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2029.2 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2029.4 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2029.6 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2029.8 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2030 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2030.2 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2030.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2030.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2030.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2031 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
2031.2 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2031.4 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2031.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2031.8 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2032 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2032.2 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2032.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2032.6 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2032.8 | 128.3248 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2033 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
2033.2 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2033.4 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2033.6 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
2033.8 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2034 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2034.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2034.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2034.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2034.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2035 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2035.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2035.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2035.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2035.8 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2036 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2036.2 | 128.5167 | 0.013753 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
2036.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2036.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2036.8 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
2037 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.57213 | 0.0083128
2037.2 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2037.4 | 128.5167 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2037.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2037.8 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2038 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2038.2 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2038.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2038.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.006713
2038.8 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2039 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2039.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2039.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2039.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2039.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2040 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2040.2 | 128.4208 | 0.013753 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2040.4 | 128.4208 | 0.013753 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
2040.6 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2040.8 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2041 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2041.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2041.4 | 128.4208 | 0.013753 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2041.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2041.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.29321 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2042 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2042.2 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2042.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2042.6 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2042.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2043 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2043.2 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2043.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
2043.6 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2043.8 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2044 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2044.2 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2044.4 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2044.6 | 128.5167 | 0.013753 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2044.8 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.18829 | 0.009912
2045 | 128.4208 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.009912
2045.2 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2045.4 | 128.4208 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2045.6 | 128.4208 | 0.018551 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2045.8 | 128.5167 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2046 | 128.5167 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2046.2 | 128.1329 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2046.4 | 128.2288 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2046.6 | 128.3248 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2046.8 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2047 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2047.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.66813 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2047.4 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2047.6 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2047.8 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2048 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2048.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2048.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2048.6 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.012867 | 0.28424 | 0.009912
2048.8 | 128.5167 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2049 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2049.2 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2049.4 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2049.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2049.8 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2050 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2050.2 | 128.4208 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2050.4 | 128.5167 | 0.012154 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2050.6 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2050.8 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2051 | 128.3248 | 0.012154 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2051.2 | 128.5167 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
2051.4 | 128.5167 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2051.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2051.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2052 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2052.2 | 128.5167 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2052.4 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2052.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2052.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2053 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2053.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2053.4 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2053.6 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2053.8 | 128.5167 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2054 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2054.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2054.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2054.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2054.8 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2055 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2055.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.006713
2055.4 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2055.6 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2055.8 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2056 | 128.5167 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.006713
2056.2 | 128.4208 | 0.0089549 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
2056.4 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2056.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2056.8 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.28424 | 0.009912
2057 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2057.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2057.4 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2057.6 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2057.8 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2058 | 128.5167 | 0.010554 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2058.2 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2058.4 | 128.5167 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
2058.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2058.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2059 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2059.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2059.4 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
2059.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.009912
2059.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2060 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2060.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2060.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2060.6 | 128.6127 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2060.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2061 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2061.2 | 128.6127 | 0.010554 | 0.67775 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2061.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2061.6 | 128.7087 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2061.8 | 128.6127 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2062 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2062.2 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2062.4 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2062.6 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2062.8 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.76308 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2063 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2063.2 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2063.4 | 128.6127 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2063.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2063.8 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2064 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2064.2 | 128.8046 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
2064.4 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2064.6 | 128.7087 | 0.018551 | 0.48581 | 0.0063808 | 0.67705 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2064.8 | 128.8046 | 0.036146 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.01149 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2065 | 129.0925 | 0.040944 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2065.2 | 128.9966 | 0.034546 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.012923 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2065.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.012923 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2065.6 | 128.5167 | 0.010554 | 0.48581 | 0.01118 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2065.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2066 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
2066.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2066.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2066.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2066.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2067 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.0080692 | 0.38019 | 0.0083128
2067.2 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2067.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2067.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2067.8 | 128.7087 | 0.012154 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2068 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2068.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2068.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2068.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2068.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2069 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2069.2 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2069.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2069.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2069.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.011799 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2070 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2070.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
2070.4 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
2070.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2070.8 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2071 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2071.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2071.4 | 128.4208 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2071.6 | 128.3248 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2071.8 | 128.0369 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2072 | 127.557 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0049255 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2072.2 | 127.3651 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2072.4 | 127.4611 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
2072.6 | 127.9409 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2072.8 | 128.1329 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2073 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2073.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2073.4 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2073.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2073.8 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2074 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2074.2 | 128.5167 | 0.010554 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2074.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2074.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2074.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2075 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2075.2 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
2075.4 | 128.7087 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2075.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2075.8 | 128.8046 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2076 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2076.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
2076.4 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2076.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2076.8 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2077 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2077.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2077.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2077.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
2077.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2078 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
2078.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2078.4 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2078.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2078.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2079 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2079.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
2079.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2079.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2079.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2080 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2080.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2080.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2080.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2080.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
2081 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2081.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2081.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2081.6 | 128.6127 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
2081.8 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2082 | 128.6127 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2082.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
2082.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2082.6 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2082.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2083 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2083.2 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.011511
2083.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2083.6 | 128.6127 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2083.8 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2084 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2084.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2084.4 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2084.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2084.8 | 128.5167 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
2085 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2085.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2085.4 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2085.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2085.8 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2086 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2086.2 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2086.4 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
2086.6 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2086.8 | 128.4208 | 0.012154 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2087 | 128.5167 | 0.012154 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2087.2 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2087.4 | 128.5167 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2087.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2087.8 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2088 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2088.2 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2088.4 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2088.6 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
2088.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2089 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2089.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2089.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2089.6 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2089.8 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2090 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2090.2 | 128.5167 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
2090.4 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2090.6 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
2090.8 | 128.4208 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2091 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2091.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2091.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2091.6 | 128.4208 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2091.8 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2092 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2092.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2092.4 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2092.6 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2092.8 | 128.3248 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2093 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2093.2 | 128.2288 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2093.4 | 128.0369 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2093.6 | 128.0369 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2093.8 | 127.8449 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2094 | 127.557 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2094.2 | 127.653 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2094.4 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2094.6 | 127.653 | 0.012154 | 0.38986 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.011511
2094.8 | 127.557 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2095 | 128.0369 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2095.2 | 128.0369 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2095.4 | 128.0369 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2095.6 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2095.8 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2096 | 128.4208 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2096.2 | 128.5167 | 0.012154 | 0.58176 | 0.0047816 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2096.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2096.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2096.8 | 128.7087 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2097 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2097.2 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2097.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2097.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2097.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2098 | 128.7087 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2098.2 | 128.7087 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2098.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2098.6 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2098.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2099 | 128.7087 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2099.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2099.4 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2099.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2099.8 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2100 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2100.2 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2100.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.011511
2100.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2100.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2101 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2101.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.47618 | 0.009912
2101.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2101.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2101.8 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2102 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2102.2 | 128.6127 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2102.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2102.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2102.8 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.006713
2103 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2103.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2103.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2103.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
2103.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2104 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2104.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2104.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2104.6 | 128.6127 | 0.012154 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2104.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2105 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2105.2 | 128.6127 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2105.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2105.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2105.8 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
2106 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2106.2 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2106.4 | 128.6127 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
2106.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.38019 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2106.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2107 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
2107.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 1.1018 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2107.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2107.6 | 128.7087 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.01149 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2107.8 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2108 | 128.7087 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2108.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
2108.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2108.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2108.8 | 128.6127 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0070012 | 0.8139 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2109 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2109.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2109.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.01149 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2109.6 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2109.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2110 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2110.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2110.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2110.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2110.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.009613 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2111 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.012923 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.006713
2111.2 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2111.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2111.6 | 128.7087 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2111.8 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.76308 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2112 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2112.2 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2112.4 | 128.7087 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.38019 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2112.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2112.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2113 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2113.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2113.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2113.6 | 128.6127 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.01149 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2113.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.76308 | 0.0086004 | 0.8139 | 0.0065247 | 0.66813 | 0.01149 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2114 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2114.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2114.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.012923 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2114.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2114.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
2115 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
2115.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.012923 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2115.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2115.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.012812 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2115.8 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2116 | 128.6127 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.01149 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2116.2 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.012923 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2116.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2116.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
2116.8 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2117 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2117.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2117.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.86003 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2117.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2117.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.003271 | 0.38019 | 0.0083128
2118 | 128.6127 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
2118.2 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2118.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
2118.6 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2118.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2119 | 128.6127 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2119.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2119.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2119.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2119.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.28424 | 0.0083128
2120 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
2120.2 | 128.6127 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2120.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2120.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2120.8 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2121 | 128.6127 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2121.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2121.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2121.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2121.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2122 | 128.6127 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2122.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2122.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2122.6 | 128.7087 | 0.010554 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2122.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2123 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
2123.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2123.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2123.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2123.8 | 128.7087 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2124 | 128.7087 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2124.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2124.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2124.6 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2124.8 | 128.6127 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2125 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2125.2 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2125.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2125.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2125.8 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2126 | 128.0369 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2126.2 | 128.0369 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2126.4 | 127.749 | 0.010554 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2126.6 | 127.1732 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2126.8 | 127.2692 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2127 | 127.557 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2127.2 | 127.653 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2127.4 | 127.749 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2127.6 | 128.1329 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2127.8 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
2128 | 128.3248 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2128.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2128.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2128.6 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2128.8 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2129 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2129.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2129.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2129.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2129.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2130 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2130.2 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2130.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2130.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
2130.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2131 | 128.7087 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2131.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
2131.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2131.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2131.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2132 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2132.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2132.4 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2132.6 | 128.7087 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2132.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2133 | 128.8046 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2133.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2133.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2133.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2133.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2134 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2134.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2134.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2134.6 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2134.8 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2135 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2135.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2135.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2135.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2135.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2136 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.47618 | 0.009912
2136.2 | 128.6127 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2136.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2136.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2136.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2137 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2137.2 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2137.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2137.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2137.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2138 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2138.2 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2138.4 | 128.8046 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2138.6 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2138.8 | 128.9006 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2139 | 128.5167 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2139.2 | 128.6127 | 0.047342 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2139.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.017721 | 0.76408 | 0.014688 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2139.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.67705 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.014522 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2139.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.017721 | 0.86003 | 0.017887 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2140 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2140.2 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2140.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2140.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2140.8 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2141 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2141.2 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2141.4 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2141.6 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.009912
2141.8 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2142 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2142.2 | 128.5167 | 0.012154 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2142.4 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2142.6 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2142.8 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2143 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2143.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2143.4 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2143.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2143.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2144 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2144.2 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2144.4 | 128.5167 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2144.6 | 128.5167 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2144.8 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2145 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2145.2 | 128.4208 | 0.012154 | 0.48581 | 0.01118 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.86003 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2145.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2145.6 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2145.8 | 128.4208 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2146 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2146.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2146.4 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2146.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2146.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2147 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2147.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2147.4 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.67705 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2147.6 | 128.5167 | 0.012154 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2147.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2148 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2148.2 | 128.5167 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2148.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2148.6 | 128.5167 | 0.013753 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2148.8 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2149 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2149.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2149.4 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2149.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2149.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
2150 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2150.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2150.4 | 128.5167 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2150.6 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2150.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2151 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2151.2 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2151.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2151.6 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2151.8 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2152 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2152.2 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2152.4 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2152.6 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2152.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2153 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2153.2 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2153.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2153.6 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2153.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2154 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2154.2 | 128.5167 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2154.4 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2154.6 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2154.8 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2155 | 128.4208 | 0.016952 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2155.2 | 128.4208 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2155.4 | 128.6127 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2155.6 | 128.5167 | 0.02175 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2155.8 | 128.6127 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2156 | 128.6127 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2156.2 | 128.4208 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2156.4 | 128.6127 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.01149 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2156.6 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.0083128
2156.8 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2157 | 128.5167 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2157.2 | 128.6127 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2157.4 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2157.6 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2157.8 | 128.6127 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2158 | 128.7087 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2158.2 | 128.6127 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2158.4 | 128.6127 | 0.02175 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2158.6 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2158.8 | 128.5167 | 0.020151 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2159 | 128.5167 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2159.2 | 128.4208 | 0.018551 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2159.4 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2159.6 | 128.6127 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2159.8 | 128.6127 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2160 | 128.5167 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2160.2 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2160.4 | 128.3248 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2160.6 | 128.4208 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2160.8 | 128.3248 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2161 | 128.4208 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2161.2 | 128.4208 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2161.4 | 128.4208 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.28424 | 0.009912
2161.6 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2161.8 | 128.6127 | 0.02175 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2162 | 128.6127 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
2162.2 | 128.6127 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2162.4 | 128.7087 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2162.6 | 128.5167 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2162.8 | 128.5167 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0102 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2163 | 128.6127 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2163.2 | 128.6127 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2163.4 | 128.6127 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2163.6 | 128.6127 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2163.8 | 128.6127 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2164 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2164.2 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2164.4 | 128.5167 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2164.6 | 128.6127 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2164.8 | 128.6127 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2165 | 128.6127 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2165.2 | 128.6127 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2165.4 | 128.7087 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2165.6 | 128.5167 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2165.8 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2166 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2166.2 | 128.5167 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2166.4 | 128.4208 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2166.6 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2166.8 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.0083128
2167 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.009669 | 0.38019 | 0.009912
2167.2 | 128.5167 | 0.015352 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2167.4 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2167.6 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.006713
2167.8 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2168 | 128.5167 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2168.2 | 128.5167 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2168.4 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2168.6 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2168.8 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2169 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2169.2 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2169.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2169.6 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2169.8 | 128.5167 | 0.013753 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2170 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2170.2 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2170.4 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2170.6 | 128.5167 | 0.013753 | 0.58176 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2170.8 | 128.5167 | 0.013753 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2171 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2171.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2171.4 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2171.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2171.8 | 128.5167 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2172 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2172.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2172.4 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.006713
2172.6 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2172.8 | 128.5167 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2173 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2173.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2173.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2173.6 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.76308 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2173.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2174 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2174.2 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2174.4 | 128.5167 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2174.6 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2174.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2175 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2175.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2175.4 | 128.6127 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2175.6 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.013111
2175.8 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2176 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2176.2 | 128.2288 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2176.4 | 128.3248 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2176.6 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2176.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2177 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2177.2 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2177.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2177.6 | 128.3248 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2177.8 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.57213 | 0.009912
2178 | 128.3248 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2178.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.76308 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2178.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2178.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2178.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2179 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2179.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2179.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2179.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2179.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2180 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2180.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2180.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2180.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2180.8 | 128.7087 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2181 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2181.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2181.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2181.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2181.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2182 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2182.2 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2182.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2182.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.0083128
2182.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0102 | 0.8139 | 0.02092 | 0.76408 | 0.016288 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2183 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.014522 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2183.2 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.016288 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2183.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.02092 | 0.86003 | 0.016288 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2183.6 | 129.2844 | 0.060137 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.016122 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2183.8 | 128.4208 | 0.044143 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2184 | 128.2288 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.012923 | 0.76408 | 0.013089 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2184.2 | 128.8046 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2184.4 | 128.8046 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.011511
2184.6 | 128.4208 | 0.024949 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2184.8 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2185 | 128.7087 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2185.2 | 128.7087 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2185.4 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2185.6 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2185.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2186 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2186.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2186.4 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2186.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.011511
2186.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2187 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2187.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2187.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2187.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2187.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2188 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2188.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2188.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.0083128
2188.6 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2188.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2189 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2189.2 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2189.4 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2189.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2189.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2190 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2190.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2190.4 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2190.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2190.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2191 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2191.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2191.4 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2191.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2191.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2192 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2192.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2192.4 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2192.6 | 128.9006 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2192.8 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2193 | 128.9006 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2193.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2193.4 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2193.6 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2193.8 | 128.9006 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2194 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2194.2 | 127.653 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2194.4 | 127.4611 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2194.6 | 128.0369 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2194.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2195 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2195.2 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2195.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2195.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2195.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2196 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2196.2 | 128.9006 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2196.4 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2196.6 | 128.8046 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2196.8 | 128.9006 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2197 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2197.2 | 128.7087 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2197.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2197.6 | 128.9006 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2197.8 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2198 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2198.2 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2198.4 | 128.8046 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2198.6 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2198.8 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2199 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2199.2 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.57213 | 0.0083128
2199.4 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2199.6 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2199.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2200 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2200.2 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2200.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.86003 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2200.6 | 128.8046 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2200.8 | 128.7087 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2201 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2201.2 | 128.8046 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2201.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2201.6 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2201.8 | 128.8046 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2202 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2202.2 | 128.8046 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2202.4 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2202.6 | 128.8046 | 0.018551 | 0.58176 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2202.8 | 128.5167 | 0.026549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2203 | 128.7087 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2203.2 | 128.9006 | 0.034546 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2203.4 | 128.6127 | 0.042543 | 0.38986 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2203.6 | 129.4764 | 0.064936 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.014522 | 0.76408 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2203.8 | 128.9966 | 0.034546 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.019321 | 0.76408 | 0.01149 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2204 | 128.7087 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.017721 | 0.95602 | 0.017887 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2204.2 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.016122 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2204.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.8139 | 0.02092 | 0.76408 | 0.013089 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2204.6 | 128.7087 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.86003 | 0.016288 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2204.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.47618 | 0.0083128
2205 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2205.2 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2205.4 | 128.8046 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2205.6 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2205.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2206 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2206.2 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2206.4 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.013111
2206.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2206.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2207 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2207.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2207.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2207.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2207.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2208 | 128.7087 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2208.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2208.4 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2208.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2208.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2209 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2209.2 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2209.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2209.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2209.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2210 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2210.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2210.4 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2210.6 | 128.6127 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2210.8 | 128.6127 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.86003 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2211 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2211.2 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2211.4 | 128.5167 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2211.6 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2211.8 | 128.6127 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2212 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2212.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.011213 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2212.4 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2212.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2212.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2213 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2213.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2213.4 | 128.6127 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
2213.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2213.8 | 128.5167 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2214 | 128.4208 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2214.2 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2214.4 | 128.4208 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2214.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2214.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2215 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2215.2 | 128.5167 | 0.012154 | 0.58176 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2215.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2215.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2215.8 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2216 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2216.2 | 128.5167 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2216.4 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2216.6 | 128.4208 | 0.013753 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2216.8 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2217 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2217.2 | 128.4208 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2217.4 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2217.6 | 128.4208 | 0.013753 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2217.8 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2218 | 128.4208 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2218.2 | 128.3248 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0082906 | 0.5818 | 0.0080692 | 0.47618 | 0.009912
2218.4 | 128.5167 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.011799 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2218.6 | 128.6127 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2218.8 | 128.1329 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.01149 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2219 | 128.4208 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2219.2 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2219.4 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2219.6 | 128.4208 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2219.8 | 128.4208 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2220 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2220.2 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2220.4 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2220.6 | 128.5167 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2220.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2221 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
2221.2 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2221.4 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2221.6 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2221.8 | 128.5167 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2222 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2222.2 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.7737 | 0.009669 | 0.38019 | 0.0083128
2222.4 | 128.6127 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2222.6 | 128.5167 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.011511
2222.8 | 128.6127 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2223 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2223.2 | 128.5167 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2223.4 | 128.6127 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2223.6 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2223.8 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2224 | 128.5167 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2224.2 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2224.4 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2224.6 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2224.8 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2225 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2225.2 | 128.7087 | 0.016952 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2225.4 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2225.6 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2225.8 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
2226 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2226.2 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2226.4 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2226.6 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2226.8 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.014467 | 0.38019 | 0.009912
2227 | 128.7087 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2227.2 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2227.4 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2227.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.66813 | 0.009912
2227.8 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.009669 | 0.38019 | 0.009912
2228 | 128.6127 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2228.2 | 129.0925 | 0.036146 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2228.4 | 128.3248 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.95602 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2228.6 | 128.9006 | 0.045742 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2228.8 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2229 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2229.2 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2229.4 | 128.8046 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2229.6 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2229.8 | 128.9006 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2230 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2230.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2230.4 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2230.6 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2230.8 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2231 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2231.2 | 129.2844 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2231.4 | 129.9562 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2231.6 | 129.5724 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2231.8 | 129.1885 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2232 | 129.1885 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2232.2 | 129.0925 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2232.4 | 128.9966 | 0.018551 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2232.6 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2232.8 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2233 | 128.9006 | 0.020151 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2233.2 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2233.4 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2233.6 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2233.8 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2234 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2234.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2234.4 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2234.6 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2234.8 | 128.9006 | 0.018551 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2235 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2235.2 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.011511
2235.4 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2235.6 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2235.8 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.47618 | 0.009912
2236 | 128.9006 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2236.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2236.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2236.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2236.8 | 128.9006 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2237 | 128.9966 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2237.2 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2237.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2237.6 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2237.8 | 128.9006 | 0.018551 | 0.48581 | 0.0095798 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.006713
2238 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2238.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2238.4 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.011213 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2238.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2238.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2239 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2239.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2239.4 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.47618 | 0.0083128
2239.6 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2239.8 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2240 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2240.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2240.4 | 128.9966 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2240.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2240.8 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2241 | 128.7087 | 0.016952 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2241.2 | 128.9006 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2241.4 | 128.9006 | 0.026549 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2241.6 | 128.6127 | 0.02335 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2241.8 | 128.6127 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2242 | 128.7087 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2242.2 | 128.9966 | 0.040944 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
2242.4 | 129.0925 | 0.036146 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.014522 | 0.76408 | 0.01149 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2242.6 | 128.2288 | 0.026549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.013089 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2242.8 | 128.3248 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.76408 | 0.013089 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2243 | 129.1885 | 0.055339 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.016122 | 0.76408 | 0.013089 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2243.2 | 129.2844 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.019321 | 0.76408 | 0.016288 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2243.4 | 128.7087 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.8139 | 0.014522 | 0.76408 | 0.017887 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2243.6 | 128.8046 | 0.028148 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.016122 | 0.86003 | 0.019487 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2243.8 | 128.7087 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2244 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0048148 | 0.37923 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2244.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2244.4 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2244.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2244.8 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2245 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.67775 | 0.00647 | 0.38019 | 0.009912
2245.2 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2245.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2245.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | -0.099642 | 0.0083128
2245.8 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2246 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2246.2 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
2246.4 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2246.6 | 128.7087 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.57213 | 0.0083128
2246.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2247 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2247.2 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2247.4 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2247.6 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2247.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2248 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2248.2 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2248.4 | 128.8046 | 0.016952 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2248.6 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2248.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2249 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2249.2 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2249.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2249.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2249.8 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2250 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2250.2 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2250.4 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2250.6 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.006713
2250.8 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2251 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2251.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2251.4 | 128.8046 | 0.016952 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2251.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2251.8 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2252 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2252.2 | 128.7087 | 0.016952 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2252.4 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2252.6 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2252.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2253 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
2253.2 | 128.7087 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.009669 | 0.28424 | 0.009912
2253.4 | 128.7087 | 0.016952 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2253.6 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2253.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
2254 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.28424 | 0.0083128
2254.2 | 128.7087 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2254.4 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2254.6 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2254.8 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2255 | 128.7087 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2255.2 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2255.4 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2255.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
2255.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2256 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2256.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
2256.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2256.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2256.8 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2257 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.014688 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2257.2 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.019487 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2257.4 | 128.8046 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.016122 | 0.86003 | 0.019487 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2257.6 | 129.3804 | 0.056938 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.022519 | 0.76408 | 0.013089 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2257.8 | 128.7087 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2258 | 128.4208 | 0.034546 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2258.2 | 128.1329 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.66813 | 0.013089 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2258.4 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.014522 | 0.76408 | 0.013089 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2258.6 | 128.9006 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.016122 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2258.8 | 129.0925 | 0.047342 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.012923 | 0.66813 | 0.01149 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2259 | 129.0925 | 0.047342 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2259.2 | 128.9006 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.009912
2259.4 | 128.6127 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2259.6 | 128.7087 | 0.02335 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2259.8 | 128.9006 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2260 | 128.8046 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2260.2 | 128.9966 | 0.026549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2260.4 | 128.9006 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2260.6 | 128.9006 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2260.8 | 128.7087 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2261 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2261.2 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2261.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2261.6 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2261.8 | 128.9006 | 0.020151 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2262 | 128.9006 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.86003 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2262.2 | 128.9006 | 0.020151 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2262.4 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2262.6 | 128.8046 | 0.020151 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2262.8 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2263 | 128.7087 | 0.015352 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2263.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2263.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2263.6 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2263.8 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2264 | 128.9006 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2264.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2264.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2264.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2264.8 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2265 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2265.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2265.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2265.6 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2265.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2266 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2266.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2266.4 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2266.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2266.8 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2267 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2267.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2267.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2267.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2267.8 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2268 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2268.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2268.4 | 128.9966 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2268.6 | 129.0925 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2268.8 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.57213 | 0.0083128
2269 | 128.9966 | 0.018551 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2269.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2269.4 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2269.6 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2269.8 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2270 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2270.2 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2270.4 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2270.6 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2270.8 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2271 | 129.0925 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2271.2 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2271.4 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2271.6 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2271.8 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.76308 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2272 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2272.2 | 128.9006 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2272.4 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2272.6 | 129.0925 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2272.8 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2273 | 129.0925 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2273.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2273.4 | 128.9966 | 0.018551 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2273.6 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2273.8 | 129.0925 | 0.018551 | 0.58176 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2274 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2274.2 | 128.9966 | 0.020151 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2274.4 | 129.0925 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2274.6 | 129.0925 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2274.8 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2275 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2275.2 | 129.2844 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2275.4 | 129.2844 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.86003 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2275.6 | 129.2844 | 0.018551 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2275.8 | 129.2844 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2276 | 129.2844 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2276.2 | 129.5724 | 0.020151 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2276.4 | 129.6683 | 0.02175 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2276.6 | 130.0522 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2276.8 | 130.3401 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2277 | 129.7643 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2277.2 | 129.3804 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2277.4 | 129.1885 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2277.6 | 129.0925 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2277.8 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2278 | 129.0925 | 0.020151 | 0.58176 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2278.2 | 129.0925 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.011511
2278.4 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2278.6 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2278.8 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2279 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2279.2 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2279.4 | 128.9966 | 0.018551 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2279.6 | 128.9006 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2279.8 | 128.9006 | 0.018551 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2280 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.57213 | 0.009912
2280.2 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2280.4 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2280.6 | 128.9966 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2280.8 | 128.9966 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2281 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2281.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2281.4 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2281.6 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2281.8 | 128.9006 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 1.1576 | 0.009669 | 0.47618 | 0.009912
2282 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2282.2 | 128.9006 | 0.018551 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2282.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2282.6 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2282.8 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.37923 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2283 | 128.9006 | 0.018551 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2283.2 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.76408 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2283.4 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.016288 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2283.6 | 128.8046 | 0.028148 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.013089 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2283.8 | 129.1885 | 0.042543 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.014522 | 0.66813 | 0.013089 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2284 | 129.2844 | 0.048941 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.014522 | 0.76408 | 0.013089 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2284.2 | 129.1885 | 0.05054 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.014522 | 0.66813 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2284.4 | 128.9966 | 0.042543 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.011324 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2284.6 | 128.9966 | 0.040944 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2284.8 | 128.7087 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2285 | 128.9006 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2285.2 | 128.5167 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0102 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2285.4 | 128.5167 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.011324 | 0.76408 | 0.01149 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2285.6 | 128.6127 | 0.032947 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2285.8 | 128.6127 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2286 | 128.5167 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2286.2 | 128.4208 | 0.026549 | 0.48581 | 0.0079807 | 0.67705 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.86003 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2286.4 | 128.6127 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2286.6 | 128.5167 | 0.031347 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2286.8 | 128.8046 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2287 | 129.0925 | 0.039345 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2287.2 | 129.0925 | 0.047342 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2287.4 | 128.9006 | 0.042543 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2287.6 | 128.8046 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2287.8 | 128.8046 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2288 | 128.8046 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2288.2 | 129.0925 | 0.042543 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2288.4 | 128.8046 | 0.032947 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2288.6 | 128.5167 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2288.8 | 128.5167 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2289 | 128.5167 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.01149 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2289.2 | 128.7087 | 0.02175 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2289.4 | 128.9966 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2289.6 | 129.1885 | 0.026549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2289.8 | 129.1885 | 0.032947 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.57213 | 0.0098898 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2290 | 129.1885 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2290.2 | 129.0925 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2290.4 | 128.9006 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2290.6 | 128.8046 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2290.8 | 128.8046 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2291 | 128.7087 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2291.2 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2291.4 | 128.8046 | 0.02335 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2291.6 | 128.7087 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2291.8 | 128.9006 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2292 | 128.7087 | 0.02175 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2292.2 | 128.8046 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2292.4 | 128.7087 | 0.02175 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2292.6 | 128.8046 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2292.8 | 128.8046 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2293 | 128.8046 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2293.2 | 128.8046 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2293.4 | 128.8046 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.57213 | 0.009912
2293.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2293.8 | 128.9006 | 0.018551 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2294 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2294.2 | 128.7087 | 0.02175 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2294.4 | 128.9006 | 0.016952 | 0.67775 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2294.6 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2294.8 | 128.9006 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2295 | 128.9966 | 0.016952 | 0.38986 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2295.2 | 128.9006 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2295.4 | 128.9966 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2295.6 | 128.9966 | 0.020151 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2295.8 | 128.9966 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2296 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2296.2 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2296.4 | 128.9006 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2296.6 | 128.9006 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2296.8 | 128.9966 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2297 | 128.9966 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2297.2 | 128.9966 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2297.4 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2297.6 | 129.0925 | 0.02175 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2297.8 | 128.9966 | 0.02335 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2298 | 129.0925 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2298.2 | 129.0925 | 0.020151 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
2298.4 | 128.9966 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2298.6 | 128.9966 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2298.8 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2299 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2299.2 | 128.9966 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2299.4 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2299.6 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2299.8 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2300 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2300.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2300.4 | 128.9966 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2300.6 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2300.8 | 129.0925 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2301 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2301.2 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.014467 | 0.47618 | 0.0083128
2301.4 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2301.6 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2301.8 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2302 | 128.9006 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2302.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2302.4 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2302.6 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.011799 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.014467 | 0.38019 | 0.009912
2302.8 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2303 | 128.9006 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2303.2 | 128.9966 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2303.4 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2303.6 | 128.9006 | 0.016952 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2303.8 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2304 | 128.9006 | 0.018551 | 0.38986 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2304.2 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2304.4 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2304.6 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2304.8 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2305 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2305.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2305.4 | 128.9006 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2305.6 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2305.8 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0049255 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.006713
2306 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2306.2 | 128.8046 | 0.020151 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2306.4 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2306.6 | 128.9006 | 0.016952 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2306.8 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2307 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2307.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2307.4 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2307.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2307.8 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.011799 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2308 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2308.2 | 128.9006 | 0.016952 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2308.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.006713
2308.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2308.8 | 128.9006 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2309 | 128.8046 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2309.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2309.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2309.6 | 128.9006 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2309.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2310 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2310.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2310.4 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2310.6 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2310.8 | 128.8046 | 0.016952 | 0.58176 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2311 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2311.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2311.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2311.6 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2311.8 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2312 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2312.2 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.47618 | 0.009912
2312.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2312.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2312.8 | 128.9006 | 0.016952 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2313 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2313.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2313.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2313.6 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2313.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2314 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2314.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2314.4 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2314.6 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2314.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2315 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2315.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2315.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2315.6 | 128.9006 | 0.02175 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2315.8 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2316 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2316.2 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2316.4 | 128.9966 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2316.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.01149 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2316.8 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2317 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2317.2 | 128.9966 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2317.4 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2317.6 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2317.8 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2318 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2318.2 | 128.9006 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2318.4 | 128.9006 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2318.6 | 128.9966 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2318.8 | 128.9966 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2319 | 128.8046 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2319.2 | 128.9006 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2319.4 | 128.9966 | 0.02335 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2319.6 | 128.9966 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2319.8 | 128.9966 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2320 | 128.9966 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.011799 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2320.2 | 128.9966 | 0.024949 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2320.4 | 128.9966 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2320.6 | 128.9966 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2320.8 | 129.0925 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.7737 | 0.009669 | 0.38019 | 0.009912
2321 | 128.9966 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2321.2 | 128.9006 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2321.4 | 128.9966 | 0.02335 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2321.6 | 128.9966 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2321.8 | 128.9966 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2322 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2322.2 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2322.4 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2322.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2322.8 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2323 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2323.2 | 128.9006 | 0.015352 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2323.4 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2323.6 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2323.8 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2324 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2324.2 | 128.9006 | 0.013753 | 0.38986 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2324.4 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
2324.6 | 128.9966 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2324.8 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2325 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2325.2 | 129.0925 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2325.4 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2325.6 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2325.8 | 128.9966 | 0.018551 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2326 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2326.2 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2326.4 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2326.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.011799 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2326.8 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2327 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2327.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2327.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.86003 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2327.6 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2327.8 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2328 | 128.9966 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2328.2 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2328.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2328.6 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2328.8 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2329 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2329.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2329.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2329.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2329.8 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2330 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2330.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2330.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2330.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2330.8 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2331 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2331.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2331.4 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2331.6 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.86003 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2331.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2332 | 128.8046 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2332.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2332.4 | 128.8046 | 0.018551 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2332.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2332.8 | 128.9966 | 0.016952 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2333 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2333.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.011511
2333.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2333.6 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2333.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2334 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2334.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2334.4 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2334.6 | 128.8046 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2334.8 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2335 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2335.2 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2335.4 | 128.8046 | 0.018551 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2335.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2335.8 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2336 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2336.2 | 128.8046 | 0.018551 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2336.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.011511
2336.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2336.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2337 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.011511
2337.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2337.4 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2337.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2337.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2338 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2338.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2338.4 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2338.6 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2338.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2339 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2339.2 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2339.4 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2339.6 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2339.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2340 | 128.9006 | 0.016952 | 0.58176 | 0.0079807 | 0.67705 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2340.2 | 128.8046 | 0.015352 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2340.4 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2340.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2340.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2341 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2341.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2341.4 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2341.6 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2341.8 | 128.7087 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2342 | 128.8046 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2342.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2342.4 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2342.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2342.8 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2343 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2343.2 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2343.4 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2343.6 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2343.8 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2344 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2344.2 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2344.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2344.6 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2344.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2345 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2345.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2345.4 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2345.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2345.8 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2346 | 128.8046 | 0.016952 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2346.2 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2346.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2346.6 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2346.8 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2347 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2347.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2347.4 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2347.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2347.8 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2348 | 128.9006 | 0.016952 | 0.38986 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2348.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2348.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2348.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2348.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2349 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2349.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2349.4 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2349.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2349.8 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2350 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2350.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2350.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2350.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2350.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2351 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2351.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2351.4 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2351.6 | 128.8046 | 0.015352 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2351.8 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2352 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2352.2 | 128.9006 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2352.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2352.6 | 128.8046 | 0.016952 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2352.8 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2353 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2353.2 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2353.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.011213 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2353.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2353.8 | 128.8046 | 0.016952 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2354 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2354.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2354.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2354.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2354.8 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2355 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2355.2 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2355.4 | 128.8046 | 0.016952 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2355.6 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2355.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2356 | 128.9006 | 0.016952 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2356.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2356.4 | 128.7087 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.013111
2356.6 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2356.8 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2357 | 128.9006 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.014467 | 0.38019 | 0.009912
2357.2 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2357.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2357.6 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2357.8 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2358 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.86969 | 0.011268 | 0.47618 | 0.0083128
2358.2 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2358.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2358.6 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2358.8 | 128.9006 | 0.016952 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2359 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2359.2 | 128.8046 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2359.4 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2359.6 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2359.8 | 128.8046 | 0.018551 | 0.58176 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2360 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2360.2 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2360.4 | 128.8046 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2360.6 | 128.9006 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2360.8 | 128.8046 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2361 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2361.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2361.4 | 128.9006 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.011213 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2361.6 | 128.8046 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2361.8 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2362 | 128.8046 | 0.016952 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.011324 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2362.2 | 128.9966 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2362.4 | 128.9006 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2362.6 | 128.9966 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2362.8 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2363 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2363.2 | 128.8046 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2363.4 | 129.0925 | 0.036146 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2363.6 | 128.9006 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.57213 | 0.009912
2363.8 | 128.6127 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.012923 | 0.76408 | 0.01149 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2364 | 128.8046 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.011324 | 0.86003 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2364.2 | 129.0925 | 0.045742 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2364.4 | 129.1885 | 0.048941 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2364.6 | 129.2844 | 0.044143 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.016122 | 0.76408 | 0.013089 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2364.8 | 128.9006 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.014688 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2365 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2365.2 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2365.4 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2365.6 | 128.8046 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0098898 | 0.48581 | 0.012867 | 0.38019 | 0.009912
2365.8 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.1018 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2366 | 128.9006 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2366.2 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2366.4 | 128.9006 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2366.6 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2366.8 | 128.9966 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2367 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2367.2 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2367.4 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2367.6 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2367.8 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2368 | 128.9006 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2368.2 | 128.9006 | 0.020151 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2368.4 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2368.6 | 129.0925 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2368.8 | 128.9006 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2369 | 128.9966 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.7737 | 0.009669 | 0.38019 | 0.009912
2369.2 | 128.9966 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2369.4 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2369.6 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2369.8 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2370 | 128.9966 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2370.2 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2370.4 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2370.6 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.013111
2370.8 | 128.9966 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2371 | 129.0925 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2371.2 | 129.1885 | 0.020151 | 0.48581 | 0.0063808 | 0.67705 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.86003 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2371.4 | 129.1885 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2371.6 | 129.3804 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2371.8 | 129.6683 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2372 | 130.0522 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2372.2 | 130.4361 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.006713
2372.4 | 130.0522 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2372.6 | 129.8603 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2372.8 | 129.6683 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2373 | 129.2844 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2373.2 | 129.3804 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2373.4 | 129.2844 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2373.6 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2373.8 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2374 | 128.8046 | 0.018551 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2374.2 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2374.4 | 128.7087 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2374.6 | 128.7087 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2374.8 | 128.7087 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2375 | 128.7087 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2375.2 | 128.8046 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2375.4 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2375.6 | 128.7087 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2375.8 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2376 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2376.2 | 128.9006 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2376.4 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2376.6 | 128.9006 | 0.020151 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2376.8 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2377 | 128.9006 | 0.018551 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.57213 | 0.009912
2377.2 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2377.4 | 128.8046 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2377.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2377.8 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2378 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2378.2 | 128.6127 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2378.4 | 128.5167 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2378.6 | 128.5167 | 0.020151 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2378.8 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2379 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2379.2 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2379.4 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2379.6 | 128.5167 | 0.018551 | 0.48581 | 0.0063808 | 0.67705 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2379.8 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2380 | 128.5167 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2380.2 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2380.4 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2380.6 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2380.8 | 128.6127 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2381 | 128.7087 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2381.2 | 128.5167 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2381.4 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2381.6 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.86969 | 0.011268 | 0.38019 | 0.009912
2381.8 | 128.6127 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2382 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2382.2 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2382.4 | 128.4208 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.0083128
2382.6 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2382.8 | 128.5167 | 0.018551 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2383 | 128.4208 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2383.2 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2383.4 | 128.6127 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2383.6 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2383.8 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2384 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2384.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2384.4 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2384.6 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2384.8 | 128.7087 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2385 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2385.2 | 128.8046 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2385.4 | 128.8046 | 0.016952 | 0.58176 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2385.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2385.8 | 128.8046 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2386 | 128.8046 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2386.2 | 128.9006 | 0.024949 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.012923 | 0.66813 | 0.0098898 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2386.4 | 128.9966 | 0.05054 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2386.6 | 128.6127 | 0.05214 | 0.38986 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.017721 | 0.66813 | 0.013089 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2386.8 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2387 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2387.2 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2387.4 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
2387.6 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2387.8 | 128.6127 | 0.015352 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.18829 | 0.009912
2388 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2388.2 | 128.5167 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
2388.4 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2388.6 | 128.5167 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2388.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2389 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2389.2 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.0083128
2389.4 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2389.6 | 128.6127 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2389.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2390 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2390.2 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2390.4 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2390.6 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2390.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.76308 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2391 | 128.4208 | 0.013753 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2391.2 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2391.4 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2391.6 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2391.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2392 | 128.4208 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2392.2 | 128.3248 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2392.4 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.011799 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.014467 | 0.38019 | 0.009912
2392.6 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2392.8 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2393 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2393.2 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2393.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2393.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2393.8 | 128.4208 | 0.013753 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2394 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2394.2 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2394.4 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2394.6 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2394.8 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2395 | 128.4208 | 0.013753 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2395.2 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2395.4 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2395.6 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2395.8 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2396 | 128.5167 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2396.2 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2396.4 | 128.4208 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2396.6 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.01149 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2396.8 | 128.4208 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2397 | 128.8046 | 0.020151 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2397.2 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2397.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2397.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.01149 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2397.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2398 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
2398.2 | 128.3248 | 0.010554 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2398.4 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.47618 | 0.0083128
2398.6 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2398.8 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2399 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.57213 | 0.009912
2399.2 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2399.4 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2399.6 | 128.3248 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2399.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2400 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2400.2 | 128.3248 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2400.4 | 128.3248 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2400.6 | 128.3248 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2400.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2401 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
2401.2 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2401.4 | 128.3248 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2401.6 | 128.3248 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2401.8 | 128.2288 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2402 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2402.2 | 128.2288 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2402.4 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2402.6 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2402.8 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2403 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2403.2 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2403.4 | 128.2288 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2403.6 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2403.8 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2404 | 128.3248 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2404.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.47618 | 0.009912
2404.4 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2404.6 | 128.2288 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2404.8 | 128.2288 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2405 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2405.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2405.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2405.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2405.8 | 128.4208 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2406 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2406.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2406.4 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2406.6 | 128.3248 | 0.010554 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2406.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2407 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2407.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2407.4 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2407.6 | 128.4208 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2407.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2408 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2408.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2408.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2408.6 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2408.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2409 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2409.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2409.4 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2409.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2409.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2410 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2410.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2410.4 | 128.3248 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2410.6 | 128.4208 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2410.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2411 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2411.2 | 128.4208 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2411.4 | 128.3248 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2411.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2411.8 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2412 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2412.2 | 128.5167 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.76308 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2412.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2412.6 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2412.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2413 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2413.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2413.4 | 128.4208 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2413.6 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2413.8 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2414 | 128.4208 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.011511
2414.2 | 128.5167 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2414.4 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2414.6 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2414.8 | 128.6127 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2415 | 128.5167 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2415.2 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2415.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2415.6 | 128.5167 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2415.8 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2416 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.011799 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2416.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2416.4 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2416.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2416.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2417 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2417.2 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2417.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2417.6 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2417.8 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2418 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2418.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.011799 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2418.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2418.6 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2418.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2419 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2419.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2419.4 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2419.6 | 128.5167 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2419.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.009669 | 0.38019 | 0.009912
2420 | 128.3248 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2420.2 | 128.4208 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2420.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2420.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2420.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2421 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2421.2 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2421.4 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2421.6 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2421.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2422 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.86003 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2422.2 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
2422.4 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.009669 | 0.38019 | 0.009912
2422.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2422.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2423 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2423.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2423.4 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2423.6 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2423.8 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2424 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2424.2 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2424.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2424.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2424.8 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.011799 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.0083128
2425 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2425.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2425.4 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2425.6 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2425.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.011799 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2426 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2426.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2426.4 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2426.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2426.8 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2427 | 128.5167 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2427.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2427.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2427.6 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2427.8 | 128.4208 | 0.010554 | 0.38986 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2428 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.0083128
2428.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2428.4 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2428.6 | 128.4208 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2428.8 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2429 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2429.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2429.4 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2429.6 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
2429.8 | 128.4208 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2430 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2430.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2430.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2430.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2430.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2431 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2431.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2431.4 | 128.4208 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2431.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2431.8 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.57213 | 0.0083128
2432 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2432.2 | 128.3248 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2432.4 | 128.4208 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2432.6 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2432.8 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2433 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2433.2 | 128.4208 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2433.4 | 128.5167 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2433.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2433.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2434 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2434.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2434.4 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2434.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2434.8 | 128.5167 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2435 | 128.4208 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2435.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.76308 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2435.4 | 128.4208 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2435.6 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2435.8 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2436 | 128.4208 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2436.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2436.4 | 128.4208 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2436.6 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2436.8 | 128.4208 | 0.012154 | 0.48581 | 0.0095798 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2437 | 128.5167 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.011511
2437.2 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2437.4 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2437.6 | 128.4208 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2437.8 | 128.3248 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2438 | 128.3248 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2438.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2438.4 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2438.6 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2438.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2439 | 128.4208 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.76308 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2439.2 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.47618 | 0.009912
2439.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2439.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2439.8 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2440 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2440.2 | 128.5167 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2440.4 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
2440.6 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2440.8 | 128.5167 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.011511
2441 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2441.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2441.4 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2441.6 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2441.8 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2442 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2442.2 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2442.4 | 128.4208 | 0.012154 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2442.6 | 128.4208 | 0.012154 | 0.67775 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2442.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2443 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2443.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2443.4 | 128.4208 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2443.6 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2443.8 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2444 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2444.2 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2444.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2444.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2444.8 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2445 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2445.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2445.4 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2445.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2445.8 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2446 | 128.4208 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2446.2 | 128.4208 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2446.4 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2446.6 | 128.2288 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2446.8 | 128.4208 | 0.020151 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2447 | 128.7087 | 0.029748 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.014522 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2447.2 | 128.5167 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2447.4 | 128.4208 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2447.6 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2447.8 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2448 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2448.2 | 128.4208 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2448.4 | 128.4208 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2448.6 | 128.4208 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2448.8 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2449 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2449.2 | 128.4208 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2449.4 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2449.6 | 128.6127 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2449.8 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2450 | 128.5167 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2450.2 | 128.5167 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2450.4 | 128.5167 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.006713
2450.6 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2450.8 | 128.5167 | 0.010554 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2451 | 128.5167 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.28424 | 0.009912
2451.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2451.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2451.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2451.8 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2452 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2452.2 | 128.5167 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2452.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2452.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2452.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2453 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2453.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2453.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2453.6 | 128.6127 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2453.8 | 128.4208 | 0.012154 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2454 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2454.2 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2454.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2454.6 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2454.8 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2455 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2455.2 | 128.5167 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2455.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.009669 | 0.28424 | 0.0083128
2455.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2455.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2456 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2456.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2456.4 | 128.2288 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.006713
2456.6 | 127.8449 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2456.8 | 127.1732 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2457 | 127.1732 | 0.0089549 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2457.2 | 127.557 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2457.4 | 128.1329 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2457.6 | 128.2288 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2457.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2458 | 128.3248 | 0.010554 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2458.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2458.4 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2458.6 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2458.8 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2459 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2459.2 | 128.6127 | 0.012154 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2459.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2459.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2459.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2460 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2460.2 | 128.5167 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2460.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2460.6 | 128.5167 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2460.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.006713
2461 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2461.2 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2461.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
2461.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2461.8 | 128.6127 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2462 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2462.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2462.4 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2462.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2462.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2463 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2463.2 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2463.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2463.6 | 128.5167 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2463.8 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2464 | 128.6127 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2464.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2464.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2464.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2464.8 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2465 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2465.2 | 128.6127 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2465.4 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2465.6 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2465.8 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2466 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2466.2 | 128.6127 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2466.4 | 128.8046 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2466.6 | 128.6127 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2466.8 | 128.3248 | 0.024949 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2467 | 128.4208 | 0.032947 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2467.2 | 128.8046 | 0.032947 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.014522 | 0.66813 | 0.01149 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2467.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.014522 | 0.76408 | 0.013089 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2467.6 | 128.2288 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.011324 | 0.66813 | 0.013089 | 0.5818 | 0.011268 | 0.57213 | 0.009912
2467.8 | 128.0369 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2468 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2468.2 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2468.4 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.016122 | 0.76408 | 0.01149 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2468.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.016122 | 0.66813 | 0.014688 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2468.8 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2469 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2469.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2469.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2469.6 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2469.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2470 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2470.2 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2470.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2470.6 | 128.5167 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2470.8 | 128.5167 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2471 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2471.2 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2471.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2471.6 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2471.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2472 | 128.4208 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2472.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2472.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2472.6 | 128.4208 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2472.8 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2473 | 128.4208 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2473.2 | 128.4208 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2473.4 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2473.6 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2473.8 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2474 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2474.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2474.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2474.6 | 128.4208 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2474.8 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2475 | 128.3248 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2475.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2475.4 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2475.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2475.8 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2476 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2476.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2476.4 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2476.6 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.28424 | 0.009912
2476.8 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2477 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2477.2 | 128.5167 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2477.4 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2477.6 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2477.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2478 | 128.4208 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2478.2 | 128.4208 | 0.012154 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2478.4 | 128.3248 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2478.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2478.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2479 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2479.2 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2479.4 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2479.6 | 128.4208 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2479.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2480 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2480.2 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2480.4 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2480.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2480.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2481 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2481.2 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2481.4 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2481.6 | 128.4208 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2481.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2482 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2482.2 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2482.4 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.67705 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2482.6 | 128.3248 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2482.8 | 128.4208 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2483 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2483.2 | 128.2288 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2483.4 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2483.6 | 128.3248 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2483.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2484 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2484.2 | 128.3248 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2484.4 | 128.3248 | 0.012154 | 0.48581 | 0.01118 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2484.6 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2484.8 | 128.2288 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.86969 | 0.011268 | 0.38019 | 0.009912
2485 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2485.2 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2485.4 | 128.3248 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2485.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2485.8 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2486 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2486.2 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2486.4 | 128.3248 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2486.6 | 128.3248 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2486.8 | 128.3248 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2487 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2487.2 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.011799 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.47618 | 0.009912
2487.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2487.6 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2487.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2488 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.012867 | 0.47618 | 0.009912
2488.2 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2488.4 | 128.4208 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2488.6 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2488.8 | 128.3248 | 0.012154 | 0.38986 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2489 | 128.3248 | 0.012154 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2489.2 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2489.4 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2489.6 | 128.3248 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2489.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2490 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2490.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2490.4 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2490.6 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2490.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2491 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2491.2 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2491.4 | 128.3248 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2491.6 | 128.3248 | 0.013753 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2491.8 | 128.3248 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2492 | 128.3248 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2492.2 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2492.4 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2492.6 | 128.3248 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2492.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2493 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2493.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2493.4 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2493.6 | 128.3248 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2493.8 | 128.2288 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2494 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2494.2 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2494.4 | 128.3248 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.011213 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2494.6 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.57213 | 0.009912
2494.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2495 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2495.2 | 128.4208 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2495.4 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2495.6 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2495.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2496 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2496.2 | 128.3248 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2496.4 | 128.2288 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2496.6 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2496.8 | 128.2288 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2497 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2497.2 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2497.4 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2497.6 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2497.8 | 128.2288 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2498 | 128.2288 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2498.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2498.4 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2498.6 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2498.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2499 | 128.2288 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2499.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2499.4 | 128.3248 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2499.6 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2499.8 | 128.3248 | 0.012154 | 0.67775 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2500 | 128.2288 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2500.2 | 128.3248 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2500.4 | 128.2288 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2500.6 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2500.8 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2501 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2501.2 | 128.2288 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2501.4 | 128.1329 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2501.6 | 128.3248 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2501.8 | 128.2288 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2502 | 128.2288 | 0.013753 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2502.2 | 128.2288 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2502.4 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2502.6 | 128.3248 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2502.8 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2503 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2503.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.011799 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2503.4 | 128.3248 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2503.6 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2503.8 | 128.2288 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2504 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.47618 | 0.0083128
2504.2 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2504.4 | 128.2288 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2504.6 | 128.2288 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2504.8 | 128.2288 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2505 | 128.3248 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2505.2 | 128.2288 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2505.4 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2505.6 | 128.2288 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2505.8 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2506 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2506.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2506.4 | 128.1329 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.47518 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2506.6 | 128.2288 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2506.8 | 128.1329 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2507 | 128.3248 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2507.2 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2507.4 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2507.6 | 128.2288 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2507.8 | 128.1329 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2508 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2508.2 | 128.2288 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2508.4 | 128.2288 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2508.6 | 128.1329 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2508.8 | 128.2288 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2509 | 128.1329 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2509.2 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2509.4 | 128.2288 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2509.6 | 128.1329 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2509.8 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2510 | 128.2288 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2510.2 | 128.1329 | 0.015352 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2510.4 | 128.2288 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2510.6 | 128.0369 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2510.8 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2511 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2511.2 | 128.2288 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2511.4 | 128.2288 | 0.013753 | 0.67775 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.43001 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2511.6 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2511.8 | 128.2288 | 0.013753 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2512 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2512.2 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2512.4 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2512.6 | 128.1329 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2512.8 | 128.1329 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2513 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2513.2 | 128.2288 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2513.4 | 128.3248 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2513.6 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2513.8 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0098898 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2514 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2514.2 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2514.4 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2514.6 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2514.8 | 128.2288 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.38019 | 0.0083128
2515 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2515.2 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2515.4 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2515.6 | 128.1329 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2515.8 | 128.2288 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2516 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2516.2 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2516.4 | 128.2288 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
2516.6 | 128.2288 | 0.015352 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2516.8 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2517 | 128.3248 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2517.2 | 128.3248 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2517.4 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2517.6 | 128.3248 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2517.8 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2518 | 128.3248 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2518.2 | 128.3248 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2518.4 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2518.6 | 128.2288 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2518.8 | 128.2288 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2519 | 128.4208 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2519.2 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2519.4 | 128.3248 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2519.6 | 128.3248 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2519.8 | 128.4208 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.18829 | 0.009912
2520 | 128.3248 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2520.2 | 128.3248 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2520.4 | 128.3248 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2520.6 | 128.3248 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2520.8 | 128.3248 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2521 | 128.3248 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2521.2 | 128.3248 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2521.4 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2521.6 | 128.3248 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.011511
2521.8 | 128.3248 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2522 | 128.4208 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2522.2 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2522.4 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2522.6 | 128.4208 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2522.8 | 128.4208 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2523 | 128.5167 | 0.018551 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2523.2 | 128.4208 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2523.4 | 128.4208 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2523.6 | 128.4208 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2523.8 | 128.2288 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2524 | 128.5167 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2524.2 | 128.0369 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2524.4 | 128.6127 | 0.040944 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2524.6 | 128.4208 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2524.8 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2525 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2525.2 | 128.5167 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2525.4 | 128.5167 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2525.6 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2525.8 | 128.4208 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.76308 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.86969 | 0.011268 | 0.38019 | 0.009912
2526 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2526.2 | 128.4208 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2526.4 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2526.6 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2526.8 | 128.7087 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2527 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2527.2 | 128.5167 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2527.4 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2527.6 | 128.4208 | 0.018551 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2527.8 | 128.5167 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2528 | 128.5167 | 0.020151 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2528.2 | 128.6127 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2528.4 | 128.6127 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2528.6 | 128.5167 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2528.8 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2529 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2529.2 | 128.6127 | 0.020151 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2529.4 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2529.6 | 128.7087 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2529.8 | 128.7087 | 0.018551 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.013111
2530 | 128.9966 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2530.2 | 129.5724 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2530.4 | 129.6683 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2530.6 | 128.9006 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2530.8 | 128.9006 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2531 | 128.8046 | 0.02175 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2531.2 | 128.7087 | 0.02175 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2531.4 | 128.7087 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2531.6 | 128.6127 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2531.8 | 128.6127 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2532 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2532.2 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2532.4 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2532.6 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2532.8 | 128.6127 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2533 | 128.5167 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2533.2 | 128.6127 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2533.4 | 128.6127 | 0.020151 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2533.6 | 128.6127 | 0.020151 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2533.8 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2534 | 128.6127 | 0.020151 | 0.48581 | 0.01118 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2534.2 | 128.6127 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2534.4 | 128.6127 | 0.020151 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2534.6 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2534.8 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2535 | 128.5167 | 0.018551 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2535.2 | 128.5167 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2535.4 | 128.5167 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2535.6 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2535.8 | 128.6127 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2536 | 128.5167 | 0.020151 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2536.2 | 128.5167 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2536.4 | 128.6127 | 0.02335 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2536.6 | 128.2288 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2536.8 | 128.6127 | 0.029748 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.012923 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2537 | 128.1329 | 0.036146 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2537.2 | 128.9966 | 0.05054 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.016122 | 0.76408 | 0.01149 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2537.4 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2537.6 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2537.8 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.38019 | 0.0083128
2538 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
2538.2 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2538.4 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2538.6 | 128.5167 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2538.8 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2539 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2539.2 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2539.4 | 128.4208 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2539.6 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2539.8 | 128.4208 | 0.018551 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2540 | 128.3248 | 0.018551 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2540.2 | 128.3248 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2540.4 | 128.3248 | 0.020151 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2540.6 | 128.3248 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2540.8 | 128.3248 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2541 | 128.4208 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2541.2 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2541.4 | 128.2288 | 0.018551 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2541.6 | 128.3248 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2541.8 | 128.3248 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2542 | 128.4208 | 0.018551 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2542.2 | 128.2288 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2542.4 | 128.3248 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2542.6 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2542.8 | 128.3248 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2543 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2543.2 | 128.4208 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2543.4 | 128.3248 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2543.6 | 128.4208 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.76308 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2543.8 | 128.2288 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2544 | 128.3248 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2544.2 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2544.4 | 128.2288 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2544.6 | 128.2288 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2544.8 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2545 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2545.2 | 128.2288 | 0.015352 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2545.4 | 128.3248 | 0.015352 | 0.58176 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2545.6 | 128.3248 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2545.8 | 128.2288 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2546 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2546.2 | 128.2288 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2546.4 | 128.3248 | 0.015352 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2546.6 | 128.2288 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2546.8 | 128.1329 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2547 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2547.2 | 128.1329 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2547.4 | 128.2288 | 0.015352 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2547.6 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2547.8 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2548 | 128.1329 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2548.2 | 128.2288 | 0.013753 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.011511
2548.4 | 128.1329 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2548.6 | 128.5167 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2548.8 | 128.1329 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2549 | 128.2288 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2549.2 | 128.2288 | 0.013753 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2549.4 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2549.6 | 128.1329 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.006713
2549.8 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2550 | 128.1329 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.011511
2550.2 | 128.1329 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2550.4 | 128.2288 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2550.6 | 128.2288 | 0.013753 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2550.8 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2551 | 128.2288 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2551.2 | 128.2288 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2551.4 | 128.2288 | 0.015352 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2551.6 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2551.8 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2552 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2552.2 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.526 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2552.4 | 128.3248 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.0083128
2552.6 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2552.8 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2553 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2553.2 | 128.2288 | 0.015352 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2553.4 | 128.3248 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2553.6 | 128.3248 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2553.8 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2554 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2554.2 | 128.2288 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2554.4 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2554.6 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2554.8 | 128.3248 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2555 | 128.2288 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2555.2 | 128.2288 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2555.4 | 128.2288 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2555.6 | 128.1329 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2555.8 | 128.1329 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2556 | 128.0369 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2556.2 | 128.1329 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2556.4 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2556.6 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2556.8 | 128.2288 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2557 | 128.1329 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2557.2 | 128.2288 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2557.4 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.006713
2557.6 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2557.8 | 128.2288 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2558 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2558.2 | 128.2288 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2558.4 | 128.0369 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2558.6 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2558.8 | 128.2288 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2559 | 128.3248 | 0.015352 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2559.2 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2559.4 | 128.2288 | 0.013753 | 0.67775 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2559.6 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2559.8 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2560 | 128.2288 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2560.2 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2560.4 | 128.2288 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.48581 | 0.011268 | 0.47618 | 0.009912
2560.6 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2560.8 | 128.1329 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2561 | 128.2288 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2561.2 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2561.4 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2561.6 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2561.8 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2562 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2562.2 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2562.4 | 128.2288 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2562.6 | 128.1329 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2562.8 | 128.3248 | 0.013753 | 0.38986 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2563 | 128.3248 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2563.2 | 128.2288 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2563.4 | 128.2288 | 0.013753 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2563.6 | 128.2288 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2563.8 | 128.3248 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.0083128
2564 | 128.3248 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2564.2 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2564.4 | 128.1329 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2564.6 | 128.2288 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.86969 | 0.011268 | 0.38019 | 0.009912
2564.8 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2565 | 128.3248 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2565.2 | 128.2288 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2565.4 | 128.2288 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2565.6 | 128.3248 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2565.8 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2566 | 128.3248 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2566.2 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2566.4 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2566.6 | 128.3248 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.86003 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2566.8 | 128.3248 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2567 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2567.2 | 128.5167 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2567.4 | 128.4208 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2567.6 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2567.8 | 128.5167 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2568 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.006713
2568.2 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2568.4 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2568.6 | 128.5167 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2568.8 | 128.4208 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2569 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2569.2 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2569.4 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2569.6 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2569.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2570 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2570.2 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2570.4 | 128.5167 | 0.013753 | 0.48581 | 0.0095798 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2570.6 | 128.4208 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2570.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2571 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2571.2 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2571.4 | 128.5167 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2571.6 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2571.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2572 | 128.4208 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2572.2 | 128.5167 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2572.4 | 128.6127 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2572.6 | 128.5167 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.011511
2572.8 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.0083128
2573 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2573.2 | 128.6127 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2573.4 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2573.6 | 128.5167 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2573.8 | 128.6127 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2574 | 128.7087 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2574.2 | 128.5167 | 0.018551 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2574.4 | 128.4208 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2574.6 | 128.8046 | 0.034546 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2574.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2575 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2575.2 | 128.6127 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2575.4 | 128.4208 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2575.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2575.8 | 128.5167 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2576 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2576.2 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2576.4 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2576.6 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2576.8 | 128.4208 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.47618 | 0.009912
2577 | 128.6127 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2577.2 | 128.6127 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2577.4 | 128.5167 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2577.6 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2577.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2578 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2578.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2578.4 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2578.6 | 128.5167 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2578.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2579 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2579.2 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2579.4 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2579.6 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2579.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2580 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2580.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2580.4 | 128.6127 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2580.6 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2580.8 | 128.6127 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2581 | 128.6127 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2581.2 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2581.4 | 128.6127 | 0.012154 | 0.67775 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2581.6 | 128.6127 | 0.013753 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0049255 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2581.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2582 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2582.2 | 128.7087 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2582.4 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2582.6 | 128.6127 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
2582.8 | 128.2288 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2583 | 127.653 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2583.2 | 127.653 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2583.4 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2583.6 | 128.4208 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2583.8 | 128.5167 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2584 | 128.6127 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2584.2 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2584.4 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2584.6 | 128.7087 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2584.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2585 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2585.2 | 128.6127 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2585.4 | 128.7087 | 0.012154 | 0.48581 | 0.0095798 | 0.67705 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2585.6 | 128.7087 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2585.8 | 128.7087 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2586 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2586.2 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2586.4 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2586.6 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2586.8 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2587 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2587.2 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2587.4 | 128.7087 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2587.6 | 128.7087 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2587.8 | 128.7087 | 0.026549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2588 | 128.9006 | 0.031347 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2588.2 | 128.5167 | 0.026549 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2588.4 | 128.9966 | 0.048941 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2588.6 | 128.6127 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2588.8 | 128.6127 | 0.013753 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2589 | 128.7087 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2589.2 | 128.6127 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2589.4 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2589.6 | 128.6127 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2589.8 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2590 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2590.2 | 128.6127 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2590.4 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2590.6 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2590.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2591 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2591.2 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2591.4 | 128.6127 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2591.6 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2591.8 | 128.5167 | 0.015352 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2592 | 128.6127 | 0.013753 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2592.2 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2592.4 | 128.6127 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2592.6 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2592.8 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2593 | 128.6127 | 0.015352 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.76308 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.86969 | 0.011268 | 0.47618 | 0.009912
2593.2 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.76308 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.011511
2593.4 | 128.6127 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2593.6 | 128.5167 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.011799 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2593.8 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2594 | 128.6127 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2594.2 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2594.4 | 128.5167 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2594.6 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2594.8 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.01149 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2595 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2595.2 | 128.5167 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2595.4 | 128.5167 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2595.6 | 128.5167 | 0.016952 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2595.8 | 128.6127 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2596 | 128.4208 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2596.2 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2596.4 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.86003 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2596.6 | 128.6127 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2596.8 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2597 | 128.5167 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2597.2 | 128.5167 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2597.4 | 128.6127 | 0.018551 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2597.6 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2597.8 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2598 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2598.2 | 128.4208 | 0.016952 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2598.4 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2598.6 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2598.8 | 128.5167 | 0.020151 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2599 | 128.5167 | 0.018551 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0065247 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2599.2 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2599.4 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2599.6 | 128.5167 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2599.8 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2600 | 128.4208 | 0.016952 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2600.2 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2600.4 | 128.4208 | 0.020151 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2600.6 | 128.5167 | 0.020151 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2600.8 | 128.5167 | 0.020151 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.006713
2601 | 128.5167 | 0.018551 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2601.2 | 128.5167 | 0.018551 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2601.4 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2601.6 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2601.8 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2602 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2602.2 | 128.4208 | 0.020151 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2602.4 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2602.6 | 128.4208 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2602.8 | 128.4208 | 0.020151 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2603 | 128.5167 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2603.2 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2603.4 | 128.4208 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2603.6 | 128.5167 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2603.8 | 128.4208 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2604 | 128.5167 | 0.02175 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2604.2 | 128.4208 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2604.4 | 128.3248 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2604.6 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2604.8 | 128.3248 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2605 | 128.1329 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2605.2 | 128.2288 | 0.020151 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2605.4 | 128.3248 | 0.020151 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2605.6 | 128.3248 | 0.020151 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2605.8 | 128.3248 | 0.02175 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2606 | 128.4208 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2606.2 | 128.4208 | 0.024949 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2606.4 | 128.4208 | 0.026549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2606.6 | 128.4208 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2606.8 | 128.3248 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2607 | 128.4208 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2607.2 | 128.2288 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.0083128
2607.4 | 128.1329 | 0.016952 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2607.6 | 128.1329 | 0.018551 | 0.58176 | 0.0079807 | 0.67705 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2607.8 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2608 | 128.4208 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2608.2 | 128.4208 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2608.4 | 128.4208 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2608.6 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2608.8 | 128.2288 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.18829 | 0.009912
2609 | 128.3248 | 0.02175 | 0.58176 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2609.2 | 128.3248 | 0.02175 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2609.4 | 128.2288 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2609.6 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2609.8 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2610 | 128.4208 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2610.2 | 128.3248 | 0.02175 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2610.4 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2610.6 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2610.8 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2611 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2611.2 | 128.4208 | 0.02335 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2611.4 | 128.4208 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2611.6 | 128.4208 | 0.02175 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2611.8 | 128.4208 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2612 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2612.2 | 128.4208 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2612.4 | 128.4208 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2612.6 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2612.8 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2613 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2613.2 | 128.3248 | 0.024949 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2613.4 | 128.3248 | 0.02335 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2613.6 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2613.8 | 128.3248 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2614 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2614.2 | 128.3248 | 0.02335 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2614.4 | 128.4208 | 0.02175 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2614.6 | 128.4208 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2614.8 | 128.4208 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2615 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2615.2 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2615.4 | 128.4208 | 0.02175 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2615.6 | 128.4208 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2615.8 | 128.4208 | 0.024949 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2616 | 128.4208 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2616.2 | 128.4208 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2616.4 | 128.5167 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.8139 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2616.6 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.006713
2616.8 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2617 | 128.2288 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2617.2 | 128.3248 | 0.02335 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2617.4 | 128.4208 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2617.6 | 128.4208 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2617.8 | 128.4208 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2618 | 128.4208 | 0.02335 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2618.2 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2618.4 | 128.2288 | 0.02175 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2618.6 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2618.8 | 128.2288 | 0.02335 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2619 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2619.2 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2619.4 | 128.3248 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.006713
2619.6 | 128.3248 | 0.02175 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2619.8 | 128.3248 | 0.02335 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2620 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2620.2 | 128.2288 | 0.02335 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2620.4 | 128.3248 | 0.02175 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.0083128
2620.6 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2620.8 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2621 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2621.2 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2621.4 | 128.2288 | 0.02175 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2621.6 | 128.3248 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2621.8 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2622 | 128.2288 | 0.02335 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2622.2 | 128.2288 | 0.02175 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2622.4 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2622.6 | 128.3248 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2622.8 | 128.3248 | 0.02175 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2623 | 128.3248 | 0.02335 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2623.2 | 128.2288 | 0.02335 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2623.4 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2623.6 | 128.3248 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2623.8 | 128.3248 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2624 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2624.2 | 128.3248 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2624.4 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2624.6 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2624.8 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2625 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2625.2 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2625.4 | 128.3248 | 0.02335 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2625.6 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2625.8 | 128.2288 | 0.02175 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2626 | 128.2288 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2626.2 | 128.2288 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2626.4 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2626.6 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2626.8 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2627 | 128.3248 | 0.02335 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2627.2 | 128.2288 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2627.4 | 128.2288 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2627.6 | 128.2288 | 0.02335 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2627.8 | 128.3248 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2628 | 128.4208 | 0.02335 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2628.2 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2628.4 | 128.2288 | 0.02335 | 0.58176 | 0.0079807 | 0.67705 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2628.6 | 128.3248 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2628.8 | 128.2288 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2629 | 128.2288 | 0.024949 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2629.2 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2629.4 | 128.3248 | 0.02335 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0102 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2629.6 | 128.1329 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2629.8 | 128.2288 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2630 | 128.2288 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2630.2 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2630.4 | 128.3248 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.014467 | 0.38019 | 0.009912
2630.6 | 128.3248 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2630.8 | 128.2288 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2631 | 128.3248 | 0.024949 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2631.2 | 128.3248 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2631.4 | 128.3248 | 0.024949 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2631.6 | 128.2288 | 0.024949 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2631.8 | 128.2288 | 0.026549 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2632 | 128.3248 | 0.026549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.009669 | 0.38019 | 0.009912
2632.2 | 128.3248 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2632.4 | 128.1329 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2632.6 | 128.1329 | 0.02335 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2632.8 | 128.2288 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2633 | 128.3248 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2633.2 | 128.2288 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2633.4 | 128.2288 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2633.6 | 128.2288 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2633.8 | 128.3248 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2634 | 128.3248 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2634.2 | 128.2288 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2634.4 | 128.2288 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2634.6 | 128.3248 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2634.8 | 128.2288 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2635 | 128.3248 | 0.026549 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2635.2 | 128.3248 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2635.4 | 128.3248 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2635.6 | 128.2288 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2635.8 | 128.2288 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2636 | 128.2288 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2636.2 | 128.2288 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2636.4 | 128.3248 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2636.6 | 128.3248 | 0.026549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2636.8 | 128.3248 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2637 | 128.3248 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2637.2 | 128.3248 | 0.028148 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2637.4 | 128.3248 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2637.6 | 128.3248 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2637.8 | 128.4208 | 0.029748 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2638 | 128.4208 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2638.2 | 128.3248 | 0.026549 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2638.4 | 128.3248 | 0.026549 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2638.6 | 128.3248 | 0.026549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2638.8 | 128.3248 | 0.026549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2639 | 128.3248 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2639.2 | 128.3248 | 0.029748 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2639.4 | 128.3248 | 0.029748 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2639.6 | 128.4208 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2639.8 | 128.3248 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2640 | 128.4208 | 0.029748 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2640.2 | 128.5167 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2640.4 | 128.5167 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2640.6 | 128.4208 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2640.8 | 128.3248 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2641 | 128.4208 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2641.2 | 128.5167 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2641.4 | 128.6127 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2641.6 | 128.4208 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2641.8 | 128.5167 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2642 | 128.5167 | 0.029748 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2642.2 | 128.4208 | 0.029748 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2642.4 | 128.4208 | 0.026549 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2642.6 | 128.4208 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2642.8 | 128.4208 | 0.029748 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2643 | 128.5167 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2643.2 | 128.5167 | 0.039345 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2643.4 | 128.5167 | 0.034546 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2643.6 | 128.5167 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2643.8 | 128.5167 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2644 | 128.6127 | 0.031347 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2644.2 | 128.6127 | 0.031347 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2644.4 | 128.6127 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2644.6 | 128.6127 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2644.8 | 128.6127 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.011799 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2645 | 128.6127 | 0.032947 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2645.2 | 128.6127 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2645.4 | 128.6127 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2645.6 | 128.6127 | 0.032947 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2645.8 | 128.7087 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2646 | 128.6127 | 0.032947 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2646.2 | 128.6127 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2646.4 | 128.7087 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.86003 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2646.6 | 128.6127 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2646.8 | 128.6127 | 0.031347 | 0.48581 | 0.0063808 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.86003 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2647 | 128.6127 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2647.2 | 128.7087 | 0.032947 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2647.4 | 128.6127 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2647.6 | 128.7087 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2647.8 | 128.9006 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2648 | 129.7643 | 0.029748 | 0.48581 | 0.0095798 | 0.67705 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2648.2 | 129.3804 | 0.034546 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2648.4 | 128.9966 | 0.032947 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2648.6 | 128.9006 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2648.8 | 128.8046 | 0.032947 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2649 | 128.6127 | 0.034546 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2649.2 | 128.6127 | 0.031347 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2649.4 | 128.6127 | 0.032947 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2649.6 | 128.6127 | 0.032947 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2649.8 | 128.6127 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2650 | 128.7087 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2650.2 | 128.7087 | 0.032947 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2650.4 | 128.7087 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2650.6 | 128.7087 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2650.8 | 128.6127 | 0.032947 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2651 | 128.6127 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2651.2 | 128.7087 | 0.031347 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2651.4 | 128.6127 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2651.6 | 128.5167 | 0.029748 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2651.8 | 128.6127 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2652 | 128.8046 | 0.045742 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2652.2 | 128.5167 | 0.05214 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2652.4 | 128.6127 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2652.6 | 128.6127 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2652.8 | 128.5167 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2653 | 128.6127 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2653.2 | 128.5167 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2653.4 | 128.6127 | 0.032947 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2653.6 | 128.6127 | 0.032947 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2653.8 | 128.5167 | 0.032947 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2654 | 128.5167 | 0.032947 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2654.2 | 128.5167 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2654.4 | 128.5167 | 0.031347 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2654.6 | 128.5167 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2654.8 | 128.5167 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2655 | 128.5167 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2655.2 | 128.5167 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2655.4 | 128.4208 | 0.029748 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2655.6 | 128.4208 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2655.8 | 128.3248 | 0.031347 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2656 | 128.4208 | 0.031347 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.011799 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.012867 | 0.38019 | 0.0083128
2656.2 | 128.4208 | 0.028148 | 0.58176 | 0.0047816 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2656.4 | 128.3248 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.011511
2656.6 | 128.4208 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0102 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2656.8 | 128.4208 | 0.032947 | 0.48581 | 0.0079807 | 0.48515 | 0.011213 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2657 | 128.4208 | 0.031347 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2657.2 | 128.3248 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2657.4 | 128.4208 | 0.029748 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2657.6 | 128.4208 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2657.8 | 128.4208 | 0.029748 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2658 | 128.4208 | 0.029748 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2658.2 | 128.3248 | 0.028148 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2658.4 | 128.2288 | 0.028148 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2658.6 | 128.2288 | 0.029748 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2658.8 | 128.2288 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2659 | 128.2288 | 0.029748 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2659.2 | 128.3248 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2659.4 | 128.2288 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2659.6 | 128.2288 | 0.024949 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2659.8 | 128.2288 | 0.02175 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2660 | 128.5167 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2660.2 | 128.3248 | 0.028148 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2660.4 | 128.3248 | 0.026549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2660.6 | 128.3248 | 0.026549 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2660.8 | 128.2288 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2661 | 128.3248 | 0.026549 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2661.2 | 128.3248 | 0.026549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2661.4 | 128.3248 | 0.026549 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2661.6 | 128.3248 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2661.8 | 128.3248 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2662 | 128.3248 | 0.026549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2662.2 | 128.3248 | 0.026549 | 0.48581 | 0.0063808 | 0.67705 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2662.4 | 128.3248 | 0.026549 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2662.6 | 128.4208 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2662.8 | 128.4208 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2663 | 128.4208 | 0.026549 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2663.2 | 128.4208 | 0.024949 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2663.4 | 128.3248 | 0.024949 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2663.6 | 128.5167 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2663.8 | 128.4208 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2664 | 128.4208 | 0.026549 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2664.2 | 128.4208 | 0.026549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2664.4 | 128.4208 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2664.6 | 128.4208 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2664.8 | 128.5167 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2665 | 128.4208 | 0.026549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2665.2 | 128.3248 | 0.024949 | 0.48581 | 0.0079807 | 0.67705 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2665.4 | 128.4208 | 0.026549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2665.6 | 128.5167 | 0.024949 | 0.58176 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2665.8 | 128.4208 | 0.024949 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2666 | 128.4208 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2666.2 | 128.4208 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2666.4 | 128.4208 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2666.6 | 128.4208 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2666.8 | 128.4208 | 0.02335 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2667 | 128.4208 | 0.02335 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2667.2 | 128.5167 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2667.4 | 128.4208 | 0.02335 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2667.6 | 128.4208 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2667.8 | 128.5167 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2668 | 128.5167 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2668.2 | 128.4208 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2668.4 | 128.4208 | 0.024949 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2668.6 | 128.4208 | 0.024949 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2668.8 | 128.4208 | 0.02335 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2669 | 128.4208 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2669.2 | 128.4208 | 0.024949 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2669.4 | 128.4208 | 0.024949 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2669.6 | 128.5167 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2669.8 | 128.5167 | 0.02335 | 0.67775 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2670 | 128.4208 | 0.024949 | 0.58176 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2670.2 | 128.5167 | 0.026549 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2670.4 | 128.6127 | 0.024949 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2670.6 | 128.5167 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2670.8 | 128.6127 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2671 | 128.5167 | 0.024949 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2671.2 | 128.5167 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2671.4 | 128.6127 | 0.026549 | 0.58176 | 0.01118 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2671.6 | 128.6127 | 0.029748 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2671.8 | 128.5167 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2672 | 128.4208 | 0.024949 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2672.2 | 128.5167 | 0.029748 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2672.4 | 128.6127 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2672.6 | 128.3248 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.86969 | 0.011268 | 0.38019 | 0.0083128
2672.8 | 128.6127 | 0.045742 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2673 | 128.8046 | 0.05054 | 0.67775 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2673.2 | 128.6127 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2673.4 | 128.3248 | 0.020151 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2673.6 | 128.5167 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.011324 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2673.8 | 128.5167 | 0.024949 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2674 | 128.6127 | 0.026549 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2674.2 | 128.5167 | 0.02335 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2674.4 | 128.6127 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2674.6 | 128.6127 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
2674.8 | 128.6127 | 0.026549 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2675 | 128.5167 | 0.024949 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2675.2 | 128.6127 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2675.4 | 128.6127 | 0.02175 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2675.6 | 128.6127 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2675.8 | 128.6127 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2676 | 128.5167 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2676.2 | 128.6127 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2676.4 | 128.6127 | 0.026549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2676.6 | 128.7087 | 0.026549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2676.8 | 128.7087 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2677 | 128.6127 | 0.02335 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2677.2 | 128.6127 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2677.4 | 128.6127 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2677.6 | 128.6127 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.0083128
2677.8 | 128.6127 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2678 | 128.6127 | 0.026549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
2678.2 | 128.6127 | 0.02335 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2678.4 | 128.6127 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2678.6 | 128.6127 | 0.026549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2678.8 | 128.6127 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2679 | 128.6127 | 0.024949 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2679.2 | 128.6127 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2679.4 | 128.6127 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2679.6 | 128.6127 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2679.8 | 128.7087 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2680 | 128.6127 | 0.024949 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2680.2 | 128.7087 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2680.4 | 128.7087 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2680.6 | 128.6127 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2680.8 | 128.7087 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2681 | 128.6127 | 0.024949 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2681.2 | 128.7087 | 0.026549 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2681.4 | 128.6127 | 0.024949 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2681.6 | 128.6127 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2681.8 | 128.6127 | 0.024949 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2682 | 128.5167 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.011511
2682.2 | 128.6127 | 0.024949 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2682.4 | 128.6127 | 0.024949 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2682.6 | 128.6127 | 0.026549 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2682.8 | 128.6127 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2683 | 128.5167 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2683.2 | 128.5167 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2683.4 | 128.6127 | 0.024949 | 0.48581 | 0.0079807 | 0.67705 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2683.6 | 128.5167 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2683.8 | 128.5167 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2684 | 128.6127 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2684.2 | 128.5167 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2684.4 | 128.6127 | 0.024949 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2684.6 | 128.6127 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2684.8 | 128.5167 | 0.026549 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2685 | 128.6127 | 0.026549 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2685.2 | 128.6127 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2685.4 | 128.6127 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2685.6 | 128.5167 | 0.026549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2685.8 | 128.6127 | 0.026549 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
2686 | 128.7087 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.28424 | 0.009912
2686.2 | 128.6127 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2686.4 | 128.6127 | 0.026549 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2686.6 | 128.5167 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2686.8 | 128.5167 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2687 | 128.6127 | 0.028148 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2687.2 | 128.6127 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2687.4 | 128.6127 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2687.6 | 128.6127 | 0.026549 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2687.8 | 128.6127 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2688 | 128.5167 | 0.024949 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2688.2 | 128.6127 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2688.4 | 128.5167 | 0.026549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2688.6 | 128.4208 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2688.8 | 128.6127 | 0.028148 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2689 | 128.5167 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2689.2 | 128.5167 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2689.4 | 128.5167 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2689.6 | 128.6127 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2689.8 | 128.6127 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2690 | 128.6127 | 0.028148 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2690.2 | 128.6127 | 0.029748 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.57213 | 0.009912
2690.4 | 128.6127 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2690.6 | 128.6127 | 0.029748 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2690.8 | 128.6127 | 0.028148 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2691 | 128.6127 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2691.2 | 128.6127 | 0.029748 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2691.4 | 128.7087 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.01149 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2691.6 | 128.7087 | 0.031347 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
2691.8 | 128.6127 | 0.026549 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2692 | 128.6127 | 0.028148 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2692.2 | 128.6127 | 0.028148 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2692.4 | 128.7087 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2692.6 | 128.6127 | 0.029748 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2692.8 | 128.6127 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2693 | 128.6127 | 0.026549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2693.2 | 128.5167 | 0.028148 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2693.4 | 128.5167 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2693.6 | 128.6127 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2693.8 | 128.5167 | 0.028148 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2694 | 128.6127 | 0.029748 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2694.2 | 128.6127 | 0.026549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2694.4 | 128.6127 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2694.6 | 128.6127 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2694.8 | 128.7087 | 0.031347 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2695 | 128.7087 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2695.2 | 128.6127 | 0.026549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2695.4 | 128.7087 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2695.6 | 128.7087 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2695.8 | 128.6127 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2696 | 128.6127 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2696.2 | 128.6127 | 0.028148 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2696.4 | 128.6127 | 0.029748 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2696.6 | 128.6127 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2696.8 | 128.6127 | 0.031347 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2697 | 128.5167 | 0.028148 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2697.2 | 128.5167 | 0.029748 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2697.4 | 128.5167 | 0.029748 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2697.6 | 128.5167 | 0.031347 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2697.8 | 128.5167 | 0.028148 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2698 | 128.5167 | 0.029748 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2698.2 | 128.3248 | 0.02335 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2698.4 | 128.5167 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2698.6 | 128.9966 | 0.058538 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2698.8 | 128.5167 | 0.044143 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2699 | 128.6127 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2699.2 | 128.6127 | 0.042543 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2699.4 | 128.5167 | 0.032947 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2699.6 | 128.5167 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.011511
2699.8 | 128.6127 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2700 | 128.5167 | 0.031347 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.86003 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2700.2 | 128.4208 | 0.029748 | 0.67775 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.57213 | 0.009912
2700.4 | 128.5167 | 0.031347 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2700.6 | 128.5167 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2700.8 | 128.4208 | 0.031347 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2701 | 128.4208 | 0.031347 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2701.2 | 128.4208 | 0.031347 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2701.4 | 128.4208 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2701.6 | 128.4208 | 0.031347 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2701.8 | 128.4208 | 0.031347 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2702 | 128.4208 | 0.032947 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.86003 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2702.2 | 128.4208 | 0.034546 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2702.4 | 128.3248 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2702.6 | 128.3248 | 0.031347 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2702.8 | 128.3248 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2703 | 128.3248 | 0.031347 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2703.2 | 128.3248 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2703.4 | 128.2288 | 0.031347 | 0.48581 | 0.0079807 | 0.67705 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2703.6 | 128.4208 | 0.031347 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2703.8 | 128.3248 | 0.034546 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2704 | 128.3248 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2704.2 | 128.4208 | 0.032947 | 0.48581 | 0.0079807 | 0.48515 | 0.011213 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2704.4 | 128.3248 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2704.6 | 128.4208 | 0.034546 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2704.8 | 128.4208 | 0.036146 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2705 | 128.3248 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.011213 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2705.2 | 128.2288 | 0.034546 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2705.4 | 128.3248 | 0.034546 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2705.6 | 128.2288 | 0.034546 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2705.8 | 128.2288 | 0.032947 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2706 | 128.3248 | 0.032947 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2706.2 | 128.2288 | 0.034546 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2706.4 | 128.3248 | 0.032947 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2706.6 | 128.2288 | 0.032947 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2706.8 | 128.3248 | 0.036146 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2707 | 128.3248 | 0.034546 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2707.2 | 128.2288 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.013111
2707.4 | 128.1329 | 0.034546 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2707.6 | 128.2288 | 0.034546 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2707.8 | 128.2288 | 0.034546 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2708 | 128.3248 | 0.034546 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2708.2 | 128.3248 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2708.4 | 128.2288 | 0.036146 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2708.6 | 128.2288 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2708.8 | 128.3248 | 0.037745 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2709 | 128.3248 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2709.2 | 128.2288 | 0.036146 | 0.67775 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2709.4 | 128.2288 | 0.036146 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2709.6 | 128.1329 | 0.034546 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2709.8 | 128.3248 | 0.037745 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2710 | 128.2288 | 0.037745 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2710.2 | 128.2288 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2710.4 | 128.2288 | 0.034546 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2710.6 | 128.2288 | 0.037745 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2710.8 | 128.2288 | 0.039345 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2711 | 128.1329 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2711.2 | 128.1329 | 0.037745 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2711.4 | 128.1329 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2711.6 | 128.1329 | 0.037745 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2711.8 | 128.1329 | 0.036146 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2712 | 128.1329 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2712.2 | 128.1329 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2712.4 | 128.2288 | 0.039345 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2712.6 | 128.1329 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2712.8 | 128.2288 | 0.034546 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2713 | 128.2288 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2713.2 | 128.2288 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2713.4 | 128.1329 | 0.039345 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2713.6 | 128.2288 | 0.037745 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2713.8 | 128.2288 | 0.037745 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2714 | 128.2288 | 0.037745 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2714.2 | 128.2288 | 0.037745 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2714.4 | 128.3248 | 0.037745 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2714.6 | 128.3248 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2714.8 | 128.3248 | 0.037745 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2715 | 128.3248 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2715.2 | 128.3248 | 0.039345 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2715.4 | 128.3248 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2715.6 | 128.2288 | 0.039345 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2715.8 | 128.3248 | 0.040944 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2716 | 128.2288 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2716.2 | 128.2288 | 0.037745 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2716.4 | 128.2288 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
2716.6 | 128.2288 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2716.8 | 128.3248 | 0.037745 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2717 | 128.2288 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2717.2 | 128.2288 | 0.039345 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2717.4 | 128.2288 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2717.6 | 128.1329 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2717.8 | 128.2288 | 0.037745 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2718 | 128.2288 | 0.039345 | 0.58176 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.86003 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2718.2 | 128.4208 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2718.4 | 128.2288 | 0.037745 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2718.6 | 128.3248 | 0.040944 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2718.8 | 128.2288 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2719 | 128.2288 | 0.039345 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2719.2 | 128.2288 | 0.037745 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2719.4 | 128.2288 | 0.037745 | 0.58176 | 0.0079807 | 0.5811 | 0.012812 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2719.6 | 128.2288 | 0.037745 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2719.8 | 128.2288 | 0.037745 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2720 | 128.2288 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2720.2 | 128.2288 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2720.4 | 128.3248 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2720.6 | 128.1329 | 0.039345 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2720.8 | 128.2288 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2721 | 128.2288 | 0.037745 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2721.2 | 128.2288 | 0.037745 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2721.4 | 128.3248 | 0.040944 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2721.6 | 128.1329 | 0.039345 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2721.8 | 128.2288 | 0.036146 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2722 | 128.2288 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2722.2 | 128.3248 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2722.4 | 128.2288 | 0.039345 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
2722.6 | 128.2288 | 0.037745 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.86003 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2722.8 | 128.2288 | 0.039345 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2723 | 128.3248 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2723.2 | 128.3248 | 0.039345 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2723.4 | 128.3248 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2723.6 | 128.3248 | 0.037745 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2723.8 | 128.3248 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2724 | 128.2288 | 0.037745 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2724.2 | 128.2288 | 0.039345 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.006713
2724.4 | 128.2288 | 0.036146 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2724.6 | 128.3248 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2724.8 | 128.3248 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2725 | 128.2288 | 0.036146 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2725.2 | 128.2288 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2725.4 | 128.2288 | 0.039345 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2725.6 | 128.3248 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2725.8 | 128.3248 | 0.039345 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2726 | 128.2288 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2726.2 | 128.3248 | 0.040944 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2726.4 | 128.3248 | 0.037745 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2726.6 | 128.2288 | 0.039345 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2726.8 | 128.2288 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2727 | 128.3248 | 0.039345 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2727.2 | 128.3248 | 0.039345 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.57213 | 0.009912
2727.4 | 128.3248 | 0.039345 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2727.6 | 128.3248 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.011799 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2727.8 | 128.2288 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2728 | 128.3248 | 0.040944 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2728.2 | 128.2288 | 0.039345 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2728.4 | 128.3248 | 0.044143 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2728.6 | 128.2288 | 0.042543 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2728.8 | 128.2288 | 0.05054 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2729 | 128.3248 | 0.047342 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2729.2 | 127.9409 | 0.036146 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2729.4 | 128.6127 | 0.069734 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2729.6 | 128.4208 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2729.8 | 128.0369 | 0.028148 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2730 | 128.5167 | 0.039345 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2730.2 | 128.5167 | 0.039345 | 0.48581 | 0.0095798 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2730.4 | 128.5167 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2730.6 | 128.5167 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2730.8 | 128.4208 | 0.039345 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.76308 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2731 | 128.4208 | 0.037745 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.66813 | 0.009912
2731.2 | 128.6127 | 0.040944 | 0.58176 | 0.0079807 | 0.5811 | 0.006414 | 0.76308 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.7737 | 0.009669 | 0.38019 | 0.009912
2731.4 | 128.5167 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2731.6 | 128.5167 | 0.039345 | 0.58176 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2731.8 | 128.4208 | 0.040944 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2732 | 128.5167 | 0.039345 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2732.2 | 128.6127 | 0.040944 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2732.4 | 128.4208 | 0.037745 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2732.6 | 128.5167 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2732.8 | 128.5167 | 0.040944 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2733 | 128.5167 | 0.040944 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2733.2 | 128.5167 | 0.039345 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2733.4 | 128.5167 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2733.6 | 128.5167 | 0.042543 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2733.8 | 128.4208 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2734 | 128.5167 | 0.037745 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2734.2 | 128.5167 | 0.040944 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2734.4 | 128.5167 | 0.040944 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2734.6 | 128.6127 | 0.040944 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2734.8 | 128.4208 | 0.039345 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2735 | 128.4208 | 0.040944 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2735.2 | 128.5167 | 0.040944 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2735.4 | 128.4208 | 0.040944 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2735.6 | 128.5167 | 0.039345 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2735.8 | 128.6127 | 0.040944 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2736 | 128.6127 | 0.042543 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2736.2 | 128.5167 | 0.039345 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2736.4 | 128.5167 | 0.040944 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2736.6 | 128.5167 | 0.040944 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2736.8 | 128.5167 | 0.042543 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2737 | 128.5167 | 0.042543 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2737.2 | 128.5167 | 0.040944 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2737.4 | 128.5167 | 0.042543 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2737.6 | 128.5167 | 0.040944 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2737.8 | 128.5167 | 0.040944 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2738 | 128.5167 | 0.040944 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2738.2 | 128.6127 | 0.044143 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2738.4 | 128.6127 | 0.044143 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2738.6 | 128.5167 | 0.042543 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2738.8 | 128.5167 | 0.042543 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2739 | 128.5167 | 0.042543 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2739.2 | 128.5167 | 0.044143 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.006713
2739.4 | 128.4208 | 0.042543 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2739.6 | 128.5167 | 0.044143 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2739.8 | 128.4208 | 0.044143 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.009669 | 0.38019 | 0.009912
2740 | 128.4208 | 0.042543 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2740.2 | 128.4208 | 0.039345 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2740.4 | 128.3248 | 0.042543 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2740.6 | 128.4208 | 0.044143 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2740.8 | 128.4208 | 0.044143 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2741 | 128.5167 | 0.047342 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2741.2 | 128.5167 | 0.042543 | 0.58176 | 0.0095798 | 0.5811 | 0.011213 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2741.4 | 128.4208 | 0.042543 | 0.67775 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2741.6 | 128.3248 | 0.044143 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2741.8 | 128.2288 | 0.040944 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2742 | 128.3248 | 0.044143 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2742.2 | 128.2288 | 0.045742 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2742.4 | 128.0369 | 0.044143 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2742.6 | 127.9409 | 0.045742 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2742.8 | 128.0369 | 0.045742 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2743 | 127.653 | 0.045742 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2743.2 | 127.1732 | 0.042543 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2743.4 | 127.1732 | 0.045742 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2743.6 | 127.0772 | 0.045742 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2743.8 | 127.3651 | 0.039345 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2744 | 127.749 | 0.040944 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2744.2 | 127.653 | 0.042543 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2744.4 | 128.0369 | 0.040944 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2744.6 | 128.1329 | 0.047342 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2744.8 | 128.2288 | 0.047342 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2745 | 128.1329 | 0.044143 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2745.2 | 128.2288 | 0.045742 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2745.4 | 128.3248 | 0.045742 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2745.6 | 128.3248 | 0.045742 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2745.8 | 128.3248 | 0.044143 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2746 | 128.2288 | 0.045742 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2746.2 | 128.3248 | 0.044143 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2746.4 | 128.3248 | 0.045742 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2746.6 | 128.3248 | 0.044143 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2746.8 | 128.3248 | 0.044143 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2747 | 128.3248 | 0.044143 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2747.2 | 128.3248 | 0.044143 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2747.4 | 128.3248 | 0.044143 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2747.6 | 128.4208 | 0.044143 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2747.8 | 128.4208 | 0.042543 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2748 | 128.5167 | 0.042543 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2748.2 | 128.4208 | 0.045742 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2748.4 | 128.5167 | 0.045742 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.006713
2748.6 | 128.5167 | 0.045742 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2748.8 | 128.5167 | 0.047342 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2749 | 128.5167 | 0.045742 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2749.2 | 128.5167 | 0.047342 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2749.4 | 128.5167 | 0.045742 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2749.6 | 128.4208 | 0.047342 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2749.8 | 128.6127 | 0.047342 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2750 | 128.6127 | 0.047342 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2750.2 | 128.5167 | 0.045742 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2750.4 | 128.4208 | 0.045742 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2750.6 | 128.5167 | 0.047342 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2750.8 | 128.5167 | 0.047342 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2751 | 128.5167 | 0.045742 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2751.2 | 128.5167 | 0.047342 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2751.4 | 128.5167 | 0.045742 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2751.6 | 128.5167 | 0.047342 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2751.8 | 128.4208 | 0.048941 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2752 | 128.4208 | 0.045742 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2752.2 | 128.4208 | 0.047342 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2752.4 | 128.5167 | 0.047342 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2752.6 | 128.5167 | 0.047342 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2752.8 | 128.5167 | 0.047342 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2753 | 128.5167 | 0.048941 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2753.2 | 128.4208 | 0.047342 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2753.4 | 128.5167 | 0.048941 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2753.6 | 128.5167 | 0.048941 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2753.8 | 128.5167 | 0.048941 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2754 | 128.5167 | 0.048941 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2754.2 | 128.5167 | 0.048941 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2754.4 | 128.5167 | 0.048941 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2754.6 | 128.5167 | 0.048941 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2754.8 | 128.5167 | 0.05054 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2755 | 128.5167 | 0.05054 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2755.2 | 128.5167 | 0.05054 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2755.4 | 128.4208 | 0.048941 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2755.6 | 128.5167 | 0.05054 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2755.8 | 128.5167 | 0.05214 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.011799 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2756 | 128.5167 | 0.05054 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2756.2 | 128.5167 | 0.05054 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2756.4 | 128.5167 | 0.048941 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2756.6 | 128.5167 | 0.05214 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2756.8 | 128.5167 | 0.05054 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2757 | 128.5167 | 0.05214 | 0.58176 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2757.2 | 128.4208 | 0.05214 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2757.4 | 128.5167 | 0.05214 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2757.6 | 128.4208 | 0.05214 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2757.8 | 128.5167 | 0.05054 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2758 | 128.5167 | 0.05054 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2758.2 | 128.5167 | 0.05214 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2758.4 | 128.5167 | 0.05214 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2758.6 | 128.5167 | 0.05214 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2758.8 | 128.5167 | 0.053739 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2759 | 128.4208 | 0.053739 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2759.2 | 128.4208 | 0.053739 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2759.4 | 128.4208 | 0.05214 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2759.6 | 128.4208 | 0.053739 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2759.8 | 128.4208 | 0.053739 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2760 | 128.4208 | 0.053739 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2760.2 | 128.4208 | 0.055339 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2760.4 | 128.4208 | 0.055339 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2760.6 | 128.5167 | 0.053739 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2760.8 | 128.4208 | 0.055339 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2761 | 128.5167 | 0.053739 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2761.2 | 128.4208 | 0.055339 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2761.4 | 128.4208 | 0.053739 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.011799 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2761.6 | 128.5167 | 0.055339 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2761.8 | 128.0369 | 0.055339 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2762 | 128.3248 | 0.055339 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2762.2 | 128.4208 | 0.055339 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2762.4 | 128.2288 | 0.055339 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2762.6 | 128.2288 | 0.056938 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2762.8 | 128.3248 | 0.056938 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2763 | 128.4208 | 0.055339 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2763.2 | 128.3248 | 0.058538 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2763.4 | 128.3248 | 0.056938 | 0.58176 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2763.6 | 128.3248 | 0.058538 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2763.8 | 128.3248 | 0.058538 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2764 | 128.3248 | 0.058538 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2764.2 | 128.4208 | 0.058538 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2764.4 | 128.4208 | 0.058538 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2764.6 | 128.4208 | 0.060137 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2764.8 | 128.3248 | 0.060137 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2765 | 128.3248 | 0.058538 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2765.2 | 128.3248 | 0.058538 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2765.4 | 128.3248 | 0.058538 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2765.6 | 128.3248 | 0.058538 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2765.8 | 128.3248 | 0.060137 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2766 | 128.2288 | 0.061737 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2766.2 | 128.2288 | 0.061737 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2766.4 | 128.3248 | 0.061737 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2766.6 | 128.3248 | 0.060137 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2766.8 | 128.3248 | 0.061737 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2767 | 128.3248 | 0.061737 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2767.2 | 128.3248 | 0.061737 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2767.4 | 128.2288 | 0.060137 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2767.6 | 128.3248 | 0.063336 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2767.8 | 128.3248 | 0.063336 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2768 | 128.2288 | 0.063336 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2768.2 | 128.3248 | 0.063336 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2768.4 | 128.3248 | 0.064936 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2768.6 | 128.3248 | 0.064936 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2768.8 | 128.2288 | 0.066535 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2769 | 128.2288 | 0.068135 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2769.2 | 121.991 | 0.68073 | 0.48581 | 0.0079807 | 0.67705 | 0.0048148 | 0.66713 | 0.0102 | 0.8139 | 0.0081246 | 0.86003 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2769.4 | 116.9047 | 1.2789 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0102 | 0.90985 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | -0.099642 | 0.009912
2769.6 | 113.258 | 1.6708 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2769.8 | 110.9547 | 1.9059 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2770 | 108.8434 | 2.1122 | 0.48581 | 0.0095798 | 0.77304 | 0.0080139 | 0.76308 | 0.011799 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.48581 | 0.012867 | 0.47618 | 0.009912
2770.2 | 107.7878 | 2.2002 | 0.67775 | 0.01118 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.8139 | 0.0097238 | 0.38019 | 0.0098898 | 0.67775 | 0.012867 | 0.28424 | 0.0083128
2770.4 | 106.3483 | 2.357 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2770.6 | 105.6765 | 2.4385 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2770.8 | 104.333 | 2.5985 | 0.58176 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2771 | 103.6612 | 2.6592 | 0.58176 | 0.01118 | 0.5811 | 0.011213 | 0.47518 | 0.0102 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.18829 | 0.0083128
2771.2 | 101.6459 | 2.856 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.37923 | 0.0054014 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.48581 | 0.009669 | 0.47618 | 0.011511
2771.4 | 100.2064 | 3.0335 | 0.67775 | 0.0063808 | 0.5811 | 0.0048148 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2771.6 | 98.479 | 3.1727 | 0.67775 | 0.0063808 | 0.29321 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.006713
2771.8 | 95.2161 | 3.5421 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2772 | 92.0492 | 3.87 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2772.2 | 88.6903 | 4.2315 | 0.67775 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2772.4 | 88.4984 | 4.2331 | 0.58176 | 0.0063808 | 0.38916 | 0.011213 | 0.66713 | 0.0086004 | 0.046168 | 0.0081246 | 0.86003 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2772.6 | 96.7516 | 3.355 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2772.8 | 96.2717 | 3.395 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.86003 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2773 | 94.5443 | 3.5501 | 0.67775 | 0.0063808 | 0.48515 | 0.0080139 | 0.76308 | 0.0054014 | 0.8139 | 0.011324 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.006713
2773.2 | 97.9991 | 3.2015 | 0.67775 | 0.0079807 | 0.48515 | 0.0048148 | 0.66713 | 0.00060315 | 0.8139 | 0.0081246 | 0.57213 | 0.0082906 | 0.96565 | 0.012867 | 0.38019 | 0.009912
2773.4 | 96.7516 | 3.3646 | 0.67775 | 0.0079807 | 0.48515 | 0.014411 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2773.6 | 96.9435 | 3.3166 | 0.67775 | 0.0079807 | 0.38916 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2773.8 | 97.8072 | 3.2047 | 0.67775 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2774 | 99.0548 | 3.1039 | 0.48581 | 0.0095798 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0049255 | 0.76408 | 0.0098898 | 0.29387 | 0.011268 | 0.38019 | 0.0051138
2774.2 | 97.2314 | 3.283 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2774.4 | 98.1911 | 3.1903 | 0.67775 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2774.6 | 90.0339 | 4.0428 | 0.67775 | 0.01118 | 0.67705 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.00647 | 0.66813 | 0.013111
2774.8 | 88.0186 | 4.2699 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2775 | 86.3871 | 4.3979 | 0.67775 | 0.0079807 | 0.48515 | 0.011213 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2775.2 | 84.8516 | 4.5626 | 0.58176 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.38986 | 0.012867 | 0.38019 | 0.009912
2775.4 | 81.8767 | 4.8585 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2775.6 | 71.1283 | 5.3271 | 0.67775 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2775.8 | 76.2146 | 5.3271 | 0.67775 | 0.0095798 | 0.77304 | 0.0080139 | 0.76308 | 0.0086004 | 0.43001 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.0080692 | 0.57213 | 0.009912
2776 | 69.7848 | 5.3271 | 0.67775 | 0.0063808 | 0.67705 | 0.012812 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2776.2 | 71.4162 | 5.3271 | 0.7737 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2776.4 | 67.9614 | 5.3271 | 0.67775 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2776.6 | 27.7512 | 2.6608 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2776.8 | 4.719 | 0.21369 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2777 | 1.9359 | 0.05214 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2777.2 | 1.2642 | 0.028148 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2777.4 | 1.0723 | 0.02335 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2777.6 | 0.97627 | 0.018551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2777.8 | 0.88032 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2778 | 0.88032 | 0.015352 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2778.2 | 0.88032 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2778.4 | 0.78433 | 0.015352 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2778.6 | 0.78433 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
2778.8 | 0.88032 | 0.013753 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2779 | 0.78433 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2779.2 | 0.68838 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2779.4 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2779.6 | 0.68838 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2779.8 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
2780 | 0.68838 | 0.013753 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2780.2 | 0.68838 | 0.013753 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2780.4 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2780.6 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2780.8 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2781 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2781.2 | 0.78433 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.8139 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2781.4 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2781.6 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2781.8 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2782 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2782.2 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2782.4 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2782.6 | 0.68838 | 0.012154 | 0.58176 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2782.8 | 0.68838 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2783 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2783.2 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2783.4 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2783.6 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2783.8 | 0.68838 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2784 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2784.2 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2784.4 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2784.6 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2784.8 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2785 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2785.2 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2785.4 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2785.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2785.8 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2786 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2786.2 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2786.4 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2786.6 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2786.8 | 0.68838 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2787 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2787.2 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2787.4 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2787.6 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2787.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2788 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2788.2 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2788.4 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2788.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2788.8 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2789 | 0.68838 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2789.2 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2789.4 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2789.6 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2789.8 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2790 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2790.2 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2790.4 | 0.68838 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2790.6 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2790.8 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2791 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2791.2 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2791.4 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.67705 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2791.6 | 0.78433 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2791.8 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2792 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2792.2 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.67705 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2792.4 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2792.6 | 0.68838 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2792.8 | 0.59242 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2793 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2793.2 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2793.4 | 0.68838 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2793.6 | 0.68838 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.86003 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2793.8 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2794 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.67705 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2794.2 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2794.4 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2794.6 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.67705 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2794.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2795 | 0.68838 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2795.2 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2795.4 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.86899 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2795.6 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2795.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2796 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.90985 | 0.0097238 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2796.2 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2796.4 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2796.6 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.86969 | 0.009669 | 0.38019 | 0.009912
2796.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2797 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2797.2 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2797.4 | 0.68838 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2797.6 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2797.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2798 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2798.2 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2798.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2798.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2798.8 | 0.59242 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2799 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2799.2 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2799.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2799.6 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.011511
2799.8 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2800 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2800.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2800.4 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2800.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2800.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2801 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2801.2 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2801.4 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2801.6 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2801.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2802 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.7737 | 0.012867 | 0.47618 | 0.009912
2802.2 | 0.68838 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2802.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2802.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2802.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2803 | 0.68838 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2803.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2803.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2803.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2803.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2804 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2804.2 | 0.59242 | 0.010554 | 0.67775 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2804.4 | 0.68838 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2804.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2804.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2805 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2805.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2805.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.57213 | 0.009912
2805.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2805.8 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2806 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2806.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.012867 | 0.47618 | 0.011511
2806.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2806.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2806.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2807 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2807.2 | 0.68838 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2807.4 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.011799 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2807.6 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2807.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2808 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2808.2 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2808.4 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2808.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2808.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.8139 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2809 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2809.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2809.4 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.67705 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2809.6 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.76308 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2809.8 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2810 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2810.2 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2810.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2810.6 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2810.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2811 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.67705 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2811.2 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2811.4 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.013111
2811.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2811.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2812 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2812.2 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2812.4 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2812.6 | 0.59242 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2812.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2813 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2813.2 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.28424 | 0.009912
2813.4 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2813.6 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2813.8 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2814 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2814.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2814.4 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2814.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2814.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2815 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2815.2 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2815.4 | 0.59242 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2815.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2815.8 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2816 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.57213 | 0.011511
2816.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2816.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2816.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2816.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.57213 | 0.011511
2817 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.7737 | 0.012867 | 0.38019 | 0.009912
2817.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2817.4 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.8139 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2817.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2817.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2818 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2818.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2818.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2818.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2818.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2819 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2819.2 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2819.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2819.6 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2819.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2820 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.014467 | 0.47618 | 0.009912
2820.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2820.4 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2820.6 | 0.68838 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2820.8 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2821 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2821.2 | 0.49643 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.76308 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2821.4 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2821.6 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2821.8 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2822 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2822.2 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2822.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2822.6 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2822.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2823 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2823.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2823.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2823.6 | 0.68838 | 0.010554 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2823.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2824 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2824.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2824.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2824.6 | 0.68838 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2824.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2825 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2825.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2825.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.011213 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2825.6 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2825.8 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2826 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2826.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2826.4 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2826.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2826.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2827 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2827.2 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2827.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2827.6 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2827.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2828 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2828.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2828.4 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2828.6 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2828.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2829 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2829.2 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2829.4 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2829.6 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2829.8 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2830 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2830.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2830.4 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2830.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2830.8 | 0.68838 | 0.010554 | 0.58176 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2831 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2831.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2831.4 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2831.6 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2831.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2832 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2832.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2832.4 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2832.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2832.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2833 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2833.2 | 0.49643 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2833.4 | 0.59242 | 0.010554 | 0.58176 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2833.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2833.8 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2834 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2834.2 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2834.4 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2834.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2834.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2835 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2835.2 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2835.4 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2835.6 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2835.8 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2836 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2836.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2836.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2836.6 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2836.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2837 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2837.2 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2837.4 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.57213 | 0.009912
2837.6 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2837.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2838 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2838.2 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2838.4 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2838.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2838.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2839 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2839.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2839.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2839.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2839.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2840 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2840.2 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2840.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2840.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2840.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2841 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.86003 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2841.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2841.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.011213 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2841.6 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2841.8 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2842 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2842.2 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2842.4 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2842.6 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2842.8 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2843 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2843.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2843.4 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2843.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.8139 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2843.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2844 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2844.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2844.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2844.6 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2844.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2845 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2845.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2845.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2845.6 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2845.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2846 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.67705 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2846.2 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2846.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2846.6 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2846.8 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2847 | 0.68838 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2847.2 | 0.59242 | 0.0089549 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2847.4 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2847.6 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2847.8 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.011213 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2848 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.0083128
2848.2 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2848.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2848.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2848.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2849 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2849.2 | 0.59242 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2849.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2849.6 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2849.8 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.57213 | 0.009912
2850 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2850.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.8139 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2850.4 | 0.59242 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2850.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2850.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2851 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2851.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2851.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2851.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2851.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2852 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2852.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2852.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2852.6 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2852.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2853 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2853.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.012867 | 0.38019 | 0.009912
2853.4 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2853.6 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2853.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.67705 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2854 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2854.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2854.4 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2854.6 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2854.8 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2855 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2855.2 | 0.68838 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2855.4 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2855.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2855.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2856 | 0.49643 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2856.2 | 0.59242 | 0.0089549 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2856.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2856.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2856.8 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2857 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2857.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2857.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2857.6 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2857.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2858 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2858.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2858.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2858.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2858.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2859 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2859.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.67705 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2859.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2859.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2859.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2860 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2860.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2860.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2860.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2860.8 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2861 | 0.68838 | 0.010554 | 0.58176 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2861.2 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.011511
2861.4 | 0.49643 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2861.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2861.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2862 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2862.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2862.4 | 0.49643 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2862.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2862.8 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2863 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2863.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2863.4 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2863.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.57213 | 0.009912
2863.8 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2864 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2864.2 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2864.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2864.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2864.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2865 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2865.2 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2865.4 | 0.59242 | 0.010554 | 0.67775 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2865.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2865.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2866 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2866.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2866.4 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2866.6 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2866.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2867 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2867.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2867.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2867.6 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2867.8 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2868 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2868.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2868.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2868.6 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2868.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2869 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2869.2 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2869.4 | 0.49643 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2869.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2869.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2870 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2870.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2870.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2870.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2870.8 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2871 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2871.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2871.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2871.6 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2871.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2872 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2872.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2872.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.011213 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2872.6 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2872.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2873 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.011213 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2873.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2873.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2873.6 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2873.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2874 | 0.49643 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2874.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2874.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2874.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2874.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2875 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2875.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2875.4 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2875.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2875.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2876 | 0.59242 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2876.2 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2876.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2876.6 | 0.59242 | 0.0089549 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2876.8 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2877 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2877.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2877.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2877.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2877.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2878 | 0.59242 | 0.012154 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2878.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2878.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2878.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.011511
2878.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2879 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2879.2 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2879.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2879.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2879.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2880 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2880.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2880.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2880.6 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2880.8 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.006713
2881 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2881.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.0097238 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2881.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2881.6 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2881.8 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2882 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2882.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2882.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.011324 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2882.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2882.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2883 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2883.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.006414 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2883.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.011511
2883.6 | 0.49643 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2883.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2884 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2884.2 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2884.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.012867 | 0.38019 | 0.009912
2884.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2884.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2885 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2885.2 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2885.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2885.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2885.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2886 | 0.68838 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2886.2 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2886.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.67705 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2886.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2886.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2887 | 0.59242 | 0.0089549 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2887.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2887.4 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2887.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2887.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2888 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2888.2 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2888.4 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2888.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2888.8 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2889 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2889.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2889.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.01149 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2889.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.011213 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2889.8 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.67705 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2890 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2890.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2890.4 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2890.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2890.8 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2891 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2891.2 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.011511
2891.4 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2891.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2891.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.011511
2892 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.7737 | 0.012867 | 0.47618 | 0.009912
2892.2 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.57213 | 0.009912
2892.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2892.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2892.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2893 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2893.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2893.4 | 0.49643 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2893.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2893.8 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2894 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2894.2 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2894.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2894.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2894.8 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2895 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2895.2 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2895.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2895.6 | 0.68838 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2895.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2896 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.006713
2896.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2896.4 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2896.6 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2896.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2897 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2897.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2897.4 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
2897.6 | 0.59242 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2897.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2898 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2898.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2898.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2898.6 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2898.8 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2899 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2899.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2899.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2899.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2899.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2900 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2900.2 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2900.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2900.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2900.8 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2901 | 0.49643 | 0.0089549 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2901.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2901.4 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2901.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2901.8 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2902 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2902.2 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2902.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2902.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2902.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.67705 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2903 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2903.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2903.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2903.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.37923 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2903.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2904 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.011511
2904.2 | 0.49643 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2904.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2904.6 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2904.8 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2905 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2905.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2905.4 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.47618 | 0.009912
2905.6 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2905.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2906 | 0.68838 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2906.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.47518 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2906.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2906.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2906.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.006713
2907 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2907.2 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
2907.4 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2907.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2907.8 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.76308 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2908 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2908.2 | 0.68838 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.0083128
2908.4 | 0.68838 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2908.6 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2908.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2909 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2909.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.8139 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2909.4 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2909.6 | 0.68838 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2909.8 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2910 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2910.2 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2910.4 | 0.59242 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2910.6 | 0.68838 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2910.8 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2911 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2911.2 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2911.4 | 0.68838 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2911.6 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2911.8 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.8139 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2912 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2912.2 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2912.4 | 0.59242 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.8139 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2912.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2912.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2913 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.67705 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2913.2 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2913.4 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.67705 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2913.6 | 0.49643 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2913.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2914 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2914.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2914.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2914.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2914.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2915 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2915.2 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2915.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2915.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2915.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2916 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2916.2 | 0.59242 | 0.0089549 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2916.4 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.67705 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2916.6 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.67705 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2916.8 | 0.49643 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2917 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2917.2 | 0.49643 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.76308 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2917.4 | 0.59242 | 0.012154 | 0.58176 | 0.01118 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2917.6 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2917.8 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2918 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.67705 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2918.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2918.4 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.47618 | 0.009912
2918.6 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2918.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2919 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2919.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2919.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2919.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2919.8 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2920 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2920.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2920.4 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.57213 | 0.009912
2920.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2920.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2921 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2921.2 | 0.49643 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2921.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2921.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2921.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2922 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2922.2 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2922.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2922.6 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2922.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2923 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2923.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2923.4 | 0.68838 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2923.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2923.8 | 0.68838 | 0.0089549 | 0.67775 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2924 | 0.49643 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2924.2 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2924.4 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2924.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2924.8 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2925 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2925.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2925.4 | 0.68838 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2925.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2925.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2926 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2926.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2926.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2926.6 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2926.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2927 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2927.2 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.0083128
2927.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2927.6 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2927.8 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2928 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2928.2 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2928.4 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2928.6 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2928.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2929 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2929.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2929.4 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2929.6 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2929.8 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2930 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.012867 | 0.47618 | 0.009912
2930.2 | 0.68838 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2930.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2930.6 | 0.68838 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.47618 | 0.009912
2930.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2931 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2931.2 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2931.4 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2931.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2931.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2932 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.009912
2932.2 | 0.68838 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2932.4 | 0.49643 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2932.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2932.8 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.006713
2933 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2933.2 | 0.59242 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2933.4 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2933.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2933.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2934 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2934.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.47618 | 0.009912
2934.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2934.6 | 0.68838 | 0.010554 | 0.58176 | 0.0095798 | 0.67705 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2934.8 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2935 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2935.2 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2935.4 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.47618 | 0.009912
2935.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.012867 | 0.47618 | 0.009912
2935.8 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
2936 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2936.2 | 0.49643 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2936.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2936.6 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2936.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2937 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.8139 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2937.2 | 0.49643 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2937.4 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2937.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.38019 | 0.009912
2937.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.47618 | 0.009912
2938 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2938.2 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2938.4 | 0.68838 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2938.6 | 0.68838 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
2938.8 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
2939 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.009912
2939.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2939.4 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
2939.6 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2939.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2940 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2940.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2940.4 | 0.68838 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
2940.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
2940.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2941 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.76408 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2941.2 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
2941.4 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2941.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2941.8 | 0.59242 | 0.012154 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2942 | 0.49643 | 0.0089549 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2942.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2942.4 | 0.59242 | 0.010554 | 0.58176 | 0.0095798 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2942.6 | 0.68838 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2942.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2943 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
2943.2 | 0.68838 | 0.012154 | 0.58176 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
2943.4 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2943.6 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2943.8 | 0.59242 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.011213 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.86003 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
2944 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.009613 | 0.66713 | 0.0102 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2944.2 | 0.59242 | 0.010554 | 0.58176 | 0.0079807 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
2944.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2944.6 | 3.6634 | 0.068135 | 3.6527 | 0.065561 | 4.2278 | 0.060796 | 3.834 | 0.064581 | 3.6929 | 0.064105 | 4.1229 | 0.06747 | 4.1326 | 0.067249 | 3.4511 | 0.065893
2944.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2945 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2945.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2945.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2945.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2945.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2946 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2946.2 | -73.4943 | -1.2226 | -73.6969 | -1.23 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2946.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2946.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2262 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2946.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2947 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2947.2 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2947.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2947.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2947.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2948 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2948.2 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2948.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.5056 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2948.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2948.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2949 | -73.4943 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2949.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2949.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2949.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2949.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2950 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2950.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2950.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2950.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2950.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2951 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2951.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2951.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2951.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2951.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2952 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2952.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2952.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2952.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2952.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.5056 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2953 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2953.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8025 | -1.2265
2953.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2953.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2953.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2954 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2954.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2954.4 | -73.3983 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2954.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2954.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2955 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2955.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2955.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2955.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2955.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2956 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2956.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2956.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2956.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2956.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2957 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2957.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2957.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2957.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2957.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2958 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2958.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2958.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2958.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2958.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2959 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2959.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2959.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2959.6 | -73.4943 | -1.221 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2959.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2960 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2960.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2960.4 | -73.3983 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2960.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2960.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.5056 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2961 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2961.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2961.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2961.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2961.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2962 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2962.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2962.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2962.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2962.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2963 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2963.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.5056 | -1.2316 | -73.4196 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2963.4 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2963.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2963.8 | -73.4943 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2964 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2964.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2964.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2964.6 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2964.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2965 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2965.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2249
2965.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2965.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2965.8 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2966 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2262 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2966.2 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2966.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2966.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2966.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2967 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2967.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2967.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2967.6 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2967.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2968 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2968.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2968.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.3226 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2968.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2968.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2969 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2969.2 | -73.4943 | -1.2226 | -73.6969 | -1.23 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2969.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2249
2969.6 | -73.4943 | -1.2226 | -73.6969 | -1.23 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2969.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265

## Temperature Data
Fire Time | Time | Top TC for 3c | Side TC for 3c | Penlight Exposure Temperature | Time | North 25 C | Cable 1 | Cable 2
0 | -255 | 23.6512 | 23.9781 | 24.1739 | 0 | 24.1739 | 23.6512 | 23.9781
0.7073 | -254.2927 | 23.6429 | 23.9773 | 24.172 | 0.7073 | 24.172 | 23.6429 | 23.9773
1.7698 | -253.2302 | 23.6423 | 23.9651 | 24.1712 | 1.7698 | 24.1712 | 23.6423 | 23.9651
2.7854 | -252.2146 | 23.6556 | 23.963 | 24.1689 | 2.7854 | 24.1689 | 23.6556 | 23.963
3.7698 | -251.2302 | 23.6396 | 23.9624 | 24.1621 | 3.7698 | 24.1621 | 23.6396 | 23.9624
4.7073 | -250.2927 | 23.6492 | 23.9682 | 24.1649 | 4.7073 | 24.1649 | 23.6492 | 23.9682
5.7073 | -249.2927 | 23.6432 | 23.9549 | 24.1609 | 5.7073 | 24.1609 | 23.6432 | 23.9549
6.7229 | -248.2771 | 23.6458 | 23.9535 | 24.1651 | 6.7229 | 24.1651 | 23.6458 | 23.9535
7.7073 | -247.2927 | 23.6503 | 23.953 | 24.16 | 7.7073 | 24.16 | 23.6503 | 23.953
8.7073 | -246.2927 | 23.6514 | 23.9586 | 24.156 | 8.7073 | 24.156 | 23.6514 | 23.9586
9.7073 | -245.2927 | 23.6393 | 23.956 | 24.1598 | 9.7073 | 24.1598 | 23.6393 | 23.956
10.7073 | -244.2927 | 23.6528 | 23.9496 | 24.1555 | 10.7073 | 24.1555 | 23.6528 | 23.9496
11.7073 | -243.2927 | 23.65 | 23.9448 | 24.1533 | 11.7073 | 24.1533 | 23.65 | 23.9448
12.7073 | -242.2927 | 23.6332 | 23.9459 | 24.1491 | 12.7073 | 24.1491 | 23.6332 | 23.9459
13.7073 | -241.2927 | 23.6454 | 23.9481 | 24.1423 | 13.7073 | 24.1423 | 23.6454 | 23.9481
14.7073 | -240.2927 | 23.6448 | 23.9437 | 24.148 | 14.7073 | 24.148 | 23.6448 | 23.9437
15.7073 | -239.2927 | 23.6439 | 23.9544 | 24.1559 | 15.7073 | 24.1559 | 23.6439 | 23.9544
16.7073 | -238.2927 | 23.6359 | 23.9521 | 24.1475 | 16.7073 | 24.1475 | 23.6359 | 23.9521
17.7073 | -237.2927 | 23.6445 | 23.9565 | 24.1502 | 17.7073 | 24.1502 | 23.6445 | 23.9565
18.7073 | -236.2927 | 23.6395 | 23.9437 | 24.141 | 18.7073 | 24.141 | 23.6395 | 23.9437
19.7073 | -235.2927 | 23.6402 | 23.9358 | 24.1248 | 19.7073 | 24.1248 | 23.6402 | 23.9358
20.7073 | -234.2927 | 23.6319 | 23.9369 | 24.1381 | 20.7073 | 24.1381 | 23.6319 | 23.9369
21.7073 | -233.2927 | 23.6359 | 23.9426 | 24.1438 | 21.7073 | 24.1438 | 23.6359 | 23.9426
22.7073 | -232.2927 | 23.6406 | 23.9395 | 24.1529 | 22.7073 | 24.1529 | 23.6406 | 23.9395
23.7073 | -231.2927 | 23.638 | 23.928 | 24.1427 | 23.7073 | 24.1427 | 23.638 | 23.928
24.7073 | -230.2927 | 23.6398 | 23.9406 | 24.1366 | 24.7073 | 24.1366 | 23.6398 | 23.9406
25.7073 | -229.2927 | 23.6454 | 23.9417 | 24.1334 | 25.7073 | 24.1334 | 23.6454 | 23.9417
26.7073 | -228.2927 | 23.6429 | 23.9373 | 24.136 | 26.7073 | 24.136 | 23.6429 | 23.9373
27.7073 | -227.2927 | 23.6411 | 23.9362 | 24.1245 | 27.7073 | 24.1245 | 23.6411 | 23.9362
28.7073 | -226.2927 | 23.6367 | 23.9276 | 24.1322 | 28.7073 | 24.1322 | 23.6367 | 23.9276
29.7073 | -225.2927 | 23.6494 | 23.9334 | 24.1327 | 29.7073 | 24.1327 | 23.6494 | 23.9334
30.7073 | -224.2927 | 23.6379 | 23.9285 | 24.138 | 30.7073 | 24.138 | 23.6379 | 23.9285
31.7073 | -223.2927 | 23.6344 | 23.9321 | 24.137 | 31.7073 | 24.137 | 23.6344 | 23.9321
32.7073 | -222.2927 | 23.6287 | 23.9276 | 24.1377 | 32.7073 | 24.1377 | 23.6287 | 23.9276
33.7073 | -221.2927 | 23.6359 | 23.9312 | 24.1293 | 33.7073 | 24.1293 | 23.6359 | 23.9312
34.7073 | -220.2927 | 23.6384 | 23.9288 | 24.1201 | 34.7073 | 24.1201 | 23.6384 | 23.9288
35.7073 | -219.2927 | 23.6175 | 23.914 | 24.1276 | 35.7073 | 24.1276 | 23.6175 | 23.914
36.7073 | -218.2927 | 23.6328 | 23.9251 | 24.1198 | 36.7073 | 24.1198 | 23.6328 | 23.9251
37.7073 | -217.2927 | 23.6328 | 23.9198 | 24.1179 | 37.7073 | 24.1179 | 23.6328 | 23.9198
38.7073 | -216.2927 | 23.6366 | 23.9142 | 24.1219 | 38.7073 | 24.1219 | 23.6366 | 23.9142
39.7073 | -215.2927 | 23.6345 | 23.9178 | 24.1285 | 39.7073 | 24.1285 | 23.6345 | 23.9178
40.7073 | -214.2927 | 23.6337 | 23.9153 | 24.1153 | 40.7073 | 24.1153 | 23.6337 | 23.9153
41.7073 | -213.2927 | 23.6394 | 23.9298 | 24.1105 | 41.7073 | 24.1105 | 23.6394 | 23.9298
42.7073 | -212.2927 | 23.6301 | 23.9132 | 24.1091 | 42.7073 | 24.1091 | 23.6301 | 23.9132
43.7073 | -211.2927 | 23.632 | 23.9129 | 24.1118 | 43.7073 | 24.1118 | 23.632 | 23.9129
44.7073 | -210.2927 | 23.6332 | 23.9186 | 24.1146 | 44.7073 | 24.1146 | 23.6332 | 23.9186
45.7073 | -209.2927 | 23.6379 | 23.9203 | 24.1166 | 45.7073 | 24.1166 | 23.6379 | 23.9203
46.7073 | -208.2927 | 23.6339 | 23.9122 | 24.1118 | 46.7073 | 24.1118 | 23.6339 | 23.9122
47.7073 | -207.2927 | 23.6402 | 23.9086 | 24.1109 | 47.7073 | 24.1109 | 23.6402 | 23.9086
48.7073 | -206.2927 | 23.6307 | 23.9135 | 24.1097 | 48.7073 | 24.1097 | 23.6307 | 23.9135
49.7073 | -205.2927 | 23.6343 | 23.9089 | 24.111 | 49.7073 | 24.111 | 23.6343 | 23.9089
50.7073 | -204.2927 | 23.6344 | 23.9134 | 24.1194 | 50.7073 | 24.1194 | 23.6344 | 23.9134
51.7073 | -203.2927 | 23.6281 | 23.91 | 24.1173 | 51.7073 | 24.1173 | 23.6281 | 23.91
52.7073 | -202.2927 | 23.6312 | 23.9128 | 24.1076 | 52.7073 | 24.1076 | 23.6312 | 23.9128
53.7073 | -201.2927 | 23.6291 | 23.9032 | 24.1147 | 53.7073 | 24.1147 | 23.6291 | 23.9032
54.7073 | -200.2927 | 23.6122 | 23.9078 | 24.0972 | 54.7073 | 24.0972 | 23.6122 | 23.9078
55.7073 | -199.2927 | 23.6166 | 23.8961 | 24.1001 | 55.7073 | 24.1001 | 23.6166 | 23.8961
56.7073 | -198.2927 | 23.6241 | 23.8932 | 24.0949 | 56.7073 | 24.0949 | 23.6241 | 23.8932
57.7073 | -197.2927 | 23.6384 | 23.9137 | 24.1027 | 57.7073 | 24.1027 | 23.6384 | 23.9137
58.7073 | -196.2927 | 23.624 | 23.9045 | 24.0961 | 58.7073 | 24.0961 | 23.624 | 23.9045
59.7073 | -195.2927 | 23.6324 | 23.9039 | 24.0977 | 59.7073 | 24.0977 | 23.6324 | 23.9039
60.7073 | -194.2927 | 23.6237 | 23.8902 | 24.0888 | 60.7073 | 24.0888 | 23.6237 | 23.8902
61.7073 | -193.2927 | 23.6283 | 23.9057 | 24.0937 | 61.7073 | 24.0937 | 23.6283 | 23.9057
62.7073 | -192.2927 | 23.6277 | 23.8959 | 24.0929 | 62.7073 | 24.0929 | 23.6277 | 23.8959
63.7073 | -191.2927 | 23.6269 | 23.9012 | 24.0871 | 63.7073 | 24.0871 | 23.6269 | 23.9012
64.7073 | -190.2927 | 23.6244 | 23.8996 | 24.0831 | 64.7073 | 24.0831 | 23.6244 | 23.8996
65.7073 | -189.2927 | 23.6293 | 23.8989 | 24.0876 | 65.7073 | 24.0876 | 23.6293 | 23.8989
66.7073 | -188.2927 | 23.6362 | 23.9013 | 24.0822 | 66.7073 | 24.0822 | 23.6362 | 23.9013
67.7073 | -187.2927 | 23.6222 | 23.8989 | 24.0925 | 67.7073 | 24.0925 | 23.6222 | 23.8989
68.7073 | -186.2927 | 23.6279 | 23.901 | 24.0757 | 68.7073 | 24.0757 | 23.6279 | 23.901
69.7073 | -185.2927 | 23.6203 | 23.8898 | 24.0775 | 69.7073 | 24.0775 | 23.6203 | 23.8898
70.7073 | -184.2927 | 23.6229 | 23.8899 | 24.0836 | 70.7073 | 24.0836 | 23.6229 | 23.8899
71.7073 | -183.2927 | 23.6252 | 23.8898 | 24.0768 | 71.7073 | 24.0768 | 23.6252 | 23.8898
72.7073 | -182.2927 | 23.6254 | 23.8881 | 24.07 | 72.7073 | 24.07 | 23.6254 | 23.8881
73.7073 | -181.2927 | 23.6132 | 23.887 | 24.069 | 73.7073 | 24.069 | 23.6132 | 23.887
74.7073 | -180.2927 | 23.6234 | 23.8819 | 24.0741 | 74.7073 | 24.0741 | 23.6234 | 23.8819
75.7073 | -179.2927 | 23.6199 | 23.8876 | 24.0698 | 75.7073 | 24.0698 | 23.6199 | 23.8876
76.7073 | -178.2927 | 23.5965 | 23.8854 | 24.0686 | 76.7073 | 24.0686 | 23.5965 | 23.8854
77.7073 | -177.2927 | 23.6259 | 23.8824 | 24.0644 | 77.7073 | 24.0644 | 23.6259 | 23.8824
78.7073 | -176.2927 | 23.6142 | 23.8741 | 24.0597 | 78.7073 | 24.0597 | 23.6142 | 23.8741
79.7073 | -175.2927 | 23.6254 | 23.8796 | 24.0672 | 79.7073 | 24.0672 | 23.6254 | 23.8796
80.7073 | -174.2927 | 23.6184 | 23.8826 | 24.0679 | 80.7073 | 24.0679 | 23.6184 | 23.8826
81.7073 | -173.2927 | 23.6191 | 23.8844 | 24.0637 | 81.7073 | 24.0637 | 23.6191 | 23.8844
82.7073 | -172.2927 | 23.621 | 23.8776 | 24.0597 | 82.7073 | 24.0597 | 23.621 | 23.8776
83.7073 | -171.2927 | 23.607 | 23.8776 | 24.0543 | 83.7073 | 24.0543 | 23.607 | 23.8776
84.7073 | -170.2927 | 23.6193 | 23.8759 | 24.0616 | 84.7073 | 24.0616 | 23.6193 | 23.8759
85.7073 | -169.2927 | 23.6129 | 23.8758 | 24.0667 | 85.7073 | 24.0667 | 23.6129 | 23.8758
86.7073 | -168.2927 | 23.6181 | 23.8792 | 24.0744 | 86.7073 | 24.0744 | 23.6181 | 23.8792
87.7073 | -167.2927 | 23.6133 | 23.8758 | 24.065 | 87.7073 | 24.065 | 23.6133 | 23.8758
88.7073 | -166.2927 | 23.6173 | 23.8762 | 24.0641 | 88.7073 | 24.0641 | 23.6173 | 23.8762
89.7073 | -165.2927 | 23.6179 | 23.8643 | 24.0432 | 89.7073 | 24.0432 | 23.6179 | 23.8643
90.7073 | -164.2927 | 23.6198 | 23.8728 | 24.0444 | 90.7073 | 24.0444 | 23.6198 | 23.8728
91.7073 | -163.2927 | 23.6124 | 23.8683 | 24.0444 | 91.7073 | 24.0444 | 23.6124 | 23.8683
92.7073 | -162.2927 | 23.615 | 23.869 | 24.0434 | 92.7073 | 24.0434 | 23.615 | 23.869
93.7073 | -161.2927 | 23.6173 | 23.8663 | 24.0411 | 93.7073 | 24.0411 | 23.6173 | 23.8663
94.7073 | -160.2927 | 23.6108 | 23.8617 | 24.0481 | 94.7073 | 24.0481 | 23.6108 | 23.8617
95.7073 | -159.2927 | 23.63 | 23.8676 | 24.0397 | 95.7073 | 24.0397 | 23.63 | 23.8676
96.7073 | -158.2927 | 23.6075 | 23.8664 | 24.0389 | 96.7073 | 24.0389 | 23.6075 | 23.8664
97.7073 | -157.2927 | 23.6152 | 23.8636 | 24.0448 | 97.7073 | 24.0448 | 23.6152 | 23.8636
98.7073 | -156.2927 | 23.6141 | 23.861 | 24.0473 | 98.7073 | 24.0473 | 23.6141 | 23.861
99.7073 | -155.2927 | 23.5991 | 23.865 | 24.0411 | 99.7073 | 24.0411 | 23.5991 | 23.865
100.7073 | -154.2927 | 23.6015 | 23.8661 | 24.0435 | 100.7073 | 24.0435 | 23.6015 | 23.8661
101.7073 | -153.2927 | 23.6126 | 23.8618 | 24.0422 | 101.7073 | 24.0422 | 23.6126 | 23.8618
102.7073 | -152.2927 | 23.6138 | 23.8588 | 24.0369 | 102.7073 | 24.0369 | 23.6138 | 23.8588
103.7073 | -151.2927 | 23.6038 | 23.8606 | 24.0396 | 103.7073 | 24.0396 | 23.6038 | 23.8606
104.7073 | -150.2927 | 23.6098 | 23.8683 | 24.0342 | 104.7073 | 24.0342 | 23.6098 | 23.8683
105.7073 | -149.2927 | 23.6063 | 23.856 | 24.0335 | 105.7073 | 24.0335 | 23.6063 | 23.856
106.7073 | -148.2927 | 23.6185 | 23.8573 | 24.0409 | 106.7073 | 24.0409 | 23.6185 | 23.8573
107.7073 | -147.2927 | 23.6037 | 23.8547 | 24.032 | 107.7073 | 24.032 | 23.6037 | 23.8547
108.7073 | -146.2927 | 23.5914 | 23.8541 | 24.032 | 108.7073 | 24.032 | 23.5914 | 23.8541
109.7073 | -145.2927 | 23.6042 | 23.8579 | 24.0275 | 109.7073 | 24.0275 | 23.6042 | 23.8579
110.7073 | -144.2927 | 23.6136 | 23.8458 | 24.034 | 110.7073 | 24.034 | 23.6136 | 23.8458
111.7073 | -143.2927 | 23.6065 | 23.846 | 24.0257 | 111.7073 | 24.0257 | 23.6065 | 23.846
112.7073 | -142.2927 | 23.6096 | 23.8454 | 24.0304 | 112.7073 | 24.0304 | 23.6096 | 23.8454
113.7073 | -141.2927 | 23.6018 | 23.8489 | 24.0193 | 113.7073 | 24.0193 | 23.6018 | 23.8489
114.7073 | -140.2927 | 23.5876 | 23.8415 | 24.022 | 114.7073 | 24.022 | 23.5876 | 23.8415
115.7073 | -139.2927 | 23.6096 | 23.8435 | 24.0255 | 115.7073 | 24.0255 | 23.6096 | 23.8435
116.7073 | -138.2927 | 23.6039 | 23.8447 | 24.0177 | 116.7073 | 24.0177 | 23.6039 | 23.8447
117.7073 | -137.2927 | 23.6047 | 23.8426 | 24.0088 | 117.7073 | 24.0088 | 23.6047 | 23.8426
118.7073 | -136.2927 | 23.5944 | 23.8427 | 24.0169 | 118.7073 | 24.0169 | 23.5944 | 23.8427
119.7073 | -135.2927 | 23.5905 | 23.8412 | 24.0159 | 119.7073 | 24.0159 | 23.5905 | 23.8412
120.7073 | -134.2927 | 23.6 | 23.8402 | 24.0076 | 120.7073 | 24.0076 | 23.6 | 23.8402
121.7073 | -133.2927 | 23.5859 | 23.8442 | 24.0056 | 121.7073 | 24.0056 | 23.5859 | 23.8442
122.7073 | -132.2927 | 23.6062 | 23.8448 | 24.005 | 122.7073 | 24.005 | 23.6062 | 23.8448
123.7073 | -131.2927 | 23.6031 | 23.842 | 23.997 | 123.7073 | 23.997 | 23.6031 | 23.842
124.7073 | -130.2927 | 23.601 | 23.8356 | 24.005 | 124.7073 | 24.005 | 23.601 | 23.8356
125.7073 | -129.2927 | 23.6067 | 23.8415 | 24.0074 | 125.7073 | 24.0074 | 23.6067 | 23.8415
126.7073 | -128.2927 | 23.5978 | 23.8317 | 24.0015 | 126.7073 | 24.0015 | 23.5978 | 23.8317
127.7073 | -127.2927 | 23.605 | 23.8379 | 24.0018 | 127.7073 | 24.0018 | 23.605 | 23.8379
128.7073 | -126.2927 | 23.587 | 23.8349 | 24.0043 | 128.7073 | 24.0043 | 23.587 | 23.8349
129.7229 | -125.2771 | 23.5941 | 23.832 | 24.0179 | 129.7229 | 24.0179 | 23.5941 | 23.832
130.7073 | -124.2927 | 23.5975 | 23.8388 | 24.0044 | 130.7073 | 24.0044 | 23.5975 | 23.8388
131.7073 | -123.2927 | 23.6001 | 23.8288 | 23.9948 | 131.7073 | 23.9948 | 23.6001 | 23.8288
132.7073 | -122.2927 | 23.5997 | 23.8357 | 23.9943 | 132.7073 | 23.9943 | 23.5997 | 23.8357
133.7073 | -121.2927 | 23.5941 | 23.8341 | 23.9845 | 133.7073 | 23.9845 | 23.5941 | 23.8341
134.7073 | -120.2927 | 23.5894 | 23.8372 | 23.9857 | 134.7073 | 23.9857 | 23.5894 | 23.8372
135.7073 | -119.2927 | 23.5918 | 23.8334 | 23.9925 | 135.7073 | 23.9925 | 23.5918 | 23.8334
136.7073 | -118.2927 | 23.5935 | 23.8276 | 23.9855 | 136.7073 | 23.9855 | 23.5935 | 23.8276
137.7073 | -117.2927 | 23.5965 | 23.8294 | 23.9853 | 137.7073 | 23.9853 | 23.5965 | 23.8294
138.7073 | -116.2927 | 23.5943 | 23.8289 | 23.986 | 138.7073 | 23.986 | 23.5943 | 23.8289
139.7073 | -115.2927 | 23.5896 | 23.8256 | 23.9929 | 139.7073 | 23.9929 | 23.5896 | 23.8256
140.7073 | -114.2927 | 23.5941 | 23.8128 | 23.9844 | 140.7073 | 23.9844 | 23.5941 | 23.8128
141.7073 | -113.2927 | 23.5875 | 23.8268 | 23.9859 | 141.7073 | 23.9859 | 23.5875 | 23.8268
142.7073 | -112.2927 | 23.582 | 23.8222 | 23.9843 | 142.7073 | 23.9843 | 23.582 | 23.8222
143.7073 | -111.2927 | 23.5964 | 23.8182 | 23.975 | 143.7073 | 23.975 | 23.5964 | 23.8182
144.7073 | -110.2927 | 23.5919 | 23.823 | 23.9707 | 144.7073 | 23.9707 | 23.5919 | 23.823
145.7073 | -109.2927 | 23.5872 | 23.8187 | 23.972 | 145.7073 | 23.972 | 23.5872 | 23.8187
146.7073 | -108.2927 | 23.5777 | 23.8201 | 23.9711 | 146.7073 | 23.9711 | 23.5777 | 23.8201
147.7073 | -107.2927 | 23.591 | 23.8131 | 23.9745 | 147.7073 | 23.9745 | 23.591 | 23.8131
148.7073 | -106.2927 | 23.5847 | 23.8207 | 23.9722 | 148.7073 | 23.9722 | 23.5847 | 23.8207
149.7073 | -105.2927 | 23.5947 | 23.8153 | 23.9776 | 149.7073 | 23.9776 | 23.5947 | 23.8153
150.7073 | -104.2927 | 23.5821 | 23.8153 | 23.9708 | 150.7073 | 23.9708 | 23.5821 | 23.8153
151.7073 | -103.2927 | 23.5866 | 23.8113 | 23.9739 | 151.7073 | 23.9739 | 23.5866 | 23.8113
152.7073 | -102.2927 | 23.583 | 23.806 | 23.967 | 152.7073 | 23.967 | 23.583 | 23.806
153.7073 | -101.2927 | 23.5965 | 23.8139 | 23.9623 | 153.7073 | 23.9623 | 23.5965 | 23.8139
154.7073 | -100.2927 | 23.5822 | 23.8093 | 23.966 | 154.7073 | 23.966 | 23.5822 | 23.8093
155.7073 | -99.2927 | 23.5874 | 23.8108 | 23.962 | 155.7073 | 23.962 | 23.5874 | 23.8108
156.7073 | -98.2927 | 23.5853 | 23.8017 | 23.9612 | 156.7073 | 23.9612 | 23.5853 | 23.8017
157.7073 | -97.2927 | 23.5721 | 23.804 | 23.9611 | 157.7073 | 23.9611 | 23.5721 | 23.804
158.7073 | -96.2927 | 23.5822 | 23.8071 | 23.958 | 158.7073 | 23.958 | 23.5822 | 23.8071
159.7073 | -95.2927 | 23.5877 | 23.8025 | 23.9595 | 159.7073 | 23.9595 | 23.5877 | 23.8025
160.7073 | -94.2927 | 23.5836 | 23.8038 | 23.9607 | 160.7073 | 23.9607 | 23.5836 | 23.8038
161.7073 | -93.2927 | 23.578 | 23.8065 | 23.96 | 161.7073 | 23.96 | 23.578 | 23.8065
162.7073 | -92.2927 | 23.5806 | 23.8034 | 23.9569 | 162.7073 | 23.9569 | 23.5806 | 23.8034
163.7073 | -91.2927 | 23.5768 | 23.796 | 23.9612 | 163.7073 | 23.9612 | 23.5768 | 23.796
164.7073 | -90.2927 | 23.5818 | 23.8005 | 23.959 | 164.7073 | 23.959 | 23.5818 | 23.8005
165.7073 | -89.2927 | 23.5793 | 23.8037 | 23.9527 | 165.7073 | 23.9527 | 23.5793 | 23.8037
166.7073 | -88.2927 | 23.5789 | 23.8014 | 23.9523 | 166.7073 | 23.9523 | 23.5789 | 23.8014
167.7073 | -87.2927 | 23.5795 | 23.7946 | 23.9412 | 167.7073 | 23.9412 | 23.5795 | 23.7946
168.7073 | -86.2927 | 23.5775 | 23.7991 | 23.9434 | 168.7073 | 23.9434 | 23.5775 | 23.7991
169.7073 | -85.2927 | 23.5837 | 23.8067 | 23.942 | 169.7073 | 23.942 | 23.5837 | 23.8067
170.7073 | -84.2927 | 23.5797 | 23.7987 | 23.9534 | 170.7073 | 23.9534 | 23.5797 | 23.7987
171.7073 | -83.2927 | 23.5809 | 23.797 | 23.9495 | 171.7073 | 23.9495 | 23.5809 | 23.797
172.7073 | -82.2927 | 23.5723 | 23.791 | 23.9448 | 172.7073 | 23.9448 | 23.5723 | 23.791
173.7073 | -81.2927 | 23.5785 | 23.7913 | 23.9448 | 173.7073 | 23.9448 | 23.5785 | 23.7913
174.7073 | -80.2927 | 23.5802 | 23.7947 | 23.9456 | 174.7073 | 23.9456 | 23.5802 | 23.7947
175.7073 | -79.2927 | 23.5648 | 23.7854 | 23.9485 | 175.7073 | 23.9485 | 23.5648 | 23.7854
176.7073 | -78.2927 | 23.5739 | 23.7898 | 23.945 | 176.7073 | 23.945 | 23.5739 | 23.7898
177.7073 | -77.2927 | 23.5674 | 23.7989 | 23.9438 | 177.7073 | 23.9438 | 23.5674 | 23.7989
178.7073 | -76.2927 | 23.5771 | 23.784 | 23.9371 | 178.7073 | 23.9371 | 23.5771 | 23.784
179.7073 | -75.2927 | 23.5718 | 23.7917 | 23.9363 | 179.7073 | 23.9363 | 23.5718 | 23.7917
180.7073 | -74.2927 | 23.5779 | 23.79 | 23.9414 | 180.7073 | 23.9414 | 23.5779 | 23.79
181.7073 | -73.2927 | 23.568 | 23.7877 | 23.9451 | 181.7073 | 23.9451 | 23.568 | 23.7877
182.7073 | -72.2927 | 23.5655 | 23.789 | 23.9399 | 182.7073 | 23.9399 | 23.5655 | 23.789
183.7073 | -71.2927 | 23.5665 | 23.7909 | 23.933 | 183.7073 | 23.933 | 23.5665 | 23.7909
184.7073 | -70.2927 | 23.5675 | 23.7825 | 23.9433 | 184.7073 | 23.9433 | 23.5675 | 23.7825
185.7073 | -69.2927 | 23.5591 | 23.783 | 23.9406 | 185.7073 | 23.9406 | 23.5591 | 23.783
186.7073 | -68.2927 | 23.5551 | 23.7828 | 23.9259 | 186.7073 | 23.9259 | 23.5551 | 23.7828
187.7073 | -67.2927 | 23.5647 | 23.7844 | 23.927 | 187.7073 | 23.927 | 23.5647 | 23.7844
188.7073 | -66.2927 | 23.557 | 23.7822 | 23.937 | 188.7073 | 23.937 | 23.557 | 23.7822
189.7073 | -65.2927 | 23.5631 | 23.7852 | 23.926 | 189.7073 | 23.926 | 23.5631 | 23.7852
190.7073 | -64.2927 | 23.5593 | 23.783 | 23.9208 | 190.7073 | 23.9208 | 23.5593 | 23.783
191.7073 | -63.2927 | 23.5608 | 23.7762 | 23.9182 | 191.7073 | 23.9182 | 23.5608 | 23.7762
192.7073 | -62.2927 | 23.5442 | 23.7795 | 23.919 | 192.7073 | 23.919 | 23.5442 | 23.7795
193.7073 | -61.2927 | 23.569 | 23.7738 | 23.9162 | 193.7073 | 23.9162 | 23.569 | 23.7738
194.7073 | -60.2927 | 23.5658 | 23.7725 | 23.9194 | 194.7073 | 23.9194 | 23.5658 | 23.7725
195.7073 | -59.2927 | 23.5577 | 23.7731 | 23.9216 | 195.7073 | 23.9216 | 23.5577 | 23.7731
196.7073 | -58.2927 | 23.5519 | 23.7706 | 23.9124 | 196.7073 | 23.9124 | 23.5519 | 23.7706
197.7073 | -57.2927 | 23.5543 | 23.7776 | 23.9113 | 197.7073 | 23.9113 | 23.5543 | 23.7776
198.7073 | -56.2927 | 23.5651 | 23.7711 | 23.9104 | 198.7073 | 23.9104 | 23.5651 | 23.7711
199.7073 | -55.2927 | 23.5644 | 23.7709 | 23.9167 | 199.7073 | 23.9167 | 23.5644 | 23.7709
200.7073 | -54.2927 | 23.5447 | 23.771 | 23.9169 | 200.7073 | 23.9169 | 23.5447 | 23.771
201.7073 | -53.2927 | 23.5599 | 23.7782 | 23.9126 | 201.7073 | 23.9126 | 23.5599 | 23.7782
202.7073 | -52.2927 | 23.5632 | 23.7694 | 23.9142 | 202.7073 | 23.9142 | 23.5632 | 23.7694
203.7073 | -51.2927 | 23.558 | 23.7692 | 23.9155 | 203.7073 | 23.9155 | 23.558 | 23.7692
204.7073 | -50.2927 | 23.5539 | 23.7691 | 23.9042 | 204.7073 | 23.9042 | 23.5539 | 23.7691
205.7073 | -49.2927 | 23.5589 | 23.7686 | 23.9034 | 205.7073 | 23.9034 | 23.5589 | 23.7686
206.7073 | -48.2927 | 23.5486 | 23.7642 | 23.9031 | 206.7073 | 23.9031 | 23.5486 | 23.7642
207.7073 | -47.2927 | 23.5559 | 23.7612 | 23.9053 | 207.7073 | 23.9053 | 23.5559 | 23.7612
208.7073 | -46.2927 | 23.5558 | 23.7606 | 23.9142 | 208.7073 | 23.9142 | 23.5558 | 23.7606
209.7073 | -45.2927 | 23.5544 | 23.762 | 23.9011 | 209.7073 | 23.9011 | 23.5544 | 23.762
210.7073 | -44.2927 | 23.5571 | 23.7652 | 23.8999 | 210.7073 | 23.8999 | 23.5571 | 23.7652
211.7073 | -43.2927 | 23.5408 | 23.7536 | 23.9069 | 211.7073 | 23.9069 | 23.5408 | 23.7536
212.7073 | -42.2927 | 23.56 | 23.7574 | 23.8943 | 212.7073 | 23.8943 | 23.56 | 23.7574
213.7073 | -41.2927 | 23.5441 | 23.7624 | 23.8997 | 213.7073 | 23.8997 | 23.5441 | 23.7624
214.7073 | -40.2927 | 23.5534 | 23.7606 | 23.9085 | 214.7073 | 23.9085 | 23.5534 | 23.7606
215.7073 | -39.2927 | 23.5458 | 23.7584 | 23.901 | 215.7073 | 23.901 | 23.5458 | 23.7584
216.7073 | -38.2927 | 23.5497 | 23.7562 | 23.901 | 216.7073 | 23.901 | 23.5497 | 23.7562
217.7073 | -37.2927 | 23.5579 | 23.7605 | 23.8878 | 217.7073 | 23.8878 | 23.5579 | 23.7605
218.7073 | -36.2927 | 23.5485 | 23.7568 | 23.8936 | 218.7073 | 23.8936 | 23.5485 | 23.7568
219.7073 | -35.2927 | 23.5535 | 23.7583 | 23.8887 | 219.7073 | 23.8887 | 23.5535 | 23.7583
220.7073 | -34.2927 | 23.5552 | 23.7548 | 23.8857 | 220.7073 | 23.8857 | 23.5552 | 23.7548
221.7073 | -33.2927 | 23.5473 | 23.7509 | 23.8889 | 221.7073 | 23.8889 | 23.5473 | 23.7509
222.7073 | -32.2927 | 23.5382 | 23.7501 | 23.8856 | 222.7073 | 23.8856 | 23.5382 | 23.7501
223.7073 | -31.2927 | 23.5375 | 23.7574 | 23.8821 | 223.7073 | 23.8821 | 23.5375 | 23.7574
224.7073 | -30.2927 | 23.5445 | 23.7562 | 23.8762 | 224.7073 | 23.8762 | 23.5445 | 23.7562
225.7073 | -29.2927 | 23.5475 | 23.7525 | 23.8701 | 225.7073 | 23.8701 | 23.5475 | 23.7525
226.7073 | -28.2927 | 23.5444 | 23.7471 | 23.8725 | 226.7073 | 23.8725 | 23.5444 | 23.7471
227.7073 | -27.2927 | 23.537 | 23.7468 | 23.8734 | 227.7073 | 23.8734 | 23.537 | 23.7468
228.7073 | -26.2927 | 23.5493 | 23.7501 | 23.8776 | 228.7073 | 23.8776 | 23.5493 | 23.7501
229.7073 | -25.2927 | 23.5377 | 23.7465 | 23.8807 | 229.7073 | 23.8807 | 23.5377 | 23.7465
230.7073 | -24.2927 | 23.5448 | 23.7462 | 23.8788 | 230.7073 | 23.8788 | 23.5448 | 23.7462
231.7073 | -23.2927 | 23.5513 | 23.75 | 23.8874 | 231.7073 | 23.8874 | 23.5513 | 23.75
232.7073 | -22.2927 | 23.5415 | 23.7439 | 23.8849 | 232.7073 | 23.8849 | 23.5415 | 23.7439
233.7073 | -21.2927 | 23.5387 | 23.739 | 23.8777 | 233.7073 | 23.8777 | 23.5387 | 23.739
234.7542 | -20.2458 | 23.5406 | 23.7574 | 23.8788 | 234.7542 | 23.8788 | 23.5406 | 23.7574
235.7698 | -19.2302 | 23.5481 | 23.7501 | 23.8731 | 235.7698 | 23.8731 | 23.5481 | 23.7501
236.8323 | -18.1677 | 23.539 | 23.7459 | 23.868 | 236.8323 | 23.868 | 23.539 | 23.7459
237.7229 | -17.2771 | 23.5349 | 23.7454 | 23.8706 | 237.7229 | 23.8706 | 23.5349 | 23.7454
238.7542 | -16.2458 | 23.5379 | 23.7426 | 23.871 | 238.7542 | 23.871 | 23.5379 | 23.7426
239.7542 | -15.2458 | 23.539 | 23.745 | 23.8716 | 239.7542 | 23.8716 | 23.539 | 23.745
240.8167 | -14.1833 | 23.53 | 23.7469 | 23.8751 | 240.8167 | 23.8751 | 23.53 | 23.7469
241.7698 | -13.2302 | 23.5429 | 23.7401 | 23.8835 | 241.7698 | 23.8835 | 23.5429 | 23.7401
242.7073 | -12.2927 | 23.5415 | 23.7399 | 23.8733 | 242.7073 | 23.8733 | 23.5415 | 23.7399
243.7229 | -11.2771 | 23.5372 | 23.7349 | 23.8693 | 243.7229 | 23.8693 | 23.5372 | 23.7349
244.7073 | -10.2927 | 23.5268 | 23.7415 | 23.8669 | 244.7073 | 23.8669 | 23.5268 | 23.7415
245.7073 | -9.2927 | 23.5435 | 23.7313 | 23.8682 | 245.7073 | 23.8682 | 23.5435 | 23.7313
246.7229 | -8.2771 | 23.5261 | 23.732 | 23.8581 | 246.7229 | 23.8581 | 23.5261 | 23.732
247.7073 | -7.2927 | 23.5233 | 23.7394 | 23.8465 | 247.7073 | 23.8465 | 23.5233 | 23.7394
248.7073 | -6.2927 | 23.5332 | 23.7408 | 23.8392 | 248.7073 | 23.8392 | 23.5332 | 23.7408
249.7073 | -5.2927 | 23.5318 | 23.7321 | 23.8503 | 249.7073 | 23.8503 | 23.5318 | 23.7321
250.7073 | -4.2927 | 23.5444 | 23.7312 | 23.8472 | 250.7073 | 23.8472 | 23.5444 | 23.7312
251.7073 | -3.2927 | 23.5254 | 23.7278 | 23.8429 | 251.7073 | 23.8429 | 23.5254 | 23.7278
252.801 | -2.199 | 23.5263 | 23.7308 | 23.8501 | 252.801 | 23.8501 | 23.5263 | 23.7308
253.7229 | -1.2771 | 23.538 | 23.7324 | 23.8466 | 253.7229 | 23.8466 | 23.538 | 23.7324
254.801 | -0.199 | 23.5271 | 23.7331 | 23.8399 | 254.801 | 23.8399 | 23.5271 | 23.7331
255.7229 | 0.7229 | 23.5365 | 23.7281 | 23.8506 | 255.7229 | 23.8506 | 23.5365 | 23.7281
256.7073 | 1.7073 | 23.5163 | 23.7254 | 23.847 | 256.7073 | 23.847 | 23.5163 | 23.7254
257.7073 | 2.7073 | 23.5286 | 23.7301 | 23.8396 | 257.7073 | 23.8396 | 23.5286 | 23.7301
258.7073 | 3.7073 | 23.5252 | 23.726 | 23.843 | 258.7073 | 23.843 | 23.5252 | 23.726
259.7073 | 4.7073 | 23.5338 | 23.727 | 24.0913 | 259.7073 | 24.0913 | 23.5338 | 23.727
260.7073 | 5.7073 | 23.5264 | 23.7253 | 24.9839 | 260.7073 | 24.9839 | 23.5264 | 23.7253
261.7073 | 6.7073 | 23.5204 | 23.7285 | 26.6133 | 261.7073 | 26.6133 | 23.5204 | 23.7285
262.7073 | 7.7073 | 23.5257 | 23.7222 | 28.9164 | 262.7073 | 28.9164 | 23.5257 | 23.7222
263.7073 | 8.7073 | 23.5202 | 23.7335 | 31.787 | 263.7073 | 31.787 | 23.5202 | 23.7335
264.7073 | 9.7073 | 23.5237 | 23.7306 | 35.1163 | 264.7073 | 35.1163 | 23.5237 | 23.7306
265.7073 | 10.7073 | 23.514 | 23.7183 | 38.8566 | 265.7073 | 38.8566 | 23.514 | 23.7183
266.7073 | 11.7073 | 23.5233 | 23.7245 | 42.9207 | 266.7073 | 42.9207 | 23.5233 | 23.7245
267.7073 | 12.7073 | 23.5304 | 23.7276 | 47.2841 | 267.7073 | 47.2841 | 23.5304 | 23.7276
268.7073 | 13.7073 | 23.5297 | 23.7163 | 51.8631 | 268.7073 | 51.8631 | 23.5297 | 23.7163
269.7073 | 14.7073 | 23.5262 | 23.7287 | 56.6227 | 269.7073 | 56.6227 | 23.5262 | 23.7287
270.7073 | 15.7073 | 23.5314 | 23.7267 | 61.5363 | 270.7073 | 61.5363 | 23.5314 | 23.7267
271.7073 | 16.7073 | 23.5386 | 23.7372 | 66.6163 | 271.7073 | 66.6163 | 23.5386 | 23.7372
272.7073 | 17.7073 | 23.5348 | 23.7315 | 71.8118 | 272.7073 | 71.8118 | 23.5348 | 23.7315
273.7073 | 18.7073 | 23.5386 | 23.7455 | 77.1898 | 273.7073 | 77.1898 | 23.5386 | 23.7455
274.7073 | 19.7073 | 23.5592 | 23.7417 | 82.6608 | 274.7073 | 82.6608 | 23.5592 | 23.7417
275.7073 | 20.7073 | 23.5749 | 23.7534 | 88.2634 | 275.7073 | 88.2634 | 23.5749 | 23.7534
276.7073 | 21.7073 | 23.5839 | 23.7646 | 93.952 | 276.7073 | 93.952 | 23.5839 | 23.7646
277.7073 | 22.7073 | 23.6115 | 23.7647 | 99.6908 | 277.7073 | 99.6908 | 23.6115 | 23.7647
278.7073 | 23.7073 | 23.6201 | 23.7865 | 105.5839 | 278.7073 | 105.5839 | 23.6201 | 23.7865
279.7073 | 24.7073 | 23.641 | 23.7935 | 111.4606 | 279.7073 | 111.4606 | 23.641 | 23.7935
280.7073 | 25.7073 | 23.6738 | 23.8071 | 117.3818 | 280.7073 | 117.3818 | 23.6738 | 23.8071
281.7073 | 26.7073 | 23.7112 | 23.8393 | 123.37 | 281.7073 | 123.37 | 23.7112 | 23.8393
282.7073 | 27.7073 | 23.7428 | 23.8691 | 129.3702 | 282.7073 | 129.3702 | 23.7428 | 23.8691
283.7073 | 28.7073 | 23.7832 | 23.8906 | 135.4016 | 283.7073 | 135.4016 | 23.7832 | 23.8906
284.7073 | 29.7073 | 23.8282 | 23.9303 | 141.42 | 284.7073 | 141.42 | 23.8282 | 23.9303
285.7073 | 30.7073 | 23.8693 | 23.962 | 147.4466 | 285.7073 | 147.4466 | 23.8693 | 23.962
286.7073 | 31.7073 | 23.9315 | 23.9991 | 153.4806 | 286.7073 | 153.4806 | 23.9315 | 23.9991
287.7073 | 32.7073 | 24.0008 | 24.0361 | 159.3596 | 287.7073 | 159.3596 | 24.0008 | 24.0361
288.7073 | 33.7073 | 24.0663 | 24.0911 | 165.3272 | 288.7073 | 165.3272 | 24.0663 | 24.0911
289.7073 | 34.7073 | 24.1373 | 24.1361 | 171.2415 | 289.7073 | 171.2415 | 24.1373 | 24.1361
290.7073 | 35.7073 | 24.2255 | 24.1879 | 177.1422 | 290.7073 | 177.1422 | 24.2255 | 24.1879
291.7073 | 36.7073 | 24.2948 | 24.247 | 183.1326 | 291.7073 | 183.1326 | 24.2948 | 24.247
292.7854 | 37.7854 | 24.4149 | 24.3199 | 189.5897 | 292.7854 | 189.5897 | 24.4149 | 24.3199
293.7698 | 38.7698 | 24.5179 | 24.3976 | 195.3935 | 293.7698 | 195.3935 | 24.5179 | 24.3976
294.7073 | 39.7073 | 24.6196 | 24.4582 | 200.9317 | 294.7073 | 200.9317 | 24.6196 | 24.4582
295.7073 | 40.7073 | 24.7183 | 24.5442 | 206.9011 | 295.7073 | 206.9011 | 24.7183 | 24.5442
296.7073 | 41.7073 | 24.8744 | 24.6312 | 212.854 | 296.7073 | 212.854 | 24.8744 | 24.6312
297.7073 | 42.7073 | 25.0094 | 24.7262 | 218.6655 | 297.7073 | 218.6655 | 25.0094 | 24.7262
298.7073 | 43.7073 | 25.151 | 24.8276 | 224.5011 | 298.7073 | 224.5011 | 25.151 | 24.8276
299.7073 | 44.7073 | 25.2866 | 24.9272 | 230.4159 | 299.7073 | 230.4159 | 25.2866 | 24.9272
300.7073 | 45.7073 | 25.4584 | 25.0402 | 236.2136 | 300.7073 | 236.2136 | 25.4584 | 25.0402
301.7073 | 46.7073 | 25.6133 | 25.1569 | 241.9471 | 301.7073 | 241.9471 | 25.6133 | 25.1569
302.7073 | 47.7073 | 25.7937 | 25.2828 | 247.6646 | 302.7073 | 247.6646 | 25.7937 | 25.2828
303.7073 | 48.7073 | 25.9834 | 25.4103 | 253.4674 | 303.7073 | 253.4674 | 25.9834 | 25.4103
304.7073 | 49.7073 | 26.1811 | 25.5486 | 259.2964 | 304.7073 | 259.2964 | 26.1811 | 25.5486
305.7073 | 50.7073 | 26.3829 | 25.6972 | 265.022 | 305.7073 | 265.022 | 26.3829 | 25.6972
306.7073 | 51.7073 | 26.5966 | 25.8518 | 270.7357 | 306.7073 | 270.7357 | 26.5966 | 25.8518
307.7073 | 52.7073 | 26.8093 | 26.016 | 276.3484 | 307.7073 | 276.3484 | 26.8093 | 26.016
308.7073 | 53.7073 | 27.039 | 26.185 | 281.9772 | 308.7073 | 281.9772 | 27.039 | 26.185
309.7073 | 54.7073 | 27.3052 | 26.355 | 287.6003 | 309.7073 | 287.6003 | 27.3052 | 26.355
310.7073 | 55.7073 | 27.554 | 26.5448 | 293.292 | 310.7073 | 293.292 | 27.554 | 26.5448
311.7073 | 56.7073 | 27.8315 | 26.7499 | 299.0061 | 311.7073 | 299.0061 | 27.8315 | 26.7499
312.7073 | 57.7073 | 28.1035 | 26.9466 | 304.5371 | 312.7073 | 304.5371 | 28.1035 | 26.9466
313.7073 | 58.7073 | 28.3953 | 27.1594 | 309.914 | 313.7073 | 309.914 | 28.3953 | 27.1594
314.7073 | 59.7073 | 28.7143 | 27.3965 | 315.3589 | 314.7073 | 315.3589 | 28.7143 | 27.3965
315.7073 | 60.7073 | 29.0132 | 27.6318 | 320.8431 | 315.7073 | 320.8431 | 29.0132 | 27.6318
316.7073 | 61.7073 | 29.3539 | 27.8785 | 326.2871 | 316.7073 | 326.2871 | 29.3539 | 27.8785
317.7073 | 62.7073 | 29.6992 | 28.1305 | 331.4878 | 317.7073 | 331.4878 | 29.6992 | 28.1305
318.7073 | 63.7073 | 30.0519 | 28.3976 | 336.3249 | 318.7073 | 336.3249 | 30.0519 | 28.3976
319.7073 | 64.7073 | 30.4267 | 28.688 | 340.7283 | 319.7073 | 340.7283 | 30.4267 | 28.688
320.7073 | 65.7073 | 30.7974 | 28.9777 | 344.8079 | 320.7073 | 344.8079 | 30.7974 | 28.9777
321.7073 | 66.7073 | 31.1984 | 29.2756 | 348.5553 | 321.7073 | 348.5553 | 31.1984 | 29.2756
322.7073 | 67.7073 | 31.6029 | 29.5984 | 352.1205 | 322.7073 | 352.1205 | 31.6029 | 29.5984
323.7073 | 68.7073 | 32.0329 | 29.9351 | 355.4695 | 323.7073 | 355.4695 | 32.0329 | 29.9351
324.7073 | 69.7073 | 32.4668 | 30.2583 | 358.8685 | 324.7073 | 358.8685 | 32.4668 | 30.2583
325.7073 | 70.7073 | 32.9203 | 30.6049 | 361.9786 | 325.7073 | 361.9786 | 32.9203 | 30.6049
326.7073 | 71.7073 | 33.3885 | 30.9514 | 364.8096 | 326.7073 | 364.8096 | 33.3885 | 30.9514
327.7073 | 72.7073 | 33.863 | 31.3046 | 367.4724 | 327.7073 | 367.4724 | 33.863 | 31.3046
328.7073 | 73.7073 | 34.3521 | 31.6714 | 369.8389 | 328.7073 | 369.8389 | 34.3521 | 31.6714
329.7073 | 74.7073 | 34.8127 | 32.0464 | 371.862 | 329.7073 | 371.862 | 34.8127 | 32.0464
330.7073 | 75.7073 | 35.2212 | 32.4358 | 373.6628 | 330.7073 | 373.6628 | 35.2212 | 32.4358
331.7073 | 76.7073 | 35.6794 | 32.8179 | 375.2587 | 331.7073 | 375.2587 | 35.6794 | 32.8179
332.7073 | 77.7073 | 36.1846 | 33.2261 | 376.5677 | 332.7073 | 376.5677 | 36.1846 | 33.2261
333.7073 | 78.7073 | 36.7154 | 33.6147 | 377.6104 | 333.7073 | 377.6104 | 36.7154 | 33.6147
334.7073 | 79.7073 | 37.2763 | 34.0282 | 378.3592 | 334.7073 | 378.3592 | 37.2763 | 34.0282
335.7073 | 80.7073 | 37.8624 | 34.4684 | 379.0827 | 335.7073 | 379.0827 | 37.8624 | 34.4684
336.7073 | 81.7073 | 38.4548 | 34.9041 | 379.5515 | 336.7073 | 379.5515 | 38.4548 | 34.9041
337.7073 | 82.7073 | 39.0732 | 35.3403 | 379.894 | 337.7073 | 379.894 | 39.0732 | 35.3403
338.7073 | 83.7073 | 39.6788 | 35.7927 | 380.042 | 338.7073 | 380.042 | 39.6788 | 35.7927
339.7073 | 84.7073 | 40.2866 | 36.2642 | 380.0359 | 339.7073 | 380.0359 | 40.2866 | 36.2642
340.7073 | 85.7073 | 40.9211 | 36.7283 | 380.0936 | 340.7073 | 380.0936 | 40.9211 | 36.7283
341.7073 | 86.7073 | 41.529 | 37.2421 | 380.0868 | 341.7073 | 380.0868 | 41.529 | 37.2421
342.7073 | 87.7073 | 42.15 | 37.7473 | 379.9906 | 342.7073 | 379.9906 | 42.15 | 37.7473
343.7073 | 88.7073 | 42.7802 | 38.2579 | 379.795 | 343.7073 | 379.795 | 42.7802 | 38.2579
344.7073 | 89.7073 | 43.4168 | 38.7525 | 379.7284 | 344.7073 | 379.7284 | 43.4168 | 38.7525
345.7073 | 90.7073 | 44.0509 | 39.2723 | 379.5445 | 345.7073 | 379.5445 | 44.0509 | 39.2723
346.7073 | 91.7073 | 44.6993 | 39.7839 | 379.3432 | 346.7073 | 379.3432 | 44.6993 | 39.7839
347.7073 | 92.7073 | 45.3385 | 40.3148 | 378.9374 | 347.7073 | 378.9374 | 45.3385 | 40.3148
348.7073 | 93.7073 | 45.9886 | 40.8398 | 378.4728 | 348.7073 | 378.4728 | 45.9886 | 40.8398
349.7073 | 94.7073 | 46.6396 | 41.3659 | 377.9426 | 349.7073 | 377.9426 | 46.6396 | 41.3659
350.7073 | 95.7073 | 47.2984 | 41.8887 | 377.539 | 350.7073 | 377.539 | 47.2984 | 41.8887
351.7073 | 96.7073 | 47.9479 | 42.4199 | 377.1134 | 351.7073 | 377.1134 | 47.9479 | 42.4199
352.7073 | 97.7073 | 48.604 | 42.9561 | 376.7512 | 352.7073 | 376.7512 | 48.604 | 42.9561
353.7073 | 98.7073 | 49.2421 | 43.5002 | 376.3596 | 353.7073 | 376.3596 | 49.2421 | 43.5002
354.7073 | 99.7073 | 49.8725 | 44.0394 | 375.9759 | 354.7073 | 375.9759 | 49.8725 | 44.0394
355.7073 | 100.7073 | 50.5205 | 44.5621 | 375.6322 | 355.7073 | 375.6322 | 50.5205 | 44.5621
356.7073 | 101.7073 | 51.1439 | 45.1121 | 375.4808 | 356.7073 | 375.4808 | 51.1439 | 45.1121
357.7073 | 102.7073 | 51.765 | 45.6671 | 375.3044 | 357.7073 | 375.3044 | 51.765 | 45.6671
358.7073 | 103.7073 | 52.4013 | 46.2324 | 375.0188 | 358.7073 | 375.0188 | 52.4013 | 46.2324
359.7073 | 104.7073 | 53.0356 | 46.8262 | 374.6707 | 359.7073 | 374.6707 | 53.0356 | 46.8262
360.7073 | 105.7073 | 53.6472 | 47.4577 | 374.3559 | 360.7073 | 374.3559 | 53.6472 | 47.4577
361.7073 | 106.7073 | 54.2412 | 48.1415 | 374.1645 | 361.7073 | 374.1645 | 54.2412 | 48.1415
362.7073 | 107.7073 | 54.885 | 48.8114 | 373.866 | 362.7073 | 373.866 | 54.885 | 48.8114
363.7073 | 108.7073 | 55.4718 | 49.4715 | 373.7072 | 363.7073 | 373.7072 | 55.4718 | 49.4715
364.7073 | 109.7073 | 56.0881 | 50.156 | 373.5896 | 364.7073 | 373.5896 | 56.0881 | 50.156
365.8948 | 110.8948 | 56.8122 | 51.0722 | 373.5367 | 365.8948 | 373.5367 | 56.8122 | 51.0722
366.7542 | 111.7542 | 57.3624 | 51.6619 | 373.4198 | 366.7542 | 373.4198 | 57.3624 | 51.6619
367.7073 | 112.7073 | 57.9317 | 52.3918 | 373.3586 | 367.7073 | 373.3586 | 57.9317 | 52.3918
368.7073 | 113.7073 | 58.5323 | 53.1519 | 373.4627 | 368.7073 | 373.4627 | 58.5323 | 53.1519
369.7073 | 114.7073 | 59.1195 | 53.9666 | 373.6105 | 369.7073 | 373.6105 | 59.1195 | 53.9666
370.7073 | 115.7073 | 59.7051 | 54.7103 | 373.6257 | 370.7073 | 373.6257 | 59.7051 | 54.7103
371.7073 | 116.7073 | 60.3016 | 55.4836 | 373.7671 | 371.7073 | 373.7671 | 60.3016 | 55.4836
372.7073 | 117.7073 | 60.8874 | 56.2283 | 373.9957 | 372.7073 | 373.9957 | 60.8874 | 56.2283
373.7073 | 118.7073 | 61.4789 | 56.962 | 374.0334 | 373.7073 | 374.0334 | 61.4789 | 56.962
374.7073 | 119.7073 | 62.064 | 57.7283 | 374.1132 | 374.7073 | 374.1132 | 62.064 | 57.7283
375.7073 | 120.7073 | 62.6459 | 58.4464 | 374.4118 | 375.7073 | 374.4118 | 62.6459 | 58.4464
376.7073 | 121.7073 | 63.2079 | 59.1128 | 374.562 | 376.7073 | 374.562 | 63.2079 | 59.1128
377.7073 | 122.7073 | 63.7847 | 59.8143 | 374.6921 | 377.7073 | 374.6921 | 63.7847 | 59.8143
378.7073 | 123.7073 | 64.3688 | 60.4788 | 374.835 | 378.7073 | 374.835 | 64.3688 | 60.4788
379.7073 | 124.7073 | 64.9467 | 61.177 | 375.0662 | 379.7073 | 375.0662 | 64.9467 | 61.177
380.7073 | 125.7073 | 65.5196 | 61.8481 | 375.2848 | 380.7073 | 375.2848 | 65.5196 | 61.8481
381.7073 | 126.7073 | 66.0973 | 62.5013 | 375.4339 | 381.7073 | 375.4339 | 66.0973 | 62.5013
382.7073 | 127.7073 | 66.6761 | 63.1884 | 375.6004 | 382.7073 | 375.6004 | 66.6761 | 63.1884
383.7073 | 128.7073 | 67.2544 | 63.8556 | 375.8172 | 383.7073 | 375.8172 | 67.2544 | 63.8556
384.7073 | 129.7073 | 67.8137 | 64.5437 | 376.0914 | 384.7073 | 376.0914 | 67.8137 | 64.5437
385.7073 | 130.7073 | 68.3726 | 65.2019 | 376.2942 | 385.7073 | 376.2942 | 68.3726 | 65.2019
386.7073 | 131.7073 | 68.9267 | 65.8278 | 376.5189 | 386.7073 | 376.5189 | 68.9267 | 65.8278
387.7073 | 132.7073 | 69.4839 | 66.4726 | 376.5559 | 387.7073 | 376.5559 | 69.4839 | 66.4726
388.7073 | 133.7073 | 70.0523 | 67.1184 | 376.559 | 388.7073 | 376.559 | 70.0523 | 67.1184
389.7073 | 134.7073 | 70.6157 | 67.7179 | 376.5182 | 389.7073 | 376.5182 | 70.6157 | 67.7179
390.7073 | 135.7073 | 71.1696 | 68.3161 | 376.7582 | 390.7073 | 376.7582 | 71.1696 | 68.3161
391.7073 | 136.7073 | 71.7182 | 68.9205 | 376.9044 | 391.7073 | 376.9044 | 71.7182 | 68.9205
392.7073 | 137.7073 | 72.262 | 69.5248 | 377.0011 | 392.7073 | 377.0011 | 72.262 | 69.5248
393.7073 | 138.7073 | 72.8043 | 70.1288 | 377.2116 | 393.7073 | 377.2116 | 72.8043 | 70.1288
394.7073 | 139.7073 | 73.3362 | 70.7175 | 377.3566 | 394.7073 | 377.3566 | 73.3362 | 70.7175
395.7073 | 140.7073 | 73.8871 | 71.2906 | 377.5896 | 395.7073 | 377.5896 | 73.8871 | 71.2906
396.7073 | 141.7073 | 74.4217 | 71.8762 | 377.7206 | 396.7073 | 377.7206 | 74.4217 | 71.8762
397.7073 | 142.7073 | 74.9722 | 72.4369 | 377.8377 | 397.7073 | 377.8377 | 74.9722 | 72.4369
398.7073 | 143.7073 | 75.5092 | 73.004 | 377.9362 | 398.7073 | 377.9362 | 75.5092 | 73.004
399.7073 | 144.7073 | 76.0475 | 73.569 | 377.9846 | 399.7073 | 377.9846 | 76.0475 | 73.569
400.7073 | 145.7073 | 76.5816 | 74.113 | 377.988 | 400.7073 | 377.988 | 76.5816 | 74.113
401.7073 | 146.7073 | 77.0981 | 74.6607 | 378.018 | 401.7073 | 378.018 | 77.0981 | 74.6607
402.7073 | 147.7073 | 77.6586 | 75.2306 | 378.0132 | 402.7073 | 378.0132 | 77.6586 | 75.2306
403.7073 | 148.7073 | 78.1883 | 75.772 | 378.0111 | 403.7073 | 378.0111 | 78.1883 | 75.772
404.7073 | 149.7073 | 78.7162 | 76.3155 | 378.085 | 404.7073 | 378.085 | 78.7162 | 76.3155
405.7073 | 150.7073 | 79.2595 | 76.8437 | 378.1132 | 405.7073 | 378.1132 | 79.2595 | 76.8437
406.7073 | 151.7073 | 79.7643 | 77.3917 | 378.0675 | 406.7073 | 378.0675 | 79.7643 | 77.3917
407.7073 | 152.7073 | 80.2747 | 77.9434 | 378.1146 | 407.7073 | 378.1146 | 80.2747 | 77.9434
408.7073 | 153.7073 | 80.7971 | 78.486 | 378.0334 | 408.7073 | 378.0334 | 80.7971 | 78.486
409.7073 | 154.7073 | 81.2812 | 79.0138 | 378.0418 | 409.7073 | 378.0418 | 81.2812 | 79.0138
410.7073 | 155.7073 | 81.815 | 79.5677 | 378.006 | 410.7073 | 378.006 | 81.815 | 79.5677
411.7073 | 156.7073 | 82.3063 | 80.0954 | 378.008 | 411.7073 | 378.008 | 82.3063 | 80.0954
412.7073 | 157.7073 | 82.8257 | 80.6257 | 377.9876 | 412.7073 | 377.9876 | 82.8257 | 80.6257
413.7073 | 158.7073 | 83.3441 | 81.146 | 377.974 | 413.7073 | 377.974 | 83.3441 | 81.146
414.7073 | 159.7073 | 83.8484 | 81.6698 | 378.1436 | 414.7073 | 378.1436 | 83.8484 | 81.6698
415.7073 | 160.7073 | 84.3835 | 82.2011 | 378.2447 | 415.7073 | 378.2447 | 84.3835 | 82.2011
416.7073 | 161.7073 | 84.8928 | 82.7164 | 378.2446 | 416.7073 | 378.2446 | 84.8928 | 82.7164
417.7073 | 162.7073 | 85.4204 | 83.2567 | 377.9892 | 417.7073 | 377.9892 | 85.4204 | 83.2567
418.7073 | 163.7073 | 85.921 | 83.7688 | 377.9615 | 418.7073 | 377.9615 | 85.921 | 83.7688
419.7073 | 164.7073 | 86.4029 | 84.2623 | 377.9121 | 419.7073 | 377.9121 | 86.4029 | 84.2623
420.7073 | 165.7073 | 86.9146 | 84.7795 | 377.9544 | 420.7073 | 377.9544 | 86.9146 | 84.7795
421.7073 | 166.7073 | 87.4107 | 85.2863 | 377.9092 | 421.7073 | 377.9092 | 87.4107 | 85.2863
422.7073 | 167.7073 | 87.9061 | 85.7969 | 377.8216 | 422.7073 | 377.8216 | 87.9061 | 85.7969
423.7073 | 168.7073 | 88.3919 | 86.2977 | 377.879 | 423.7073 | 377.879 | 88.3919 | 86.2977
424.7073 | 169.7073 | 88.8604 | 86.7923 | 377.8994 | 424.7073 | 377.8994 | 88.8604 | 86.7923
425.7073 | 170.7073 | 89.3477 | 87.2848 | 377.9364 | 425.7073 | 377.9364 | 89.3477 | 87.2848
426.7073 | 171.7073 | 89.7983 | 87.7699 | 378.0104 | 426.7073 | 378.0104 | 89.7983 | 87.7699
427.7073 | 172.7073 | 90.3206 | 88.246 | 377.8746 | 427.7073 | 377.8746 | 90.3206 | 88.246
428.7073 | 173.7073 | 90.8174 | 88.7409 | 377.8034 | 428.7073 | 377.8034 | 90.8174 | 88.7409
429.7073 | 174.7073 | 91.3064 | 89.2271 | 377.8496 | 429.7073 | 377.8496 | 91.3064 | 89.2271
430.7073 | 175.7073 | 91.81 | 89.7163 | 377.8996 | 430.7073 | 377.8996 | 91.81 | 89.7163
431.7073 | 176.7073 | 92.2805 | 90.2024 | 377.8822 | 431.7073 | 377.8822 | 92.2805 | 90.2024
432.7073 | 177.7073 | 92.7749 | 90.6862 | 377.8504 | 432.7073 | 377.8504 | 92.7749 | 90.6862
433.7073 | 178.7073 | 93.2589 | 91.1549 | 377.8177 | 433.7073 | 377.8177 | 93.2589 | 91.1549
434.7073 | 179.7073 | 93.7482 | 91.6407 | 377.7689 | 434.7073 | 377.7689 | 93.7482 | 91.6407
435.7073 | 180.7073 | 94.2438 | 92.1148 | 377.7548 | 435.7073 | 377.7548 | 94.2438 | 92.1148
436.7073 | 181.7073 | 94.7139 | 92.5944 | 377.6771 | 436.7073 | 377.6771 | 94.7139 | 92.5944
437.7073 | 182.7073 | 95.1782 | 93.0686 | 377.5633 | 437.7073 | 377.5633 | 95.1782 | 93.0686
438.7073 | 183.7073 | 95.6228 | 93.5319 | 377.581 | 438.7073 | 377.581 | 95.6228 | 93.5319
439.7073 | 184.7073 | 96.0747 | 94.0143 | 377.6826 | 439.7073 | 377.6826 | 96.0747 | 94.0143
440.7073 | 185.7073 | 96.5313 | 94.479 | 377.6219 | 440.7073 | 377.6219 | 96.5313 | 94.479
441.7073 | 186.7073 | 96.9772 | 94.9608 | 377.5798 | 441.7073 | 377.5798 | 96.9772 | 94.9608
442.7073 | 187.7073 | 97.4365 | 95.4291 | 377.5998 | 442.7073 | 377.5998 | 97.4365 | 95.4291
443.7073 | 188.7073 | 97.8949 | 95.8962 | 377.7317 | 443.7073 | 377.7317 | 97.8949 | 95.8962
444.7073 | 189.7073 | 98.3357 | 96.3599 | 377.7875 | 444.7073 | 377.7875 | 98.3357 | 96.3599
445.7073 | 190.7073 | 98.7731 | 96.8251 | 377.7331 | 445.7073 | 377.7331 | 98.7731 | 96.8251
446.7073 | 191.7073 | 99.2227 | 97.2826 | 377.8057 | 446.7073 | 377.8057 | 99.2227 | 97.2826
447.7073 | 192.7073 | 99.6584 | 97.745 | 377.8481 | 447.7073 | 377.8481 | 99.6584 | 97.745
448.7073 | 193.7073 | 100.0912 | 98.2096 | 377.8462 | 448.7073 | 377.8462 | 100.0912 | 98.2096
449.7073 | 194.7073 | 100.5388 | 98.6673 | 378.0259 | 449.7073 | 378.0259 | 100.5388 | 98.6673
450.7073 | 195.7073 | 100.9868 | 99.1271 | 378.2189 | 450.7073 | 378.2189 | 100.9868 | 99.1271
451.7073 | 196.7073 | 101.4379 | 99.5991 | 378.1542 | 451.7073 | 378.1542 | 101.4379 | 99.5991
452.7073 | 197.7073 | 101.8897 | 100.0637 | 378.1586 | 452.7073 | 378.1586 | 101.8897 | 100.0637
453.7073 | 198.7073 | 102.3329 | 100.5218 | 378.2462 | 453.7073 | 378.2462 | 102.3329 | 100.5218
454.7073 | 199.7073 | 102.7794 | 100.9767 | 378.3495 | 454.7073 | 378.3495 | 102.7794 | 100.9767
455.7073 | 200.7073 | 103.2093 | 101.4436 | 378.4278 | 455.7073 | 378.4278 | 103.2093 | 101.4436
456.7073 | 201.7073 | 103.6442 | 101.9059 | 378.5764 | 456.7073 | 378.5764 | 103.6442 | 101.9059
457.7073 | 202.7073 | 104.1063 | 102.375 | 378.7075 | 457.7073 | 378.7075 | 104.1063 | 102.375
458.7073 | 203.7073 | 104.5567 | 102.8258 | 378.6745 | 458.7073 | 378.6745 | 104.5567 | 102.8258
459.7073 | 204.7073 | 104.9995 | 103.2715 | 378.6283 | 459.7073 | 378.6283 | 104.9995 | 103.2715
460.7073 | 205.7073 | 105.4576 | 103.7242 | 378.6404 | 460.7073 | 378.6404 | 105.4576 | 103.7242
461.8635 | 206.8635 | 105.9764 | 104.258 | 378.7407 | 461.8635 | 378.7407 | 105.9764 | 104.258
462.801 | 207.801 | 106.3895 | 104.6869 | 378.829 | 462.801 | 378.829 | 106.3895 | 104.6869
463.7854 | 208.7854 | 106.7981 | 105.1306 | 378.923 | 463.7854 | 378.923 | 106.7981 | 105.1306
464.7542 | 209.7542 | 107.2018 | 105.5828 | 379.0518 | 464.7542 | 379.0518 | 107.2018 | 105.5828
465.7073 | 210.7073 | 107.6291 | 106.0116 | 379.1338 | 465.7073 | 379.1338 | 107.6291 | 106.0116
466.7073 | 211.7073 | 108.0615 | 106.4791 | 379.1635 | 466.7073 | 379.1635 | 108.0615 | 106.4791
467.7073 | 212.7073 | 108.4823 | 106.9209 | 379.2341 | 467.7073 | 379.2341 | 108.4823 | 106.9209
468.7073 | 213.7073 | 108.9214 | 107.3798 | 379.1925 | 468.7073 | 379.1925 | 108.9214 | 107.3798
469.7073 | 214.7073 | 109.3623 | 107.8305 | 379.1934 | 469.7073 | 379.1934 | 109.3623 | 107.8305
470.7073 | 215.7073 | 109.7836 | 108.2701 | 379.1816 | 470.7073 | 379.1816 | 109.7836 | 108.2701
471.7073 | 216.7073 | 110.2123 | 108.7177 | 379.169 | 471.7073 | 379.169 | 110.2123 | 108.7177
472.7073 | 217.7073 | 110.6614 | 109.1648 | 379.0801 | 472.7073 | 379.0801 | 110.6614 | 109.1648
473.7073 | 218.7073 | 111.0757 | 109.6119 | 378.9437 | 473.7073 | 378.9437 | 111.0757 | 109.6119
474.7073 | 219.7073 | 111.5052 | 110.0602 | 378.8304 | 474.7073 | 378.8304 | 111.5052 | 110.0602
475.7073 | 220.7073 | 111.9305 | 110.5045 | 378.8328 | 475.7073 | 378.8328 | 111.9305 | 110.5045
476.7073 | 221.7073 | 112.3653 | 110.9413 | 378.9407 | 476.7073 | 378.9407 | 112.3653 | 110.9413
477.7073 | 222.7073 | 112.7971 | 111.3881 | 378.9111 | 477.7073 | 378.9111 | 112.7971 | 111.3881
478.7073 | 223.7073 | 113.235 | 111.8235 | 378.8232 | 478.7073 | 378.8232 | 113.235 | 111.8235
479.7073 | 224.7073 | 113.665 | 112.2749 | 378.6482 | 479.7073 | 378.6482 | 113.665 | 112.2749
480.7073 | 225.7073 | 114.1113 | 112.7313 | 378.5847 | 480.7073 | 378.5847 | 114.1113 | 112.7313
481.7073 | 226.7073 | 114.5211 | 113.1734 | 378.5031 | 481.7073 | 378.5031 | 114.5211 | 113.1734
482.7073 | 227.7073 | 114.9279 | 113.6221 | 378.4687 | 482.7073 | 378.4687 | 114.9279 | 113.6221
483.7073 | 228.7073 | 115.3366 | 114.0819 | 378.4335 | 483.7073 | 378.4335 | 115.3366 | 114.0819
484.7073 | 229.7073 | 115.7486 | 114.5122 | 378.4034 | 484.7073 | 378.4034 | 115.7486 | 114.5122
485.7073 | 230.7073 | 116.156 | 114.9483 | 378.4969 | 485.7073 | 378.4969 | 116.156 | 114.9483
486.7073 | 231.7073 | 116.5472 | 115.3846 | 378.4461 | 486.7073 | 378.4461 | 116.5472 | 115.3846
487.7073 | 232.7073 | 116.9711 | 115.8247 | 378.3712 | 487.7073 | 378.3712 | 116.9711 | 115.8247
488.7073 | 233.7073 | 117.381 | 116.2474 | 378.4778 | 488.7073 | 378.4778 | 117.381 | 116.2474
489.7073 | 234.7073 | 117.7762 | 116.6809 | 378.594 | 489.7073 | 378.594 | 117.7762 | 116.6809
490.7073 | 235.7073 | 118.1879 | 117.1135 | 378.6442 | 490.7073 | 378.6442 | 118.1879 | 117.1135
491.7073 | 236.7073 | 118.5948 | 117.5404 | 378.483 | 491.7073 | 378.483 | 118.5948 | 117.5404
492.7073 | 237.7073 | 118.9982 | 117.9611 | 378.4688 | 492.7073 | 378.4688 | 118.9982 | 117.9611
493.7073 | 238.7073 | 119.3594 | 118.3848 | 378.3218 | 493.7073 | 378.3218 | 119.3594 | 118.3848
494.7073 | 239.7073 | 119.7079 | 118.8059 | 378.2236 | 494.7073 | 378.2236 | 119.7079 | 118.8059
495.7073 | 240.7073 | 120.0702 | 119.224 | 378.2211 | 495.7073 | 378.2211 | 120.0702 | 119.224
496.7073 | 241.7073 | 120.4265 | 119.6499 | 378.2414 | 496.7073 | 378.2414 | 120.4265 | 119.6499
497.7073 | 242.7073 | 120.7994 | 120.0555 | 378.3423 | 497.7073 | 378.3423 | 120.7994 | 120.0555
498.7073 | 243.7073 | 121.1668 | 120.4671 | 378.2428 | 498.7073 | 378.2428 | 121.1668 | 120.4671
499.7073 | 244.7073 | 121.5087 | 120.8733 | 378.0841 | 499.7073 | 378.0841 | 121.5087 | 120.8733
500.7073 | 245.7073 | 121.8334 | 121.2962 | 377.9481 | 500.7073 | 377.9481 | 121.8334 | 121.2962
501.7073 | 246.7073 | 122.1546 | 121.7184 | 377.8105 | 501.7073 | 377.8105 | 122.1546 | 121.7184
502.7073 | 247.7073 | 122.4315 | 122.1323 | 377.8755 | 502.7073 | 377.8755 | 122.4315 | 122.1323
503.7073 | 248.7073 | 122.7456 | 122.5496 | 377.8266 | 503.7073 | 377.8266 | 122.7456 | 122.5496
504.7073 | 249.7073 | 123.0579 | 122.9513 | 377.772 | 504.7073 | 377.772 | 123.0579 | 122.9513
505.7073 | 250.7073 | 123.3482 | 123.3828 | 377.7341 | 505.7073 | 377.7341 | 123.3482 | 123.3828
506.7073 | 251.7073 | 123.6383 | 123.781 | 377.635 | 506.7073 | 377.635 | 123.6383 | 123.781
507.7073 | 252.7073 | 123.9359 | 124.1698 | 377.503 | 507.7073 | 377.503 | 123.9359 | 124.1698
508.7073 | 253.7073 | 124.2353 | 124.5548 | 377.5169 | 508.7073 | 377.5169 | 124.2353 | 124.5548
509.7073 | 254.7073 | 124.5165 | 124.9451 | 377.5972 | 509.7073 | 377.5972 | 124.5165 | 124.9451
510.7073 | 255.7073 | 124.8044 | 125.3424 | 377.6828 | 510.7073 | 377.6828 | 124.8044 | 125.3424
511.7073 | 256.7073 | 125.0627 | 125.7226 | 377.6699 | 511.7073 | 377.6699 | 125.0627 | 125.7226
512.7073 | 257.7073 | 125.3311 | 126.1071 | 377.5955 | 512.7073 | 377.5955 | 125.3311 | 126.1071
513.7073 | 258.7073 | 125.6351 | 126.484 | 377.6686 | 513.7073 | 377.6686 | 125.6351 | 126.484
514.7073 | 259.7073 | 125.9123 | 126.8438 | 377.7463 | 514.7073 | 377.7463 | 125.9123 | 126.8438
515.7073 | 260.7073 | 126.1591 | 127.2063 | 377.8676 | 515.7073 | 377.8676 | 126.1591 | 127.2063
516.7073 | 261.7073 | 126.4517 | 127.5606 | 377.8992 | 516.7073 | 377.8992 | 126.4517 | 127.5606
517.7073 | 262.7073 | 126.7205 | 127.8866 | 377.9533 | 517.7073 | 377.9533 | 126.7205 | 127.8866
518.7073 | 263.7073 | 126.9953 | 128.2075 | 377.9037 | 518.7073 | 377.9037 | 126.9953 | 128.2075
519.7073 | 264.7073 | 127.265 | 128.5405 | 377.7483 | 519.7073 | 377.7483 | 127.265 | 128.5405
520.7073 | 265.7073 | 127.5264 | 128.8578 | 377.6848 | 520.7073 | 377.6848 | 127.5264 | 128.8578
521.7073 | 266.7073 | 127.8065 | 129.1732 | 377.7377 | 521.7073 | 377.7377 | 127.8065 | 129.1732
522.7073 | 267.7073 | 128.0949 | 129.4836 | 377.7684 | 522.7073 | 377.7684 | 128.0949 | 129.4836
523.7073 | 268.7073 | 128.384 | 129.8224 | 377.7451 | 523.7073 | 377.7451 | 128.384 | 129.8224
524.7073 | 269.7073 | 128.6646 | 130.1582 | 377.734 | 524.7073 | 377.734 | 128.6646 | 130.1582
525.7073 | 270.7073 | 128.9526 | 130.4796 | 377.6912 | 525.7073 | 377.6912 | 128.9526 | 130.4796
526.7073 | 271.7073 | 129.2502 | 130.7887 | 377.7879 | 526.7073 | 377.7879 | 129.2502 | 130.7887
527.7073 | 272.7073 | 129.5628 | 131.0986 | 377.8997 | 527.7073 | 377.8997 | 129.5628 | 131.0986
528.7073 | 273.7073 | 129.8971 | 131.4193 | 377.9106 | 528.7073 | 377.9106 | 129.8971 | 131.4193
529.7073 | 274.7073 | 130.2208 | 131.7222 | 377.794 | 529.7073 | 377.794 | 130.2208 | 131.7222
530.7073 | 275.7073 | 130.5412 | 132.0488 | 377.807 | 530.7073 | 377.807 | 130.5412 | 132.0488
531.7073 | 276.7073 | 130.874 | 132.3648 | 377.6214 | 531.7073 | 377.6214 | 130.874 | 132.3648
532.7073 | 277.7073 | 131.2009 | 132.698 | 377.4887 | 532.7073 | 377.4887 | 131.2009 | 132.698
533.7073 | 278.7073 | 131.5334 | 133.0313 | 377.4845 | 533.7073 | 377.4845 | 131.5334 | 133.0313
534.7073 | 279.7073 | 131.8842 | 133.3535 | 377.4487 | 534.7073 | 377.4487 | 131.8842 | 133.3535
535.7073 | 280.7073 | 132.2291 | 133.6873 | 377.3183 | 535.7073 | 377.3183 | 132.2291 | 133.6873
536.7073 | 281.7073 | 132.5937 | 134.0277 | 377.3373 | 536.7073 | 377.3373 | 132.5937 | 134.0277
537.7073 | 282.7073 | 132.9716 | 134.3615 | 377.3339 | 537.7073 | 377.3339 | 132.9716 | 134.3615
538.7073 | 283.7073 | 133.3403 | 134.6733 | 377.2027 | 538.7073 | 377.2027 | 133.3403 | 134.6733
539.7073 | 284.7073 | 133.6775 | 134.9979 | 377.106 | 539.7073 | 377.106 | 133.6775 | 134.9979
540.7073 | 285.7073 | 134.0348 | 135.2966 | 376.9725 | 540.7073 | 376.9725 | 134.0348 | 135.2966
541.7073 | 286.7073 | 134.3687 | 135.6141 | 376.8255 | 541.7073 | 376.8255 | 134.3687 | 135.6141
542.7073 | 287.7073 | 134.7327 | 135.9012 | 376.7104 | 542.7073 | 376.7104 | 134.7327 | 135.9012
543.7073 | 288.7073 | 135.1069 | 136.1928 | 376.548 | 543.7073 | 376.548 | 135.1069 | 136.1928
544.7073 | 289.7073 | 135.4479 | 136.5101 | 376.4206 | 544.7073 | 376.4206 | 135.4479 | 136.5101
545.7073 | 290.7073 | 135.7766 | 136.8182 | 376.2985 | 545.7073 | 376.2985 | 135.7766 | 136.8182
546.7073 | 291.7073 | 136.1006 | 137.1048 | 376.1662 | 546.7073 | 376.1662 | 136.1006 | 137.1048
547.7073 | 292.7073 | 136.4214 | 137.3798 | 376.1112 | 547.7073 | 376.1112 | 136.4214 | 137.3798
548.7073 | 293.7073 | 136.769 | 137.6673 | 375.9647 | 548.7073 | 375.9647 | 136.769 | 137.6673
549.7073 | 294.7073 | 137.1197 | 137.9605 | 375.9607 | 549.7073 | 375.9607 | 137.1197 | 137.9605
550.7073 | 295.7073 | 137.4359 | 138.2632 | 376.1478 | 550.7073 | 376.1478 | 137.4359 | 138.2632
551.7073 | 296.7073 | 137.7534 | 138.5464 | 376.209 | 551.7073 | 376.209 | 137.7534 | 138.5464
552.7073 | 297.7073 | 138.0767 | 138.828 | 376.1967 | 552.7073 | 376.1967 | 138.0767 | 138.828
553.7073 | 298.7073 | 138.3918 | 139.1039 | 376.3107 | 553.7073 | 376.3107 | 138.3918 | 139.1039
554.7073 | 299.7073 | 138.7483 | 139.3976 | 376.3669 | 554.7073 | 376.3669 | 138.7483 | 139.3976
555.7073 | 300.7073 | 139.0971 | 139.6956 | 376.4115 | 555.7073 | 376.4115 | 139.0971 | 139.6956
556.7073 | 301.7073 | 139.4249 | 139.9879 | 376.5558 | 556.7073 | 376.5558 | 139.4249 | 139.9879
557.7073 | 302.7073 | 139.769 | 140.2689 | 376.6157 | 557.7073 | 376.6157 | 139.769 | 140.2689
558.7073 | 303.7073 | 140.0979 | 140.5382 | 376.7014 | 558.7073 | 376.7014 | 140.0979 | 140.5382
559.7073 | 304.7073 | 140.4119 | 140.8264 | 376.5918 | 559.7073 | 376.5918 | 140.4119 | 140.8264
560.7073 | 305.7073 | 140.7302 | 141.1056 | 376.5107 | 560.7073 | 376.5107 | 140.7302 | 141.1056
561.7073 | 306.7073 | 141.0209 | 141.3889 | 376.3527 | 561.7073 | 376.3527 | 141.0209 | 141.3889
562.7073 | 307.7073 | 141.3061 | 141.6434 | 376.1273 | 562.7073 | 376.1273 | 141.3061 | 141.6434
563.7073 | 308.7073 | 141.5993 | 141.9209 | 376.0142 | 563.7073 | 376.0142 | 141.5993 | 141.9209
564.7073 | 309.7073 | 141.9314 | 142.1882 | 375.949 | 564.7073 | 375.949 | 141.9314 | 142.1882
565.7073 | 310.7073 | 142.2701 | 142.4686 | 375.9399 | 565.7073 | 375.9399 | 142.2701 | 142.4686
566.7073 | 311.7073 | 142.6338 | 142.7375 | 376.0161 | 566.7073 | 376.0161 | 142.6338 | 142.7375
567.7073 | 312.7073 | 142.9546 | 142.9739 | 376.1647 | 567.7073 | 376.1647 | 142.9546 | 142.9739
568.7073 | 313.7073 | 143.3148 | 143.2206 | 376.2154 | 568.7073 | 376.2154 | 143.3148 | 143.2206
569.7073 | 314.7073 | 143.6171 | 143.4688 | 376.0809 | 569.7073 | 376.0809 | 143.6171 | 143.4688
570.7073 | 315.7073 | 143.9352 | 143.7106 | 376.1688 | 570.7073 | 376.1688 | 143.9352 | 143.7106
571.7073 | 316.7073 | 144.2429 | 143.8969 | 376.1648 | 571.7073 | 376.1648 | 144.2429 | 143.8969
572.7073 | 317.7073 | 144.5732 | 144.0988 | 376.063 | 572.7073 | 376.063 | 144.5732 | 144.0988
573.7073 | 318.7073 | 144.8841 | 144.3163 | 376.0222 | 573.7073 | 376.0222 | 144.8841 | 144.3163
574.7073 | 319.7073 | 145.193 | 144.4961 | 375.8983 | 574.7073 | 375.8983 | 145.193 | 144.4961
575.7073 | 320.7073 | 145.4888 | 144.6831 | 375.7801 | 575.7073 | 375.7801 | 145.4888 | 144.6831
576.7073 | 321.7073 | 145.8349 | 144.9123 | 375.7464 | 576.7073 | 375.7464 | 145.8349 | 144.9123
577.7073 | 322.7073 | 146.1415 | 145.1323 | 375.7895 | 577.7073 | 375.7895 | 146.1415 | 145.1323
578.7073 | 323.7073 | 146.4523 | 145.3591 | 375.7662 | 578.7073 | 375.7662 | 146.4523 | 145.3591
579.7073 | 324.7073 | 146.7691 | 145.564 | 375.6651 | 579.7073 | 375.6651 | 146.7691 | 145.564
580.7073 | 325.7073 | 147.0877 | 145.8119 | 375.573 | 580.7073 | 375.573 | 147.0877 | 145.8119
581.7073 | 326.7073 | 147.4359 | 146.0451 | 375.4594 | 581.7073 | 375.4594 | 147.4359 | 146.0451
582.7073 | 327.7073 | 147.7518 | 146.2453 | 375.5108 | 582.7073 | 375.5108 | 147.7518 | 146.2453
583.7073 | 328.7073 | 148.0809 | 146.4585 | 375.5037 | 583.7073 | 375.5037 | 148.0809 | 146.4585
584.7073 | 329.7073 | 148.4071 | 146.7055 | 375.5183 | 584.7073 | 375.5183 | 148.4071 | 146.7055
585.7073 | 330.7073 | 148.7497 | 146.9331 | 375.5203 | 585.7073 | 375.5203 | 148.7497 | 146.9331
586.7073 | 331.7073 | 149.0894 | 147.1639 | 375.4436 | 586.7073 | 375.4436 | 149.0894 | 147.1639
587.7073 | 332.7073 | 149.4133 | 147.4 | 375.41 | 587.7073 | 375.41 | 149.4133 | 147.4
588.7073 | 333.7073 | 149.7378 | 147.6204 | 375.3943 | 588.7073 | 375.3943 | 149.7378 | 147.6204
589.7073 | 334.7073 | 150.0795 | 147.8697 | 375.5778 | 589.7073 | 375.5778 | 150.0795 | 147.8697
590.7073 | 335.7073 | 150.4067 | 148.0769 | 375.5766 | 590.7073 | 375.5766 | 150.4067 | 148.0769
591.7073 | 336.7073 | 150.744 | 148.2969 | 375.5769 | 591.7073 | 375.5769 | 150.744 | 148.2969
592.7073 | 337.7073 | 151.0848 | 148.497 | 375.7131 | 592.7073 | 375.7131 | 151.0848 | 148.497
593.7073 | 338.7073 | 151.4364 | 148.6533 | 375.6499 | 593.7073 | 375.6499 | 151.4364 | 148.6533
594.7073 | 339.7073 | 151.8045 | 148.8474 | 375.5834 | 594.7073 | 375.5834 | 151.8045 | 148.8474
595.7073 | 340.7073 | 152.152 | 149.0626 | 375.6651 | 595.7073 | 375.6651 | 152.152 | 149.0626
596.7073 | 341.7073 | 152.5019 | 149.2821 | 375.671 | 596.7073 | 375.671 | 152.5019 | 149.2821
597.7073 | 342.7073 | 152.847 | 149.5057 | 375.6066 | 597.7073 | 375.6066 | 152.847 | 149.5057
598.7073 | 343.7073 | 153.212 | 149.7056 | 375.7234 | 598.7073 | 375.7234 | 153.212 | 149.7056
599.7073 | 344.7073 | 153.5569 | 149.9132 | 375.8772 | 599.7073 | 375.8772 | 153.5569 | 149.9132
600.7073 | 345.7073 | 153.9071 | 150.1506 | 376.041 | 600.7073 | 376.041 | 153.9071 | 150.1506
601.7073 | 346.7073 | 154.2611 | 150.3683 | 376.0006 | 601.7073 | 376.0006 | 154.2611 | 150.3683
602.7073 | 347.7073 | 154.6192 | 150.5766 | 376.081 | 602.7073 | 376.081 | 154.6192 | 150.5766
603.7073 | 348.7073 | 154.9673 | 150.7707 | 376.2327 | 603.7073 | 376.2327 | 154.9673 | 150.7707
604.7073 | 349.7073 | 155.3139 | 151.019 | 376.2432 | 604.7073 | 376.2432 | 155.3139 | 151.019
605.7073 | 350.7073 | 155.6728 | 151.2733 | 376.4141 | 605.7073 | 376.4141 | 155.6728 | 151.2733
606.7073 | 351.7073 | 156.0414 | 151.537 | 376.5445 | 606.7073 | 376.5445 | 156.0414 | 151.537
607.7073 | 352.7073 | 156.4094 | 151.8021 | 376.6668 | 607.7073 | 376.6668 | 156.4094 | 151.8021
608.7073 | 353.7073 | 156.7657 | 152.0542 | 376.7655 | 608.7073 | 376.7655 | 156.7657 | 152.0542
609.7073 | 354.7073 | 157.1245 | 152.3379 | 376.7281 | 609.7073 | 376.7281 | 157.1245 | 152.3379
610.7073 | 355.7073 | 157.485 | 152.5858 | 376.8121 | 610.7073 | 376.8121 | 157.485 | 152.5858
611.7073 | 356.7073 | 157.8464 | 152.8291 | 376.785 | 611.7073 | 376.785 | 157.8464 | 152.8291
612.7073 | 357.7073 | 158.2182 | 153.096 | 376.8215 | 612.7073 | 376.8215 | 158.2182 | 153.096
613.7073 | 358.7073 | 158.5863 | 153.3609 | 376.8994 | 613.7073 | 376.8994 | 158.5863 | 153.3609
614.7073 | 359.7073 | 158.953 | 153.6196 | 377.0529 | 614.7073 | 377.0529 | 158.953 | 153.6196
615.7073 | 360.7073 | 159.3139 | 153.8807 | 377.1426 | 615.7073 | 377.1426 | 159.3139 | 153.8807
616.7073 | 361.7073 | 159.6775 | 154.1426 | 377.0761 | 616.7073 | 377.0761 | 159.6775 | 154.1426
617.7073 | 362.7073 | 160.0363 | 154.4177 | 377.0137 | 617.7073 | 377.0137 | 160.0363 | 154.4177
618.7073 | 363.7073 | 160.4101 | 154.6878 | 377.0361 | 618.7073 | 377.0361 | 160.4101 | 154.6878
619.7073 | 364.7073 | 160.7712 | 154.9491 | 376.956 | 619.7073 | 376.956 | 160.7712 | 154.9491
620.7073 | 365.7073 | 161.1262 | 155.2101 | 376.9105 | 620.7073 | 376.9105 | 161.1262 | 155.2101
621.7073 | 366.7073 | 161.4952 | 155.4474 | 376.9976 | 621.7073 | 376.9976 | 161.4952 | 155.4474
622.7073 | 367.7073 | 161.8589 | 155.6965 | 377.043 | 622.7073 | 377.043 | 161.8589 | 155.6965
623.7073 | 368.7073 | 162.2268 | 155.9319 | 377.2006 | 623.7073 | 377.2006 | 162.2268 | 155.9319
624.7073 | 369.7073 | 162.6072 | 156.1791 | 377.3573 | 624.7073 | 377.3573 | 162.6072 | 156.1791
625.7073 | 370.7073 | 162.9611 | 156.4121 | 377.4786 | 625.7073 | 377.4786 | 162.9611 | 156.4121
626.7073 | 371.7073 | 163.3223 | 156.698 | 377.4576 | 626.7073 | 377.4576 | 163.3223 | 156.698
627.7073 | 372.7073 | 163.695 | 156.9738 | 377.3302 | 627.7073 | 377.3302 | 163.695 | 156.9738
628.7073 | 373.7073 | 164.0474 | 157.2531 | 377.3094 | 628.7073 | 377.3094 | 164.0474 | 157.2531
629.7073 | 374.7073 | 164.4078 | 157.5184 | 377.4353 | 629.7073 | 377.4353 | 164.4078 | 157.5184
630.7073 | 375.7073 | 164.7673 | 157.7801 | 377.3796 | 630.7073 | 377.3796 | 164.7673 | 157.7801
631.7073 | 376.7073 | 165.1326 | 158.0517 | 377.3273 | 631.7073 | 377.3273 | 165.1326 | 158.0517
632.7073 | 377.7073 | 165.4815 | 158.3189 | 377.3554 | 632.7073 | 377.3554 | 165.4815 | 158.3189
633.7073 | 378.7073 | 165.8355 | 158.6057 | 377.3085 | 633.7073 | 377.3085 | 165.8355 | 158.6057
634.7073 | 379.7073 | 166.1893 | 158.8947 | 377.3197 | 634.7073 | 377.3197 | 166.1893 | 158.8947
635.7073 | 380.7073 | 166.5407 | 159.1712 | 377.283 | 635.7073 | 377.283 | 166.5407 | 159.1712
636.7073 | 381.7073 | 166.8954 | 159.4541 | 377.269 | 636.7073 | 377.269 | 166.8954 | 159.4541
637.7073 | 382.7073 | 167.2567 | 159.7182 | 377.2612 | 637.7073 | 377.2612 | 167.2567 | 159.7182
638.7073 | 383.7073 | 167.6042 | 160.0196 | 377.1921 | 638.7073 | 377.1921 | 167.6042 | 160.0196
639.7073 | 384.7073 | 167.9579 | 160.3031 | 377.105 | 639.7073 | 377.105 | 167.9579 | 160.3031
640.7073 | 385.7073 | 168.3163 | 160.573 | 376.9839 | 640.7073 | 376.9839 | 168.3163 | 160.573
641.7073 | 386.7073 | 168.6695 | 160.863 | 376.8309 | 641.7073 | 376.8309 | 168.6695 | 160.863
642.7073 | 387.7073 | 169.0235 | 161.1507 | 376.8012 | 642.7073 | 376.8012 | 169.0235 | 161.1507
643.7073 | 388.7073 | 169.3557 | 161.4295 | 376.8969 | 643.7073 | 376.8969 | 169.3557 | 161.4295
644.7073 | 389.7073 | 169.7104 | 161.7015 | 376.709 | 644.7073 | 376.709 | 169.7104 | 161.7015
645.7073 | 390.7073 | 170.066 | 161.992 | 376.7065 | 645.7073 | 376.7065 | 170.066 | 161.992
646.7073 | 391.7073 | 170.4096 | 162.2762 | 376.7264 | 646.7073 | 376.7264 | 170.4096 | 162.2762
647.7073 | 392.7073 | 170.7741 | 162.5549 | 376.7126 | 647.7073 | 376.7126 | 170.7741 | 162.5549
648.7073 | 393.7073 | 171.1003 | 162.8108 | 376.6095 | 648.7073 | 376.6095 | 171.1003 | 162.8108
649.7073 | 394.7073 | 171.4506 | 163.0686 | 376.5666 | 649.7073 | 376.5666 | 171.4506 | 163.0686
650.7073 | 395.7073 | 171.8212 | 163.321 | 376.628 | 650.7073 | 376.628 | 171.8212 | 163.321
651.7073 | 396.7073 | 172.1738 | 163.5816 | 376.6111 | 651.7073 | 376.6111 | 172.1738 | 163.5816
652.7073 | 397.7073 | 172.5063 | 163.8371 | 376.6284 | 652.7073 | 376.6284 | 172.5063 | 163.8371
653.7073 | 398.7073 | 172.8522 | 164.1191 | 376.7997 | 653.7073 | 376.7997 | 172.8522 | 164.1191
654.7073 | 399.7073 | 173.1965 | 164.4016 | 376.8959 | 654.7073 | 376.8959 | 173.1965 | 164.4016
655.7542 | 400.7542 | 173.5457 | 164.7071 | 376.8492 | 655.7542 | 376.8492 | 173.5457 | 164.7071
656.7073 | 401.7073 | 173.8865 | 164.9864 | 376.8076 | 656.7073 | 376.8076 | 173.8865 | 164.9864
657.7073 | 402.7073 | 174.233 | 165.2973 | 376.7878 | 657.7073 | 376.7878 | 174.233 | 165.2973
658.7073 | 403.7073 | 174.5569 | 165.5619 | 376.7783 | 658.7073 | 376.7783 | 174.5569 | 165.5619
659.7073 | 404.7073 | 174.907 | 165.8412 | 376.704 | 659.7073 | 376.704 | 174.907 | 165.8412
660.7073 | 405.7073 | 175.2544 | 166.1128 | 376.794 | 660.7073 | 376.794 | 175.2544 | 166.1128
661.7073 | 406.7073 | 175.5919 | 166.3855 | 376.7674 | 661.7073 | 376.7674 | 175.5919 | 166.3855
662.7073 | 407.7073 | 175.9356 | 166.6672 | 376.6904 | 662.7073 | 376.6904 | 175.9356 | 166.6672
663.7073 | 408.7073 | 176.2767 | 166.9289 | 376.7971 | 663.7073 | 376.7971 | 176.2767 | 166.9289
664.7073 | 409.7073 | 176.6096 | 167.2037 | 376.7764 | 664.7073 | 376.7764 | 176.6096 | 167.2037
665.7073 | 410.7073 | 176.9421 | 167.4802 | 376.7745 | 665.7073 | 376.7745 | 176.9421 | 167.4802
666.7073 | 411.7073 | 177.2855 | 167.7435 | 376.7935 | 666.7073 | 376.7935 | 177.2855 | 167.7435
667.7073 | 412.7073 | 177.6187 | 168.0174 | 376.7826 | 667.7073 | 376.7826 | 177.6187 | 168.0174
668.7073 | 413.7073 | 177.9562 | 168.2963 | 376.823 | 668.7073 | 376.823 | 177.9562 | 168.2963
669.7073 | 414.7073 | 178.2959 | 168.5939 | 376.7878 | 669.7073 | 376.7878 | 178.2959 | 168.5939
670.7073 | 415.7073 | 178.6208 | 168.8878 | 376.7609 | 670.7073 | 376.7609 | 178.6208 | 168.8878
671.7073 | 416.7073 | 178.9718 | 169.1756 | 376.8174 | 671.7073 | 376.8174 | 178.9718 | 169.1756
672.7073 | 417.7073 | 179.3084 | 169.4689 | 376.9194 | 672.7073 | 376.9194 | 179.3084 | 169.4689
673.7073 | 418.7073 | 179.6247 | 169.7591 | 376.9885 | 673.7073 | 376.9885 | 179.6247 | 169.7591
674.7073 | 419.7073 | 179.9678 | 170.0429 | 377.0761 | 674.7073 | 377.0761 | 179.9678 | 170.0429
675.7073 | 420.7073 | 180.2974 | 170.3335 | 377.1721 | 675.7073 | 377.1721 | 180.2974 | 170.3335
676.7073 | 421.7073 | 180.6181 | 170.6346 | 377.102 | 676.7073 | 377.102 | 180.6181 | 170.6346
677.7073 | 422.7073 | 180.9504 | 170.933 | 377.0247 | 677.7073 | 377.0247 | 180.9504 | 170.933
678.7073 | 423.7073 | 181.2798 | 171.2396 | 377.0986 | 678.7073 | 377.0986 | 181.2798 | 171.2396
679.7073 | 424.7073 | 181.6362 | 171.5238 | 377.205 | 679.7073 | 377.205 | 181.6362 | 171.5238
680.7073 | 425.7073 | 181.9607 | 171.8213 | 377.1516 | 680.7073 | 377.1516 | 181.9607 | 171.8213
681.7073 | 426.7073 | 182.2923 | 172.0972 | 377.1672 | 681.7073 | 377.1672 | 182.2923 | 172.0972
682.7073 | 427.7073 | 182.6317 | 172.3643 | 377.1212 | 682.7073 | 377.1212 | 182.6317 | 172.3643
683.7073 | 428.7073 | 182.9496 | 172.6516 | 377.0079 | 683.7073 | 377.0079 | 182.9496 | 172.6516
684.7073 | 429.7073 | 183.2744 | 172.9318 | 376.9064 | 684.7073 | 376.9064 | 183.2744 | 172.9318
685.7073 | 430.7073 | 183.6129 | 173.1953 | 376.8249 | 685.7073 | 376.8249 | 183.6129 | 173.1953
686.7073 | 431.7073 | 183.9342 | 173.483 | 376.7234 | 686.7073 | 376.7234 | 183.9342 | 173.483
687.7073 | 432.7073 | 184.2734 | 173.7885 | 376.8606 | 687.7073 | 376.8606 | 184.2734 | 173.7885
688.7073 | 433.7073 | 184.5892 | 174.074 | 376.9846 | 688.7073 | 376.9846 | 184.5892 | 174.074
689.7073 | 434.7073 | 184.9082 | 174.3642 | 377.0549 | 689.7073 | 377.0549 | 184.9082 | 174.3642
690.7073 | 435.7073 | 185.2469 | 174.6459 | 377.1301 | 690.7073 | 377.1301 | 185.2469 | 174.6459
691.7073 | 436.7073 | 185.5572 | 174.9245 | 377.0463 | 691.7073 | 377.0463 | 185.5572 | 174.9245
692.7073 | 437.7073 | 185.8838 | 175.212 | 376.9779 | 692.7073 | 376.9779 | 185.8838 | 175.212
693.7073 | 438.7073 | 186.2183 | 175.4908 | 376.9712 | 693.7073 | 376.9712 | 186.2183 | 175.4908
694.7073 | 439.7073 | 186.5322 | 175.7709 | 376.9508 | 694.7073 | 376.9508 | 186.5322 | 175.7709
695.7073 | 440.7073 | 186.8594 | 176.0411 | 376.9807 | 695.7073 | 376.9807 | 186.8594 | 176.0411
696.7073 | 441.7073 | 187.1738 | 176.3227 | 376.9839 | 696.7073 | 376.9839 | 187.1738 | 176.3227
697.7073 | 442.7073 | 187.4893 | 176.573 | 376.8388 | 697.7073 | 376.8388 | 187.4893 | 176.573
698.7073 | 443.7073 | 187.8132 | 176.8525 | 376.597 | 698.7073 | 376.597 | 187.8132 | 176.8525
699.7073 | 444.7073 | 188.1297 | 177.1117 | 376.4899 | 699.7073 | 376.4899 | 188.1297 | 177.1117
700.7073 | 445.7073 | 188.4593 | 177.3815 | 376.372 | 700.7073 | 376.372 | 188.4593 | 177.3815
701.7073 | 446.7073 | 188.7731 | 177.6711 | 376.3774 | 701.7073 | 376.3774 | 188.7731 | 177.6711
702.7073 | 447.7073 | 189.0836 | 177.9517 | 376.2337 | 702.7073 | 376.2337 | 189.0836 | 177.9517
703.7073 | 448.7073 | 189.399 | 178.2206 | 376.026 | 703.7073 | 376.026 | 189.399 | 178.2206
704.7073 | 449.7073 | 189.7171 | 178.4858 | 375.909 | 704.7073 | 375.909 | 189.7171 | 178.4858
705.7073 | 450.7073 | 190.0365 | 178.7457 | 375.87 | 705.7073 | 375.87 | 190.0365 | 178.7457
706.7073 | 451.7073 | 190.3641 | 179.0194 | 375.8089 | 706.7073 | 375.8089 | 190.3641 | 179.0194
707.7073 | 452.7073 | 190.6619 | 179.2432 | 375.7342 | 707.7073 | 375.7342 | 190.6619 | 179.2432
708.7073 | 453.7073 | 190.9926 | 179.4904 | 375.7715 | 708.7073 | 375.7715 | 190.9926 | 179.4904
709.7073 | 454.7073 | 191.2965 | 179.7239 | 375.9016 | 709.7073 | 375.9016 | 191.2965 | 179.7239
710.7073 | 455.7073 | 191.6071 | 179.9932 | 375.8082 | 710.7073 | 375.8082 | 191.6071 | 179.9932
711.7073 | 456.7073 | 191.9242 | 180.2402 | 375.7241 | 711.7073 | 375.7241 | 191.9242 | 180.2402
712.7073 | 457.7073 | 192.2302 | 180.507 | 375.6491 | 712.7073 | 375.6491 | 192.2302 | 180.507
713.7073 | 458.7073 | 192.5546 | 180.7584 | 375.5642 | 713.7073 | 375.5642 | 192.5546 | 180.7584
714.7073 | 459.7073 | 192.8545 | 181.0324 | 375.615 | 714.7073 | 375.615 | 192.8545 | 181.0324
715.7073 | 460.7073 | 193.1551 | 181.2961 | 375.5881 | 715.7073 | 375.5881 | 193.1551 | 181.2961
716.7073 | 461.7073 | 193.448 | 181.5354 | 375.5475 | 716.7073 | 375.5475 | 193.448 | 181.5354
717.7073 | 462.7073 | 193.7626 | 181.8166 | 375.5752 | 717.7073 | 375.5752 | 193.7626 | 181.8166
718.7073 | 463.7073 | 194.0648 | 182.0423 | 375.4294 | 718.7073 | 375.4294 | 194.0648 | 182.0423
719.7073 | 464.7073 | 194.3613 | 182.2764 | 375.347 | 719.7073 | 375.347 | 194.3613 | 182.2764
720.7073 | 465.7073 | 194.6642 | 182.4839 | 375.3425 | 720.7073 | 375.3425 | 194.6642 | 182.4839
721.7073 | 466.7073 | 194.9538 | 182.735 | 375.2835 | 721.7073 | 375.2835 | 194.9538 | 182.735
722.7073 | 467.7073 | 195.253 | 182.9918 | 375.2198 | 722.7073 | 375.2198 | 195.253 | 182.9918
723.7073 | 468.7073 | 195.5514 | 183.2496 | 375.2748 | 723.7073 | 375.2748 | 195.5514 | 183.2496
724.7073 | 469.7073 | 195.8418 | 183.5041 | 375.4087 | 724.7073 | 375.4087 | 195.8418 | 183.5041
725.7073 | 470.7073 | 196.1476 | 183.7593 | 375.5158 | 725.7073 | 375.5158 | 196.1476 | 183.7593
726.7073 | 471.7073 | 196.4419 | 184.0285 | 375.528 | 726.7073 | 375.528 | 196.4419 | 184.0285
727.7073 | 472.7073 | 196.7273 | 184.2699 | 375.5628 | 727.7073 | 375.5628 | 196.7273 | 184.2699
728.7073 | 473.7073 | 196.9999 | 184.5009 | 375.6091 | 728.7073 | 375.6091 | 196.9999 | 184.5009
729.7073 | 474.7073 | 197.3113 | 184.6922 | 375.6639 | 729.7073 | 375.6639 | 197.3113 | 184.6922
730.7073 | 475.7073 | 197.6007 | 184.9542 | 375.7608 | 730.7073 | 375.7608 | 197.6007 | 184.9542
731.7073 | 476.7073 | 197.9031 | 185.1855 | 375.7395 | 731.7073 | 375.7395 | 197.9031 | 185.1855
732.7073 | 477.7073 | 198.1748 | 185.406 | 375.703 | 732.7073 | 375.703 | 198.1748 | 185.406
733.7073 | 478.7073 | 198.4783 | 185.6242 | 375.5566 | 733.7073 | 375.5566 | 198.4783 | 185.6242
734.7073 | 479.7073 | 198.7709 | 185.8337 | 375.2776 | 734.7073 | 375.2776 | 198.7709 | 185.8337
735.7073 | 480.7073 | 199.0578 | 186.0844 | 375.2035 | 735.7073 | 375.2035 | 199.0578 | 186.0844
736.7073 | 481.7073 | 199.345 | 186.3158 | 375.1336 | 736.7073 | 375.1336 | 199.345 | 186.3158
737.7073 | 482.7073 | 199.6423 | 186.5177 | 375.1382 | 737.7073 | 375.1382 | 199.6423 | 186.5177
738.7073 | 483.7073 | 199.9225 | 186.7402 | 374.9803 | 738.7073 | 374.9803 | 199.9225 | 186.7402
739.7073 | 484.7073 | 200.2136 | 186.9959 | 374.8596 | 739.7073 | 374.8596 | 200.2136 | 186.9959
740.7073 | 485.7073 | 200.5108 | 187.2125 | 374.7564 | 740.7073 | 374.7564 | 200.5108 | 187.2125
741.7073 | 486.7073 | 200.7944 | 187.4096 | 374.5926 | 741.7073 | 374.5926 | 200.7944 | 187.4096
742.7073 | 487.7073 | 201.0888 | 187.6219 | 374.5791 | 742.7073 | 374.5791 | 201.0888 | 187.6219
743.7073 | 488.7073 | 201.3624 | 187.6935 | 374.615 | 743.7073 | 374.615 | 201.3624 | 187.6935
744.7073 | 489.7073 | 201.6625 | 187.8963 | 374.5837 | 744.7073 | 374.5837 | 201.6625 | 187.8963
745.7073 | 490.7073 | 201.9338 | 188.1201 | 374.4685 | 745.7073 | 374.4685 | 201.9338 | 188.1201
746.7073 | 491.7073 | 202.2269 | 188.3287 | 374.4307 | 746.7073 | 374.4307 | 202.2269 | 188.3287
747.7073 | 492.7073 | 202.5099 | 188.5455 | 374.4772 | 747.7073 | 374.4772 | 202.5099 | 188.5455
748.7073 | 493.7073 | 202.7887 | 188.718 | 374.3807 | 748.7073 | 374.3807 | 202.7887 | 188.718
749.7073 | 494.7073 | 203.0725 | 188.8781 | 374.366 | 749.7073 | 374.366 | 203.0725 | 188.8781
750.7073 | 495.7073 | 203.3306 | 189.0076 | 374.4263 | 750.7073 | 374.4263 | 203.3306 | 189.0076
751.7073 | 496.7073 | 203.6183 | 189.1914 | 374.4508 | 751.7073 | 374.4508 | 203.6183 | 189.1914
752.7073 | 497.7073 | 203.8985 | 189.4038 | 374.607 | 752.7073 | 374.607 | 203.8985 | 189.4038
753.7073 | 498.7073 | 204.1618 | 189.5953 | 374.6461 | 753.7073 | 374.6461 | 204.1618 | 189.5953
754.7073 | 499.7073 | 204.4503 | 189.7258 | 374.7231 | 754.7073 | 374.7231 | 204.4503 | 189.7258
755.7073 | 500.7073 | 204.7326 | 189.7676 | 374.7523 | 755.7073 | 374.7523 | 204.7326 | 189.7676
756.7073 | 501.7073 | 205.0054 | 189.8929 | 374.6995 | 756.7073 | 374.6995 | 205.0054 | 189.8929
757.7073 | 502.7073 | 205.2768 | 190.0593 | 374.7566 | 757.7073 | 374.7566 | 205.2768 | 190.0593
758.7073 | 503.7073 | 205.5507 | 190.1934 | 374.7571 | 758.7073 | 374.7571 | 205.5507 | 190.1934
759.7073 | 504.7073 | 205.821 | 190.133 | 374.7164 | 759.7073 | 374.7164 | 205.821 | 190.133
760.7073 | 505.7073 | 206.1044 | 189.9238 | 374.6508 | 760.7073 | 374.6508 | 206.1044 | 189.9238
761.7073 | 506.7073 | 206.3728 | 189.9266 | 374.6838 | 761.7073 | 374.6838 | 206.3728 | 189.9266
762.7073 | 507.7073 | 206.6487 | 189.9879 | 374.7026 | 762.7073 | 374.7026 | 206.6487 | 189.9879
763.7073 | 508.7073 | 206.9139 | 189.9171 | 374.777 | 763.7073 | 374.777 | 206.9139 | 189.9171
764.7073 | 509.7073 | 207.1983 | 189.8756 | 374.8303 | 764.7073 | 374.8303 | 207.1983 | 189.8756
765.7073 | 510.7073 | 207.4771 | 190.0193 | 374.9041 | 765.7073 | 374.9041 | 207.4771 | 190.0193
766.7073 | 511.7073 | 207.7494 | 190.2589 | 374.9668 | 766.7073 | 374.9668 | 207.7494 | 190.2589
767.7073 | 512.7073 | 208.0211 | 190.5322 | 374.975 | 767.7073 | 374.975 | 208.0211 | 190.5322
768.7073 | 513.7073 | 208.2979 | 190.798 | 375.1017 | 768.7073 | 375.1017 | 208.2979 | 190.798
769.7073 | 514.7073 | 208.565 | 191.0541 | 375.028 | 769.7073 | 375.028 | 208.565 | 191.0541
770.7073 | 515.7073 | 208.8263 | 191.2682 | 375.0105 | 770.7073 | 375.0105 | 208.8263 | 191.2682
771.7073 | 516.7073 | 209.1087 | 191.5229 | 375.1197 | 771.7073 | 375.1197 | 209.1087 | 191.5229
772.7073 | 517.7073 | 209.3857 | 191.8009 | 375.1643 | 772.7073 | 375.1643 | 209.3857 | 191.8009
773.7073 | 518.7073 | 209.6463 | 192.0473 | 375.2038 | 773.7073 | 375.2038 | 209.6463 | 192.0473
774.7073 | 519.7073 | 209.9257 | 192.3076 | 375.2065 | 774.7073 | 375.2065 | 209.9257 | 192.3076
775.7073 | 520.7073 | 210.1866 | 192.5182 | 375.2163 | 775.7073 | 375.2163 | 210.1866 | 192.5182
776.7073 | 521.7073 | 210.4549 | 192.7823 | 375.3099 | 776.7073 | 375.3099 | 210.4549 | 192.7823
777.7073 | 522.7073 | 210.733 | 193.0345 | 375.3414 | 777.7073 | 375.3414 | 210.733 | 193.0345
778.7073 | 523.7073 | 211.0082 | 193.312 | 375.3032 | 778.7073 | 375.3032 | 211.0082 | 193.312
779.7073 | 524.7073 | 211.2802 | 193.5855 | 375.2566 | 779.7073 | 375.2566 | 211.2802 | 193.5855
780.7073 | 525.7073 | 211.5382 | 193.8427 | 375.1418 | 780.7073 | 375.1418 | 211.5382 | 193.8427
781.7073 | 526.7073 | 211.8141 | 194.0074 | 375.1273 | 781.7073 | 375.1273 | 211.8141 | 194.0074
782.7073 | 527.7073 | 212.079 | 194.2378 | 375.0951 | 782.7073 | 375.0951 | 212.079 | 194.2378
783.7073 | 528.7073 | 212.3499 | 194.4874 | 375.0436 | 783.7073 | 375.0436 | 212.3499 | 194.4874
784.7073 | 529.7073 | 212.6208 | 194.7867 | 375.0945 | 784.7073 | 375.0945 | 212.6208 | 194.7867
785.7073 | 530.7073 | 212.8969 | 195.0651 | 375.1814 | 785.7073 | 375.1814 | 212.8969 | 195.0651
786.7073 | 531.7073 | 213.1873 | 195.3188 | 375.2074 | 786.7073 | 375.2074 | 213.1873 | 195.3188
787.7073 | 532.7073 | 213.4484 | 195.6009 | 375.1966 | 787.7073 | 375.1966 | 213.4484 | 195.6009
788.7073 | 533.7073 | 213.7104 | 195.8509 | 375.0978 | 788.7073 | 375.0978 | 213.7104 | 195.8509
789.7073 | 534.7073 | 213.9408 | 196.1186 | 374.9912 | 789.7073 | 374.9912 | 213.9408 | 196.1186
790.7073 | 535.7073 | 214.1285 | 196.3409 | 375.0608 | 790.7073 | 375.0608 | 214.1285 | 196.3409
791.7073 | 536.7073 | 214.3788 | 196.6721 | 375.0761 | 791.7073 | 375.0761 | 214.3788 | 196.6721
792.7073 | 537.7073 | 214.6474 | 196.8665 | 374.9906 | 792.7073 | 374.9906 | 214.6474 | 196.8665
793.7073 | 538.7073 | 214.9322 | 196.9562 | 374.977 | 793.7073 | 374.977 | 214.9322 | 196.9562
794.7073 | 539.7073 | 215.2202 | 197.3715 | 374.9196 | 794.7073 | 374.9196 | 215.2202 | 197.3715
795.7073 | 540.7073 | 215.5281 | 197.4797 | 374.8737 | 795.7073 | 374.8737 | 215.5281 | 197.4797
796.7073 | 541.7073 | 215.8276 | 197.7489 | 374.9746 | 796.7073 | 374.9746 | 215.8276 | 197.7489
797.7073 | 542.7073 | 216.1182 | 198.0251 | 374.8529 | 797.7073 | 374.8529 | 216.1182 | 198.0251
798.7073 | 543.7073 | 216.4175 | 198.2899 | 374.8429 | 798.7073 | 374.8429 | 216.4175 | 198.2899
799.7073 | 544.7073 | 216.6945 | 198.5754 | 374.835 | 799.7073 | 374.835 | 216.6945 | 198.5754
800.7073 | 545.7073 | 216.9773 | 198.8413 | 374.8123 | 800.7073 | 374.8123 | 216.9773 | 198.8413
801.7073 | 546.7073 | 217.2352 | 199.1176 | 374.8482 | 801.7073 | 374.8482 | 217.2352 | 199.1176
802.7073 | 547.7073 | 217.4933 | 199.3958 | 374.9678 | 802.7073 | 374.9678 | 217.4933 | 199.3958
803.7073 | 548.7073 | 217.8103 | 199.6622 | 374.9815 | 803.7073 | 374.9815 | 217.8103 | 199.6622
804.7073 | 549.7073 | 218.0455 | 199.9352 | 374.8811 | 804.7073 | 374.8811 | 218.0455 | 199.9352
805.7073 | 550.7073 | 218.3391 | 200.2067 | 374.8209 | 805.7073 | 374.8209 | 218.3391 | 200.2067
806.7073 | 551.7073 | 218.6686 | 200.4837 | 374.7222 | 806.7073 | 374.7222 | 218.6686 | 200.4837
807.7073 | 552.7073 | 218.9329 | 200.7547 | 374.8749 | 807.7073 | 374.8749 | 218.9329 | 200.7547
808.7073 | 553.7073 | 219.2066 | 201.0176 | 374.9737 | 808.7073 | 374.9737 | 219.2066 | 201.0176
809.7073 | 554.7073 | 219.4726 | 201.3044 | 374.907 | 809.7073 | 374.907 | 219.4726 | 201.3044
810.7073 | 555.7073 | 219.6947 | 201.5699 | 374.8575 | 810.7073 | 374.8575 | 219.6947 | 201.5699
811.8323 | 556.8323 | 220.0633 | 201.8747 | 374.8056 | 811.8323 | 374.8056 | 220.0633 | 201.8747
812.7542 | 557.7542 | 220.333 | 202.1227 | 374.8575 | 812.7542 | 374.8575 | 220.333 | 202.1227
813.7073 | 558.7073 | 220.6467 | 202.378 | 374.8385 | 813.7073 | 374.8385 | 220.6467 | 202.378
814.7073 | 559.7073 | 220.9713 | 202.6503 | 374.7632 | 814.7073 | 374.7632 | 220.9713 | 202.6503
815.7073 | 560.7073 | 221.2457 | 202.9215 | 374.8013 | 815.7073 | 374.8013 | 221.2457 | 202.9215
816.7073 | 561.7073 | 221.5203 | 203.1893 | 374.7263 | 816.7073 | 374.7263 | 221.5203 | 203.1893
817.7073 | 562.7073 | 221.7786 | 203.4541 | 374.7526 | 817.7073 | 374.7526 | 221.7786 | 203.4541
818.7073 | 563.7073 | 222.0691 | 203.7303 | 374.8012 | 818.7073 | 374.8012 | 222.0691 | 203.7303
819.7073 | 564.7073 | 222.3378 | 203.9958 | 374.7698 | 819.7073 | 374.7698 | 222.3378 | 203.9958
820.7073 | 565.7073 | 222.6211 | 204.2677 | 374.6868 | 820.7073 | 374.6868 | 222.6211 | 204.2677
821.7073 | 566.7073 | 222.883 | 204.5287 | 374.682 | 821.7073 | 374.682 | 222.883 | 204.5287
822.7073 | 567.7073 | 223.0134 | 204.7885 | 374.7345 | 822.7073 | 374.7345 | 223.0134 | 204.7885
823.7073 | 568.7073 | 222.9083 | 205.0531 | 374.77 | 823.7073 | 374.77 | 222.9083 | 205.0531
824.7073 | 569.7073 | 223.2463 | 205.3299 | 374.7165 | 824.7073 | 374.7165 | 223.2463 | 205.3299
825.7073 | 570.7073 | 223.4119 | 205.5839 | 374.565 | 825.7073 | 374.565 | 223.4119 | 205.5839
826.7073 | 571.7073 | 223.4057 | 205.8496 | 374.5477 | 826.7073 | 374.5477 | 223.4057 | 205.8496
827.7073 | 572.7073 | 223.7469 | 206.1065 | 374.6204 | 827.7073 | 374.6204 | 223.7469 | 206.1065
828.7073 | 573.7073 | 224.038 | 206.3722 | 374.6534 | 828.7073 | 374.6534 | 224.038 | 206.3722
829.7073 | 574.7073 | 224.3369 | 206.6301 | 374.6457 | 829.7073 | 374.6457 | 224.3369 | 206.6301
830.7073 | 575.7073 | 224.5785 | 206.8939 | 374.6842 | 830.7073 | 374.6842 | 224.5785 | 206.8939
831.7073 | 576.7073 | 224.9675 | 207.1458 | 374.5737 | 831.7073 | 374.5737 | 224.9675 | 207.1458
832.7073 | 577.7073 | 225.278 | 207.4032 | 374.5819 | 832.7073 | 374.5819 | 225.278 | 207.4032
833.7073 | 578.7073 | 225.5238 | 207.6678 | 374.5715 | 833.7073 | 374.5715 | 225.5238 | 207.6678
834.7073 | 579.7073 | 225.8249 | 207.9261 | 374.632 | 834.7073 | 374.632 | 225.8249 | 207.9261
835.7073 | 580.7073 | 226.0903 | 208.1868 | 374.7534 | 835.7073 | 374.7534 | 226.0903 | 208.1868
836.7073 | 581.7073 | 226.3635 | 208.4367 | 374.8537 | 836.7073 | 374.8537 | 226.3635 | 208.4367
837.7073 | 582.7073 | 226.6277 | 208.6905 | 374.9321 | 837.7073 | 374.9321 | 226.6277 | 208.6905
838.7073 | 583.7073 | 226.3771 | 208.9407 | 374.9721 | 838.7073 | 374.9721 | 226.3771 | 208.9407
839.7073 | 584.7073 | 226.8361 | 209.1954 | 374.9842 | 839.7073 | 374.9842 | 226.8361 | 209.1954
840.7073 | 585.7073 | 227.0414 | 209.4451 | 375.0026 | 840.7073 | 375.0026 | 227.0414 | 209.4451
841.7073 | 586.7073 | 227.3295 | 209.6834 | 374.995 | 841.7073 | 374.995 | 227.3295 | 209.6834
842.7073 | 587.7073 | 227.2361 | 209.9405 | 375.0568 | 842.7073 | 375.0568 | 227.2361 | 209.9405
843.7073 | 588.7073 | 227.5503 | 210.1881 | 375.1914 | 843.7073 | 375.1914 | 227.5503 | 210.1881
844.7073 | 589.7073 | 227.8468 | 210.436 | 375.3412 | 844.7073 | 375.3412 | 227.8468 | 210.436
845.7073 | 590.7073 | 228.1396 | 210.6866 | 375.5507 | 845.7073 | 375.5507 | 228.1396 | 210.6866
846.7073 | 591.7073 | 228.2893 | 210.9284 | 375.713 | 846.7073 | 375.713 | 228.2893 | 210.9284
847.7073 | 592.7073 | 228.3782 | 211.1905 | 375.8635 | 847.7073 | 375.8635 | 228.3782 | 211.1905
848.7073 | 593.7073 | 228.539 | 211.4369 | 375.9123 | 848.7073 | 375.9123 | 228.539 | 211.4369
849.7073 | 594.7073 | 228.6623 | 211.6719 | 375.9262 | 849.7073 | 375.9262 | 228.6623 | 211.6719
850.7073 | 595.7073 | 228.9053 | 211.9165 | 375.965 | 850.7073 | 375.965 | 228.9053 | 211.9165
851.7073 | 596.7073 | 229.1021 | 212.1646 | 375.9314 | 851.7073 | 375.9314 | 229.1021 | 212.1646
852.7073 | 597.7073 | 229.2988 | 212.408 | 375.9537 | 852.7073 | 375.9537 | 229.2988 | 212.408
853.7073 | 598.7073 | 229.4991 | 212.6499 | 375.9869 | 853.7073 | 375.9869 | 229.4991 | 212.6499
854.7073 | 599.7073 | 229.7195 | 212.8926 | 375.9183 | 854.7073 | 375.9183 | 229.7195 | 212.8926
855.7073 | 600.7073 | 229.2327 | 213.1318 | 375.9157 | 855.7073 | 375.9157 | 229.2327 | 213.1318
856.7073 | 601.7073 | 229.4904 | 213.37 | 376.0132 | 856.7073 | 376.0132 | 229.4904 | 213.37
857.7073 | 602.7073 | 229.5287 | 213.6032 | 376.0405 | 857.7073 | 376.0405 | 229.5287 | 213.6032
858.7073 | 603.7073 | 229.6688 | 213.854 | 376.1942 | 858.7073 | 376.1942 | 229.6688 | 213.854
859.7073 | 604.7073 | 228.2812 | 214.0858 | 376.1474 | 859.7073 | 376.1474 | 228.2812 | 214.0858
860.7073 | 605.7073 | 228.5623 | 214.3245 | 376.0818 | 860.7073 | 376.0818 | 228.5623 | 214.3245
861.7073 | 606.7073 | 228.9568 | 214.5616 | 376.1904 | 861.7073 | 376.1904 | 228.9568 | 214.5616
862.7073 | 607.7073 | 228.799 | 214.7967 | 376.1709 | 862.7073 | 376.1709 | 228.799 | 214.7967
863.7073 | 608.7073 | 229.1291 | 215.0407 | 376.239 | 863.7073 | 376.239 | 229.1291 | 215.0407
864.7073 | 609.7073 | 229.1704 | 215.2671 | 376.2653 | 864.7073 | 376.2653 | 229.1704 | 215.2671
865.7073 | 610.7073 | 229.4581 | 215.5096 | 376.3571 | 865.7073 | 376.3571 | 229.4581 | 215.5096
866.7073 | 611.7073 | 229.6765 | 215.7375 | 376.2199 | 866.7073 | 376.2199 | 229.6765 | 215.7375
867.7073 | 612.7073 | 229.927 | 215.9593 | 376.2892 | 867.7073 | 376.2892 | 229.927 | 215.9593
868.7073 | 613.7073 | 230.1093 | 216.1938 | 376.2298 | 868.7073 | 376.2298 | 230.1093 | 216.1938
869.7073 | 614.7073 | 230.3631 | 216.417 | 376.2443 | 869.7073 | 376.2443 | 230.3631 | 216.417
870.7073 | 615.7073 | 230.5725 | 216.6512 | 376.1709 | 870.7073 | 376.1709 | 230.5725 | 216.6512
871.7073 | 616.7073 | 230.7983 | 216.8946 | 376.1028 | 871.7073 | 376.1028 | 230.7983 | 216.8946
872.7073 | 617.7073 | 230.7784 | 217.1224 | 376.1555 | 872.7073 | 376.1555 | 230.7784 | 217.1224
873.7073 | 618.7073 | 229.8687 | 217.3442 | 376.1799 | 873.7073 | 376.1799 | 229.8687 | 217.3442
874.7073 | 619.7073 | 229.6126 | 217.5675 | 375.9967 | 874.7073 | 375.9967 | 229.6126 | 217.5675
875.7073 | 620.7073 | 229.089 | 217.7954 | 375.8128 | 875.7073 | 375.8128 | 229.089 | 217.7954
876.7073 | 621.7073 | 229.3896 | 218.0181 | 375.8755 | 876.7073 | 375.8755 | 229.3896 | 218.0181
877.7073 | 622.7073 | 229.594 | 218.2276 | 375.878 | 877.7073 | 375.878 | 229.594 | 218.2276
878.7073 | 623.7073 | 229.7779 | 218.4649 | 375.7592 | 878.7073 | 375.7592 | 229.7779 | 218.4649
879.7073 | 624.7073 | 229.8505 | 218.6926 | 375.7367 | 879.7073 | 375.7367 | 229.8505 | 218.6926
880.7073 | 625.7073 | 229.886 | 218.9156 | 375.7512 | 880.7073 | 375.7512 | 229.886 | 218.9156
881.7698 | 626.7698 | 230.1296 | 219.1427 | 375.7266 | 881.7698 | 375.7266 | 230.1296 | 219.1427
882.8323 | 627.8323 | 230.3801 | 219.3883 | 375.6917 | 882.8323 | 375.6917 | 230.3801 | 219.3883
883.7073 | 628.7073 | 230.4788 | 219.5873 | 375.7659 | 883.7073 | 375.7659 | 230.4788 | 219.5873
884.7073 | 629.7073 | 230.5573 | 219.81 | 375.8493 | 884.7073 | 375.8493 | 230.5573 | 219.81
885.8167 | 630.8167 | 230.9325 | 220.0537 | 375.8019 | 885.8167 | 375.8019 | 230.9325 | 220.0537
886.7229 | 631.7229 | 231.1059 | 220.2588 | 375.6965 | 886.7229 | 375.6965 | 231.1059 | 220.2588
887.7073 | 632.7073 | 231.2219 | 220.4705 | 375.7545 | 887.7073 | 375.7545 | 231.2219 | 220.4705
888.7073 | 633.7073 | 231.0958 | 220.6998 | 375.8188 | 888.7073 | 375.8188 | 231.0958 | 220.6998
889.7073 | 634.7073 | 231.0192 | 220.9195 | 375.8028 | 889.7073 | 375.8028 | 231.0192 | 220.9195
890.7073 | 635.7073 | 230.9931 | 221.1387 | 375.7298 | 890.7073 | 375.7298 | 230.9931 | 221.1387
891.7073 | 636.7073 | 231.1151 | 221.3563 | 375.6808 | 891.7073 | 375.6808 | 231.1151 | 221.3563
892.7073 | 637.7073 | 231.4444 | 221.5715 | 375.6447 | 892.7073 | 375.6447 | 231.4444 | 221.5715
893.7073 | 638.7073 | 231.5332 | 221.7803 | 375.5313 | 893.7073 | 375.5313 | 231.5332 | 221.7803
894.7073 | 639.7073 | 231.3915 | 221.9977 | 375.3928 | 894.7073 | 375.3928 | 231.3915 | 221.9977
895.7073 | 640.7073 | 231.5961 | 222.2215 | 375.433 | 895.7073 | 375.433 | 231.5961 | 222.2215
896.7073 | 641.7073 | 231.3561 | 222.4315 | 375.3906 | 896.7073 | 375.3906 | 231.3561 | 222.4315
897.7073 | 642.7073 | 231.4176 | 222.6426 | 375.3797 | 897.7073 | 375.3797 | 231.4176 | 222.6426
898.7073 | 643.7073 | 231.3465 | 222.8513 | 375.4297 | 898.7073 | 375.4297 | 231.3465 | 222.8513
899.7073 | 644.7073 | 231.5941 | 223.0665 | 375.5691 | 899.7073 | 375.5691 | 231.5941 | 223.0665
900.7073 | 645.7073 | 231.3485 | 223.285 | 375.6875 | 900.7073 | 375.6875 | 231.3485 | 223.285
901.9104 | 646.9104 | 231.4733 | 223.5235 | 375.8423 | 901.9104 | 375.8423 | 231.4733 | 223.5235
902.7073 | 647.7073 | 231.6579 | 223.6995 | 375.9387 | 902.7073 | 375.9387 | 231.6579 | 223.6995
903.7542 | 648.7542 | 231.5036 | 223.9147 | 375.8906 | 903.7542 | 375.8906 | 231.5036 | 223.9147
904.7073 | 649.7073 | 231.2929 | 224.1179 | 375.6312 | 904.7073 | 375.6312 | 231.2929 | 224.1179
905.7073 | 650.7073 | 231.0744 | 224.3159 | 375.5726 | 905.7073 | 375.5726 | 231.0744 | 224.3159
906.7073 | 651.7073 | 230.4374 | 224.5266 | 375.633 | 906.7073 | 375.633 | 230.4374 | 224.5266
907.7073 | 652.7073 | 230.5503 | 224.7319 | 375.5715 | 907.7073 | 375.5715 | 230.5503 | 224.7319
908.7073 | 653.7073 | 229.9849 | 224.9288 | 375.5052 | 908.7073 | 375.5052 | 229.9849 | 224.9288
909.7073 | 654.7073 | 230.0559 | 225.1303 | 375.4533 | 909.7073 | 375.4533 | 230.0559 | 225.1303
910.7854 | 655.7854 | 230.3046 | 225.3479 | 375.398 | 910.7854 | 375.398 | 230.3046 | 225.3479
911.7073 | 656.7073 | 230.3204 | 225.5399 | 375.3852 | 911.7073 | 375.3852 | 230.3204 | 225.5399
912.801 | 657.801 | 230.5419 | 225.7574 | 375.3813 | 912.801 | 375.3813 | 230.5419 | 225.7574
913.9885 | 658.9885 | 230.2656 | 225.9939 | 375.5051 | 913.9885 | 375.5051 | 230.2656 | 225.9939
914.8792 | 659.8792 | 230.2745 | 226.1778 | 375.5622 | 914.8792 | 375.5622 | 230.2745 | 226.1778
915.7229 | 660.7229 | 230.6298 | 226.3447 | 375.5898 | 915.7229 | 375.5898 | 230.6298 | 226.3447
916.7698 | 661.7698 | 230.7376 | 226.5632 | 375.6904 | 916.7698 | 375.6904 | 230.7376 | 226.5632
917.7542 | 662.7542 | 230.9863 | 226.7498 | 375.6743 | 917.7542 | 375.6743 | 230.9863 | 226.7498
918.7073 | 663.7073 | 231.5249 | 226.9281 | 375.7251 | 918.7073 | 375.7251 | 231.5249 | 226.9281
919.7073 | 664.7073 | 232.0857 | 227.1146 | 375.7674 | 919.7073 | 375.7674 | 232.0857 | 227.1146
920.7073 | 665.7073 | 232.5325 | 227.2959 | 375.768 | 920.7073 | 375.768 | 232.5325 | 227.2959
921.7073 | 666.7073 | 233.0827 | 227.4729 | 375.9051 | 921.7073 | 375.9051 | 233.0827 | 227.4729
922.7073 | 667.7073 | 234.3831 | 227.637 | 376.0944 | 922.7073 | 376.0944 | 234.3831 | 227.637
923.7073 | 668.7073 | 234.6857 | 227.7897 | 376.2987 | 923.7073 | 376.2987 | 234.6857 | 227.7897
924.7073 | 669.7073 | 234.9694 | 227.962 | 376.3491 | 924.7073 | 376.3491 | 234.9694 | 227.962
925.7073 | 670.7073 | 235.0834 | 228.1255 | 376.3288 | 925.7073 | 376.3288 | 235.0834 | 228.1255
926.7073 | 671.7073 | 235.0325 | 228.2742 | 376.2784 | 926.7073 | 376.2784 | 235.0325 | 228.2742
927.7073 | 672.7073 | 235.4973 | 228.4033 | 376.2683 | 927.7073 | 376.2683 | 235.4973 | 228.4033
928.7073 | 673.7073 | 235.8839 | 228.5446 | 376.2773 | 928.7073 | 376.2773 | 235.8839 | 228.5446
929.7073 | 674.7073 | 236.3464 | 228.6827 | 376.2518 | 929.7073 | 376.2518 | 236.3464 | 228.6827
930.7073 | 675.7073 | 236.9988 | 228.8096 | 376.2547 | 930.7073 | 376.2547 | 236.9988 | 228.8096
931.7073 | 676.7073 | 237.2059 | 228.9416 | 376.2479 | 931.7073 | 376.2479 | 237.2059 | 228.9416
932.7073 | 677.7073 | 237.5252 | 229.0704 | 376.181 | 932.7073 | 376.181 | 237.5252 | 229.0704
933.7073 | 678.7073 | 237.6516 | 229.2282 | 376.3449 | 933.7073 | 376.3449 | 237.6516 | 229.2282
934.7073 | 679.7073 | 237.4881 | 229.3364 | 376.3788 | 934.7073 | 376.3788 | 237.4881 | 229.3364
935.7073 | 680.7073 | 237.7227 | 229.4405 | 376.3794 | 935.7073 | 376.3794 | 237.7227 | 229.4405
936.7073 | 681.7073 | 237.9431 | 229.5845 | 376.3453 | 936.7073 | 376.3453 | 237.9431 | 229.5845
937.7073 | 682.7073 | 238.1111 | 229.7311 | 376.3769 | 937.7073 | 376.3769 | 238.1111 | 229.7311
938.7073 | 683.7073 | 238.2692 | 229.8604 | 376.3074 | 938.7073 | 376.3074 | 238.2692 | 229.8604
939.7073 | 684.7073 | 238.498 | 229.9864 | 376.3632 | 939.7073 | 376.3632 | 238.498 | 229.9864
940.7073 | 685.7073 | 238.6568 | 230.1226 | 376.4483 | 940.7073 | 376.4483 | 238.6568 | 230.1226
941.7073 | 686.7073 | 238.7458 | 230.2662 | 376.5488 | 941.7073 | 376.5488 | 238.7458 | 230.2662
942.7073 | 687.7073 | 238.6993 | 230.4004 | 376.5056 | 942.7073 | 376.5056 | 238.6993 | 230.4004
943.7073 | 688.7073 | 239.2398 | 230.5321 | 376.5117 | 943.7073 | 376.5117 | 239.2398 | 230.5321
944.7073 | 689.7073 | 239.6492 | 230.6592 | 376.333 | 944.7073 | 376.333 | 239.6492 | 230.6592
945.7073 | 690.7073 | 239.6903 | 230.7948 | 376.3069 | 945.7073 | 376.3069 | 239.6903 | 230.7948
946.7073 | 691.7073 | 239.9884 | 230.92 | 376.2952 | 946.7073 | 376.2952 | 239.9884 | 230.92
947.7073 | 692.7073 | 240.1142 | 231.0585 | 376.2812 | 947.7073 | 376.2812 | 240.1142 | 231.0585
948.7073 | 693.7073 | 240.4639 | 231.1989 | 376.3735 | 948.7073 | 376.3735 | 240.4639 | 231.1989
949.7229 | 694.7229 | 240.5215 | 231.3252 | 376.3863 | 949.7229 | 376.3863 | 240.5215 | 231.3252
950.7385 | 695.7385 | 240.8676 | 231.4555 | 376.3586 | 950.7385 | 376.3586 | 240.8676 | 231.4555
951.7854 | 696.7854 | 241.0523 | 231.5986 | 376.215 | 951.7854 | 376.215 | 241.0523 | 231.5986
952.7854 | 697.7854 | 241.2787 | 231.7346 | 376.085 | 952.7854 | 376.085 | 241.2787 | 231.7346
953.7854 | 698.7854 | 241.6655 | 231.8764 | 376.0246 | 953.7854 | 376.0246 | 241.6655 | 231.8764
954.7073 | 699.7073 | 242.0058 | 231.9931 | 376.1139 | 954.7073 | 376.1139 | 242.0058 | 231.9931
955.7073 | 700.7073 | 242.0403 | 232.1429 | 376.1772 | 955.7073 | 376.1772 | 242.0403 | 232.1429
956.7073 | 701.7073 | 242.7829 | 232.2799 | 376.0557 | 956.7073 | 376.0557 | 242.7829 | 232.2799
957.7073 | 702.7073 | 243.1072 | 232.4128 | 375.9223 | 957.7073 | 375.9223 | 243.1072 | 232.4128
958.7073 | 703.7073 | 244.2321 | 232.5432 | 375.7581 | 958.7073 | 375.7581 | 244.2321 | 232.5432
959.7073 | 704.7073 | 244.4406 | 232.7024 | 375.6222 | 959.7073 | 375.6222 | 244.4406 | 232.7024
960.7073 | 705.7073 | 244.4957 | 232.844 | 375.6321 | 960.7073 | 375.6321 | 244.4957 | 232.844
961.7073 | 706.7073 | 244.7171 | 232.9984 | 375.7243 | 961.7073 | 375.7243 | 244.7171 | 232.9984
962.801 | 707.801 | 244.8537 | 233.1858 | 375.7167 | 962.801 | 375.7167 | 244.8537 | 233.1858
963.7073 | 708.7073 | 245.1876 | 233.3189 | 375.7062 | 963.7073 | 375.7062 | 245.1876 | 233.3189
964.7073 | 709.7073 | 245.4634 | 233.4793 | 375.6744 | 964.7073 | 375.6744 | 245.4634 | 233.4793
965.7073 | 710.7073 | 245.5408 | 233.6395 | 375.617 | 965.7073 | 375.617 | 245.5408 | 233.6395
966.8479 | 711.8479 | 245.6201 | 233.8165 | 375.6617 | 966.8479 | 375.6617 | 245.6201 | 233.8165
967.7073 | 712.7073 | 245.6456 | 233.9536 | 375.6874 | 967.7073 | 375.6874 | 245.6456 | 233.9536
968.7073 | 713.7073 | 245.856 | 234.1138 | 375.6553 | 968.7073 | 375.6553 | 245.856 | 234.1138
969.7073 | 714.7073 | 245.9869 | 234.3004 | 375.675 | 969.7073 | 375.675 | 245.9869 | 234.3004
970.7073 | 715.7073 | 246.269 | 234.4675 | 375.6323 | 970.7073 | 375.6323 | 246.269 | 234.4675
971.7073 | 716.7073 | 246.4697 | 234.6212 | 375.8181 | 971.7073 | 375.8181 | 246.4697 | 234.6212
972.7073 | 717.7073 | 246.6666 | 234.7941 | 375.8109 | 972.7073 | 375.8109 | 246.6666 | 234.7941
973.7073 | 718.7073 | 246.6568 | 234.984 | 375.8281 | 973.7073 | 375.8281 | 246.6568 | 234.984
974.7073 | 719.7073 | 246.8271 | 235.1596 | 375.8216 | 974.7073 | 375.8216 | 246.8271 | 235.1596
975.7073 | 720.7073 | 247.0826 | 235.3168 | 375.7868 | 975.7073 | 375.7868 | 247.0826 | 235.3168
976.7073 | 721.7073 | 247.2888 | 235.4706 | 375.8306 | 976.7073 | 375.8306 | 247.2888 | 235.4706
977.7073 | 722.7073 | 247.2798 | 235.6393 | 375.7762 | 977.7073 | 375.7762 | 247.2798 | 235.6393
978.7073 | 723.7073 | 247.3577 | 235.8085 | 375.7472 | 978.7073 | 375.7472 | 247.3577 | 235.8085
979.7073 | 724.7073 | 247.5463 | 235.9905 | 375.8258 | 979.7073 | 375.8258 | 247.5463 | 235.9905
980.7073 | 725.7073 | 247.741 | 236.1694 | 375.9465 | 980.7073 | 375.9465 | 247.741 | 236.1694
981.7073 | 726.7073 | 248.0016 | 236.3567 | 375.9544 | 981.7073 | 375.9544 | 248.0016 | 236.3567
982.7073 | 727.7073 | 248.2297 | 236.5297 | 375.9111 | 982.7073 | 375.9111 | 248.2297 | 236.5297
983.7073 | 728.7073 | 248.2482 | 236.6899 | 375.8824 | 983.7073 | 375.8824 | 248.2482 | 236.6899
984.7073 | 729.7073 | 248.4211 | 236.8408 | 375.9027 | 984.7073 | 375.9027 | 248.4211 | 236.8408
985.7073 | 730.7073 | 248.6033 | 237.0142 | 375.9931 | 985.7073 | 375.9931 | 248.6033 | 237.0142
986.7073 | 731.7073 | 248.304 | 237.1753 | 375.933 | 986.7073 | 375.933 | 248.304 | 237.1753
987.7073 | 732.7073 | 248.4405 | 237.3343 | 375.9675 | 987.7073 | 375.9675 | 248.4405 | 237.3343
988.7073 | 733.7073 | 248.3482 | 237.4998 | 376.0193 | 988.7073 | 376.0193 | 248.3482 | 237.4998
989.7073 | 734.7073 | 248.494 | 237.6627 | 375.9966 | 989.7073 | 375.9966 | 248.494 | 237.6627
990.7073 | 735.7073 | 248.7263 | 237.8099 | 376.1205 | 990.7073 | 376.1205 | 248.7263 | 237.8099
991.7073 | 736.7073 | 249.0015 | 238.0041 | 376.3165 | 991.7073 | 376.3165 | 249.0015 | 238.0041
992.7073 | 737.7073 | 249.1406 | 238.1908 | 376.4538 | 992.7073 | 376.4538 | 249.1406 | 238.1908
993.7073 | 738.7073 | 249.196 | 238.3744 | 376.4696 | 993.7073 | 376.4696 | 249.196 | 238.3744
994.7073 | 739.7073 | 249.1656 | 238.5791 | 376.3905 | 994.7073 | 376.3905 | 249.1656 | 238.5791
995.7073 | 740.7073 | 249.1679 | 238.7757 | 376.2905 | 995.7073 | 376.2905 | 249.1679 | 238.7757
996.7073 | 741.7073 | 249.3181 | 238.9718 | 376.2306 | 996.7073 | 376.2306 | 249.3181 | 238.9718
997.7073 | 742.7073 | 249.4748 | 239.1624 | 376.2687 | 997.7073 | 376.2687 | 249.4748 | 239.1624
998.7073 | 743.7073 | 249.5735 | 239.3457 | 376.3317 | 998.7073 | 376.3317 | 249.5735 | 239.3457
999.7073 | 744.7073 | 249.6283 | 239.5418 | 376.385 | 999.7073 | 376.385 | 249.6283 | 239.5418
1000.7073 | 745.7073 | 249.7359 | 239.7481 | 376.4555 | 1000.7073 | 376.4555 | 249.7359 | 239.7481
1001.7073 | 746.7073 | 249.9964 | 239.9584 | 376.511 | 1001.7073 | 376.511 | 249.9964 | 239.9584
1002.7073 | 747.7073 | 250.1507 | 240.1652 | 376.6851 | 1002.7073 | 376.6851 | 250.1507 | 240.1652
1003.7073 | 748.7073 | 249.7291 | 240.3583 | 376.6582 | 1003.7073 | 376.6582 | 249.7291 | 240.3583
1004.7073 | 749.7073 | 249.8067 | 240.5479 | 376.633 | 1004.7073 | 376.633 | 249.8067 | 240.5479
1005.7073 | 750.7073 | 249.981 | 240.7287 | 376.6704 | 1005.7073 | 376.6704 | 249.981 | 240.7287
1006.7073 | 751.7073 | 249.8887 | 240.913 | 376.6537 | 1006.7073 | 376.6537 | 249.8887 | 240.913
1007.7073 | 752.7073 | 249.7936 | 241.0782 | 376.5986 | 1007.7073 | 376.5986 | 249.7936 | 241.0782
1008.7073 | 753.7073 | 249.9742 | 241.2673 | 376.6483 | 1008.7073 | 376.6483 | 249.9742 | 241.2673
1009.7073 | 754.7073 | 250.2948 | 241.4541 | 376.687 | 1009.7073 | 376.687 | 250.2948 | 241.4541
1010.7073 | 755.7073 | 250.554 | 241.6056 | 376.7058 | 1010.7073 | 376.7058 | 250.554 | 241.6056
1011.7073 | 756.7073 | 250.7558 | 241.7679 | 376.5094 | 1011.7073 | 376.5094 | 250.7558 | 241.7679
1012.7073 | 757.7073 | 250.9463 | 241.9401 | 376.3699 | 1012.7073 | 376.3699 | 250.9463 | 241.9401
1013.7073 | 758.7073 | 250.9199 | 242.109 | 376.3174 | 1013.7073 | 376.3174 | 250.9199 | 242.109
1014.7073 | 759.7073 | 250.949 | 242.2757 | 376.2615 | 1014.7073 | 376.2615 | 250.949 | 242.2757
1015.7073 | 760.7073 | 250.8714 | 242.4399 | 376.2476 | 1015.7073 | 376.2476 | 250.8714 | 242.4399
1016.7073 | 761.7073 | 251.0357 | 242.5825 | 376.1261 | 1016.7073 | 376.1261 | 251.0357 | 242.5825
1017.7073 | 762.7073 | 251.2754 | 242.7247 | 376.0872 | 1017.7073 | 376.0872 | 251.2754 | 242.7247
1018.7073 | 763.7073 | 251.4113 | 242.8703 | 375.9007 | 1018.7073 | 375.9007 | 251.4113 | 242.8703
1019.7073 | 764.7073 | 251.5726 | 243.0256 | 375.9257 | 1019.7073 | 375.9257 | 251.5726 | 243.0256
1020.7073 | 765.7073 | 251.7246 | 243.1737 | 375.9572 | 1020.7073 | 375.9572 | 251.7246 | 243.1737
1021.7073 | 766.7073 | 251.6635 | 243.3234 | 376.0846 | 1021.7073 | 376.0846 | 251.6635 | 243.3234
1022.7073 | 767.7073 | 251.4059 | 243.4808 | 376.0483 | 1022.7073 | 376.0483 | 251.4059 | 243.4808
1023.7073 | 768.7073 | 251.4323 | 243.6364 | 376.1115 | 1023.7073 | 376.1115 | 251.4323 | 243.6364
1024.7073 | 769.7073 | 251.5942 | 243.8165 | 376.13 | 1024.7073 | 376.13 | 251.5942 | 243.8165
1025.7073 | 770.7073 | 251.6754 | 243.9794 | 376.1694 | 1025.7073 | 376.1694 | 251.6754 | 243.9794
1026.7073 | 771.7073 | 251.5305 | 244.1378 | 376.2507 | 1026.7073 | 376.2507 | 251.5305 | 244.1378
1027.7073 | 772.7073 | 251.8242 | 244.3022 | 376.1825 | 1027.7073 | 376.1825 | 251.8242 | 244.3022
1028.7073 | 773.7073 | 251.9259 | 244.477 | 376.1216 | 1028.7073 | 376.1216 | 251.9259 | 244.477
1029.7073 | 774.7073 | 251.8977 | 244.6696 | 376.2125 | 1029.7073 | 376.2125 | 251.8977 | 244.6696
1030.7073 | 775.7073 | 252.0526 | 244.8481 | 376.2436 | 1030.7073 | 376.2436 | 252.0526 | 244.8481
1031.7073 | 776.7073 | 252.1269 | 245.032 | 376.1712 | 1031.7073 | 376.1712 | 252.1269 | 245.032
1032.7073 | 777.7073 | 252.2485 | 245.1923 | 376.1134 | 1032.7073 | 376.1134 | 252.2485 | 245.1923
1033.7073 | 778.7073 | 252.3718 | 245.3566 | 376.0497 | 1033.7073 | 376.0497 | 252.3718 | 245.3566
1034.7073 | 779.7073 | 252.4854 | 245.5375 | 375.8638 | 1034.7073 | 375.8638 | 252.4854 | 245.5375
1035.7073 | 780.7073 | 252.4631 | 245.709 | 375.7421 | 1035.7073 | 375.7421 | 252.4631 | 245.709
1036.7073 | 781.7073 | 252.3032 | 245.8721 | 375.8304 | 1036.7073 | 375.8304 | 252.3032 | 245.8721
1037.7073 | 782.7073 | 252.446 | 246.0341 | 375.7133 | 1037.7073 | 375.7133 | 252.446 | 246.0341
1038.7073 | 783.7073 | 252.4659 | 246.1938 | 375.6699 | 1038.7073 | 375.6699 | 252.4659 | 246.1938
1039.7073 | 784.7073 | 252.5137 | 246.3599 | 375.6019 | 1039.7073 | 375.6019 | 252.5137 | 246.3599
1040.7073 | 785.7073 | 252.5948 | 246.5171 | 375.5931 | 1040.7073 | 375.5931 | 252.5948 | 246.5171
1041.7073 | 786.7073 | 252.6706 | 246.6755 | 375.4892 | 1041.7073 | 375.4892 | 252.6706 | 246.6755
1042.7073 | 787.7073 | 252.6571 | 246.8448 | 375.4815 | 1042.7073 | 375.4815 | 252.6571 | 246.8448
1043.7073 | 788.7073 | 252.6169 | 247.0018 | 375.5023 | 1043.7073 | 375.5023 | 252.6169 | 247.0018
1044.7073 | 789.7073 | 252.8459 | 247.1631 | 375.5771 | 1044.7073 | 375.5771 | 252.8459 | 247.1631
1045.7073 | 790.7073 | 252.9234 | 247.3173 | 375.6861 | 1045.7073 | 375.6861 | 252.9234 | 247.3173
1046.7073 | 791.7073 | 252.9183 | 247.4688 | 375.6517 | 1046.7073 | 375.6517 | 252.9183 | 247.4688
1047.7073 | 792.7073 | 253.0325 | 247.6359 | 375.5281 | 1047.7073 | 375.5281 | 253.0325 | 247.6359
1048.7073 | 793.7073 | 253.0798 | 247.7733 | 375.4615 | 1048.7073 | 375.4615 | 253.0798 | 247.7733
1049.7073 | 794.7073 | 253.0632 | 247.9492 | 375.465 | 1049.7073 | 375.465 | 253.0632 | 247.9492
1050.7073 | 795.7073 | 253.1748 | 248.1164 | 375.3408 | 1050.7073 | 375.3408 | 253.1748 | 248.1164
1051.7073 | 796.7073 | 253.0246 | 248.2835 | 375.1688 | 1051.7073 | 375.1688 | 253.0246 | 248.2835
1052.7073 | 797.7073 | 253.1264 | 248.4346 | 375.0627 | 1052.7073 | 375.0627 | 253.1264 | 248.4346
1053.7073 | 798.7073 | 253.2315 | 248.6068 | 375.0642 | 1053.7073 | 375.0642 | 253.2315 | 248.6068
1054.7073 | 799.7073 | 253.3305 | 248.7872 | 375.1523 | 1054.7073 | 375.1523 | 253.3305 | 248.7872
1055.7073 | 800.7073 | 253.4082 | 248.938 | 375.0966 | 1055.7073 | 375.0966 | 253.4082 | 248.938
1056.7073 | 801.7073 | 253.4729 | 249.0665 | 375.0948 | 1056.7073 | 375.0948 | 253.4729 | 249.0665
1057.7073 | 802.7073 | 253.3815 | 249.2162 | 375.0304 | 1057.7073 | 375.0304 | 253.3815 | 249.2162
1058.7073 | 803.7073 | 253.475 | 249.3854 | 375.0378 | 1058.7073 | 375.0378 | 253.475 | 249.3854
1059.7073 | 804.7073 | 253.5619 | 249.5511 | 374.9375 | 1059.7073 | 374.9375 | 253.5619 | 249.5511
1060.7073 | 805.7073 | 253.5892 | 249.6908 | 374.9334 | 1060.7073 | 374.9334 | 253.5892 | 249.6908
1061.7073 | 806.7073 | 253.5143 | 249.8436 | 374.8434 | 1061.7073 | 374.8434 | 253.5143 | 249.8436
1062.7073 | 807.7073 | 253.3396 | 250.0055 | 374.7715 | 1062.7073 | 374.7715 | 253.3396 | 250.0055
1063.7073 | 808.7073 | 253.6169 | 250.1612 | 374.7927 | 1063.7073 | 374.7927 | 253.6169 | 250.1612
1064.7073 | 809.7073 | 253.6304 | 250.314 | 374.8677 | 1064.7073 | 374.8677 | 253.6304 | 250.314
1065.7073 | 810.7073 | 253.7105 | 250.4766 | 374.8892 | 1065.7073 | 374.8892 | 253.7105 | 250.4766
1066.7073 | 811.7073 | 254.0745 | 250.6324 | 374.8643 | 1066.7073 | 374.8643 | 254.0745 | 250.6324
1067.7073 | 812.7073 | 254.2267 | 250.7888 | 374.7859 | 1067.7073 | 374.7859 | 254.2267 | 250.7888
1068.7073 | 813.7073 | 254.3717 | 250.9409 | 374.6585 | 1068.7073 | 374.6585 | 254.3717 | 250.9409
1069.7073 | 814.7073 | 254.4869 | 251.0855 | 374.6005 | 1069.7073 | 374.6005 | 254.4869 | 251.0855
1070.7073 | 815.7073 | 254.4869 | 251.2262 | 374.5452 | 1070.7073 | 374.5452 | 254.4869 | 251.2262
1071.7073 | 816.7073 | 254.5738 | 251.3696 | 374.5685 | 1071.7073 | 374.5685 | 254.5738 | 251.3696
1072.7073 | 817.7073 | 254.6251 | 251.5126 | 374.545 | 1072.7073 | 374.545 | 254.6251 | 251.5126
1073.7073 | 818.7073 | 254.6644 | 251.6502 | 374.6276 | 1073.7073 | 374.6276 | 254.6644 | 251.6502
1074.7073 | 819.7073 | 254.7035 | 251.7828 | 374.6519 | 1074.7073 | 374.6519 | 254.7035 | 251.7828
1075.7073 | 820.7073 | 254.7169 | 251.9195 | 374.6464 | 1075.7073 | 374.6464 | 254.7169 | 251.9195
1076.7073 | 821.7073 | 254.7553 | 252.0602 | 374.6577 | 1076.7073 | 374.6577 | 254.7553 | 252.0602
1077.7073 | 822.7073 | 254.8001 | 252.1831 | 374.6804 | 1077.7073 | 374.6804 | 254.8001 | 252.1831
1078.7073 | 823.7073 | 254.8134 | 252.3044 | 374.6299 | 1078.7073 | 374.6299 | 254.8134 | 252.3044
1079.7073 | 824.7073 | 254.8492 | 252.4331 | 374.6002 | 1079.7073 | 374.6002 | 254.8492 | 252.4331
1080.7073 | 825.7073 | 254.9051 | 252.5715 | 374.6104 | 1080.7073 | 374.6104 | 254.9051 | 252.5715
1081.7073 | 826.7073 | 254.8683 | 252.7072 | 374.5901 | 1081.7073 | 374.5901 | 254.8683 | 252.7072
1082.7073 | 827.7073 | 255.0133 | 252.8397 | 374.578 | 1082.7073 | 374.578 | 255.0133 | 252.8397
1083.7073 | 828.7073 | 255.1183 | 252.9742 | 374.5518 | 1083.7073 | 374.5518 | 255.1183 | 252.9742
1084.7073 | 829.7073 | 255.0319 | 253.1 | 374.5019 | 1084.7073 | 374.5019 | 255.0319 | 253.1
1085.7073 | 830.7073 | 255.1857 | 253.24 | 374.4429 | 1085.7073 | 374.4429 | 255.1857 | 253.24
1086.7073 | 831.7073 | 255.2364 | 253.3689 | 374.4164 | 1086.7073 | 374.4164 | 255.2364 | 253.3689
1087.7854 | 832.7854 | 255.2055 | 253.5057 | 374.4928 | 1087.7854 | 374.4928 | 255.2055 | 253.5057
1088.801 | 833.801 | 255.0361 | 253.6316 | 374.4715 | 1088.801 | 374.4715 | 255.0361 | 253.6316
1089.7073 | 834.7073 | 255.2778 | 253.753 | 374.3471 | 1089.7073 | 374.3471 | 255.2778 | 253.753
1090.7385 | 835.7385 | 255.3324 | 253.8812 | 374.2601 | 1090.7385 | 374.2601 | 255.3324 | 253.8812
1091.7073 | 836.7073 | 255.0912 | 254.0035 | 374.3685 | 1091.7073 | 374.3685 | 255.0912 | 254.0035
1092.7073 | 837.7073 | 255.0725 | 254.1258 | 374.4959 | 1092.7073 | 374.4959 | 255.0725 | 254.1258
1093.7073 | 838.7073 | 255.2052 | 254.2649 | 374.5322 | 1093.7073 | 374.5322 | 255.2052 | 254.2649
1094.7073 | 839.7073 | 255.1235 | 254.3985 | 374.569 | 1094.7073 | 374.569 | 255.1235 | 254.3985
1095.8479 | 840.8479 | 255.2497 | 254.5698 | 374.5727 | 1095.8479 | 374.5727 | 255.2497 | 254.5698
1096.7073 | 841.7073 | 255.2946 | 254.7008 | 374.5575 | 1096.7073 | 374.5575 | 255.2946 | 254.7008
1097.7073 | 842.7073 | 255.2949 | 254.8486 | 374.6326 | 1097.7073 | 374.6326 | 255.2949 | 254.8486
1098.8635 | 843.8635 | 255.1211 | 255.0229 | 374.634 | 1098.8635 | 374.634 | 255.1211 | 255.0229
1099.7854 | 844.7854 | 254.8903 | 255.1635 | 374.7476 | 1099.7854 | 374.7476 | 254.8903 | 255.1635
1100.8479 | 845.8479 | 254.9503 | 255.3073 | 374.901 | 1100.8479 | 374.901 | 254.9503 | 255.3073
1101.7073 | 846.7073 | 254.5448 | 255.4277 | 374.8219 | 1101.7073 | 374.8219 | 254.5448 | 255.4277
1102.7073 | 847.7073 | 254.2219 | 255.5574 | 374.7875 | 1102.7073 | 374.7875 | 254.2219 | 255.5574
1103.7073 | 848.7073 | 253.7293 | 255.6943 | 374.8094 | 1103.7073 | 374.8094 | 253.7293 | 255.6943
1104.7073 | 849.7073 | 253.4201 | 255.8302 | 374.895 | 1104.7073 | 374.895 | 253.4201 | 255.8302
1105.7073 | 850.7073 | 253.2333 | 255.9665 | 375.0455 | 1105.7073 | 375.0455 | 253.2333 | 255.9665
1106.8792 | 851.8792 | 253.2067 | 256.1214 | 375.0668 | 1106.8792 | 375.0668 | 253.2067 | 256.1214
1107.7073 | 852.7073 | 253.0683 | 256.2429 | 375.1328 | 1107.7073 | 375.1328 | 253.0683 | 256.2429
1108.7542 | 853.7542 | 252.9526 | 256.3756 | 375.1755 | 1108.7542 | 375.1755 | 252.9526 | 256.3756
1109.8167 | 854.8167 | 252.8912 | 256.5255 | 375.2347 | 1109.8167 | 375.2347 | 252.8912 | 256.5255
1110.7542 | 855.7542 | 253.0205 | 256.648 | 375.3237 | 1110.7542 | 375.3237 | 253.0205 | 256.648
1111.7073 | 856.7073 | 252.9375 | 256.771 | 375.3681 | 1111.7073 | 375.3681 | 252.9375 | 256.771
1112.7854 | 857.7854 | 252.9433 | 256.9057 | 375.3554 | 1112.7854 | 375.3554 | 252.9433 | 256.9057
1113.7073 | 858.7073 | 253.336 | 257.0155 | 375.2706 | 1113.7073 | 375.2706 | 253.336 | 257.0155
1114.8323 | 859.8323 | 254.0333 | 257.1316 | 375.2021 | 1114.8323 | 375.2021 | 254.0333 | 257.1316
1115.7385 | 860.7385 | 253.9126 | 257.2073 | 375.167 | 1115.7385 | 375.167 | 253.9126 | 257.2073
1116.7073 | 861.7073 | 253.9497 | 257.2923 | 375.2063 | 1116.7073 | 375.2063 | 253.9497 | 257.2923
1117.7073 | 862.7073 | 253.7922 | 257.3967 | 375.315 | 1117.7073 | 375.315 | 253.7922 | 257.3967
1118.7073 | 863.7073 | 253.8296 | 257.4929 | 375.4153 | 1118.7073 | 375.4153 | 253.8296 | 257.4929
1119.7073 | 864.7073 | 253.8945 | 257.601 | 375.5338 | 1119.7073 | 375.5338 | 253.8945 | 257.601
1120.7073 | 865.7073 | 253.9067 | 257.7015 | 375.4979 | 1120.7073 | 375.4979 | 253.9067 | 257.7015
1121.7073 | 866.7073 | 253.9335 | 257.804 | 375.5007 | 1121.7073 | 375.5007 | 253.9335 | 257.804
1122.7073 | 867.7073 | 253.9505 | 257.9085 | 375.4767 | 1122.7073 | 375.4767 | 253.9505 | 257.9085
1123.7073 | 868.7073 | 254.0016 | 258.0126 | 375.2943 | 1123.7073 | 375.2943 | 254.0016 | 258.0126
1124.7073 | 869.7073 | 254.0392 | 258.1041 | 375.1364 | 1124.7073 | 375.1364 | 254.0392 | 258.1041
1125.7073 | 870.7073 | 254.1606 | 258.2169 | 375.0931 | 1125.7073 | 375.0931 | 254.1606 | 258.2169
1126.7073 | 871.7073 | 254.2871 | 258.3245 | 374.971 | 1126.7073 | 374.971 | 254.2871 | 258.3245
1127.7073 | 872.7073 | 254.3754 | 258.4215 | 374.8935 | 1127.7073 | 374.8935 | 254.3754 | 258.4215
1128.7073 | 873.7073 | 254.4364 | 258.51 | 374.8807 | 1128.7073 | 374.8807 | 254.4364 | 258.51
1129.7073 | 874.7073 | 254.4462 | 258.6098 | 374.8431 | 1129.7073 | 374.8431 | 254.4462 | 258.6098
1130.7073 | 875.7073 | 254.5203 | 258.7103 | 374.8189 | 1130.7073 | 374.8189 | 254.5203 | 258.7103
1131.7073 | 876.7073 | 254.6885 | 258.8058 | 374.795 | 1131.7073 | 374.795 | 254.6885 | 258.8058
1132.7073 | 877.7073 | 254.7561 | 258.9032 | 374.7934 | 1132.7073 | 374.7934 | 254.7561 | 258.9032
1133.7073 | 878.7073 | 254.867 | 258.9976 | 374.7844 | 1133.7073 | 374.7844 | 254.867 | 258.9976
1134.7073 | 879.7073 | 254.9149 | 259.0884 | 374.7421 | 1134.7073 | 374.7421 | 254.9149 | 259.0884
1135.7073 | 880.7073 | 255.0262 | 259.1795 | 374.8171 | 1135.7073 | 374.8171 | 255.0262 | 259.1795
1136.7073 | 881.7073 | 255.1089 | 259.2762 | 374.8728 | 1136.7073 | 374.8728 | 255.1089 | 259.2762
1137.7073 | 882.7073 | 255.2574 | 259.3958 | 374.9177 | 1137.7073 | 374.9177 | 255.2574 | 259.3958
1138.7073 | 883.7073 | 255.348 | 259.5046 | 374.8236 | 1138.7073 | 374.8236 | 255.348 | 259.5046
1139.7073 | 884.7073 | 255.4419 | 259.6304 | 374.7236 | 1139.7073 | 374.7236 | 255.4419 | 259.6304
1140.7073 | 885.7073 | 255.4428 | 259.7537 | 374.6801 | 1140.7073 | 374.6801 | 255.4428 | 259.7537
1141.7073 | 886.7073 | 255.5386 | 259.868 | 374.7919 | 1141.7073 | 374.7919 | 255.5386 | 259.868
1142.7073 | 887.7073 | 255.6228 | 259.9876 | 374.9028 | 1142.7073 | 374.9028 | 255.6228 | 259.9876
1143.7073 | 888.7073 | 255.6334 | 260.0937 | 374.8933 | 1143.7073 | 374.8933 | 255.6334 | 260.0937
1144.7073 | 889.7073 | 255.6931 | 260.2037 | 374.7548 | 1144.7073 | 374.7548 | 255.6931 | 260.2037
1145.7073 | 890.7073 | 255.7905 | 260.311 | 374.7477 | 1145.7073 | 374.7477 | 255.7905 | 260.311
1146.7073 | 891.7073 | 255.8789 | 260.4085 | 374.8874 | 1146.7073 | 374.8874 | 255.8789 | 260.4085
1147.7073 | 892.7073 | 255.9708 | 260.4921 | 374.993 | 1147.7073 | 374.993 | 255.9708 | 260.4921
1148.7073 | 893.7073 | 256.0969 | 260.5726 | 375.0343 | 1148.7073 | 375.0343 | 256.0969 | 260.5726
1149.7073 | 894.7073 | 256.2093 | 260.6494 | 375.0777 | 1149.7073 | 375.0777 | 256.2093 | 260.6494
1150.7073 | 895.7073 | 256.2963 | 260.7203 | 375.0287 | 1150.7073 | 375.0287 | 256.2963 | 260.7203
1151.7073 | 896.7073 | 256.314 | 260.7915 | 374.9807 | 1151.7073 | 374.9807 | 256.314 | 260.7915
1152.7073 | 897.7073 | 256.4302 | 260.8557 | 375.0572 | 1152.7073 | 375.0572 | 256.4302 | 260.8557
1153.7073 | 898.7073 | 256.5958 | 260.9185 | 375.2198 | 1153.7073 | 375.2198 | 256.5958 | 260.9185
1154.7073 | 899.7073 | 256.7379 | 260.977 | 375.3536 | 1154.7073 | 375.3536 | 256.7379 | 260.977
1155.7073 | 900.7073 | 256.8817 | 261.0379 | 375.3912 | 1155.7073 | 375.3912 | 256.8817 | 261.0379
1156.7073 | 901.7073 | 256.9826 | 261.0994 | 375.4304 | 1156.7073 | 375.4304 | 256.9826 | 261.0994
1157.7073 | 902.7073 | 257.1034 | 261.1756 | 375.3565 | 1157.7073 | 375.3565 | 257.1034 | 261.1756
1158.7073 | 903.7073 | 257.1401 | 261.247 | 375.4816 | 1158.7073 | 375.4816 | 257.1401 | 261.247
1159.7073 | 904.7073 | 257.3868 | 261.3215 | 375.6 | 1159.7073 | 375.6 | 257.3868 | 261.3215
1160.7073 | 905.7073 | 257.7006 | 261.3904 | 375.648 | 1160.7073 | 375.648 | 257.7006 | 261.3904
1161.7073 | 906.7073 | 257.8076 | 261.4608 | 375.6341 | 1161.7073 | 375.6341 | 257.8076 | 261.4608
1162.7073 | 907.7073 | 257.9247 | 261.5199 | 375.565 | 1162.7073 | 375.565 | 257.9247 | 261.5199
1163.7073 | 908.7073 | 258.0118 | 261.5896 | 375.5543 | 1163.7073 | 375.5543 | 258.0118 | 261.5896
1164.7073 | 909.7073 | 258.108 | 261.659 | 375.4832 | 1164.7073 | 375.4832 | 258.108 | 261.659
1165.7073 | 910.7073 | 258.1959 | 261.7314 | 375.4202 | 1165.7073 | 375.4202 | 258.1959 | 261.7314
1166.7073 | 911.7073 | 258.3087 | 261.7948 | 375.406 | 1166.7073 | 375.406 | 258.3087 | 261.7948
1167.7073 | 912.7073 | 258.4242 | 261.8653 | 375.3502 | 1167.7073 | 375.3502 | 258.4242 | 261.8653
1168.7073 | 913.7073 | 258.4917 | 261.9367 | 375.2919 | 1168.7073 | 375.2919 | 258.4917 | 261.9367
1169.7073 | 914.7073 | 258.5982 | 262.0083 | 375.2668 | 1169.7073 | 375.2668 | 258.5982 | 262.0083
1170.7073 | 915.7073 | 258.6599 | 262.0713 | 375.1545 | 1170.7073 | 375.1545 | 258.6599 | 262.0713
1171.7073 | 916.7073 | 258.7665 | 262.1387 | 375.158 | 1171.7073 | 375.158 | 258.7665 | 262.1387
1172.7073 | 917.7073 | 258.8786 | 262.2015 | 375.0527 | 1172.7073 | 375.0527 | 258.8786 | 262.2015
1173.7073 | 918.7073 | 258.9709 | 262.2657 | 375.0884 | 1173.7073 | 375.0884 | 258.9709 | 262.2657
1174.7073 | 919.7073 | 259.0613 | 262.3326 | 374.9729 | 1174.7073 | 374.9729 | 259.0613 | 262.3326
1175.7073 | 920.7073 | 259.1494 | 262.3989 | 374.9651 | 1175.7073 | 374.9651 | 259.1494 | 262.3989
1176.801 | 921.801 | 259.2463 | 262.4726 | 374.9982 | 1176.801 | 374.9982 | 259.2463 | 262.4726
1177.7073 | 922.7073 | 259.2553 | 262.5376 | 375.0758 | 1177.7073 | 375.0758 | 259.2553 | 262.5376
1178.7073 | 923.7073 | 259.4158 | 262.6022 | 375.1619 | 1178.7073 | 375.1619 | 259.4158 | 262.6022
1179.7073 | 924.7073 | 259.5606 | 262.6652 | 375.0683 | 1179.7073 | 375.0683 | 259.5606 | 262.6652
1180.7073 | 925.7073 | 259.6577 | 262.7293 | 375.053 | 1180.7073 | 375.053 | 259.6577 | 262.7293
1181.7073 | 926.7073 | 259.7569 | 262.8029 | 375.1257 | 1181.7073 | 375.1257 | 259.7569 | 262.8029
1182.7854 | 927.7854 | 259.832 | 262.873 | 375.0842 | 1182.7854 | 375.0842 | 259.832 | 262.873
1183.7229 | 928.7229 | 259.9228 | 262.9269 | 374.9218 | 1183.7229 | 374.9218 | 259.9228 | 262.9269
1184.7385 | 929.7385 | 260.0099 | 262.9926 | 374.957 | 1184.7385 | 374.957 | 260.0099 | 262.9926
1185.7385 | 930.7385 | 260.089 | 263.0611 | 374.9317 | 1185.7385 | 374.9317 | 260.089 | 263.0611
1186.7229 | 931.7229 | 260.1884 | 263.1223 | 374.8552 | 1186.7229 | 374.8552 | 260.1884 | 263.1223
1187.7854 | 932.7854 | 260.2526 | 263.1953 | 374.9641 | 1187.7854 | 374.9641 | 260.2526 | 263.1953
1188.7854 | 933.7854 | 260.3486 | 263.2439 | 374.9011 | 1188.7854 | 374.9011 | 260.3486 | 263.2439
1189.8479 | 934.8479 | 260.4586 | 263.3277 | 374.8244 | 1189.8479 | 374.8244 | 260.4586 | 263.3277
1190.801 | 935.801 | 260.5419 | 263.3961 | 374.8241 | 1190.801 | 374.8241 | 260.5419 | 263.3961
1191.7073 | 936.7073 | 260.6361 | 263.4516 | 374.7608 | 1191.7073 | 374.7608 | 260.6361 | 263.4516
1192.7073 | 937.7073 | 260.7237 | 263.5148 | 374.8098 | 1192.7073 | 374.8098 | 260.7237 | 263.5148
1193.7073 | 938.7073 | 260.806 | 263.5802 | 374.8181 | 1193.7073 | 374.8181 | 260.806 | 263.5802
1194.7073 | 939.7073 | 260.9198 | 263.6533 | 374.8033 | 1194.7073 | 374.8033 | 260.9198 | 263.6533
1195.7073 | 940.7073 | 261.0503 | 263.7062 | 374.892 | 1195.7073 | 374.892 | 261.0503 | 263.7062
1196.7073 | 941.7073 | 261.166 | 263.7747 | 374.8284 | 1196.7073 | 374.8284 | 261.166 | 263.7747
1197.7073 | 942.7073 | 261.2149 | 263.8313 | 374.7609 | 1197.7073 | 374.7609 | 261.2149 | 263.8313
1198.7073 | 943.7073 | 261.3063 | 263.9023 | 374.8043 | 1198.7073 | 374.8043 | 261.3063 | 263.9023
1199.7073 | 944.7073 | 261.4112 | 263.9616 | 374.8964 | 1199.7073 | 374.8964 | 261.4112 | 263.9616
1200.7073 | 945.7073 | 261.5062 | 264.0292 | 374.9486 | 1200.7073 | 374.9486 | 261.5062 | 264.0292
1201.7073 | 946.7073 | 261.6084 | 264.0987 | 374.9656 | 1201.7073 | 374.9656 | 261.6084 | 264.0987
1202.7073 | 947.7073 | 261.7174 | 264.1763 | 374.9503 | 1202.7073 | 374.9503 | 261.7174 | 264.1763
1203.7073 | 948.7073 | 261.8203 | 264.2541 | 374.9474 | 1203.7073 | 374.9474 | 261.8203 | 264.2541
1204.7073 | 949.7073 | 261.9151 | 264.3249 | 374.9881 | 1204.7073 | 374.9881 | 261.9151 | 264.3249
1205.7073 | 950.7073 | 262.0033 | 264.3932 | 375.1232 | 1205.7073 | 375.1232 | 262.0033 | 264.3932
1206.7073 | 951.7073 | 262.0938 | 264.4514 | 375.2328 | 1206.7073 | 375.2328 | 262.0938 | 264.4514
1207.7073 | 952.7073 | 262.2026 | 264.5317 | 375.2545 | 1207.7073 | 375.2545 | 262.2026 | 264.5317
1208.7073 | 953.7073 | 262.2996 | 264.6116 | 375.1873 | 1208.7073 | 375.1873 | 262.2996 | 264.6116
1209.7073 | 954.7073 | 262.3886 | 264.6849 | 375.0424 | 1209.7073 | 375.0424 | 262.3886 | 264.6849
1210.7073 | 955.7073 | 262.5043 | 264.7557 | 375.0884 | 1210.7073 | 375.0884 | 262.5043 | 264.7557
1211.7073 | 956.7073 | 262.5887 | 264.8452 | 375.0768 | 1211.7073 | 375.0768 | 262.5887 | 264.8452
1212.7073 | 957.7073 | 262.6987 | 264.9209 | 375.1017 | 1212.7073 | 375.1017 | 262.6987 | 264.9209
1213.7073 | 958.7073 | 262.8042 | 264.9831 | 375.0165 | 1213.7073 | 375.0165 | 262.8042 | 264.9831
1214.7073 | 959.7073 | 262.8964 | 265.0547 | 374.9692 | 1214.7073 | 374.9692 | 262.8964 | 265.0547
1215.7073 | 960.7073 | 263.0113 | 265.1288 | 374.9063 | 1215.7073 | 374.9063 | 263.0113 | 265.1288
1216.7073 | 961.7073 | 263.1433 | 265.2029 | 374.8386 | 1216.7073 | 374.8386 | 263.1433 | 265.2029
1217.7073 | 962.7073 | 263.2445 | 265.2694 | 374.8006 | 1217.7073 | 374.8006 | 263.2445 | 265.2694
1218.7073 | 963.7073 | 263.3647 | 265.3236 | 374.8251 | 1218.7073 | 374.8251 | 263.3647 | 265.3236
1219.7073 | 964.7073 | 263.4923 | 265.3924 | 375.0012 | 1219.7073 | 375.0012 | 263.4923 | 265.3924
1220.7073 | 965.7073 | 263.6231 | 265.4669 | 374.8863 | 1220.7073 | 374.8863 | 263.6231 | 265.4669
1221.7073 | 966.7073 | 263.7458 | 265.543 | 374.7325 | 1221.7073 | 374.7325 | 263.7458 | 265.543
1222.7073 | 967.7073 | 263.8347 | 265.6372 | 374.823 | 1222.7073 | 374.823 | 263.8347 | 265.6372
1223.7073 | 968.7073 | 263.9803 | 265.7109 | 374.9255 | 1223.7073 | 374.9255 | 263.9803 | 265.7109
1224.7073 | 969.7073 | 264.142 | 265.7749 | 375.0165 | 1224.7073 | 375.0165 | 264.142 | 265.7749
1225.7073 | 970.7073 | 264.4503 | 265.831 | 375.0858 | 1225.7073 | 375.0858 | 264.4503 | 265.831
1226.7073 | 971.7073 | 264.6716 | 265.8671 | 375.1261 | 1226.7073 | 375.1261 | 264.6716 | 265.8671
1227.7073 | 972.7073 | 264.8651 | 265.9045 | 375.1188 | 1227.7073 | 375.1188 | 264.8651 | 265.9045
1228.7073 | 973.7073 | 265.0526 | 265.9473 | 375.1178 | 1228.7073 | 375.1178 | 265.0526 | 265.9473
1229.7073 | 974.7073 | 265.2217 | 265.9851 | 375.2565 | 1229.7073 | 375.2565 | 265.2217 | 265.9851
1230.7073 | 975.7073 | 265.4056 | 266.0243 | 375.303 | 1230.7073 | 375.303 | 265.4056 | 266.0243
1231.7073 | 976.7073 | 265.5715 | 266.0616 | 375.2389 | 1231.7073 | 375.2389 | 265.5715 | 266.0616
1232.7073 | 977.7073 | 265.7218 | 266.1091 | 375.2267 | 1232.7073 | 375.2267 | 265.7218 | 266.1091
1233.7073 | 978.7073 | 265.8936 | 266.1407 | 375.3077 | 1233.7073 | 375.3077 | 265.8936 | 266.1407
1234.7073 | 979.7073 | 266.0417 | 266.1697 | 375.2589 | 1234.7073 | 375.2589 | 266.0417 | 266.1697
1235.7073 | 980.7073 | 266.2305 | 266.2111 | 375.256 | 1235.7073 | 375.256 | 266.2305 | 266.2111
1236.7073 | 981.7073 | 266.383 | 266.2436 | 375.1113 | 1236.7073 | 375.1113 | 266.383 | 266.2436
1237.7073 | 982.7073 | 266.5463 | 266.28 | 375.1234 | 1237.7073 | 375.1234 | 266.5463 | 266.28
1238.801 | 983.801 | 266.7111 | 266.3249 | 375.2025 | 1238.801 | 375.2025 | 266.7111 | 266.3249
1239.801 | 984.801 | 266.8558 | 266.3562 | 375.1423 | 1239.801 | 375.1423 | 266.8558 | 266.3562
1240.7229 | 985.7229 | 266.9843 | 266.4076 | 375.1094 | 1240.7229 | 375.1094 | 266.9843 | 266.4076
1241.8323 | 986.8323 | 267.1324 | 266.4456 | 375.0682 | 1241.8323 | 375.0682 | 267.1324 | 266.4456
1242.7542 | 987.7542 | 267.276 | 266.4855 | 374.9619 | 1242.7542 | 374.9619 | 267.276 | 266.4855
1243.7073 | 988.7073 | 267.4123 | 266.526 | 374.9123 | 1243.7073 | 374.9123 | 267.4123 | 266.526
1244.7073 | 989.7073 | 267.5664 | 266.5614 | 374.8555 | 1244.7073 | 374.8555 | 267.5664 | 266.5614
1245.7073 | 990.7073 | 267.673 | 266.6056 | 374.8575 | 1245.7073 | 374.8575 | 267.673 | 266.6056
1246.7073 | 991.7073 | 267.814 | 266.6393 | 374.737 | 1246.7073 | 374.737 | 267.814 | 266.6393
1247.7073 | 992.7073 | 267.9382 | 266.6734 | 374.6712 | 1247.7073 | 374.6712 | 267.9382 | 266.6734
1248.7073 | 993.7073 | 268.0667 | 266.7203 | 374.6624 | 1248.7073 | 374.6624 | 268.0667 | 266.7203
1249.7073 | 994.7073 | 268.1793 | 266.754 | 374.6304 | 1249.7073 | 374.6304 | 268.1793 | 266.754
1250.7073 | 995.7073 | 268.3376 | 266.792 | 374.5582 | 1250.7073 | 374.5582 | 268.3376 | 266.792
1251.7073 | 996.7073 | 268.4788 | 266.8259 | 374.4969 | 1251.7073 | 374.4969 | 268.4788 | 266.8259
1252.7073 | 997.7073 | 268.6052 | 266.8665 | 374.535 | 1252.7073 | 374.535 | 268.6052 | 266.8665
1253.7073 | 998.7073 | 268.7286 | 266.9139 | 374.6659 | 1253.7073 | 374.6659 | 268.7286 | 266.9139
1254.8323 | 999.8323 | 268.8591 | 266.9544 | 374.8128 | 1254.8323 | 374.8128 | 268.8591 | 266.9544
1255.7385 | 1000.7385 | 268.9638 | 267.0005 | 374.809 | 1255.7385 | 374.809 | 268.9638 | 267.0005
1256.7073 | 1001.7073 | 269.0776 | 267.0303 | 374.8082 | 1256.7073 | 374.8082 | 269.0776 | 267.0303
1257.7073 | 1002.7073 | 269.1863 | 267.0909 | 374.9222 | 1257.7073 | 374.9222 | 269.1863 | 267.0909
1258.7073 | 1003.7073 | 269.2962 | 267.1204 | 374.868 | 1258.7073 | 374.868 | 269.2962 | 267.1204
1259.7073 | 1004.7073 | 269.4052 | 267.1589 | 374.795 | 1259.7073 | 374.795 | 269.4052 | 267.1589
1260.7073 | 1005.7073 | 269.5112 | 267.2122 | 374.7926 | 1260.7073 | 374.7926 | 269.5112 | 267.2122
1261.7073 | 1006.7073 | 269.6004 | 267.2534 | 374.8065 | 1261.7073 | 374.8065 | 269.6004 | 267.2534
1262.7073 | 1007.7073 | 269.721 | 267.2994 | 374.7599 | 1262.7073 | 374.7599 | 269.721 | 267.2994
1263.7073 | 1008.7073 | 269.8428 | 267.3402 | 374.7857 | 1263.7073 | 374.7857 | 269.8428 | 267.3402
1264.7073 | 1009.7073 | 269.941 | 267.3902 | 374.8247 | 1264.7073 | 374.8247 | 269.941 | 267.3902
1265.7073 | 1010.7073 | 270.0613 | 267.4248 | 374.8266 | 1265.7073 | 374.8266 | 270.0613 | 267.4248
1266.7073 | 1011.7073 | 270.169 | 267.4734 | 374.9125 | 1266.7073 | 374.9125 | 270.169 | 267.4734
1267.7073 | 1012.7073 | 270.2863 | 267.5171 | 374.8963 | 1267.7073 | 374.8963 | 270.2863 | 267.5171
1268.7073 | 1013.7073 | 270.3966 | 267.5516 | 374.8451 | 1268.7073 | 374.8451 | 270.3966 | 267.5516
1269.7073 | 1014.7073 | 270.495 | 267.5971 | 374.7244 | 1269.7073 | 374.7244 | 270.495 | 267.5971
1270.7073 | 1015.7073 | 270.6045 | 267.638 | 374.7295 | 1270.7073 | 374.7295 | 270.6045 | 267.638
1271.7073 | 1016.7073 | 270.71 | 267.6825 | 374.7143 | 1271.7073 | 374.7143 | 270.71 | 267.6825
1272.7073 | 1017.7073 | 270.8005 | 267.7275 | 374.7357 | 1272.7073 | 374.7357 | 270.8005 | 267.7275
1273.7073 | 1018.7073 | 270.9211 | 267.7721 | 374.7906 | 1273.7073 | 374.7906 | 270.9211 | 267.7721
1274.7073 | 1019.7073 | 271.0187 | 267.8147 | 374.9172 | 1274.7073 | 374.9172 | 271.0187 | 267.8147
1275.7073 | 1020.7073 | 271.1459 | 267.8664 | 375.0023 | 1275.7073 | 375.0023 | 271.1459 | 267.8664
1276.7073 | 1021.7073 | 271.2476 | 267.9056 | 375.0642 | 1276.7073 | 375.0642 | 271.2476 | 267.9056
1277.7073 | 1022.7073 | 271.3673 | 267.961 | 375.2068 | 1277.7073 | 375.2068 | 271.3673 | 267.961
1278.7073 | 1023.7073 | 271.4756 | 268.0006 | 375.3187 | 1278.7073 | 375.3187 | 271.4756 | 268.0006
1279.7073 | 1024.7073 | 271.5756 | 268.0502 | 375.4206 | 1279.7073 | 375.4206 | 271.5756 | 268.0502
1280.7073 | 1025.7073 | 271.675 | 268.0967 | 375.5416 | 1280.7073 | 375.5416 | 271.675 | 268.0967
1281.7073 | 1026.7073 | 271.7992 | 268.1338 | 375.6979 | 1281.7073 | 375.6979 | 271.7992 | 268.1338
1282.7073 | 1027.7073 | 271.8968 | 268.1768 | 375.691 | 1282.7073 | 375.691 | 271.8968 | 268.1768
1283.7073 | 1028.7073 | 272.0059 | 268.2207 | 375.7344 | 1283.7073 | 375.7344 | 272.0059 | 268.2207
1284.7073 | 1029.7073 | 272.1104 | 268.2625 | 375.7381 | 1284.7073 | 375.7381 | 272.1104 | 268.2625
1285.7073 | 1030.7073 | 272.2099 | 268.3013 | 375.7778 | 1285.7073 | 375.7778 | 272.2099 | 268.3013
1286.7073 | 1031.7073 | 272.3274 | 268.3503 | 375.8159 | 1286.7073 | 375.8159 | 272.3274 | 268.3503
1287.7073 | 1032.7073 | 272.437 | 268.3905 | 375.8177 | 1287.7073 | 375.8177 | 272.437 | 268.3905
1288.7073 | 1033.7073 | 272.5465 | 268.4332 | 375.736 | 1288.7073 | 375.736 | 272.5465 | 268.4332
1289.7073 | 1034.7073 | 272.6621 | 268.4699 | 375.5677 | 1289.7073 | 375.5677 | 272.6621 | 268.4699
1290.7073 | 1035.7073 | 272.7646 | 268.5213 | 375.3706 | 1290.7073 | 375.3706 | 272.7646 | 268.5213
1291.7073 | 1036.7073 | 272.8728 | 268.5637 | 375.3262 | 1291.7073 | 375.3262 | 272.8728 | 268.5637
1292.7073 | 1037.7073 | 272.9982 | 268.6171 | 375.3352 | 1292.7073 | 375.3352 | 272.9982 | 268.6171
1293.7073 | 1038.7073 | 273.0836 | 268.6718 | 375.2653 | 1293.7073 | 375.2653 | 273.0836 | 268.6718
1294.7073 | 1039.7073 | 273.206 | 268.7327 | 375.2138 | 1294.7073 | 375.2138 | 273.206 | 268.7327
1295.7073 | 1040.7073 | 273.3093 | 268.7923 | 375.2285 | 1295.7073 | 375.2285 | 273.3093 | 268.7923
1296.7073 | 1041.7073 | 273.4 | 268.8296 | 375.1188 | 1296.7073 | 375.1188 | 273.4 | 268.8296
1297.7073 | 1042.7073 | 273.488 | 268.8926 | 375.1361 | 1297.7073 | 375.1361 | 273.488 | 268.8926
1298.7073 | 1043.7073 | 273.6168 | 268.9733 | 375.2054 | 1298.7073 | 375.2054 | 273.6168 | 268.9733
1299.7073 | 1044.7073 | 273.7596 | 269.0573 | 375.2559 | 1299.7073 | 375.2559 | 273.7596 | 269.0573
1300.7073 | 1045.7073 | 273.8778 | 269.1218 | 375.1207 | 1300.7073 | 375.1207 | 273.8778 | 269.1218
1301.7073 | 1046.7073 | 274.0046 | 269.1813 | 375.1433 | 1301.7073 | 375.1433 | 274.0046 | 269.1813
1302.7854 | 1047.7854 | 274.1295 | 269.2651 | 375.1546 | 1302.7854 | 375.1546 | 274.1295 | 269.2651
1303.7698 | 1048.7698 | 274.2477 | 269.3288 | 375.052 | 1303.7698 | 375.052 | 274.2477 | 269.3288
1304.7073 | 1049.7073 | 274.3762 | 269.389 | 375.0634 | 1304.7073 | 375.0634 | 274.3762 | 269.389
1305.7073 | 1050.7073 | 274.4915 | 269.4652 | 375.1518 | 1305.7073 | 375.1518 | 274.4915 | 269.4652
1306.7073 | 1051.7073 | 274.5897 | 269.5301 | 375.163 | 1306.7073 | 375.163 | 274.5897 | 269.5301
1307.7073 | 1052.7073 | 274.7062 | 269.6079 | 375.2914 | 1307.7073 | 375.2914 | 274.7062 | 269.6079
1308.7073 | 1053.7073 | 274.8027 | 269.6787 | 375.3835 | 1308.7073 | 375.3835 | 274.8027 | 269.6787
1309.7073 | 1054.7073 | 274.9282 | 269.7449 | 375.5251 | 1309.7073 | 375.5251 | 274.9282 | 269.7449
1310.7073 | 1055.7073 | 275.033 | 269.8186 | 375.6317 | 1310.7073 | 375.6317 | 275.033 | 269.8186
1311.7073 | 1056.7073 | 275.128 | 269.8884 | 375.7007 | 1311.7073 | 375.7007 | 275.128 | 269.8884
1312.7073 | 1057.7073 | 275.2533 | 269.9678 | 375.7384 | 1312.7073 | 375.7384 | 275.2533 | 269.9678
1313.7073 | 1058.7073 | 275.3409 | 270.0353 | 375.7037 | 1313.7073 | 375.7037 | 275.3409 | 270.0353
1314.7073 | 1059.7073 | 275.4562 | 270.1025 | 375.7182 | 1314.7073 | 375.7182 | 275.4562 | 270.1025
1315.7542 | 1060.7542 | 275.5522 | 270.1768 | 375.8259 | 1315.7542 | 375.8259 | 275.5522 | 270.1768
1316.8323 | 1061.8323 | 275.6688 | 270.2479 | 375.8488 | 1316.8323 | 375.8488 | 275.6688 | 270.2479
1317.801 | 1062.801 | 275.7671 | 270.3148 | 375.9034 | 1317.801 | 375.9034 | 275.7671 | 270.3148
1318.7073 | 1063.7073 | 275.861 | 270.3782 | 375.8707 | 1318.7073 | 375.8707 | 275.861 | 270.3782
1319.7229 | 1064.7229 | 275.9691 | 270.4433 | 375.9288 | 1319.7229 | 375.9288 | 275.9691 | 270.4433
1320.7073 | 1065.7073 | 276.0668 | 270.518 | 375.9258 | 1320.7073 | 375.9258 | 276.0668 | 270.518
1321.7073 | 1066.7073 | 276.1738 | 270.5873 | 375.8973 | 1321.7073 | 375.8973 | 276.1738 | 270.5873
1322.7073 | 1067.7073 | 276.2614 | 270.6531 | 375.982 | 1322.7073 | 375.982 | 276.2614 | 270.6531
1323.7073 | 1068.7073 | 276.3756 | 270.719 | 376.1189 | 1323.7073 | 376.1189 | 276.3756 | 270.719
1324.7073 | 1069.7073 | 276.4715 | 270.7853 | 376.0722 | 1324.7073 | 376.0722 | 276.4715 | 270.7853
1325.7073 | 1070.7073 | 276.5744 | 270.8564 | 376.0283 | 1325.7073 | 376.0283 | 276.5744 | 270.8564
1326.7073 | 1071.7073 | 276.6705 | 270.9166 | 375.9686 | 1326.7073 | 375.9686 | 276.6705 | 270.9166
1327.7073 | 1072.7073 | 276.7585 | 270.9774 | 375.8774 | 1327.7073 | 375.8774 | 276.7585 | 270.9774
1328.7073 | 1073.7073 | 276.8693 | 271.041 | 375.6948 | 1328.7073 | 375.6948 | 276.8693 | 271.041
1329.7073 | 1074.7073 | 276.9549 | 271.1059 | 375.5897 | 1329.7073 | 375.5897 | 276.9549 | 271.1059
1330.7073 | 1075.7073 | 277.0667 | 271.1664 | 375.4997 | 1330.7073 | 375.4997 | 277.0667 | 271.1664
1331.7073 | 1076.7073 | 277.1607 | 271.2295 | 375.4641 | 1331.7073 | 375.4641 | 277.1607 | 271.2295
1332.7073 | 1077.7073 | 277.2619 | 271.2949 | 375.3872 | 1332.7073 | 375.3872 | 277.2619 | 271.2949
1333.7073 | 1078.7073 | 277.365 | 271.3574 | 375.3911 | 1333.7073 | 375.3911 | 277.365 | 271.3574
1334.7073 | 1079.7073 | 277.4599 | 271.4181 | 375.434 | 1334.7073 | 375.434 | 277.4599 | 271.4181
1335.7073 | 1080.7073 | 277.5553 | 271.4822 | 375.4255 | 1335.7073 | 375.4255 | 277.5553 | 271.4822
1336.7073 | 1081.7073 | 277.6292 | 271.5549 | 375.4714 | 1336.7073 | 375.4714 | 277.6292 | 271.5549
1337.7073 | 1082.7073 | 277.762 | 271.6196 | 375.4865 | 1337.7073 | 375.4865 | 277.762 | 271.6196
1338.7073 | 1083.7073 | 277.8507 | 271.6844 | 375.4389 | 1338.7073 | 375.4389 | 277.8507 | 271.6844
1339.7073 | 1084.7073 | 277.9468 | 271.7477 | 375.4833 | 1339.7073 | 375.4833 | 277.9468 | 271.7477
1340.7073 | 1085.7073 | 278.0473 | 271.8136 | 375.4897 | 1340.7073 | 375.4897 | 278.0473 | 271.8136
1341.7073 | 1086.7073 | 278.1445 | 271.8809 | 375.3942 | 1341.7073 | 375.3942 | 278.1445 | 271.8809
1342.7073 | 1087.7073 | 278.2364 | 271.9381 | 375.3655 | 1342.7073 | 375.3655 | 278.2364 | 271.9381
1343.7073 | 1088.7073 | 278.3489 | 272.0116 | 375.4033 | 1343.7073 | 375.4033 | 278.3489 | 272.0116
1344.7073 | 1089.7073 | 278.451 | 272.0722 | 375.342 | 1344.7073 | 375.342 | 278.451 | 272.0722
1345.7073 | 1090.7073 | 278.5455 | 272.1454 | 375.3053 | 1345.7073 | 375.3053 | 278.5455 | 272.1454
1346.7073 | 1091.7073 | 278.6701 | 272.204 | 375.3229 | 1346.7073 | 375.3229 | 278.6701 | 272.204
1347.7073 | 1092.7073 | 278.7675 | 272.2778 | 375.3798 | 1347.7073 | 375.3798 | 278.7675 | 272.2778
1348.7073 | 1093.7073 | 278.8729 | 272.3433 | 375.3051 | 1348.7073 | 375.3051 | 278.8729 | 272.3433
1349.7073 | 1094.7073 | 278.9573 | 272.4039 | 375.3736 | 1349.7073 | 375.3736 | 278.9573 | 272.4039
1350.7073 | 1095.7073 | 279.0554 | 272.4711 | 375.4899 | 1350.7073 | 375.4899 | 279.0554 | 272.4711
1351.7073 | 1096.7073 | 279.1641 | 272.5423 | 375.444 | 1351.7073 | 375.444 | 279.1641 | 272.5423
1352.7073 | 1097.7073 | 279.26 | 272.6106 | 375.4176 | 1352.7073 | 375.4176 | 279.26 | 272.6106
1353.7073 | 1098.7073 | 279.362 | 272.6852 | 375.4167 | 1353.7073 | 375.4167 | 279.362 | 272.6852
1354.7073 | 1099.7073 | 279.4646 | 272.7542 | 375.4072 | 1354.7073 | 375.4072 | 279.4646 | 272.7542
1355.7073 | 1100.7073 | 279.5678 | 272.8164 | 375.3513 | 1355.7073 | 375.3513 | 279.5678 | 272.8164
1356.7073 | 1101.7073 | 279.6705 | 272.8926 | 375.2199 | 1356.7073 | 375.2199 | 279.6705 | 272.8926
1357.7073 | 1102.7073 | 279.7683 | 272.9718 | 375.2758 | 1357.7073 | 375.2758 | 279.7683 | 272.9718
1358.7073 | 1103.7073 | 279.8855 | 273.0352 | 375.2945 | 1358.7073 | 375.2945 | 279.8855 | 273.0352
1359.7073 | 1104.7073 | 279.9688 | 273.1051 | 375.282 | 1359.7073 | 375.282 | 279.9688 | 273.1051
1360.7073 | 1105.7073 | 280.0731 | 273.1778 | 375.2729 | 1360.7073 | 375.2729 | 280.0731 | 273.1778
1361.7073 | 1106.7073 | 280.1744 | 273.2527 | 375.2263 | 1361.7073 | 375.2263 | 280.1744 | 273.2527
1362.7073 | 1107.7073 | 280.2816 | 273.3303 | 375.2318 | 1362.7073 | 375.2318 | 280.2816 | 273.3303
1363.7073 | 1108.7073 | 280.3844 | 273.4075 | 375.186 | 1363.7073 | 375.186 | 280.3844 | 273.4075
1364.7073 | 1109.7073 | 280.499 | 273.4858 | 375.0697 | 1364.7073 | 375.0697 | 280.499 | 273.4858
1365.7073 | 1110.7073 | 280.5983 | 273.5518 | 375.1944 | 1365.7073 | 375.1944 | 280.5983 | 273.5518
1366.7073 | 1111.7073 | 280.6983 | 273.6216 | 375.3032 | 1366.7073 | 375.3032 | 280.6983 | 273.6216
1367.7073 | 1112.7073 | 280.8055 | 273.7203 | 375.4104 | 1367.7073 | 375.4104 | 280.8055 | 273.7203
1368.7073 | 1113.7073 | 280.8974 | 273.796 | 375.3115 | 1368.7073 | 375.3115 | 280.8974 | 273.796
1369.7073 | 1114.7073 | 281.0089 | 273.8557 | 375.1404 | 1369.7073 | 375.1404 | 281.0089 | 273.8557
1370.7073 | 1115.7073 | 281.1139 | 273.9492 | 375.2062 | 1370.7073 | 375.2062 | 281.1139 | 273.9492
1371.7073 | 1116.7073 | 281.224 | 274.0181 | 375.2594 | 1371.7073 | 375.2594 | 281.224 | 274.0181
1372.7073 | 1117.7073 | 281.313 | 274.0899 | 375.2754 | 1372.7073 | 375.2754 | 281.313 | 274.0899
1373.7073 | 1118.7073 | 281.4249 | 274.1752 | 375.2258 | 1373.7073 | 375.2258 | 281.4249 | 274.1752
1374.7073 | 1119.7073 | 281.5266 | 274.253 | 375.314 | 1374.7073 | 375.314 | 281.5266 | 274.253
1375.7073 | 1120.7073 | 281.6244 | 274.3305 | 375.2424 | 1375.7073 | 375.2424 | 281.6244 | 274.3305
1376.7073 | 1121.7073 | 281.7144 | 274.4084 | 375.1542 | 1376.7073 | 375.1542 | 281.7144 | 274.4084
1377.7073 | 1122.7073 | 281.8378 | 274.489 | 375.0439 | 1377.7073 | 375.0439 | 281.8378 | 274.489
1378.7073 | 1123.7073 | 281.9423 | 274.5722 | 375.0974 | 1378.7073 | 375.0974 | 281.9423 | 274.5722
1379.7073 | 1124.7073 | 282.0485 | 274.6558 | 375.1092 | 1379.7073 | 375.1092 | 282.0485 | 274.6558
1380.7073 | 1125.7073 | 282.1434 | 274.7354 | 375.1275 | 1380.7073 | 375.1275 | 282.1434 | 274.7354
1381.7073 | 1126.7073 | 282.2587 | 274.8143 | 375.1575 | 1381.7073 | 375.1575 | 282.2587 | 274.8143
1382.7073 | 1127.7073 | 282.3569 | 274.8936 | 375.1501 | 1382.7073 | 375.1501 | 282.3569 | 274.8936
1383.7073 | 1128.7073 | 282.4455 | 274.9778 | 375.0573 | 1383.7073 | 375.0573 | 282.4455 | 274.9778
1384.7073 | 1129.7073 | 282.5591 | 275.0607 | 374.9572 | 1384.7073 | 374.9572 | 282.5591 | 275.0607
1385.7073 | 1130.7073 | 282.6584 | 275.1445 | 374.9314 | 1385.7073 | 374.9314 | 282.6584 | 275.1445
1386.7073 | 1131.7073 | 282.7702 | 275.2262 | 375.0154 | 1386.7073 | 375.0154 | 282.7702 | 275.2262
1387.7073 | 1132.7073 | 282.8947 | 275.3135 | 375.1144 | 1387.7073 | 375.1144 | 282.8947 | 275.3135
1388.7073 | 1133.7073 | 282.9421 | 275.397 | 375.1342 | 1388.7073 | 375.1342 | 282.9421 | 275.397
1389.7073 | 1134.7073 | 283.066 | 275.48 | 375.1046 | 1389.7073 | 375.1046 | 283.066 | 275.48
1390.7073 | 1135.7073 | 283.1492 | 275.5567 | 375.0263 | 1390.7073 | 375.0263 | 283.1492 | 275.5567
1391.7073 | 1136.7073 | 283.2461 | 275.6553 | 375.0119 | 1391.7073 | 375.0119 | 283.2461 | 275.6553
1392.7073 | 1137.7073 | 283.3425 | 275.7399 | 374.9602 | 1392.7073 | 374.9602 | 283.3425 | 275.7399
1393.7073 | 1138.7073 | 283.4515 | 275.8233 | 374.9816 | 1393.7073 | 374.9816 | 283.4515 | 275.8233
1394.7073 | 1139.7073 | 283.5487 | 275.9099 | 375.1241 | 1394.7073 | 375.1241 | 283.5487 | 275.9099
1395.7073 | 1140.7073 | 283.6602 | 275.996 | 375.1373 | 1395.7073 | 375.1373 | 283.6602 | 275.996
1396.801 | 1141.801 | 283.7732 | 276.0916 | 375.0507 | 1396.801 | 375.0507 | 283.7732 | 276.0916
1397.7073 | 1142.7073 | 283.8635 | 276.1741 | 375.0435 | 1397.7073 | 375.0435 | 283.8635 | 276.1741
1398.7073 | 1143.7073 | 284.0106 | 276.2563 | 374.9983 | 1398.7073 | 374.9983 | 284.0106 | 276.2563
1399.7698 | 1144.7698 | 284.1277 | 276.3465 | 375.0452 | 1399.7698 | 375.0452 | 284.1277 | 276.3465
1400.7854 | 1145.7854 | 284.2301 | 276.4323 | 375.0139 | 1400.7854 | 375.0139 | 284.2301 | 276.4323
1401.7542 | 1146.7542 | 284.3206 | 276.5177 | 374.889 | 1401.7542 | 374.889 | 284.3206 | 276.5177
1402.7073 | 1147.7073 | 284.4091 | 276.6117 | 374.7426 | 1402.7073 | 374.7426 | 284.4091 | 276.6117
1403.7073 | 1148.7073 | 284.4993 | 276.6937 | 374.6111 | 1403.7073 | 374.6111 | 284.4993 | 276.6937
1404.7073 | 1149.7073 | 284.5944 | 276.7868 | 374.5595 | 1404.7073 | 374.5595 | 284.5944 | 276.7868
1405.7698 | 1150.7698 | 284.6754 | 276.8811 | 374.6526 | 1405.7698 | 374.6526 | 284.6754 | 276.8811
1406.7073 | 1151.7073 | 284.7869 | 276.9616 | 374.5033 | 1406.7073 | 374.5033 | 284.7869 | 276.9616
1407.7073 | 1152.7073 | 284.8728 | 277.0462 | 374.422 | 1407.7073 | 374.422 | 284.8728 | 277.0462
1408.7073 | 1153.7073 | 284.9769 | 277.1487 | 374.5511 | 1408.7073 | 374.5511 | 284.9769 | 277.1487
1409.7073 | 1154.7073 | 285.0566 | 277.2261 | 374.5745 | 1409.7073 | 374.5745 | 285.0566 | 277.2261
1410.7073 | 1155.7073 | 285.1302 | 277.3262 | 374.6303 | 1410.7073 | 374.6303 | 285.1302 | 277.3262
1411.7073 | 1156.7073 | 285.2176 | 277.4113 | 374.7208 | 1411.7073 | 374.7208 | 285.2176 | 277.4113
1412.7073 | 1157.7073 | 285.3025 | 277.5031 | 374.7622 | 1412.7073 | 374.7622 | 285.3025 | 277.5031
1413.7073 | 1158.7073 | 285.3885 | 277.5915 | 374.792 | 1413.7073 | 374.792 | 285.3885 | 277.5915
1414.7073 | 1159.7073 | 285.4697 | 277.6901 | 374.7805 | 1414.7073 | 374.7805 | 285.4697 | 277.6901
1415.7073 | 1160.7073 | 285.5542 | 277.7834 | 374.7702 | 1415.7073 | 374.7702 | 285.5542 | 277.7834
1416.7073 | 1161.7073 | 285.6501 | 277.8695 | 374.7143 | 1416.7073 | 374.7143 | 285.6501 | 277.8695
1417.7073 | 1162.7073 | 285.7309 | 277.9626 | 374.7035 | 1417.7073 | 374.7035 | 285.7309 | 277.9626
1418.7073 | 1163.7073 | 285.8209 | 278.0516 | 374.6646 | 1418.7073 | 374.6646 | 285.8209 | 278.0516
1419.7073 | 1164.7073 | 285.9019 | 278.1482 | 374.6468 | 1419.7073 | 374.6468 | 285.9019 | 278.1482
1420.7073 | 1165.7073 | 286.0238 | 278.2441 | 374.6662 | 1420.7073 | 374.6662 | 286.0238 | 278.2441
1421.7073 | 1166.7073 | 286.1182 | 278.3325 | 374.7839 | 1421.7073 | 374.7839 | 286.1182 | 278.3325
1422.7073 | 1167.7073 | 286.2047 | 278.4288 | 374.7311 | 1422.7073 | 374.7311 | 286.2047 | 278.4288
1423.7073 | 1168.7073 | 286.2738 | 278.5293 | 374.6331 | 1423.7073 | 374.6331 | 286.2738 | 278.5293
1424.7073 | 1169.7073 | 286.3698 | 278.6154 | 374.6307 | 1424.7073 | 374.6307 | 286.3698 | 278.6154
1425.7073 | 1170.7073 | 286.4619 | 278.7177 | 374.7146 | 1425.7073 | 374.7146 | 286.4619 | 278.7177
1426.7073 | 1171.7073 | 286.5535 | 278.8052 | 374.8732 | 1426.7073 | 374.8732 | 286.5535 | 278.8052
1427.7073 | 1172.7073 | 286.6364 | 278.8956 | 374.9546 | 1427.7073 | 374.9546 | 286.6364 | 278.8956
1428.7073 | 1173.7073 | 286.7452 | 278.9901 | 375.0821 | 1428.7073 | 375.0821 | 286.7452 | 278.9901
1429.7073 | 1174.7073 | 286.8525 | 279.0804 | 375.2203 | 1429.7073 | 375.2203 | 286.8525 | 279.0804
1430.7073 | 1175.7073 | 286.9568 | 279.1755 | 375.308 | 1430.7073 | 375.308 | 286.9568 | 279.1755
1431.7073 | 1176.7073 | 287.0365 | 279.2691 | 375.2313 | 1431.7073 | 375.2313 | 287.0365 | 279.2691
1432.7073 | 1177.7073 | 287.1087 | 279.3611 | 375.2354 | 1432.7073 | 375.2354 | 287.1087 | 279.3611
1433.7073 | 1178.7073 | 287.2209 | 279.4554 | 375.2729 | 1433.7073 | 375.2729 | 287.2209 | 279.4554
1434.7073 | 1179.7073 | 287.2974 | 279.5458 | 375.2342 | 1434.7073 | 375.2342 | 287.2974 | 279.5458
1435.7073 | 1180.7073 | 287.3826 | 279.6466 | 375.1314 | 1435.7073 | 375.1314 | 287.3826 | 279.6466
1436.7073 | 1181.7073 | 287.4614 | 279.7356 | 375.2184 | 1436.7073 | 375.2184 | 287.4614 | 279.7356
1437.7073 | 1182.7073 | 287.5633 | 279.8208 | 375.2481 | 1437.7073 | 375.2481 | 287.5633 | 279.8208
1438.7073 | 1183.7073 | 287.6359 | 279.9182 | 375.0804 | 1438.7073 | 375.0804 | 287.6359 | 279.9182
1439.7073 | 1184.7073 | 287.746 | 280.0097 | 374.924 | 1439.7073 | 374.924 | 287.746 | 280.0097
1440.7073 | 1185.7073 | 287.8265 | 280.1019 | 374.8661 | 1440.7073 | 374.8661 | 287.8265 | 280.1019
1441.7073 | 1186.7073 | 287.9148 | 280.2001 | 374.7799 | 1441.7073 | 374.7799 | 287.9148 | 280.2001
1442.7073 | 1187.7073 | 288.0214 | 280.2907 | 374.7458 | 1442.7073 | 374.7458 | 288.0214 | 280.2907
1443.7073 | 1188.7073 | 288.1084 | 280.3831 | 374.7696 | 1443.7073 | 374.7696 | 288.1084 | 280.3831
1444.7073 | 1189.7073 | 288.2084 | 280.4792 | 374.8803 | 1444.7073 | 374.8803 | 288.2084 | 280.4792
1445.7073 | 1190.7073 | 288.2979 | 280.5706 | 375.0506 | 1445.7073 | 375.0506 | 288.2979 | 280.5706
1446.7073 | 1191.7073 | 288.3901 | 280.6628 | 375.1274 | 1446.7073 | 375.1274 | 288.3901 | 280.6628
1447.7073 | 1192.7073 | 288.4859 | 280.7584 | 375.0491 | 1447.7073 | 375.0491 | 288.4859 | 280.7584
1448.7854 | 1193.7854 | 288.589 | 280.8644 | 375.048 | 1448.7854 | 375.048 | 288.589 | 280.8644
1449.8479 | 1194.8479 | 288.6877 | 280.9646 | 375.1618 | 1449.8479 | 375.1618 | 288.6877 | 280.9646
1450.8167 | 1195.8167 | 288.7665 | 281.0461 | 375.1859 | 1450.8167 | 375.1859 | 288.7665 | 281.0461
1451.8323 | 1196.8323 | 288.8738 | 281.1442 | 375.0739 | 1451.8323 | 375.0739 | 288.8738 | 281.1442
1452.7698 | 1197.7698 | 288.9557 | 281.2257 | 374.9894 | 1452.7698 | 374.9894 | 288.9557 | 281.2257
1453.7073 | 1198.7073 | 289.0471 | 281.3192 | 375.0232 | 1453.7073 | 375.0232 | 289.0471 | 281.3192
1454.7073 | 1199.7073 | 289.1351 | 281.4103 | 375.1784 | 1454.7073 | 375.1784 | 289.1351 | 281.4103
1455.7073 | 1200.7073 | 289.2367 | 281.5027 | 375.249 | 1455.7073 | 375.249 | 289.2367 | 281.5027
1456.7073 | 1201.7073 | 289.3377 | 281.5871 | 375.2936 | 1456.7073 | 375.2936 | 289.3377 | 281.5871
1457.7073 | 1202.7073 | 289.4228 | 281.6986 | 375.2728 | 1457.7073 | 375.2728 | 289.4228 | 281.6986
1458.7073 | 1203.7073 | 289.5251 | 281.7824 | 375.2752 | 1458.7073 | 375.2752 | 289.5251 | 281.7824
1459.7073 | 1204.7073 | 289.6094 | 281.8718 | 375.4032 | 1459.7073 | 375.4032 | 289.6094 | 281.8718
1460.7073 | 1205.7073 | 289.6927 | 281.9688 | 375.4455 | 1460.7073 | 375.4455 | 289.6927 | 281.9688
1461.7073 | 1206.7073 | 289.7927 | 282.0607 | 375.4211 | 1461.7073 | 375.4211 | 289.7927 | 282.0607
1462.7073 | 1207.7073 | 289.9001 | 282.1494 | 375.3047 | 1462.7073 | 375.3047 | 289.9001 | 282.1494
1463.7073 | 1208.7073 | 289.9645 | 282.237 | 375.4688 | 1463.7073 | 375.4688 | 289.9645 | 282.237
1464.7073 | 1209.7073 | 290.0524 | 282.3259 | 375.6897 | 1464.7073 | 375.6897 | 290.0524 | 282.3259
1465.7073 | 1210.7073 | 290.1667 | 282.4272 | 375.755 | 1465.7073 | 375.755 | 290.1667 | 282.4272
1466.7073 | 1211.7073 | 290.2488 | 282.5186 | 375.9521 | 1466.7073 | 375.9521 | 290.2488 | 282.5186
1467.7073 | 1212.7073 | 290.3519 | 282.6049 | 376.0589 | 1467.7073 | 376.0589 | 290.3519 | 282.6049
1468.7073 | 1213.7073 | 290.453 | 282.6994 | 376.152 | 1468.7073 | 376.152 | 290.453 | 282.6994
1469.7073 | 1214.7073 | 290.529 | 282.7904 | 376.2261 | 1469.7073 | 376.2261 | 290.529 | 282.7904
1470.7073 | 1215.7073 | 290.6218 | 282.8844 | 376.1003 | 1470.7073 | 376.1003 | 290.6218 | 282.8844
1471.7073 | 1216.7073 | 290.7218 | 282.9705 | 376.1055 | 1471.7073 | 376.1055 | 290.7218 | 282.9705
1472.7073 | 1217.7073 | 290.8031 | 283.0593 | 376.1796 | 1472.7073 | 376.1796 | 290.8031 | 283.0593
1473.7073 | 1218.7073 | 290.8962 | 283.1589 | 376.3838 | 1473.7073 | 376.3838 | 290.8962 | 283.1589
1474.7073 | 1219.7073 | 290.9809 | 283.2491 | 376.4016 | 1474.7073 | 376.4016 | 290.9809 | 283.2491
1475.7073 | 1220.7073 | 291.0759 | 283.337 | 376.4609 | 1475.7073 | 376.4609 | 291.0759 | 283.337
1476.7073 | 1221.7073 | 291.1709 | 283.4272 | 376.3202 | 1476.7073 | 376.3202 | 291.1709 | 283.4272
1477.7073 | 1222.7073 | 291.2473 | 283.5224 | 376.1882 | 1477.7073 | 376.1882 | 291.2473 | 283.5224
1478.7073 | 1223.7073 | 291.3362 | 283.6136 | 375.8901 | 1478.7073 | 375.8901 | 291.3362 | 283.6136
1479.7073 | 1224.7073 | 291.4423 | 283.6973 | 375.8162 | 1479.7073 | 375.8162 | 291.4423 | 283.6973
1480.7073 | 1225.7073 | 291.5266 | 283.7913 | 375.7792 | 1480.7073 | 375.7792 | 291.5266 | 283.7913
1481.7073 | 1226.7073 | 291.6054 | 283.8832 | 375.7452 | 1481.7073 | 375.7452 | 291.6054 | 283.8832
1482.7073 | 1227.7073 | 291.7014 | 283.9735 | 375.7862 | 1482.7073 | 375.7862 | 291.7014 | 283.9735
1483.7073 | 1228.7073 | 291.7945 | 284.0602 | 375.7127 | 1483.7073 | 375.7127 | 291.7945 | 284.0602
1484.7073 | 1229.7073 | 291.879 | 284.1572 | 375.6058 | 1484.7073 | 375.6058 | 291.879 | 284.1572
1485.7073 | 1230.7073 | 291.9642 | 284.2383 | 375.4669 | 1485.7073 | 375.4669 | 291.9642 | 284.2383
1486.7073 | 1231.7073 | 292.0512 | 284.3338 | 375.4138 | 1486.7073 | 375.4138 | 292.0512 | 284.3338
1487.7073 | 1232.7073 | 292.1475 | 284.4287 | 375.5183 | 1487.7073 | 375.5183 | 292.1475 | 284.4287
1488.7073 | 1233.7073 | 292.2312 | 284.5176 | 375.5451 | 1488.7073 | 375.5451 | 292.2312 | 284.5176
1489.7073 | 1234.7073 | 292.325 | 284.6054 | 375.502 | 1489.7073 | 375.502 | 292.325 | 284.6054
1490.7073 | 1235.7073 | 292.4119 | 284.6994 | 375.3856 | 1490.7073 | 375.3856 | 292.4119 | 284.6994
1491.7073 | 1236.7073 | 292.5065 | 284.7895 | 375.3507 | 1491.7073 | 375.3507 | 292.5065 | 284.7895
1492.7073 | 1237.7073 | 292.5919 | 284.8735 | 375.7795 | 1492.7073 | 375.7795 | 292.5919 | 284.8735
1493.7073 | 1238.7073 | 292.6764 | 284.9686 | 377.0837 | 1493.7073 | 377.0837 | 292.6764 | 284.9686
1494.7073 | 1239.7073 | 292.7552 | 285.0553 | 379.2808 | 1494.7073 | 379.2808 | 292.7552 | 285.0553
1495.7073 | 1240.7073 | 292.834 | 285.1496 | 381.9505 | 1495.7073 | 381.9505 | 292.834 | 285.1496
1496.7073 | 1241.7073 | 292.9212 | 285.2458 | 385.0932 | 1496.7073 | 385.0932 | 292.9212 | 285.2458
1497.7073 | 1242.7073 | 293.0227 | 285.3231 | 388.4812 | 1497.7073 | 388.4812 | 293.0227 | 285.3231
1498.7073 | 1243.7073 | 293.0997 | 285.4135 | 391.859 | 1498.7073 | 391.859 | 293.0997 | 285.4135
1499.7073 | 1244.7073 | 293.176 | 285.5059 | 395.242 | 1499.7073 | 395.242 | 293.176 | 285.5059
1500.7073 | 1245.7073 | 293.2784 | 285.5964 | 398.4156 | 1500.7073 | 398.4156 | 293.2784 | 285.5964
1501.7073 | 1246.7073 | 293.3573 | 285.6889 | 401.1453 | 1501.7073 | 401.1453 | 293.3573 | 285.6889
1502.7073 | 1247.7073 | 293.4327 | 285.7552 | 403.5669 | 1502.7073 | 403.5669 | 293.4327 | 285.7552
1503.7073 | 1248.7073 | 293.5332 | 285.8584 | 405.7851 | 1503.7073 | 405.7851 | 293.5332 | 285.8584
1504.7073 | 1249.7073 | 293.6074 | 285.9813 | 407.5732 | 1504.7073 | 407.5732 | 293.6074 | 285.9813
1505.7073 | 1250.7073 | 293.685 | 286.0491 | 408.8771 | 1505.7073 | 408.8771 | 293.685 | 286.0491
1506.7073 | 1251.7073 | 293.7885 | 286.138 | 410.0059 | 1506.7073 | 410.0059 | 293.7885 | 286.138
1507.7073 | 1252.7073 | 293.8754 | 286.2375 | 410.8768 | 1507.7073 | 410.8768 | 293.8754 | 286.2375
1508.7073 | 1253.7073 | 293.9733 | 286.3337 | 411.4412 | 1508.7073 | 411.4412 | 293.9733 | 286.3337
1509.7073 | 1254.7073 | 294.0554 | 286.4358 | 411.7731 | 1509.7073 | 411.7731 | 294.0554 | 286.4358
1510.7073 | 1255.7073 | 294.1489 | 286.5263 | 411.9341 | 1510.7073 | 411.9341 | 294.1489 | 286.5263
1511.7073 | 1256.7073 | 294.241 | 286.6257 | 411.9834 | 1511.7073 | 411.9834 | 294.241 | 286.6257
1512.7073 | 1257.7073 | 294.3438 | 286.7345 | 411.9277 | 1512.7073 | 411.9277 | 294.3438 | 286.7345
1513.7073 | 1258.7073 | 294.4471 | 286.8378 | 411.9722 | 1513.7073 | 411.9722 | 294.4471 | 286.8378
1514.7073 | 1259.7073 | 294.5454 | 286.9552 | 411.7203 | 1514.7073 | 411.7203 | 294.5454 | 286.9552
1515.7073 | 1260.7073 | 294.6635 | 287.0639 | 411.3497 | 1515.7073 | 411.3497 | 294.6635 | 287.0639
1516.7073 | 1261.7073 | 294.7675 | 287.1815 | 411.0557 | 1516.7073 | 411.0557 | 294.7675 | 287.1815
1517.7073 | 1262.7073 | 294.8728 | 287.2966 | 410.6656 | 1517.7073 | 410.6656 | 294.8728 | 287.2966
1518.7073 | 1263.7073 | 294.981 | 287.4106 | 410.0902 | 1518.7073 | 410.0902 | 294.981 | 287.4106
1519.7073 | 1264.7073 | 295.1047 | 287.5344 | 409.5873 | 1519.7073 | 409.5873 | 295.1047 | 287.5344
1520.7073 | 1265.7073 | 295.2189 | 287.6603 | 408.9104 | 1520.7073 | 408.9104 | 295.2189 | 287.6603
1521.7073 | 1266.7073 | 295.3303 | 287.7851 | 408.2339 | 1521.7073 | 408.2339 | 295.3303 | 287.7851
1522.7073 | 1267.7073 | 295.4598 | 287.9087 | 407.6926 | 1522.7073 | 407.6926 | 295.4598 | 287.9087
1523.7073 | 1268.7073 | 295.5758 | 288.0459 | 407.1434 | 1523.7073 | 407.1434 | 295.5758 | 288.0459
1524.7073 | 1269.7073 | 295.7123 | 288.1829 | 406.5724 | 1524.7073 | 406.5724 | 295.7123 | 288.1829
1525.7073 | 1270.7073 | 295.8247 | 288.3124 | 406.0451 | 1525.7073 | 406.0451 | 295.8247 | 288.3124
1526.7073 | 1271.7073 | 295.9705 | 288.4501 | 405.4548 | 1526.7073 | 405.4548 | 295.9705 | 288.4501
1527.7073 | 1272.7073 | 296.0957 | 288.5809 | 404.8545 | 1527.7073 | 404.8545 | 296.0957 | 288.5809
1528.7073 | 1273.7073 | 296.2221 | 288.7277 | 404.2971 | 1528.7073 | 404.2971 | 296.2221 | 288.7277
1529.7073 | 1274.7073 | 296.3586 | 288.8653 | 403.9395 | 1529.7073 | 403.9395 | 296.3586 | 288.8653
1530.7073 | 1275.7073 | 296.4965 | 289.0147 | 403.6032 | 1530.7073 | 403.6032 | 296.4965 | 289.0147
1531.7073 | 1276.7073 | 296.632 | 289.1499 | 403.1981 | 1531.7073 | 403.1981 | 296.632 | 289.1499
1532.7073 | 1277.7073 | 296.7658 | 289.2962 | 402.6788 | 1532.7073 | 402.6788 | 296.7658 | 289.2962
1533.7073 | 1278.7073 | 296.8825 | 289.4396 | 402.1575 | 1533.7073 | 402.1575 | 296.8825 | 289.4396
1534.7073 | 1279.7073 | 297.0368 | 289.5868 | 401.7341 | 1534.7073 | 401.7341 | 297.0368 | 289.5868
1535.7073 | 1280.7073 | 297.1844 | 289.735 | 401.3303 | 1535.7073 | 401.3303 | 297.1844 | 289.735
1536.7073 | 1281.7073 | 297.3329 | 289.8816 | 400.7468 | 1536.7073 | 400.7468 | 297.3329 | 289.8816
1537.7073 | 1282.7073 | 297.475 | 290.0296 | 400.2428 | 1537.7073 | 400.2428 | 297.475 | 290.0296
1538.7073 | 1283.7073 | 297.6248 | 290.186 | 399.7931 | 1538.7073 | 399.7931 | 297.6248 | 290.186
1539.7073 | 1284.7073 | 297.7574 | 290.3333 | 399.4241 | 1539.7073 | 399.4241 | 297.7574 | 290.3333
1540.7073 | 1285.7073 | 297.898 | 290.4791 | 399.0556 | 1540.7073 | 399.0556 | 297.898 | 290.4791
1541.7073 | 1286.7073 | 298.0528 | 290.6315 | 398.4997 | 1541.7073 | 398.4997 | 298.0528 | 290.6315
1542.7073 | 1287.7073 | 298.1706 | 290.787 | 398.1294 | 1542.7073 | 398.1294 | 298.1706 | 290.787
1543.7073 | 1288.7073 | 298.331 | 290.9295 | 397.7866 | 1543.7073 | 397.7866 | 298.331 | 290.9295
1544.7073 | 1289.7073 | 298.484 | 291.083 | 397.5611 | 1544.7073 | 397.5611 | 298.484 | 291.083
1545.7073 | 1290.7073 | 298.597 | 291.2387 | 397.3836 | 1545.7073 | 397.3836 | 298.597 | 291.2387
1546.7073 | 1291.7073 | 298.7434 | 291.3912 | 397.2819 | 1546.7073 | 397.2819 | 298.7434 | 291.3912
1547.7073 | 1292.7073 | 298.8925 | 291.5444 | 397.1173 | 1547.7073 | 397.1173 | 298.8925 | 291.5444
1548.7073 | 1293.7073 | 299.0335 | 291.694 | 397.0655 | 1548.7073 | 397.0655 | 299.0335 | 291.694
1549.7073 | 1294.7073 | 299.1785 | 291.8443 | 397.0385 | 1549.7073 | 397.0385 | 299.1785 | 291.8443
1550.7073 | 1295.7073 | 299.3315 | 291.9967 | 397.0712 | 1550.7073 | 397.0712 | 299.3315 | 291.9967
1551.7073 | 1296.7073 | 299.4633 | 292.1493 | 397.0489 | 1551.7073 | 397.0489 | 299.4633 | 292.1493
1552.7073 | 1297.7073 | 299.6215 | 292.2992 | 397.1038 | 1552.7073 | 397.1038 | 299.6215 | 292.2992
1553.7073 | 1298.7073 | 299.7547 | 292.459 | 397.1197 | 1553.7073 | 397.1197 | 299.7547 | 292.459
1554.7073 | 1299.7073 | 299.8951 | 292.6057 | 397.1778 | 1554.7073 | 397.1778 | 299.8951 | 292.6057
1555.7073 | 1300.7073 | 300.0319 | 292.7553 | 397.2507 | 1555.7073 | 397.2507 | 300.0319 | 292.7553
1556.7073 | 1301.7073 | 300.1797 | 292.8993 | 397.3059 | 1556.7073 | 397.3059 | 300.1797 | 292.8993
1557.7073 | 1302.7073 | 300.3011 | 293.0493 | 397.3041 | 1557.7073 | 397.3041 | 300.3011 | 293.0493
1558.7073 | 1303.7073 | 300.4349 | 293.1961 | 397.3659 | 1558.7073 | 397.3659 | 300.4349 | 293.1961
1559.7073 | 1304.7073 | 300.591 | 293.3467 | 397.5605 | 1559.7073 | 397.5605 | 300.591 | 293.3467
1560.7073 | 1305.7073 | 300.7034 | 293.4937 | 397.7226 | 1560.7073 | 397.7226 | 300.7034 | 293.4937
1561.7073 | 1306.7073 | 300.8492 | 293.6437 | 397.8291 | 1561.7073 | 397.8291 | 300.8492 | 293.6437
1562.7073 | 1307.7073 | 300.9789 | 293.7896 | 397.9346 | 1562.7073 | 397.9346 | 300.9789 | 293.7896
1563.7073 | 1308.7073 | 301.123 | 293.9359 | 398.1489 | 1563.7073 | 398.1489 | 301.123 | 293.9359
1564.7073 | 1309.7073 | 301.2312 | 294.0889 | 398.4077 | 1564.7073 | 398.4077 | 301.2312 | 294.0889
1565.7073 | 1310.7073 | 301.3707 | 294.2354 | 398.523 | 1565.7073 | 398.523 | 301.3707 | 294.2354
1566.7073 | 1311.7073 | 301.514 | 294.3755 | 398.7586 | 1566.7073 | 398.7586 | 301.514 | 294.3755
1567.7073 | 1312.7073 | 301.6385 | 294.5199 | 399.0172 | 1567.7073 | 399.0172 | 301.6385 | 294.5199
1568.7073 | 1313.7073 | 301.7588 | 294.6654 | 399.1653 | 1568.7073 | 399.1653 | 301.7588 | 294.6654
1569.7073 | 1314.7073 | 301.895 | 294.8095 | 399.3531 | 1569.7073 | 399.3531 | 301.895 | 294.8095
1570.7073 | 1315.7073 | 302.0316 | 294.9526 | 399.4714 | 1570.7073 | 399.4714 | 302.0316 | 294.9526
1571.7073 | 1316.7073 | 302.1501 | 295.0984 | 399.5354 | 1571.7073 | 399.5354 | 302.1501 | 295.0984
1572.7073 | 1317.7073 | 302.2668 | 295.2405 | 399.5555 | 1572.7073 | 399.5555 | 302.2668 | 295.2405
1573.7073 | 1318.7073 | 302.3987 | 295.3927 | 399.6673 | 1573.7073 | 399.6673 | 302.3987 | 295.3927
1574.7073 | 1319.7073 | 302.5263 | 295.5261 | 399.7166 | 1574.7073 | 399.7166 | 302.5263 | 295.5261
1575.7073 | 1320.7073 | 302.6508 | 295.6617 | 399.7362 | 1575.7073 | 399.7362 | 302.6508 | 295.6617
1576.7073 | 1321.7073 | 302.7791 | 295.8112 | 399.7567 | 1576.7073 | 399.7567 | 302.7791 | 295.8112
1577.7073 | 1322.7073 | 302.9041 | 295.9502 | 399.8423 | 1577.7073 | 399.8423 | 302.9041 | 295.9502
1578.7073 | 1323.7073 | 303.0164 | 296.0991 | 399.8713 | 1578.7073 | 399.8713 | 303.0164 | 296.0991
1579.7073 | 1324.7073 | 303.1459 | 296.2323 | 399.9668 | 1579.7073 | 399.9668 | 303.1459 | 296.2323
1580.7073 | 1325.7073 | 303.2415 | 296.3696 | 399.8376 | 1580.7073 | 399.8376 | 303.2415 | 296.3696
1581.7073 | 1326.7073 | 303.3898 | 296.5108 | 399.863 | 1581.7073 | 399.863 | 303.3898 | 296.5108
1582.7073 | 1327.7073 | 303.5125 | 296.6484 | 399.8195 | 1582.7073 | 399.8195 | 303.5125 | 296.6484
1583.7073 | 1328.7073 | 303.6452 | 296.7864 | 399.9217 | 1583.7073 | 399.9217 | 303.6452 | 296.7864
1584.7073 | 1329.7073 | 303.7523 | 296.9202 | 399.9486 | 1584.7073 | 399.9486 | 303.7523 | 296.9202
1585.7073 | 1330.7073 | 303.8658 | 297.0618 | 399.7546 | 1585.7073 | 399.7546 | 303.8658 | 297.0618
1586.7073 | 1331.7073 | 303.9874 | 297.1966 | 399.5565 | 1586.7073 | 399.5565 | 303.9874 | 297.1966
1587.7073 | 1332.7073 | 304.107 | 297.332 | 399.4889 | 1587.7073 | 399.4889 | 304.107 | 297.332
1588.7073 | 1333.7073 | 304.2134 | 297.4712 | 399.5568 | 1588.7073 | 399.5568 | 304.2134 | 297.4712
1589.7073 | 1334.7073 | 304.3183 | 297.6164 | 399.6159 | 1589.7073 | 399.6159 | 304.3183 | 297.6164
1590.7073 | 1335.7073 | 304.447 | 297.747 | 399.4639 | 1590.7073 | 399.4639 | 304.447 | 297.747
1591.7073 | 1336.7073 | 304.5619 | 297.892 | 399.3544 | 1591.7073 | 399.3544 | 304.5619 | 297.892
1592.7073 | 1337.7073 | 304.6796 | 298.0266 | 399.2778 | 1592.7073 | 399.2778 | 304.6796 | 298.0266
1593.7073 | 1338.7073 | 304.7958 | 298.1605 | 399.1277 | 1593.7073 | 399.1277 | 304.7958 | 298.1605
1594.7073 | 1339.7073 | 304.9089 | 298.2931 | 399.2287 | 1594.7073 | 399.2287 | 304.9089 | 298.2931
1595.7073 | 1340.7073 | 305.0052 | 298.4264 | 399.3649 | 1595.7073 | 399.3649 | 305.0052 | 298.4264
1596.7073 | 1341.7073 | 305.155 | 298.5604 | 399.4253 | 1596.7073 | 399.4253 | 305.155 | 298.5604
1597.7073 | 1342.7073 | 305.2464 | 298.6992 | 399.4083 | 1597.7073 | 399.4083 | 305.2464 | 298.6992
1598.7073 | 1343.7073 | 305.3706 | 298.8256 | 399.3702 | 1598.7073 | 399.3702 | 305.3706 | 298.8256
1599.7073 | 1344.7073 | 305.4873 | 298.9592 | 399.3033 | 1599.7073 | 399.3033 | 305.4873 | 298.9592
1600.7073 | 1345.7073 | 305.5978 | 299.0891 | 399.2936 | 1600.7073 | 399.2936 | 305.5978 | 299.0891
1601.7073 | 1346.7073 | 305.7186 | 299.2248 | 399.4026 | 1601.7073 | 399.4026 | 305.7186 | 299.2248
1602.7073 | 1347.7073 | 305.8194 | 299.3583 | 399.325 | 1602.7073 | 399.325 | 305.8194 | 299.3583
1603.7073 | 1348.7073 | 305.9449 | 299.488 | 399.4407 | 1603.7073 | 399.4407 | 305.9449 | 299.488
1604.7073 | 1349.7073 | 306.0568 | 299.627 | 399.5797 | 1604.7073 | 399.5797 | 306.0568 | 299.627
1605.7073 | 1350.7073 | 306.1708 | 299.7509 | 399.6014 | 1605.7073 | 399.6014 | 306.1708 | 299.7509
1606.7073 | 1351.7073 | 306.2966 | 299.8824 | 399.6509 | 1606.7073 | 399.6509 | 306.2966 | 299.8824
1607.7073 | 1352.7073 | 306.404 | 300.0136 | 399.821 | 1607.7073 | 399.821 | 306.404 | 300.0136
1608.7073 | 1353.7073 | 306.5117 | 300.1435 | 399.8778 | 1608.7073 | 399.8778 | 306.5117 | 300.1435
1609.7073 | 1354.7073 | 306.5949 | 300.2743 | 400.0305 | 1609.7073 | 400.0305 | 306.5949 | 300.2743
1610.7073 | 1355.7073 | 306.688 | 300.4091 | 400.1119 | 1610.7073 | 400.1119 | 306.688 | 300.4091
1611.7073 | 1356.7073 | 306.7841 | 300.5386 | 400.1235 | 1611.7073 | 400.1235 | 306.7841 | 300.5386
1612.7073 | 1357.7073 | 306.918 | 300.6682 | 400.1989 | 1612.7073 | 400.1989 | 306.918 | 300.6682
1613.7073 | 1358.7073 | 307.0381 | 300.8091 | 400.2947 | 1613.7073 | 400.2947 | 307.0381 | 300.8091
1614.7073 | 1359.7073 | 307.1539 | 300.9142 | 400.3987 | 1614.7073 | 400.3987 | 307.1539 | 300.9142
1615.7073 | 1360.7073 | 307.2718 | 301.0835 | 400.4883 | 1615.7073 | 400.4883 | 307.2718 | 301.0835
1616.8167 | 1361.8167 | 307.3992 | 301.2156 | 400.5004 | 1616.8167 | 400.5004 | 307.3992 | 301.2156
1617.7073 | 1362.7073 | 307.4959 | 301.3187 | 400.4554 | 1617.7073 | 400.4554 | 307.4959 | 301.3187
1618.9104 | 1363.9104 | 307.6461 | 301.4597 | 400.4434 | 1618.9104 | 400.4434 | 307.6461 | 301.4597
1619.8167 | 1364.8167 | 307.7471 | 301.5894 | 400.4383 | 1619.8167 | 400.4383 | 307.7471 | 301.5894
1620.7229 | 1365.7229 | 307.8461 | 301.6984 | 400.4286 | 1620.7229 | 400.4286 | 307.8461 | 301.6984
1621.7073 | 1366.7073 | 307.9557 | 301.8292 | 400.5113 | 1621.7073 | 400.5113 | 307.9557 | 301.8292
1622.7073 | 1367.7073 | 308.0784 | 301.962 | 400.7039 | 1622.7073 | 400.7039 | 308.0784 | 301.962
1623.7073 | 1368.7073 | 308.183 | 302.0836 | 400.7396 | 1623.7073 | 400.7396 | 308.183 | 302.0836
1624.7073 | 1369.7073 | 308.3002 | 302.2088 | 400.7183 | 1624.7073 | 400.7183 | 308.3002 | 302.2088
1625.7073 | 1370.7073 | 308.3874 | 302.3327 | 400.6066 | 1625.7073 | 400.6066 | 308.3874 | 302.3327
1626.7073 | 1371.7073 | 308.516 | 302.4591 | 400.5855 | 1626.7073 | 400.5855 | 308.516 | 302.4591
1627.7073 | 1372.7073 | 308.6164 | 302.5867 | 400.6367 | 1627.7073 | 400.6367 | 308.6164 | 302.5867
1628.7073 | 1373.7073 | 308.7316 | 302.7159 | 400.5819 | 1628.7073 | 400.5819 | 308.7316 | 302.7159
1629.7073 | 1374.7073 | 308.8338 | 302.8386 | 400.5853 | 1629.7073 | 400.5853 | 308.8338 | 302.8386
1630.7073 | 1375.7073 | 308.9531 | 302.9603 | 400.732 | 1630.7073 | 400.732 | 308.9531 | 302.9603
1631.7073 | 1376.7073 | 309.0622 | 303.0868 | 400.7523 | 1631.7073 | 400.7523 | 309.0622 | 303.0868
1632.7073 | 1377.7073 | 309.1758 | 303.1975 | 400.7174 | 1632.7073 | 400.7174 | 309.1758 | 303.1975
1633.7073 | 1378.7073 | 309.2765 | 303.3252 | 400.6408 | 1633.7073 | 400.6408 | 309.2765 | 303.3252
1634.7073 | 1379.7073 | 309.3853 | 303.4629 | 400.6562 | 1634.7073 | 400.6562 | 309.3853 | 303.4629
1635.7073 | 1380.7073 | 309.4474 | 303.5822 | 400.6731 | 1635.7073 | 400.6731 | 309.4474 | 303.5822
1636.7073 | 1381.7073 | 309.5155 | 303.7078 | 400.7615 | 1636.7073 | 400.7615 | 309.5155 | 303.7078
1637.7073 | 1382.7073 | 309.5723 | 303.8339 | 400.7853 | 1637.7073 | 400.7853 | 309.5723 | 303.8339
1638.7073 | 1383.7073 | 309.6506 | 303.9594 | 400.8697 | 1638.7073 | 400.8697 | 309.6506 | 303.9594
1639.7073 | 1384.7073 | 309.7329 | 304.08 | 400.8976 | 1639.7073 | 400.8976 | 309.7329 | 304.08
1640.7073 | 1385.7073 | 309.7809 | 304.2064 | 401.0553 | 1640.7073 | 401.0553 | 309.7809 | 304.2064
1641.7073 | 1386.7073 | 309.8821 | 304.3287 | 401.0721 | 1641.7073 | 401.0721 | 309.8821 | 304.3287
1642.7073 | 1387.7073 | 310.0054 | 304.4552 | 401.0702 | 1642.7073 | 401.0702 | 310.0054 | 304.4552
1643.7073 | 1388.7073 | 310.0975 | 304.5773 | 401.2101 | 1643.7073 | 401.2101 | 310.0975 | 304.5773
1644.7073 | 1389.7073 | 310.1964 | 304.7011 | 401.3752 | 1644.7073 | 401.3752 | 310.1964 | 304.7011
1645.7073 | 1390.7073 | 310.2892 | 304.8196 | 401.3543 | 1645.7073 | 401.3543 | 310.2892 | 304.8196
1646.7073 | 1391.7073 | 310.3947 | 304.9468 | 401.2957 | 1646.7073 | 401.2957 | 310.3947 | 304.9468
1647.7073 | 1392.7073 | 310.5186 | 305.0652 | 401.271 | 1647.7073 | 401.271 | 310.5186 | 305.0652
1648.7073 | 1393.7073 | 310.6466 | 305.1907 | 401.2893 | 1648.7073 | 401.2893 | 310.6466 | 305.1907
1649.7073 | 1394.7073 | 310.7515 | 305.3102 | 401.2805 | 1649.7073 | 401.2805 | 310.7515 | 305.3102
1650.7073 | 1395.7073 | 310.87 | 305.4307 | 401.2617 | 1650.7073 | 401.2617 | 310.87 | 305.4307
1651.7073 | 1396.7073 | 310.9836 | 305.5651 | 401.224 | 1651.7073 | 401.224 | 310.9836 | 305.5651
1652.7073 | 1397.7073 | 311.1052 | 305.6835 | 401.1612 | 1652.7073 | 401.1612 | 311.1052 | 305.6835
1653.7073 | 1398.7073 | 311.2084 | 305.8041 | 401.0722 | 1653.7073 | 401.0722 | 311.2084 | 305.8041
1654.7073 | 1399.7073 | 311.3442 | 305.9323 | 401.0474 | 1654.7073 | 401.0474 | 311.3442 | 305.9323
1655.7073 | 1400.7073 | 311.4648 | 306.0478 | 401.0196 | 1655.7073 | 401.0196 | 311.4648 | 306.0478
1656.7073 | 1401.7073 | 311.5337 | 306.18 | 400.9307 | 1656.7073 | 400.9307 | 311.5337 | 306.18
1657.7073 | 1402.7073 | 311.6173 | 306.2917 | 400.8212 | 1657.7073 | 400.8212 | 311.6173 | 306.2917
1658.7073 | 1403.7073 | 311.7458 | 306.416 | 400.8651 | 1658.7073 | 400.8651 | 311.7458 | 306.416
1659.7073 | 1404.7073 | 311.8493 | 306.533 | 400.896 | 1659.7073 | 400.896 | 311.8493 | 306.533
1660.7073 | 1405.7073 | 311.9816 | 306.6582 | 400.9483 | 1660.7073 | 400.9483 | 311.9816 | 306.6582
1661.7073 | 1406.7073 | 312.1305 | 306.7792 | 400.9002 | 1661.7073 | 400.9002 | 312.1305 | 306.7792
1662.7073 | 1407.7073 | 312.2386 | 306.9023 | 400.883 | 1662.7073 | 400.883 | 312.2386 | 306.9023
1663.7073 | 1408.7073 | 312.3502 | 307.0408 | 400.9131 | 1663.7073 | 400.9131 | 312.3502 | 307.0408
1664.7073 | 1409.7073 | 312.4496 | 307.1558 | 400.7798 | 1664.7073 | 400.7798 | 312.4496 | 307.1558
1665.7073 | 1410.7073 | 312.5677 | 307.2736 | 400.59 | 1665.7073 | 400.59 | 312.5677 | 307.2736
1666.7073 | 1411.7073 | 312.6759 | 307.3886 | 400.5202 | 1666.7073 | 400.5202 | 312.6759 | 307.3886
1667.7073 | 1412.7073 | 312.7552 | 307.5002 | 400.5269 | 1667.7073 | 400.5269 | 312.7552 | 307.5002
1668.7073 | 1413.7073 | 312.868 | 307.6246 | 400.5459 | 1668.7073 | 400.5459 | 312.868 | 307.6246
1669.7073 | 1414.7073 | 312.9779 | 307.7429 | 400.6663 | 1669.7073 | 400.6663 | 312.9779 | 307.7429
1670.7073 | 1415.7073 | 313.1182 | 307.865 | 400.6473 | 1670.7073 | 400.6473 | 313.1182 | 307.865
1671.7073 | 1416.7073 | 313.222 | 307.9819 | 400.5077 | 1671.7073 | 400.5077 | 313.222 | 307.9819
1672.7073 | 1417.7073 | 313.3235 | 308.086 | 400.3735 | 1672.7073 | 400.3735 | 313.3235 | 308.086
1673.7073 | 1418.7073 | 313.3883 | 308.1927 | 400.2542 | 1673.7073 | 400.2542 | 313.3883 | 308.1927
1674.7073 | 1419.7073 | 313.492 | 308.3266 | 400.0935 | 1674.7073 | 400.0935 | 313.492 | 308.3266
1675.7073 | 1420.7073 | 313.5964 | 308.4431 | 399.9512 | 1675.7073 | 399.9512 | 313.5964 | 308.4431
1676.7073 | 1421.7073 | 313.6863 | 308.5385 | 399.8851 | 1676.7073 | 399.8851 | 313.6863 | 308.5385
1677.7073 | 1422.7073 | 313.8047 | 308.6592 | 399.8637 | 1677.7073 | 399.8637 | 313.8047 | 308.6592
1678.7073 | 1423.7073 | 313.8883 | 308.7823 | 399.8686 | 1678.7073 | 399.8686 | 313.8883 | 308.7823
1679.7073 | 1424.7073 | 313.9784 | 308.8986 | 399.7582 | 1679.7073 | 399.7582 | 313.9784 | 308.8986
1680.7073 | 1425.7073 | 314.121 | 309.0019 | 399.6085 | 1680.7073 | 399.6085 | 314.121 | 309.0019
1681.7542 | 1426.7542 | 314.2615 | 309.1263 | 399.6893 | 1681.7542 | 399.6893 | 314.2615 | 309.1263
1682.7073 | 1427.7073 | 314.3392 | 309.2264 | 399.6965 | 1682.7073 | 399.6965 | 314.3392 | 309.2264
1683.7542 | 1428.7542 | 314.3931 | 309.3499 | 399.6635 | 1683.7542 | 399.6635 | 314.3931 | 309.3499
1684.7698 | 1429.7698 | 314.4055 | 309.4722 | 399.5304 | 1684.7698 | 399.5304 | 314.4055 | 309.4722
1685.7073 | 1430.7073 | 314.512 | 309.5605 | 399.502 | 1685.7073 | 399.502 | 314.512 | 309.5605
1686.7073 | 1431.7073 | 314.6361 | 309.6775 | 399.5395 | 1686.7073 | 399.5395 | 314.6361 | 309.6775
1687.7073 | 1432.7073 | 314.7184 | 309.8064 | 399.4599 | 1687.7073 | 399.4599 | 314.7184 | 309.8064
1688.7073 | 1433.7073 | 314.8056 | 309.9114 | 399.3028 | 1688.7073 | 399.3028 | 314.8056 | 309.9114
1689.7229 | 1434.7229 | 314.8486 | 310.013 | 399.3602 | 1689.7229 | 399.3602 | 314.8486 | 310.013
1690.7073 | 1435.7073 | 314.9375 | 310.1247 | 399.276 | 1690.7073 | 399.276 | 314.9375 | 310.1247
1691.7073 | 1436.7073 | 315.022 | 310.243 | 399.198 | 1691.7073 | 399.198 | 315.022 | 310.243
1692.7229 | 1437.7229 | 315.1297 | 310.3532 | 399.2324 | 1692.7229 | 399.2324 | 315.1297 | 310.3532
1693.7073 | 1438.7073 | 315.1648 | 310.452 | 399.3066 | 1693.7073 | 399.3066 | 315.1648 | 310.452
1694.7073 | 1439.7073 | 315.2759 | 310.5704 | 399.3202 | 1694.7073 | 399.3202 | 315.2759 | 310.5704
1695.7073 | 1440.7073 | 315.3442 | 310.6792 | 399.4773 | 1695.7073 | 399.4773 | 315.3442 | 310.6792
1696.7073 | 1441.7073 | 315.448 | 310.7815 | 399.6264 | 1696.7073 | 399.6264 | 315.448 | 310.7815
1697.7073 | 1442.7073 | 315.5393 | 310.8956 | 399.6777 | 1697.7073 | 399.6777 | 315.5393 | 310.8956
1698.7073 | 1443.7073 | 315.6493 | 311.0032 | 399.8082 | 1698.7073 | 399.8082 | 315.6493 | 311.0032
1699.7073 | 1444.7073 | 315.7196 | 311.1113 | 399.9523 | 1699.7073 | 399.9523 | 315.7196 | 311.1113
1700.7073 | 1445.7073 | 315.8018 | 311.2146 | 400.0039 | 1700.7073 | 400.0039 | 315.8018 | 311.2146
1701.7073 | 1446.7073 | 315.8802 | 311.3179 | 399.9232 | 1701.7073 | 399.9232 | 315.8802 | 311.3179
1702.7073 | 1447.7073 | 315.9951 | 311.4242 | 399.9804 | 1702.7073 | 399.9804 | 315.9951 | 311.4242
1703.7073 | 1448.7073 | 316.0596 | 311.5266 | 400.0851 | 1703.7073 | 400.0851 | 316.0596 | 311.5266
1704.7073 | 1449.7073 | 316.1786 | 311.6479 | 400.1071 | 1704.7073 | 400.1071 | 316.1786 | 311.6479
1705.7073 | 1450.7073 | 316.2707 | 311.7483 | 400.2123 | 1705.7073 | 400.2123 | 316.2707 | 311.7483
1706.7073 | 1451.7073 | 316.3813 | 311.8361 | 400.2799 | 1706.7073 | 400.2799 | 316.3813 | 311.8361
1707.7073 | 1452.7073 | 316.5835 | 311.9475 | 400.3972 | 1707.7073 | 400.3972 | 316.5835 | 311.9475
1708.7073 | 1453.7073 | 316.7234 | 312.058 | 400.4209 | 1708.7073 | 400.4209 | 316.7234 | 312.058
1709.7073 | 1454.7073 | 316.7792 | 312.1538 | 400.4 | 1709.7073 | 400.4 | 316.7792 | 312.1538
1710.7073 | 1455.7073 | 316.7726 | 312.2567 | 400.5903 | 1710.7073 | 400.5903 | 316.7726 | 312.2567
1711.7073 | 1456.7073 | 316.8053 | 312.3659 | 400.814 | 1711.7073 | 400.814 | 316.8053 | 312.3659
1712.7073 | 1457.7073 | 316.9374 | 312.4697 | 400.91 | 1712.7073 | 400.91 | 316.9374 | 312.4697
1713.7073 | 1458.7073 | 317.0202 | 312.5732 | 401.0519 | 1713.7073 | 401.0519 | 317.0202 | 312.5732
1714.7073 | 1459.7073 | 317.1 | 312.6756 | 401.1228 | 1714.7073 | 401.1228 | 317.1 | 312.6756
1715.7073 | 1460.7073 | 317.1994 | 312.7808 | 400.9999 | 1715.7073 | 400.9999 | 317.1994 | 312.7808
1716.7073 | 1461.7073 | 317.3274 | 312.8778 | 400.8973 | 1716.7073 | 400.8973 | 317.3274 | 312.8778
1717.7073 | 1462.7073 | 317.3897 | 312.9833 | 400.8235 | 1717.7073 | 400.8235 | 317.3897 | 312.9833
1718.7073 | 1463.7073 | 317.4673 | 313.0879 | 400.8894 | 1718.7073 | 400.8894 | 317.4673 | 313.0879
1719.7073 | 1464.7073 | 317.5355 | 313.1881 | 401.0536 | 1719.7073 | 401.0536 | 317.5355 | 313.1881
1720.7073 | 1465.7073 | 317.6048 | 313.2899 | 400.9964 | 1720.7073 | 400.9964 | 317.6048 | 313.2899
1721.7073 | 1466.7073 | 317.703 | 313.3916 | 400.8966 | 1721.7073 | 400.8966 | 317.703 | 313.3916
1722.7073 | 1467.7073 | 317.7857 | 313.494 | 400.8191 | 1722.7073 | 400.8191 | 317.7857 | 313.494
1723.7073 | 1468.7073 | 317.8753 | 313.5999 | 400.8062 | 1723.7073 | 400.8062 | 317.8753 | 313.5999
1724.7073 | 1469.7073 | 317.9606 | 313.6948 | 400.8221 | 1724.7073 | 400.8221 | 317.9606 | 313.6948
1725.7073 | 1470.7073 | 318.0584 | 313.7937 | 400.7276 | 1725.7073 | 400.7276 | 318.0584 | 313.7937
1726.7073 | 1471.7073 | 318.1392 | 313.8989 | 400.5882 | 1726.7073 | 400.5882 | 318.1392 | 313.8989
1727.7073 | 1472.7073 | 318.224 | 313.9936 | 400.444 | 1727.7073 | 400.444 | 318.224 | 313.9936
1728.7073 | 1473.7073 | 318.3125 | 314.101 | 400.4997 | 1728.7073 | 400.4997 | 318.3125 | 314.101
1729.7073 | 1474.7073 | 318.3933 | 314.2023 | 400.4046 | 1729.7073 | 400.4046 | 318.3933 | 314.2023
1730.7073 | 1475.7073 | 318.476 | 314.3011 | 400.4391 | 1730.7073 | 400.4391 | 318.476 | 314.3011
1731.7073 | 1476.7073 | 318.5784 | 314.3942 | 400.2851 | 1731.7073 | 400.2851 | 318.5784 | 314.3942
1732.7073 | 1477.7073 | 318.6668 | 314.4947 | 400.1006 | 1732.7073 | 400.1006 | 318.6668 | 314.4947
1733.7073 | 1478.7073 | 318.7347 | 314.5965 | 399.9644 | 1733.7073 | 399.9644 | 318.7347 | 314.5965
1734.7073 | 1479.7073 | 318.829 | 314.6973 | 400.0224 | 1734.7073 | 400.0224 | 318.829 | 314.6973
1735.7073 | 1480.7073 | 318.9123 | 314.8013 | 400.0731 | 1735.7073 | 400.0731 | 318.9123 | 314.8013
1736.7073 | 1481.7073 | 319.0078 | 314.9004 | 400.0158 | 1736.7073 | 400.0158 | 319.0078 | 314.9004
1737.7073 | 1482.7073 | 319.0751 | 314.9976 | 399.9738 | 1737.7073 | 399.9738 | 319.0751 | 314.9976
1738.7073 | 1483.7073 | 319.1505 | 315.0906 | 399.9954 | 1738.7073 | 399.9954 | 319.1505 | 315.0906
1739.7073 | 1484.7073 | 319.2416 | 315.1915 | 399.9359 | 1739.7073 | 399.9359 | 319.2416 | 315.1915
1740.7073 | 1485.7073 | 319.3364 | 315.2925 | 399.7922 | 1740.7073 | 399.7922 | 319.3364 | 315.2925
1741.7073 | 1486.7073 | 319.4176 | 315.3885 | 399.5261 | 1741.7073 | 399.5261 | 319.4176 | 315.3885
1742.7073 | 1487.7073 | 319.5033 | 315.4851 | 399.5564 | 1742.7073 | 399.5564 | 319.5033 | 315.4851
1743.7073 | 1488.7073 | 319.5981 | 315.585 | 399.5829 | 1743.7073 | 399.5829 | 319.5981 | 315.585
1744.7073 | 1489.7073 | 319.6723 | 315.6819 | 399.5077 | 1744.7073 | 399.5077 | 319.6723 | 315.6819
1745.7073 | 1490.7073 | 319.7739 | 315.7809 | 399.334 | 1745.7073 | 399.334 | 319.7739 | 315.7809
1746.7073 | 1491.7073 | 319.87 | 315.875 | 399.1296 | 1746.7073 | 399.1296 | 319.87 | 315.875
1747.7073 | 1492.7073 | 319.97 | 315.9691 | 398.9968 | 1747.7073 | 398.9968 | 319.97 | 315.9691
1748.7073 | 1493.7073 | 320.0398 | 316.0649 | 398.912 | 1748.7073 | 398.912 | 320.0398 | 316.0649
1749.7073 | 1494.7073 | 320.1285 | 316.17 | 398.8704 | 1749.7073 | 398.8704 | 320.1285 | 316.17
1750.7073 | 1495.7073 | 320.219 | 316.2651 | 398.6996 | 1750.7073 | 398.6996 | 320.219 | 316.2651
1751.7073 | 1496.7073 | 320.3138 | 316.3552 | 398.7257 | 1751.7073 | 398.7257 | 320.3138 | 316.3552
1752.7073 | 1497.7073 | 320.3884 | 316.4531 | 398.7123 | 1752.7073 | 398.7123 | 320.3884 | 316.4531
1753.7073 | 1498.7073 | 320.4702 | 316.5459 | 398.8474 | 1753.7073 | 398.8474 | 320.4702 | 316.5459
1754.7073 | 1499.7073 | 320.5599 | 316.6524 | 398.9805 | 1754.7073 | 398.9805 | 320.5599 | 316.6524
1755.7073 | 1500.7073 | 320.6545 | 316.7464 | 398.9624 | 1755.7073 | 398.9624 | 320.6545 | 316.7464
1756.7073 | 1501.7073 | 320.7326 | 316.8342 | 398.9432 | 1756.7073 | 398.9432 | 320.7326 | 316.8342
1757.7073 | 1502.7073 | 320.8148 | 316.9243 | 398.8733 | 1757.7073 | 398.8733 | 320.8148 | 316.9243
1758.7073 | 1503.7073 | 320.9009 | 317.027 | 398.7629 | 1758.7073 | 398.7629 | 320.9009 | 317.027
1759.7073 | 1504.7073 | 320.9763 | 317.1152 | 398.6635 | 1759.7073 | 398.6635 | 320.9763 | 317.1152
1760.7073 | 1505.7073 | 321.0509 | 317.203 | 398.5984 | 1760.7073 | 398.5984 | 321.0509 | 317.203
1761.7073 | 1506.7073 | 321.147 | 317.2948 | 398.6131 | 1761.7073 | 398.6131 | 321.147 | 317.2948
1762.7073 | 1507.7073 | 321.2225 | 317.3779 | 398.559 | 1762.7073 | 398.559 | 321.2225 | 317.3779
1763.7073 | 1508.7073 | 321.3126 | 317.4747 | 398.3648 | 1763.7073 | 398.3648 | 321.3126 | 317.4747
1764.7073 | 1509.7073 | 321.3936 | 317.5616 | 398.3137 | 1764.7073 | 398.3137 | 321.3936 | 317.5616
1765.7073 | 1510.7073 | 321.4792 | 317.6511 | 398.2083 | 1765.7073 | 398.2083 | 321.4792 | 317.6511
1766.7073 | 1511.7073 | 321.5458 | 317.7393 | 398.3061 | 1766.7073 | 398.3061 | 321.5458 | 317.7393
1767.7073 | 1512.7073 | 321.6077 | 317.8315 | 398.4418 | 1767.7073 | 398.4418 | 321.6077 | 317.8315
1768.7073 | 1513.7073 | 321.7028 | 317.9136 | 398.4181 | 1768.7073 | 398.4181 | 321.7028 | 317.9136
1769.7073 | 1514.7073 | 321.7688 | 318.0101 | 398.5422 | 1769.7073 | 398.5422 | 321.7688 | 318.0101
1770.7073 | 1515.7073 | 321.8663 | 318.0908 | 398.629 | 1770.7073 | 398.629 | 321.8663 | 318.0908
1771.7073 | 1516.7073 | 321.9197 | 318.1742 | 398.6622 | 1771.7073 | 398.6622 | 321.9197 | 318.1742
1772.7073 | 1517.7073 | 322.0197 | 318.2597 | 398.613 | 1772.7073 | 398.613 | 322.0197 | 318.2597
1773.7073 | 1518.7073 | 322.0934 | 318.3484 | 398.5428 | 1773.7073 | 398.5428 | 322.0934 | 318.3484
1774.7073 | 1519.7073 | 322.1696 | 318.437 | 398.5209 | 1774.7073 | 398.5209 | 322.1696 | 318.437
1775.7073 | 1520.7073 | 322.2532 | 318.5225 | 398.6977 | 1775.7073 | 398.6977 | 322.2532 | 318.5225
1776.7073 | 1521.7073 | 322.3186 | 318.6024 | 398.8998 | 1776.7073 | 398.8998 | 322.3186 | 318.6024
1777.7073 | 1522.7073 | 322.4059 | 318.6794 | 398.9627 | 1777.7073 | 398.9627 | 322.4059 | 318.6794
1778.7073 | 1523.7073 | 322.4715 | 318.777 | 398.9548 | 1778.7073 | 398.9548 | 322.4715 | 318.777
1779.7073 | 1524.7073 | 322.5474 | 318.86 | 399.062 | 1779.7073 | 399.062 | 322.5474 | 318.86
1780.7073 | 1525.7073 | 322.6278 | 318.9295 | 399.2545 | 1780.7073 | 399.2545 | 322.6278 | 318.9295
1781.7073 | 1526.7073 | 322.6945 | 319.0097 | 399.5007 | 1781.7073 | 399.5007 | 322.6945 | 319.0097
1782.7073 | 1527.7073 | 322.7758 | 319.0971 | 399.5925 | 1782.7073 | 399.5925 | 322.7758 | 319.0971
1783.7073 | 1528.7073 | 322.8471 | 319.1773 | 399.5374 | 1783.7073 | 399.5374 | 322.8471 | 319.1773
1784.7073 | 1529.7073 | 322.9246 | 319.24 | 399.4741 | 1784.7073 | 399.4741 | 322.9246 | 319.24
1785.7073 | 1530.7073 | 322.9734 | 319.3384 | 399.4975 | 1785.7073 | 399.4975 | 322.9734 | 319.3384
1786.7073 | 1531.7073 | 323.0764 | 319.425 | 399.5572 | 1786.7073 | 399.5572 | 323.0764 | 319.425
1787.7073 | 1532.7073 | 323.1601 | 319.4961 | 399.4963 | 1787.7073 | 399.4963 | 323.1601 | 319.4961
1788.7073 | 1533.7073 | 323.2436 | 319.5696 | 399.4541 | 1788.7073 | 399.4541 | 323.2436 | 319.5696
1789.7073 | 1534.7073 | 323.3207 | 319.6525 | 399.3689 | 1789.7073 | 399.3689 | 323.3207 | 319.6525
1790.7073 | 1535.7073 | 323.399 | 319.7455 | 399.3754 | 1790.7073 | 399.3754 | 323.399 | 319.7455
1791.7073 | 1536.7073 | 323.4606 | 319.8149 | 399.4371 | 1791.7073 | 399.4371 | 323.4606 | 319.8149
1792.7073 | 1537.7073 | 323.5528 | 319.8893 | 399.4414 | 1792.7073 | 399.4414 | 323.5528 | 319.8893
1793.7073 | 1538.7073 | 323.6376 | 319.9669 | 399.5595 | 1793.7073 | 399.5595 | 323.6376 | 319.9669
1794.7073 | 1539.7073 | 323.6964 | 320.053 | 399.584 | 1794.7073 | 399.584 | 323.6964 | 320.053
1795.7073 | 1540.7073 | 323.789 | 320.1244 | 399.5375 | 1795.7073 | 399.5375 | 323.789 | 320.1244
1796.7073 | 1541.7073 | 323.8551 | 320.1986 | 399.4027 | 1796.7073 | 399.4027 | 323.8551 | 320.1986
1797.7073 | 1542.7073 | 323.932 | 320.2868 | 399.4526 | 1797.7073 | 399.4526 | 323.932 | 320.2868
1798.7073 | 1543.7073 | 324.0229 | 320.362 | 399.3836 | 1798.7073 | 399.3836 | 324.0229 | 320.362
1799.7073 | 1544.7073 | 324.0859 | 320.4273 | 399.375 | 1799.7073 | 399.375 | 324.0859 | 320.4273
1800.7073 | 1545.7073 | 324.1673 | 320.5071 | 399.3311 | 1800.7073 | 399.3311 | 324.1673 | 320.5071
1801.7073 | 1546.7073 | 324.2628 | 320.5733 | 399.3648 | 1801.7073 | 399.3648 | 324.2628 | 320.5733
1802.7073 | 1547.7073 | 324.3356 | 320.6644 | 399.2212 | 1802.7073 | 399.2212 | 324.3356 | 320.6644
1803.7073 | 1548.7073 | 324.41 | 320.7375 | 399.136 | 1803.7073 | 399.136 | 324.41 | 320.7375
1804.7073 | 1549.7073 | 324.4826 | 320.8134 | 398.9574 | 1804.7073 | 398.9574 | 324.4826 | 320.8134
1805.7073 | 1550.7073 | 324.5812 | 320.8775 | 398.8091 | 1805.7073 | 398.8091 | 324.5812 | 320.8775
1806.7073 | 1551.7073 | 324.6468 | 320.956 | 398.7124 | 1806.7073 | 398.7124 | 324.6468 | 320.956
1807.7073 | 1552.7073 | 324.719 | 321.0354 | 398.6095 | 1807.7073 | 398.6095 | 324.719 | 321.0354
1808.7073 | 1553.7073 | 324.8052 | 321.1023 | 398.4972 | 1808.7073 | 398.4972 | 324.8052 | 321.1023
1809.7073 | 1554.7073 | 324.8892 | 321.1741 | 398.5186 | 1809.7073 | 398.5186 | 324.8892 | 321.1741
1810.7073 | 1555.7073 | 324.938 | 321.2529 | 398.4256 | 1810.7073 | 398.4256 | 324.938 | 321.2529
1811.7073 | 1556.7073 | 325.0342 | 321.3252 | 398.3806 | 1811.7073 | 398.3806 | 325.0342 | 321.3252
1812.7073 | 1557.7073 | 325.1001 | 321.3966 | 398.4421 | 1812.7073 | 398.4421 | 325.1001 | 321.3966
1813.7073 | 1558.7073 | 325.1963 | 321.4721 | 398.469 | 1813.7073 | 398.469 | 325.1963 | 321.4721
1814.7073 | 1559.7073 | 325.269 | 321.5412 | 398.3627 | 1814.7073 | 398.3627 | 325.269 | 321.5412
1815.7073 | 1560.7073 | 325.3422 | 321.6103 | 398.3563 | 1815.7073 | 398.3563 | 325.3422 | 321.6103
1816.7073 | 1561.7073 | 325.4271 | 321.6848 | 398.433 | 1816.7073 | 398.433 | 325.4271 | 321.6848
1817.7073 | 1562.7073 | 325.4959 | 321.7511 | 398.3143 | 1817.7073 | 398.3143 | 325.4959 | 321.7511
1818.7073 | 1563.7073 | 325.5733 | 321.8378 | 398.2617 | 1818.7073 | 398.2617 | 325.5733 | 321.8378
1819.7073 | 1564.7073 | 325.65 | 321.9031 | 398.3398 | 1819.7073 | 398.3398 | 325.65 | 321.9031
1820.7073 | 1565.7073 | 325.7223 | 321.9745 | 398.4612 | 1820.7073 | 398.4612 | 325.7223 | 321.9745
1821.7073 | 1566.7073 | 325.7947 | 322.0593 | 398.5794 | 1821.7073 | 398.5794 | 325.7947 | 322.0593
1822.7073 | 1567.7073 | 325.8829 | 322.1144 | 398.6148 | 1822.7073 | 398.6148 | 325.8829 | 322.1144
1823.7073 | 1568.7073 | 325.961 | 322.1805 | 398.6477 | 1823.7073 | 398.6477 | 325.961 | 322.1805
1824.7073 | 1569.7073 | 326.0332 | 322.2502 | 398.596 | 1824.7073 | 398.596 | 326.0332 | 322.2502
1825.7073 | 1570.7073 | 326.0998 | 322.329 | 398.5484 | 1825.7073 | 398.5484 | 326.0998 | 322.329
1826.7073 | 1571.7073 | 326.1643 | 322.3975 | 398.5193 | 1826.7073 | 398.5193 | 326.1643 | 322.3975
1827.7073 | 1572.7073 | 326.2438 | 322.4578 | 398.5652 | 1827.7073 | 398.5652 | 326.2438 | 322.4578
1828.7073 | 1573.7073 | 326.3215 | 322.5239 | 398.6177 | 1828.7073 | 398.6177 | 326.3215 | 322.5239
1829.7073 | 1574.7073 | 326.3803 | 322.6079 | 398.5807 | 1829.7073 | 398.5807 | 326.3803 | 322.6079
1830.7073 | 1575.7073 | 326.4607 | 322.6687 | 398.5934 | 1830.7073 | 398.5934 | 326.4607 | 322.6687
1831.7542 | 1576.7542 | 326.5291 | 322.7388 | 398.5573 | 1831.7542 | 398.5573 | 326.5291 | 322.7388
1832.7542 | 1577.7542 | 326.6001 | 322.8007 | 398.6738 | 1832.7542 | 398.6738 | 326.6001 | 322.8007
1833.7542 | 1578.7542 | 326.6619 | 322.866 | 398.8126 | 1833.7542 | 398.8126 | 326.6619 | 322.866
1834.7073 | 1579.7073 | 326.7253 | 322.9248 | 398.7424 | 1834.7073 | 398.7424 | 326.7253 | 322.9248
1835.7073 | 1580.7073 | 326.8019 | 322.9905 | 398.6575 | 1835.7073 | 398.6575 | 326.8019 | 322.9905
1836.7073 | 1581.7073 | 326.871 | 323.0696 | 398.8013 | 1836.7073 | 398.8013 | 326.871 | 323.0696
1837.7073 | 1582.7073 | 326.9334 | 323.1425 | 398.8992 | 1837.7073 | 398.8992 | 326.9334 | 323.1425
1838.7073 | 1583.7073 | 327.0057 | 323.1961 | 399.0556 | 1838.7073 | 399.0556 | 327.0057 | 323.1961
1839.7073 | 1584.7073 | 327.072 | 323.2558 | 399.0946 | 1839.7073 | 399.0946 | 327.072 | 323.2558
1840.8479 | 1585.8479 | 327.1542 | 323.3385 | 399.1088 | 1840.8479 | 399.1088 | 327.1542 | 323.3385
1841.7698 | 1586.7698 | 327.2209 | 323.401 | 399.0947 | 1841.7698 | 399.0947 | 327.2209 | 323.401
1842.7073 | 1587.7073 | 327.2749 | 323.4683 | 399.125 | 1842.7073 | 399.125 | 327.2749 | 323.4683
1843.7854 | 1588.7854 | 327.3414 | 323.5262 | 399.0222 | 1843.7854 | 399.0222 | 327.3414 | 323.5262
1844.7073 | 1589.7073 | 327.4111 | 323.5826 | 399.128 | 1844.7073 | 399.128 | 327.4111 | 323.5826
1845.7073 | 1590.7073 | 327.4588 | 323.6405 | 399.194 | 1845.7073 | 399.194 | 327.4588 | 323.6405
1846.7073 | 1591.7073 | 327.537 | 323.7038 | 399.1933 | 1846.7073 | 399.1933 | 327.537 | 323.7038
1847.7073 | 1592.7073 | 327.6114 | 323.7925 | 399.2634 | 1847.7073 | 399.2634 | 327.6114 | 323.7925
1848.7073 | 1593.7073 | 327.6745 | 323.8584 | 399.2765 | 1848.7073 | 399.2765 | 327.6745 | 323.8584
1849.7073 | 1594.7073 | 327.7241 | 323.8971 | 399.387 | 1849.7073 | 399.387 | 327.7241 | 323.8971
1850.7073 | 1595.7073 | 327.801 | 323.9601 | 399.424 | 1850.7073 | 399.424 | 327.801 | 323.9601
1851.7073 | 1596.7073 | 327.8671 | 324.0288 | 399.3724 | 1851.7073 | 399.3724 | 327.8671 | 324.0288
1852.7073 | 1597.7073 | 327.9453 | 324.0972 | 399.4164 | 1852.7073 | 399.4164 | 327.9453 | 324.0972
1853.7073 | 1598.7073 | 328.0101 | 324.1586 | 399.6587 | 1853.7073 | 399.6587 | 328.0101 | 324.1586
1854.7073 | 1599.7073 | 328.0642 | 324.2228 | 399.91 | 1854.7073 | 399.91 | 328.0642 | 324.2228
1855.7073 | 1600.7073 | 328.1423 | 324.2957 | 399.9396 | 1855.7073 | 399.9396 | 328.1423 | 324.2957
1856.7073 | 1601.7073 | 328.1881 | 324.3494 | 399.8762 | 1856.7073 | 399.8762 | 328.1881 | 324.3494
1857.7073 | 1602.7073 | 328.2596 | 324.4042 | 399.9052 | 1857.7073 | 399.9052 | 328.2596 | 324.4042
1858.7073 | 1603.7073 | 328.3364 | 324.466 | 399.9159 | 1858.7073 | 399.9159 | 328.3364 | 324.466
1859.7854 | 1604.7854 | 328.3961 | 324.5292 | 399.9699 | 1859.7854 | 399.9699 | 328.3961 | 324.5292
1860.7542 | 1605.7542 | 328.4544 | 324.5825 | 400.0185 | 1860.7542 | 400.0185 | 328.4544 | 324.5825
1861.7073 | 1606.7073 | 328.5202 | 324.6575 | 400.0198 | 1861.7073 | 400.0198 | 328.5202 | 324.6575
1862.7229 | 1607.7229 | 328.5951 | 324.7118 | 400.0161 | 1862.7229 | 400.0161 | 328.5951 | 324.7118
1863.7073 | 1608.7073 | 328.6449 | 324.7713 | 399.8928 | 1863.7073 | 399.8928 | 328.6449 | 324.7713
1864.7073 | 1609.7073 | 328.7223 | 324.831 | 399.8465 | 1864.7073 | 399.8465 | 328.7223 | 324.831
1865.7073 | 1610.7073 | 328.7835 | 324.8762 | 399.758 | 1865.7073 | 399.758 | 328.7835 | 324.8762
1866.7073 | 1611.7073 | 328.8474 | 324.9429 | 399.7868 | 1866.7073 | 399.7868 | 328.8474 | 324.9429
1867.7073 | 1612.7073 | 328.9168 | 325.0129 | 399.7454 | 1867.7073 | 399.7454 | 328.9168 | 325.0129
1868.7073 | 1613.7073 | 328.983 | 325.0704 | 399.6998 | 1868.7073 | 399.6998 | 328.983 | 325.0704
1869.7073 | 1614.7073 | 329.0475 | 325.1164 | 399.5407 | 1869.7073 | 399.5407 | 329.0475 | 325.1164
1870.7073 | 1615.7073 | 329.1039 | 325.1754 | 399.4405 | 1870.7073 | 399.4405 | 329.1039 | 325.1754
1871.7073 | 1616.7073 | 329.1759 | 325.2381 | 399.3671 | 1871.7073 | 399.3671 | 329.1759 | 325.2381
1872.7073 | 1617.7073 | 329.2317 | 325.2969 | 399.32 | 1872.7073 | 399.32 | 329.2317 | 325.2969
1873.7073 | 1618.7073 | 329.3021 | 325.3562 | 399.2571 | 1873.7073 | 399.2571 | 329.3021 | 325.3562
1874.7073 | 1619.7073 | 329.3534 | 325.4029 | 399.31 | 1874.7073 | 399.31 | 329.3534 | 325.4029
1875.7073 | 1620.7073 | 329.4231 | 325.4711 | 399.2384 | 1875.7073 | 399.2384 | 329.4231 | 325.4711
1876.7073 | 1621.7073 | 329.4913 | 325.5346 | 399.2837 | 1876.7073 | 399.2837 | 329.4913 | 325.5346
1877.7073 | 1622.7073 | 329.5658 | 325.5881 | 399.2413 | 1877.7073 | 399.2413 | 329.5658 | 325.5881
1878.7073 | 1623.7073 | 329.6265 | 325.6372 | 399.067 | 1878.7073 | 399.067 | 329.6265 | 325.6372
1879.7073 | 1624.7073 | 329.6859 | 325.6975 | 399.0811 | 1879.7073 | 399.0811 | 329.6859 | 325.6975
1880.7073 | 1625.7073 | 329.7517 | 325.7584 | 399.1742 | 1880.7073 | 399.1742 | 329.7517 | 325.7584
1881.7073 | 1626.7073 | 329.8092 | 325.8264 | 399.12 | 1881.7073 | 399.12 | 329.8092 | 325.8264
1882.7073 | 1627.7073 | 329.8814 | 325.8795 | 399.0923 | 1882.7073 | 399.0923 | 329.8814 | 325.8795
1883.7073 | 1628.7073 | 329.9455 | 325.9374 | 399.128 | 1883.7073 | 399.128 | 329.9455 | 325.9374
1884.7073 | 1629.7073 | 330.0151 | 326.0099 | 399.1046 | 1884.7073 | 399.1046 | 330.0151 | 326.0099
1885.7073 | 1630.7073 | 330.077 | 326.0399 | 399.1381 | 1885.7073 | 399.1381 | 330.077 | 326.0399
1886.7073 | 1631.7073 | 330.1514 | 326.0734 | 399.2023 | 1886.7073 | 399.2023 | 330.1514 | 326.0734
1887.7073 | 1632.7073 | 330.2074 | 326.1591 | 399.1601 | 1887.7073 | 399.1601 | 330.2074 | 326.1591
1888.7073 | 1633.7073 | 330.2791 | 326.2092 | 399.2051 | 1888.7073 | 399.2051 | 330.2791 | 326.2092
1889.7073 | 1634.7073 | 330.3288 | 326.2669 | 399.2858 | 1889.7073 | 399.2858 | 330.3288 | 326.2669
1890.7073 | 1635.7073 | 330.3975 | 326.322 | 399.3357 | 1890.7073 | 399.3357 | 330.3975 | 326.322
1891.7073 | 1636.7073 | 330.4747 | 326.3798 | 399.4108 | 1891.7073 | 399.4108 | 330.4747 | 326.3798
1892.7073 | 1637.7073 | 330.5361 | 326.4317 | 399.4916 | 1892.7073 | 399.4916 | 330.5361 | 326.4317
1893.7073 | 1638.7073 | 330.5939 | 326.4889 | 399.4624 | 1893.7073 | 399.4624 | 330.5939 | 326.4889
1894.7073 | 1639.7073 | 330.6606 | 326.5421 | 399.5085 | 1894.7073 | 399.5085 | 330.6606 | 326.5421
1895.7073 | 1640.7073 | 330.7352 | 326.6036 | 399.6075 | 1895.7073 | 399.6075 | 330.7352 | 326.6036
1896.7073 | 1641.7073 | 330.7998 | 326.6536 | 399.7624 | 1896.7073 | 399.7624 | 330.7998 | 326.6536
1897.7073 | 1642.7073 | 330.8629 | 326.6996 | 399.7985 | 1897.7073 | 399.7985 | 330.8629 | 326.6996
1898.7073 | 1643.7073 | 330.9384 | 326.758 | 399.9578 | 1898.7073 | 399.9578 | 330.9384 | 326.758
1899.7073 | 1644.7073 | 330.9998 | 326.8167 | 399.996 | 1899.7073 | 399.996 | 330.9998 | 326.8167
1900.7073 | 1645.7073 | 331.0554 | 326.8671 | 399.9315 | 1900.7073 | 399.9315 | 331.0554 | 326.8671
1901.7073 | 1646.7073 | 331.1174 | 326.9095 | 400.0045 | 1901.7073 | 400.0045 | 331.1174 | 326.9095
1902.7073 | 1647.7073 | 331.1682 | 326.9654 | 400.068 | 1902.7073 | 400.068 | 331.1682 | 326.9654
1903.7073 | 1648.7073 | 331.2501 | 327.0277 | 400.0499 | 1903.7073 | 400.0499 | 331.2501 | 327.0277
1904.7073 | 1649.7073 | 331.3247 | 327.0857 | 400.0899 | 1904.7073 | 400.0899 | 331.3247 | 327.0857
1905.7073 | 1650.7073 | 331.388 | 327.1253 | 399.9782 | 1905.7073 | 399.9782 | 331.388 | 327.1253
1906.7073 | 1651.7073 | 331.4564 | 327.1741 | 399.8472 | 1906.7073 | 399.8472 | 331.4564 | 327.1741
1907.7073 | 1652.7073 | 331.5092 | 327.2397 | 399.6977 | 1907.7073 | 399.6977 | 331.5092 | 327.2397
1908.7073 | 1653.7073 | 331.5734 | 327.2891 | 399.6216 | 1908.7073 | 399.6216 | 331.5734 | 327.2891
1909.7073 | 1654.7073 | 331.6486 | 327.3429 | 399.5748 | 1909.7073 | 399.5748 | 331.6486 | 327.3429
1910.7073 | 1655.7073 | 331.7059 | 327.4007 | 399.5233 | 1910.7073 | 399.5233 | 331.7059 | 327.4007
1911.7073 | 1656.7073 | 331.7769 | 327.4613 | 399.5208 | 1911.7073 | 399.5208 | 331.7769 | 327.4613
1912.7073 | 1657.7073 | 331.8518 | 327.5035 | 399.4208 | 1912.7073 | 399.4208 | 331.8518 | 327.5035
1913.7073 | 1658.7073 | 331.9167 | 327.5562 | 399.3201 | 1913.7073 | 399.3201 | 331.9167 | 327.5562
1914.7073 | 1659.7073 | 331.973 | 327.6109 | 399.2061 | 1914.7073 | 399.2061 | 331.973 | 327.6109
1915.7073 | 1660.7073 | 332.0431 | 327.6678 | 399.0946 | 1915.7073 | 399.0946 | 332.0431 | 327.6678
1916.7073 | 1661.7073 | 332.1129 | 327.7115 | 399.0268 | 1916.7073 | 399.0268 | 332.1129 | 327.7115
1917.7073 | 1662.7073 | 332.1791 | 327.7675 | 399.0489 | 1917.7073 | 399.0489 | 332.1791 | 327.7675
1918.7073 | 1663.7073 | 332.2502 | 327.8283 | 399.2245 | 1918.7073 | 399.2245 | 332.2502 | 327.8283
1919.7073 | 1664.7073 | 332.2977 | 327.8694 | 399.2307 | 1919.7073 | 399.2307 | 332.2977 | 327.8694
1920.7073 | 1665.7073 | 332.3723 | 327.9222 | 399.1369 | 1920.7073 | 399.1369 | 332.3723 | 327.9222
1921.7073 | 1666.7073 | 332.4273 | 327.9877 | 399.2607 | 1921.7073 | 399.2607 | 332.4273 | 327.9877
1922.7073 | 1667.7073 | 332.5043 | 328.0431 | 399.3107 | 1922.7073 | 399.3107 | 332.5043 | 328.0431
1923.7073 | 1668.7073 | 332.5712 | 328.0913 | 399.2363 | 1923.7073 | 399.2363 | 332.5712 | 328.0913
1924.7073 | 1669.7073 | 332.6385 | 328.1484 | 399.2346 | 1924.7073 | 399.2346 | 332.6385 | 328.1484
1925.7073 | 1670.7073 | 332.7016 | 328.1956 | 399.3043 | 1925.7073 | 399.3043 | 332.7016 | 328.1956
1926.7073 | 1671.7073 | 332.76 | 328.2504 | 399.1773 | 1926.7073 | 399.1773 | 332.76 | 328.2504
1927.7073 | 1672.7073 | 332.8279 | 328.3127 | 399.0928 | 1927.7073 | 399.0928 | 332.8279 | 328.3127
1928.7073 | 1673.7073 | 332.8871 | 328.3538 | 399.1825 | 1928.7073 | 399.1825 | 332.8871 | 328.3538
1929.7073 | 1674.7073 | 332.9469 | 328.4162 | 399.2111 | 1929.7073 | 399.2111 | 332.9469 | 328.4162
1930.7073 | 1675.7073 | 333.034 | 328.4723 | 399.1597 | 1930.7073 | 399.1597 | 333.034 | 328.4723
1931.7073 | 1676.7073 | 333.0971 | 328.525 | 399.133 | 1931.7073 | 399.133 | 333.0971 | 328.525
1932.7073 | 1677.7073 | 333.1711 | 328.5637 | 399.1339 | 1932.7073 | 399.1339 | 333.1711 | 328.5637
1933.7073 | 1678.7073 | 333.2314 | 328.6178 | 399.1501 | 1933.7073 | 399.1501 | 333.2314 | 328.6178
1934.7073 | 1679.7073 | 333.2929 | 328.6709 | 399.2347 | 1934.7073 | 399.2347 | 333.2929 | 328.6709
1935.7073 | 1680.7073 | 333.3707 | 328.7218 | 399.2511 | 1935.7073 | 399.2511 | 333.3707 | 328.7218
1936.7073 | 1681.7073 | 333.4203 | 328.7779 | 399.2218 | 1936.7073 | 399.2218 | 333.4203 | 328.7779
1937.7073 | 1682.7073 | 333.4913 | 328.8256 | 399.2221 | 1937.7073 | 399.2221 | 333.4913 | 328.8256
1938.7073 | 1683.7073 | 333.5626 | 328.8742 | 399.1157 | 1938.7073 | 399.1157 | 333.5626 | 328.8742
1939.7073 | 1684.7073 | 333.6331 | 328.9189 | 398.9445 | 1939.7073 | 398.9445 | 333.6331 | 328.9189
1940.7073 | 1685.7073 | 333.693 | 328.9893 | 398.891 | 1940.7073 | 398.891 | 333.693 | 328.9893
1941.7073 | 1686.7073 | 333.7576 | 329.033 | 398.7567 | 1941.7073 | 398.7567 | 333.7576 | 329.033
1942.7073 | 1687.7073 | 333.8219 | 329.0814 | 398.7495 | 1942.7073 | 398.7495 | 333.8219 | 329.0814
1943.7073 | 1688.7073 | 333.877 | 329.1343 | 398.6757 | 1943.7073 | 398.6757 | 333.877 | 329.1343
1944.7073 | 1689.7073 | 333.9508 | 329.1875 | 398.6051 | 1944.7073 | 398.6051 | 333.9508 | 329.1875
1945.7073 | 1690.7073 | 334.0211 | 329.2264 | 398.7051 | 1945.7073 | 398.7051 | 334.0211 | 329.2264
1946.7073 | 1691.7073 | 334.086 | 329.2868 | 398.8707 | 1946.7073 | 398.8707 | 334.086 | 329.2868
1947.7073 | 1692.7073 | 334.1407 | 329.3361 | 399.0218 | 1947.7073 | 399.0218 | 334.1407 | 329.3361
1948.7073 | 1693.7073 | 334.2038 | 329.3805 | 398.9691 | 1948.7073 | 398.9691 | 334.2038 | 329.3805
1949.7073 | 1694.7073 | 334.2744 | 329.4319 | 398.8806 | 1949.7073 | 398.8806 | 334.2744 | 329.4319
1950.7073 | 1695.7073 | 334.3371 | 329.485 | 398.9185 | 1950.7073 | 398.9185 | 334.3371 | 329.485
1951.7073 | 1696.7073 | 334.4002 | 329.541 | 398.9311 | 1951.7073 | 398.9311 | 334.4002 | 329.541
1952.7073 | 1697.7073 | 334.4507 | 329.5706 | 399.0463 | 1952.7073 | 399.0463 | 334.4507 | 329.5706
1953.7073 | 1698.7073 | 334.5035 | 329.6156 | 399.0401 | 1953.7073 | 399.0401 | 334.5035 | 329.6156
1954.7073 | 1699.7073 | 334.5763 | 329.6885 | 399.08 | 1954.7073 | 399.08 | 334.5763 | 329.6885
1955.7073 | 1700.7073 | 334.6266 | 329.7406 | 399.1336 | 1955.7073 | 399.1336 | 334.6266 | 329.7406
1956.7073 | 1701.7073 | 334.6962 | 329.7843 | 399.154 | 1956.7073 | 399.154 | 334.6962 | 329.7843
1957.7073 | 1702.7073 | 334.7489 | 329.8286 | 399.148 | 1957.7073 | 399.148 | 334.7489 | 329.8286
1958.7073 | 1703.7073 | 334.8282 | 329.8748 | 399.1769 | 1958.7073 | 399.1769 | 334.8282 | 329.8748
1959.7073 | 1704.7073 | 334.8645 | 329.9262 | 399.3535 | 1959.7073 | 399.3535 | 334.8645 | 329.9262
1960.7073 | 1705.7073 | 334.9171 | 329.9725 | 399.4939 | 1960.7073 | 399.4939 | 334.9171 | 329.9725
1961.7073 | 1706.7073 | 335.0012 | 330.0122 | 399.5913 | 1961.7073 | 399.5913 | 335.0012 | 330.0122
1962.7073 | 1707.7073 | 335.049 | 330.0666 | 399.5526 | 1962.7073 | 399.5526 | 335.049 | 330.0666
1963.7073 | 1708.7073 | 335.1153 | 330.1099 | 399.3944 | 1963.7073 | 399.3944 | 335.1153 | 330.1099
1964.7073 | 1709.7073 | 335.18 | 330.1621 | 399.3696 | 1964.7073 | 399.3696 | 335.18 | 330.1621
1965.7073 | 1710.7073 | 335.226 | 330.2068 | 399.4118 | 1965.7073 | 399.4118 | 335.226 | 330.2068
1966.7073 | 1711.7073 | 335.2851 | 330.258 | 399.3292 | 1966.7073 | 399.3292 | 335.2851 | 330.258
1967.7073 | 1712.7073 | 335.3602 | 330.3156 | 399.3862 | 1967.7073 | 399.3862 | 335.3602 | 330.3156
1968.7073 | 1713.7073 | 335.4117 | 330.3614 | 399.4019 | 1968.7073 | 399.4019 | 335.4117 | 330.3614
1969.7073 | 1714.7073 | 335.474 | 330.4023 | 399.4221 | 1969.7073 | 399.4221 | 335.474 | 330.4023
1970.7073 | 1715.7073 | 335.5227 | 330.4455 | 399.3767 | 1970.7073 | 399.3767 | 335.5227 | 330.4455
1971.7073 | 1716.7073 | 335.5872 | 330.4983 | 399.3571 | 1971.7073 | 399.3571 | 335.5872 | 330.4983
1972.7073 | 1717.7073 | 335.6403 | 330.5492 | 399.428 | 1972.7073 | 399.428 | 335.6403 | 330.5492
1973.7073 | 1718.7073 | 335.6989 | 330.5938 | 399.5362 | 1973.7073 | 399.5362 | 335.6989 | 330.5938
1974.7073 | 1719.7073 | 335.7624 | 330.6377 | 399.4617 | 1974.7073 | 399.4617 | 335.7624 | 330.6377
1975.7073 | 1720.7073 | 335.8181 | 330.6862 | 399.5933 | 1975.7073 | 399.5933 | 335.8181 | 330.6862
1976.7073 | 1721.7073 | 335.8758 | 330.7335 | 399.6871 | 1976.7073 | 399.6871 | 335.8758 | 330.7335
1977.7073 | 1722.7073 | 335.9327 | 330.7778 | 399.7264 | 1977.7073 | 399.7264 | 335.9327 | 330.7778
1978.7073 | 1723.7073 | 335.9967 | 330.8248 | 399.6059 | 1978.7073 | 399.6059 | 335.9967 | 330.8248
1979.7073 | 1724.7073 | 336.0628 | 330.8708 | 399.5852 | 1979.7073 | 399.5852 | 336.0628 | 330.8708
1980.7073 | 1725.7073 | 336.1204 | 330.9269 | 399.5949 | 1980.7073 | 399.5949 | 336.1204 | 330.9269
1981.7073 | 1726.7073 | 336.1759 | 330.9743 | 399.668 | 1981.7073 | 399.668 | 336.1759 | 330.9743
1982.7073 | 1727.7073 | 336.2333 | 331.0118 | 399.6518 | 1982.7073 | 399.6518 | 336.2333 | 331.0118
1983.7073 | 1728.7073 | 336.2993 | 331.0608 | 399.6595 | 1983.7073 | 399.6595 | 336.2993 | 331.0608
1984.7073 | 1729.7073 | 336.3688 | 331.1144 | 399.5873 | 1984.7073 | 399.5873 | 336.3688 | 331.1144
1985.7073 | 1730.7073 | 336.4152 | 331.1606 | 399.5828 | 1985.7073 | 399.5828 | 336.4152 | 331.1606
1986.7073 | 1731.7073 | 336.4807 | 331.1951 | 399.6452 | 1986.7073 | 399.6452 | 336.4807 | 331.1951
1987.7073 | 1732.7073 | 336.5442 | 331.2388 | 399.5132 | 1987.7073 | 399.5132 | 336.5442 | 331.2388
1988.7073 | 1733.7073 | 336.6053 | 331.2932 | 399.3537 | 1988.7073 | 399.3537 | 336.6053 | 331.2932
1989.7073 | 1734.7073 | 336.6805 | 331.3398 | 399.2418 | 1989.7073 | 399.2418 | 336.6805 | 331.3398
1990.7073 | 1735.7073 | 336.7346 | 331.3815 | 399.2782 | 1990.7073 | 399.2782 | 336.7346 | 331.3815
1991.7073 | 1736.7073 | 336.8056 | 331.4317 | 399.3159 | 1991.7073 | 399.3159 | 336.8056 | 331.4317
1992.7073 | 1737.7073 | 336.8695 | 331.4859 | 399.3273 | 1992.7073 | 399.3273 | 336.8695 | 331.4859
1993.7073 | 1738.7073 | 336.9219 | 331.5286 | 399.3654 | 1993.7073 | 399.3654 | 336.9219 | 331.5286
1994.7073 | 1739.7073 | 336.9965 | 331.5769 | 399.2554 | 1994.7073 | 399.2554 | 336.9965 | 331.5769
1995.7073 | 1740.7073 | 337.0575 | 331.6225 | 399.1271 | 1995.7073 | 399.1271 | 337.0575 | 331.6225
1996.7073 | 1741.7073 | 337.122 | 331.6716 | 399.0659 | 1996.7073 | 399.0659 | 337.122 | 331.6716
1997.7073 | 1742.7073 | 337.1993 | 331.719 | 399.0062 | 1997.7073 | 399.0062 | 337.1993 | 331.719
1998.7073 | 1743.7073 | 337.2563 | 331.7587 | 398.9131 | 1998.7073 | 398.9131 | 337.2563 | 331.7587
1999.7073 | 1744.7073 | 337.3131 | 331.8097 | 398.793 | 1999.7073 | 398.793 | 337.3131 | 331.8097
2000.7073 | 1745.7073 | 337.3874 | 331.8404 | 398.7553 | 2000.7073 | 398.7553 | 337.3874 | 331.8404
2001.7073 | 1746.7073 | 337.4365 | 331.8991 | 398.7644 | 2001.7073 | 398.7644 | 337.4365 | 331.8991
2002.7073 | 1747.7073 | 337.5128 | 331.9589 | 398.807 | 2002.7073 | 398.807 | 337.5128 | 331.9589
2003.7073 | 1748.7073 | 337.5843 | 332.0083 | 398.6519 | 2003.7073 | 398.6519 | 337.5843 | 332.0083
2004.7073 | 1749.7073 | 337.6405 | 332.0374 | 398.5822 | 2004.7073 | 398.5822 | 337.6405 | 332.0374
2005.7073 | 1750.7073 | 337.7244 | 332.0821 | 398.5766 | 2005.7073 | 398.5766 | 337.7244 | 332.0821
2006.7073 | 1751.7073 | 337.7896 | 332.1396 | 398.5714 | 2006.7073 | 398.5714 | 337.7896 | 332.1396
2007.7073 | 1752.7073 | 337.8493 | 332.18 | 398.5401 | 2007.7073 | 398.5401 | 337.8493 | 332.18
2008.7073 | 1753.7073 | 337.9267 | 332.2241 | 398.4187 | 2008.7073 | 398.4187 | 337.9267 | 332.2241
2009.7073 | 1754.7073 | 337.9777 | 332.2715 | 398.3858 | 2009.7073 | 398.3858 | 337.9777 | 332.2715
2010.7073 | 1755.7073 | 338.0451 | 332.3205 | 398.2947 | 2010.7073 | 398.2947 | 338.0451 | 332.3205
2011.7073 | 1756.7073 | 338.1198 | 332.3656 | 398.2241 | 2011.7073 | 398.2241 | 338.1198 | 332.3656
2012.7073 | 1757.7073 | 338.1783 | 332.4134 | 398.342 | 2012.7073 | 398.342 | 338.1783 | 332.4134
2013.7073 | 1758.7073 | 338.2454 | 332.4518 | 398.4847 | 2013.7073 | 398.4847 | 338.2454 | 332.4518
2014.7073 | 1759.7073 | 338.3134 | 332.5016 | 398.5279 | 2014.7073 | 398.5279 | 338.3134 | 332.5016
2015.7073 | 1760.7073 | 338.3807 | 332.5503 | 398.6057 | 2015.7073 | 398.6057 | 338.3807 | 332.5503
2016.7073 | 1761.7073 | 338.4477 | 332.5909 | 398.7508 | 2016.7073 | 398.7508 | 338.4477 | 332.5909
2017.7073 | 1762.7073 | 338.5124 | 332.6376 | 398.7822 | 2017.7073 | 398.7822 | 338.5124 | 332.6376
2018.7073 | 1763.7073 | 338.5769 | 332.6841 | 398.8666 | 2018.7073 | 398.8666 | 338.5769 | 332.6841
2019.7073 | 1764.7073 | 338.6494 | 332.7316 | 399.0578 | 2019.7073 | 399.0578 | 338.6494 | 332.7316
2020.7073 | 1765.7073 | 338.7055 | 332.7718 | 399.0266 | 2020.7073 | 399.0266 | 338.7055 | 332.7718
2021.7073 | 1766.7073 | 338.7711 | 332.8114 | 399.0045 | 2021.7073 | 399.0045 | 338.7711 | 332.8114
2022.7073 | 1767.7073 | 338.8237 | 332.8721 | 399.0957 | 2022.7073 | 399.0957 | 338.8237 | 332.8721
2023.7073 | 1768.7073 | 338.8798 | 332.9112 | 399.1566 | 2023.7073 | 399.1566 | 338.8798 | 332.9112
2024.7073 | 1769.7073 | 338.9523 | 332.9508 | 399.2022 | 2024.7073 | 399.2022 | 338.9523 | 332.9508
2025.7073 | 1770.7073 | 339.0199 | 332.9973 | 399.3331 | 2025.7073 | 399.3331 | 339.0199 | 332.9973
2026.7073 | 1771.7073 | 339.065 | 333.042 | 399.3454 | 2026.7073 | 399.3454 | 339.065 | 333.042
2027.7073 | 1772.7073 | 339.1435 | 333.0804 | 399.3189 | 2027.7073 | 399.3189 | 339.1435 | 333.0804
2028.7073 | 1773.7073 | 339.2088 | 333.1247 | 399.1341 | 2028.7073 | 399.1341 | 339.2088 | 333.1247
2029.7073 | 1774.7073 | 339.2733 | 333.1667 | 399.2269 | 2029.7073 | 399.2269 | 339.2733 | 333.1667
2030.7073 | 1775.7073 | 339.3181 | 333.2189 | 399.2548 | 2030.7073 | 399.2548 | 339.3181 | 333.2189
2031.7073 | 1776.7073 | 339.3932 | 333.2585 | 399.1877 | 2031.7073 | 399.1877 | 339.3932 | 333.2585
2032.7073 | 1777.7073 | 339.4498 | 333.2985 | 399.2193 | 2032.7073 | 399.2193 | 339.4498 | 333.2985
2033.7073 | 1778.7073 | 339.5161 | 333.3443 | 399.3142 | 2033.7073 | 399.3142 | 339.5161 | 333.3443
2034.7073 | 1779.7073 | 339.5753 | 333.3874 | 399.3949 | 2034.7073 | 399.3949 | 339.5753 | 333.3874
2035.7073 | 1780.7073 | 339.6357 | 333.4332 | 399.323 | 2035.7073 | 399.323 | 339.6357 | 333.4332
2036.7073 | 1781.7073 | 339.6993 | 333.4702 | 399.3234 | 2036.7073 | 399.3234 | 339.6993 | 333.4702
2037.7073 | 1782.7073 | 339.7671 | 333.5134 | 399.4498 | 2037.7073 | 399.4498 | 339.7671 | 333.5134
2038.7073 | 1783.7073 | 339.8136 | 333.5598 | 399.5244 | 2038.7073 | 399.5244 | 339.8136 | 333.5598
2039.7073 | 1784.7073 | 339.885 | 333.6047 | 399.3926 | 2039.7073 | 399.3926 | 339.885 | 333.6047
2040.7073 | 1785.7073 | 339.9491 | 333.6591 | 399.3958 | 2040.7073 | 399.3958 | 339.9491 | 333.6591
2041.7073 | 1786.7073 | 339.9998 | 333.685 | 399.3424 | 2041.7073 | 399.3424 | 339.9998 | 333.685
2042.7073 | 1787.7073 | 340.0708 | 333.7261 | 399.3561 | 2042.7073 | 399.3561 | 340.0708 | 333.7261
2043.7073 | 1788.7073 | 340.1298 | 333.7727 | 399.3155 | 2043.7073 | 399.3155 | 340.1298 | 333.7727
2044.7073 | 1789.7073 | 340.1897 | 333.8173 | 399.3681 | 2044.7073 | 399.3681 | 340.1897 | 333.8173
2045.7073 | 1790.7073 | 340.2607 | 333.8635 | 399.4664 | 2045.7073 | 399.4664 | 340.2607 | 333.8635
2046.7073 | 1791.7073 | 340.3238 | 333.9084 | 399.4607 | 2046.7073 | 399.4607 | 340.3238 | 333.9084
2047.7073 | 1792.7073 | 340.3948 | 333.9433 | 399.4618 | 2047.7073 | 399.4618 | 340.3948 | 333.9433
2048.7073 | 1793.7073 | 340.4556 | 333.993 | 399.37 | 2048.7073 | 399.37 | 340.4556 | 333.993
2049.7073 | 1794.7073 | 340.519 | 334.0403 | 399.3182 | 2049.7073 | 399.3182 | 340.519 | 334.0403
2050.7073 | 1795.7073 | 340.5869 | 334.0881 | 399.37 | 2050.7073 | 399.37 | 340.5869 | 334.0881
2051.7073 | 1796.7073 | 340.6401 | 334.1236 | 399.3782 | 2051.7073 | 399.3782 | 340.6401 | 334.1236
2052.7073 | 1797.7073 | 340.6957 | 334.1669 | 399.3177 | 2052.7073 | 399.3177 | 340.6957 | 334.1669
2053.7073 | 1798.7073 | 340.7774 | 334.2206 | 399.3398 | 2053.7073 | 399.3398 | 340.7774 | 334.2206
2054.7073 | 1799.7073 | 340.8329 | 334.2548 | 399.2391 | 2054.7073 | 399.2391 | 340.8329 | 334.2548
2055.7073 | 1800.7073 | 340.8988 | 334.297 | 399.1155 | 2055.7073 | 399.1155 | 340.8988 | 334.297
2056.7073 | 1801.7073 | 340.9779 | 334.3445 | 398.9899 | 2056.7073 | 398.9899 | 340.9779 | 334.3445
2057.7073 | 1802.7073 | 341.0353 | 334.3937 | 398.992 | 2057.7073 | 398.992 | 341.0353 | 334.3937
2058.7073 | 1803.7073 | 341.0968 | 334.437 | 398.9598 | 2058.7073 | 398.9598 | 341.0968 | 334.437
2059.7073 | 1804.7073 | 341.1715 | 334.4842 | 398.8221 | 2059.7073 | 398.8221 | 341.1715 | 334.4842
2060.7073 | 1805.7073 | 341.2365 | 334.5226 | 398.8285 | 2060.7073 | 398.8285 | 341.2365 | 334.5226
2061.7073 | 1806.7073 | 341.3076 | 334.562 | 398.8812 | 2061.7073 | 398.8812 | 341.3076 | 334.562
2062.7073 | 1807.7073 | 341.3531 | 334.6211 | 398.6214 | 2062.7073 | 398.6214 | 341.3531 | 334.6211
2063.7073 | 1808.7073 | 341.4175 | 334.6584 | 398.4953 | 2063.7073 | 398.4953 | 341.4175 | 334.6584
2064.7073 | 1809.7073 | 341.5042 | 334.7092 | 398.3445 | 2064.7073 | 398.3445 | 341.5042 | 334.7092
2065.7073 | 1810.7073 | 341.5687 | 334.7568 | 398.3067 | 2065.7073 | 398.3067 | 341.5687 | 334.7568
2066.7073 | 1811.7073 | 341.6356 | 334.807 | 398.1857 | 2066.7073 | 398.1857 | 341.6356 | 334.807
2067.7073 | 1812.7073 | 341.69 | 334.8425 | 398.145 | 2067.7073 | 398.145 | 341.69 | 334.8425
2068.7073 | 1813.7073 | 341.7707 | 334.8891 | 398.0585 | 2068.7073 | 398.0585 | 341.7707 | 334.8891
2069.7073 | 1814.7073 | 341.8184 | 334.9379 | 398.1037 | 2069.7073 | 398.1037 | 341.8184 | 334.9379
2070.7073 | 1815.7073 | 341.8857 | 334.9873 | 398.0064 | 2070.7073 | 398.0064 | 341.8857 | 334.9873
2071.7073 | 1816.7073 | 341.9504 | 335.0208 | 397.9162 | 2071.7073 | 397.9162 | 341.9504 | 335.0208
2072.7073 | 1817.7073 | 342.0156 | 335.0753 | 398.0021 | 2072.7073 | 398.0021 | 342.0156 | 335.0753
2073.7073 | 1818.7073 | 342.0942 | 335.1198 | 397.9288 | 2073.7073 | 397.9288 | 342.0942 | 335.1198
2074.7073 | 1819.7073 | 342.1333 | 335.1615 | 397.8551 | 2074.7073 | 397.8551 | 342.1333 | 335.1615
2075.7073 | 1820.7073 | 342.2059 | 335.2068 | 397.8007 | 2075.7073 | 397.8007 | 342.2059 | 335.2068
2076.7073 | 1821.7073 | 342.2665 | 335.2617 | 397.7534 | 2076.7073 | 397.7534 | 342.2665 | 335.2617
2077.7073 | 1822.7073 | 342.3373 | 335.3155 | 397.7272 | 2077.7073 | 397.7272 | 342.3373 | 335.3155
2078.7073 | 1823.7073 | 342.4005 | 335.3544 | 397.6596 | 2078.7073 | 397.6596 | 342.4005 | 335.3544
2079.7073 | 1824.7073 | 342.4611 | 335.3975 | 397.5981 | 2079.7073 | 397.5981 | 342.4611 | 335.3975
2080.7073 | 1825.7073 | 342.5312 | 335.4401 | 397.4704 | 2080.7073 | 397.4704 | 342.5312 | 335.4401
2081.7073 | 1826.7073 | 342.5944 | 335.4705 | 397.5026 | 2081.7073 | 397.5026 | 342.5944 | 335.4705
2082.7073 | 1827.7073 | 342.6489 | 335.5178 | 397.3712 | 2082.7073 | 397.3712 | 342.6489 | 335.5178
2083.7073 | 1828.7073 | 342.7297 | 335.5662 | 397.2506 | 2083.7073 | 397.2506 | 342.7297 | 335.5662
2084.7073 | 1829.7073 | 342.7773 | 335.6219 | 397.2697 | 2084.7073 | 397.2697 | 342.7773 | 335.6219
2085.7073 | 1830.7073 | 342.8466 | 335.6633 | 397.2784 | 2085.7073 | 397.2784 | 342.8466 | 335.6633
2086.7073 | 1831.7073 | 342.9098 | 335.6934 | 397.3589 | 2086.7073 | 397.3589 | 342.9098 | 335.6934
2087.7073 | 1832.7073 | 342.9714 | 335.7341 | 397.412 | 2087.7073 | 397.412 | 342.9714 | 335.7341
2088.7073 | 1833.7073 | 343.0322 | 335.7727 | 397.4121 | 2088.7073 | 397.4121 | 343.0322 | 335.7727
2089.7073 | 1834.7073 | 343.101 | 335.8222 | 397.5106 | 2089.7073 | 397.5106 | 343.101 | 335.8222
2090.7073 | 1835.7073 | 343.1636 | 335.8592 | 397.5633 | 2090.7073 | 397.5633 | 343.1636 | 335.8592
2091.7073 | 1836.7073 | 343.2214 | 335.9007 | 397.5748 | 2091.7073 | 397.5748 | 343.2214 | 335.9007
2092.7073 | 1837.7073 | 343.2957 | 335.9411 | 397.8398 | 2092.7073 | 397.8398 | 343.2957 | 335.9411
2093.7073 | 1838.7073 | 343.3555 | 335.9895 | 397.9047 | 2093.7073 | 397.9047 | 343.3555 | 335.9895
2094.7073 | 1839.7073 | 343.4231 | 336.0374 | 398.2466 | 2094.7073 | 398.2466 | 343.4231 | 336.0374
2095.7073 | 1840.7073 | 343.473 | 336.0657 | 399.3433 | 2095.7073 | 399.3433 | 343.473 | 336.0657
2096.7073 | 1841.7073 | 343.5472 | 336.1165 | 401.2298 | 2096.7073 | 401.2298 | 343.5472 | 336.1165
2097.7073 | 1842.7073 | 343.6142 | 336.1633 | 403.584 | 2097.7073 | 403.584 | 343.6142 | 336.1633
2098.7073 | 1843.7073 | 343.6466 | 336.1978 | 406.2202 | 2098.7073 | 406.2202 | 343.6466 | 336.1978
2099.8479 | 1844.8479 | 343.7312 | 336.2437 | 409.686 | 2099.8479 | 409.686 | 343.7312 | 336.2437
2100.7073 | 1845.7073 | 343.7896 | 336.2796 | 412.5566 | 2100.7073 | 412.5566 | 343.7896 | 336.2796
2101.7073 | 1846.7073 | 343.8285 | 336.3176 | 415.8007 | 2101.7073 | 415.8007 | 343.8285 | 336.3176
2102.7073 | 1847.7073 | 343.8847 | 336.3657 | 419.0715 | 2102.7073 | 419.0715 | 343.8847 | 336.3657
2103.7698 | 1848.7698 | 343.9521 | 336.4072 | 422.1866 | 2103.7698 | 422.1866 | 343.9521 | 336.4072
2104.7385 | 1849.7385 | 344.0266 | 336.4526 | 424.7278 | 2104.7385 | 424.7278 | 344.0266 | 336.4526
2105.7229 | 1850.7229 | 344.0755 | 336.4917 | 426.972 | 2105.7229 | 426.972 | 344.0755 | 336.4917
2106.7542 | 1851.7542 | 344.1296 | 336.537 | 429.0774 | 2106.7542 | 429.0774 | 344.1296 | 336.537
2107.7073 | 1852.7073 | 344.2157 | 336.5821 | 430.5741 | 2107.7073 | 430.5741 | 344.2157 | 336.5821
2108.7229 | 1853.7229 | 344.2715 | 336.6319 | 431.8737 | 2108.7229 | 431.8737 | 344.2715 | 336.6319
2109.7073 | 1854.7073 | 344.3305 | 336.6896 | 432.8473 | 2109.7073 | 432.8473 | 344.3305 | 336.6896
2110.7073 | 1855.7073 | 344.4196 | 336.74 | 433.7104 | 2110.7073 | 433.7104 | 344.4196 | 336.74
2111.7073 | 1856.7073 | 344.4901 | 336.791 | 434.3551 | 2111.7073 | 434.3551 | 344.4901 | 336.791
2112.7073 | 1857.7073 | 344.5802 | 336.8565 | 434.7449 | 2112.7073 | 434.7449 | 344.5802 | 336.8565
2113.7073 | 1858.7073 | 344.6494 | 336.9349 | 434.9329 | 2113.7073 | 434.9329 | 344.6494 | 336.9349
2114.7073 | 1859.7073 | 344.7254 | 336.9891 | 434.9663 | 2114.7073 | 434.9663 | 344.7254 | 336.9891
2115.7073 | 1860.7073 | 344.8012 | 337.0694 | 434.9638 | 2115.7073 | 434.9638 | 344.8012 | 337.0694
2116.7073 | 1861.7073 | 344.9029 | 337.1222 | 435.0014 | 2116.7073 | 435.0014 | 344.9029 | 337.1222
2117.7073 | 1862.7073 | 344.9946 | 337.1983 | 434.8874 | 2117.7073 | 434.8874 | 344.9946 | 337.1983
2118.7073 | 1863.7073 | 345.0849 | 337.2908 | 434.7706 | 2118.7073 | 434.7706 | 345.0849 | 337.2908
2119.7073 | 1864.7073 | 345.1842 | 337.3776 | 434.6215 | 2119.7073 | 434.6215 | 345.1842 | 337.3776
2120.7073 | 1865.7073 | 345.2913 | 337.4552 | 434.3603 | 2120.7073 | 434.3603 | 345.2913 | 337.4552
2121.7073 | 1866.7073 | 345.3923 | 337.5505 | 434.0428 | 2121.7073 | 434.0428 | 345.3923 | 337.5505
2122.7073 | 1867.7073 | 345.514 | 337.6531 | 433.8421 | 2122.7073 | 433.8421 | 345.514 | 337.6531
2123.7073 | 1868.7073 | 345.6172 | 337.7471 | 433.6576 | 2123.7073 | 433.6576 | 345.6172 | 337.7471
2124.7073 | 1869.7073 | 345.7352 | 337.8458 | 433.4126 | 2124.7073 | 433.4126 | 345.7352 | 337.8458
2125.7073 | 1870.7073 | 345.8543 | 337.9555 | 433.061 | 2125.7073 | 433.061 | 345.8543 | 337.9555
2126.7073 | 1871.7073 | 345.9744 | 338.0576 | 432.945 | 2126.7073 | 432.945 | 345.9744 | 338.0576
2127.7073 | 1872.7073 | 346.1076 | 338.1722 | 432.8934 | 2127.7073 | 432.8934 | 346.1076 | 338.1722
2128.7073 | 1873.7073 | 346.2316 | 338.2877 | 432.7122 | 2128.7073 | 432.7122 | 346.2316 | 338.2877
2129.7073 | 1874.7073 | 346.3661 | 338.4053 | 432.4242 | 2129.7073 | 432.4242 | 346.3661 | 338.4053
2130.7073 | 1875.7073 | 346.4786 | 338.5227 | 432.1997 | 2130.7073 | 432.1997 | 346.4786 | 338.5227
2131.7073 | 1876.7073 | 346.6299 | 338.6464 | 432.148 | 2131.7073 | 432.148 | 346.6299 | 338.6464
2132.7073 | 1877.7073 | 346.7631 | 338.7748 | 432.1124 | 2132.7073 | 432.1124 | 346.7631 | 338.7748
2133.7073 | 1878.7073 | 346.9108 | 338.904 | 431.9088 | 2133.7073 | 431.9088 | 346.9108 | 338.904
2134.7073 | 1879.7073 | 347.0478 | 339.0407 | 431.9357 | 2134.7073 | 431.9357 | 347.0478 | 339.0407
2135.7073 | 1880.7073 | 347.1987 | 339.1688 | 431.8982 | 2135.7073 | 431.8982 | 347.1987 | 339.1688
2136.7073 | 1881.7073 | 347.344 | 339.2872 | 431.865 | 2136.7073 | 431.865 | 347.344 | 339.2872
2137.7073 | 1882.7073 | 347.4809 | 339.4236 | 431.7518 | 2137.7073 | 431.7518 | 347.4809 | 339.4236
2138.7073 | 1883.7073 | 347.6085 | 339.5677 | 431.6354 | 2138.7073 | 431.6354 | 347.6085 | 339.5677
2139.7073 | 1884.7073 | 347.7798 | 339.7037 | 431.6955 | 2139.7073 | 431.6955 | 347.7798 | 339.7037
2140.7073 | 1885.7073 | 347.9401 | 339.8384 | 431.9089 | 2140.7073 | 431.9089 | 347.9401 | 339.8384
2141.7073 | 1886.7073 | 348.0888 | 339.9853 | 432.0629 | 2141.7073 | 432.0629 | 348.0888 | 339.9853
2142.7073 | 1887.7073 | 348.247 | 340.1234 | 432.0767 | 2142.7073 | 432.0767 | 348.247 | 340.1234
2143.7073 | 1888.7073 | 348.399 | 340.2674 | 431.9763 | 2143.7073 | 431.9763 | 348.399 | 340.2674
2144.7073 | 1889.7073 | 348.5571 | 340.4079 | 432.0373 | 2144.7073 | 432.0373 | 348.5571 | 340.4079
2145.7073 | 1890.7073 | 348.6977 | 340.5587 | 432.1259 | 2145.7073 | 432.1259 | 348.6977 | 340.5587
2146.7073 | 1891.7073 | 348.8533 | 340.6948 | 432.3816 | 2146.7073 | 432.3816 | 348.8533 | 340.6948
2147.7073 | 1892.7073 | 349.0257 | 340.8281 | 432.3973 | 2147.7073 | 432.3973 | 349.0257 | 340.8281
2148.7073 | 1893.7073 | 349.1672 | 340.9807 | 432.3444 | 2148.7073 | 432.3444 | 349.1672 | 340.9807
2149.7073 | 1894.7073 | 349.3319 | 341.1309 | 432.3397 | 2149.7073 | 432.3397 | 349.3319 | 341.1309
2150.7073 | 1895.7073 | 349.49 | 341.2834 | 432.5458 | 2150.7073 | 432.5458 | 349.49 | 341.2834
2151.7073 | 1896.7073 | 349.6508 | 341.4285 | 432.7062 | 2151.7073 | 432.7062 | 349.6508 | 341.4285
2152.7073 | 1897.7073 | 349.8056 | 341.5721 | 432.8618 | 2152.7073 | 432.8618 | 349.8056 | 341.5721
2153.7073 | 1898.7073 | 349.9539 | 341.7247 | 433.0245 | 2153.7073 | 433.0245 | 349.9539 | 341.7247
2154.7073 | 1899.7073 | 350.1347 | 341.8718 | 433.141 | 2154.7073 | 433.141 | 350.1347 | 341.8718
2155.7073 | 1900.7073 | 350.2858 | 342.0281 | 433.195 | 2155.7073 | 433.195 | 350.2858 | 342.0281
2156.7073 | 1901.7073 | 350.4442 | 342.177 | 433.1573 | 2156.7073 | 433.1573 | 350.4442 | 342.177
2157.7073 | 1902.7073 | 350.6001 | 342.3256 | 433.1672 | 2157.7073 | 433.1672 | 350.6001 | 342.3256
2158.7073 | 1903.7073 | 350.7683 | 342.4637 | 433.2924 | 2158.7073 | 433.2924 | 350.7683 | 342.4637
2159.7073 | 1904.7073 | 350.9253 | 342.6202 | 433.6045 | 2159.7073 | 433.6045 | 350.9253 | 342.6202
2160.7073 | 1905.7073 | 351.0661 | 342.7764 | 433.7658 | 2160.7073 | 433.7658 | 351.0661 | 342.7764
2161.7073 | 1906.7073 | 351.2434 | 342.915 | 433.8444 | 2161.7073 | 433.8444 | 351.2434 | 342.915
2162.7073 | 1907.7073 | 351.4034 | 343.0759 | 433.8388 | 2162.7073 | 433.8388 | 351.4034 | 343.0759
2163.7073 | 1908.7073 | 351.5522 | 343.2249 | 433.8749 | 2163.7073 | 433.8749 | 351.5522 | 343.2249
2164.7073 | 1909.7073 | 351.7178 | 343.3663 | 434.0915 | 2164.7073 | 434.0915 | 351.7178 | 343.3663
2165.7073 | 1910.7073 | 351.8555 | 343.5097 | 434.252 | 2165.7073 | 434.252 | 351.8555 | 343.5097
2166.7073 | 1911.7073 | 352.0303 | 343.6664 | 434.3111 | 2166.7073 | 434.3111 | 352.0303 | 343.6664
2167.7073 | 1912.7073 | 352.1839 | 343.8223 | 434.3759 | 2167.7073 | 434.3759 | 352.1839 | 343.8223
2168.7073 | 1913.7073 | 352.3333 | 343.9749 | 434.446 | 2168.7073 | 434.446 | 352.3333 | 343.9749
2169.7073 | 1914.7073 | 352.4913 | 344.1126 | 434.4815 | 2169.7073 | 434.4815 | 352.4913 | 344.1126
2170.7073 | 1915.7073 | 352.6444 | 344.2654 | 434.4638 | 2170.7073 | 434.4638 | 352.6444 | 344.2654
2171.7073 | 1916.7073 | 352.8152 | 344.4137 | 434.464 | 2171.7073 | 434.464 | 352.8152 | 344.4137
2172.7073 | 1917.7073 | 352.9767 | 344.5807 | 434.4403 | 2172.7073 | 434.4403 | 352.9767 | 344.5807
2173.7073 | 1918.7073 | 353.1274 | 344.7302 | 434.4745 | 2173.7073 | 434.4745 | 353.1274 | 344.7302
2174.7073 | 1919.7073 | 353.2811 | 344.8738 | 434.5672 | 2174.7073 | 434.5672 | 353.2811 | 344.8738
2175.7073 | 1920.7073 | 353.4505 | 345.019 | 434.7028 | 2175.7073 | 434.7028 | 353.4505 | 345.019
2176.7073 | 1921.7073 | 353.6047 | 345.1844 | 434.6314 | 2176.7073 | 434.6314 | 353.6047 | 345.1844
2177.7073 | 1922.7073 | 353.7602 | 345.3312 | 434.6115 | 2177.7073 | 434.6115 | 353.7602 | 345.3312
2178.7073 | 1923.7073 | 353.9348 | 345.4814 | 434.7541 | 2178.7073 | 434.7541 | 353.9348 | 345.4814
2179.7073 | 1924.7073 | 354.099 | 345.6397 | 434.8511 | 2179.7073 | 434.8511 | 354.099 | 345.6397
2180.7073 | 1925.7073 | 354.2513 | 345.782 | 434.8924 | 2180.7073 | 434.8924 | 354.2513 | 345.782
2181.7073 | 1926.7073 | 354.411 | 345.9287 | 434.8663 | 2181.7073 | 434.8663 | 354.411 | 345.9287
2182.7073 | 1927.7073 | 354.5692 | 346.0807 | 434.8704 | 2182.7073 | 434.8704 | 354.5692 | 346.0807
2183.7073 | 1928.7073 | 354.7266 | 346.2344 | 434.829 | 2183.7073 | 434.829 | 354.7266 | 346.2344
2184.7073 | 1929.7073 | 354.8902 | 346.3709 | 434.8254 | 2184.7073 | 434.8254 | 354.8902 | 346.3709
2185.7073 | 1930.7073 | 355.0443 | 346.5174 | 434.9594 | 2185.7073 | 434.9594 | 355.0443 | 346.5174
2186.7073 | 1931.7073 | 355.2051 | 346.6566 | 435.0239 | 2186.7073 | 435.0239 | 355.2051 | 346.6566
2187.7073 | 1932.7073 | 355.3591 | 346.8078 | 435.1479 | 2187.7073 | 435.1479 | 355.3591 | 346.8078
2188.7073 | 1933.7073 | 355.5123 | 346.9515 | 435.2475 | 2188.7073 | 435.2475 | 355.5123 | 346.9515
2189.7073 | 1934.7073 | 355.6827 | 347.0907 | 435.1857 | 2189.7073 | 435.1857 | 355.6827 | 347.0907
2190.7073 | 1935.7073 | 355.8426 | 347.2266 | 435.0625 | 2190.7073 | 435.0625 | 355.8426 | 347.2266
2191.7073 | 1936.7073 | 355.9768 | 347.3744 | 434.93 | 2191.7073 | 434.93 | 355.9768 | 347.3744
2192.7073 | 1937.7073 | 356.1487 | 347.5181 | 434.8861 | 2192.7073 | 434.8861 | 356.1487 | 347.5181
2193.7073 | 1938.7073 | 356.3078 | 347.6567 | 434.8428 | 2193.7073 | 434.8428 | 356.3078 | 347.6567
2194.7073 | 1939.7073 | 356.4593 | 347.8023 | 434.8647 | 2194.7073 | 434.8647 | 356.4593 | 347.8023
2195.7073 | 1940.7073 | 356.6237 | 347.9423 | 434.7595 | 2195.7073 | 434.7595 | 356.6237 | 347.9423
2196.7073 | 1941.7073 | 356.767 | 348.0801 | 434.7668 | 2196.7073 | 434.7668 | 356.767 | 348.0801
2197.7073 | 1942.7073 | 356.933 | 348.2272 | 434.9872 | 2197.7073 | 434.9872 | 356.933 | 348.2272
2198.7073 | 1943.7073 | 357.0775 | 348.3703 | 435.0508 | 2198.7073 | 435.0508 | 357.0775 | 348.3703
2199.7073 | 1944.7073 | 357.2346 | 348.514 | 434.9582 | 2199.7073 | 434.9582 | 357.2346 | 348.514
2200.7073 | 1945.7073 | 357.394 | 348.6503 | 434.8247 | 2200.7073 | 434.8247 | 357.394 | 348.6503
2201.7073 | 1946.7073 | 357.5109 | 348.7934 | 434.8215 | 2201.7073 | 434.8215 | 357.5109 | 348.7934
2202.7073 | 1947.7073 | 357.6553 | 348.9302 | 434.7699 | 2202.7073 | 434.7699 | 357.6553 | 348.9302
2203.7073 | 1948.7073 | 357.8023 | 349.0799 | 434.8183 | 2203.7073 | 434.8183 | 357.8023 | 349.0799
2204.7073 | 1949.7073 | 357.9564 | 349.2132 | 434.8993 | 2204.7073 | 434.8993 | 357.9564 | 349.2132
2205.7073 | 1950.7073 | 358.0948 | 349.3502 | 434.9023 | 2205.7073 | 434.9023 | 358.0948 | 349.3502
2206.7073 | 1951.7073 | 358.2469 | 349.4873 | 434.8342 | 2206.7073 | 434.8342 | 358.2469 | 349.4873
2207.7073 | 1952.7073 | 358.3973 | 349.6262 | 434.8211 | 2207.7073 | 434.8211 | 358.3973 | 349.6262
2208.7073 | 1953.7073 | 358.5564 | 349.7719 | 434.7974 | 2208.7073 | 434.7974 | 358.5564 | 349.7719
2209.7073 | 1954.7073 | 358.704 | 349.914 | 434.6535 | 2209.7073 | 434.6535 | 358.704 | 349.914
2210.7073 | 1955.7073 | 358.842 | 350.0591 | 434.5097 | 2210.7073 | 434.5097 | 358.842 | 350.0591
2211.7073 | 1956.7073 | 359.0091 | 350.2029 | 434.387 | 2211.7073 | 434.387 | 359.0091 | 350.2029
2212.7073 | 1957.7073 | 359.1421 | 350.3413 | 434.3359 | 2212.7073 | 434.3359 | 359.1421 | 350.3413
2213.7073 | 1958.7073 | 359.3 | 350.4821 | 434.2076 | 2213.7073 | 434.2076 | 359.3 | 350.4821
2214.7073 | 1959.7073 | 359.4743 | 350.6272 | 434.2551 | 2214.7073 | 434.2551 | 359.4743 | 350.6272
2215.7073 | 1960.7073 | 359.6268 | 350.7645 | 434.1444 | 2215.7073 | 434.1444 | 359.6268 | 350.7645
2216.7073 | 1961.7073 | 359.774 | 350.9049 | 433.914 | 2216.7073 | 433.914 | 359.774 | 350.9049
2217.7073 | 1962.7073 | 359.918 | 351.0429 | 433.7524 | 2217.7073 | 433.7524 | 359.918 | 351.0429
2218.7073 | 1963.7073 | 360.0652 | 351.1864 | 433.6427 | 2218.7073 | 433.6427 | 360.0652 | 351.1864
2219.7073 | 1964.7073 | 360.23 | 351.3278 | 433.6375 | 2219.7073 | 433.6375 | 360.23 | 351.3278
2220.7073 | 1965.7073 | 360.3869 | 351.4663 | 433.6749 | 2220.7073 | 433.6749 | 360.3869 | 351.4663
2221.7073 | 1966.7073 | 360.5503 | 351.598 | 433.7378 | 2221.7073 | 433.7378 | 360.5503 | 351.598
2222.7073 | 1967.7073 | 360.692 | 351.7458 | 433.56 | 2222.7073 | 433.56 | 360.692 | 351.7458
2223.7073 | 1968.7073 | 360.8602 | 351.879 | 433.4427 | 2223.7073 | 433.4427 | 360.8602 | 351.879
2224.7073 | 1969.7073 | 361.0211 | 352.0102 | 433.4432 | 2224.7073 | 433.4432 | 361.0211 | 352.0102
2225.7073 | 1970.7073 | 360.738 | 352.1378 | 433.4906 | 2225.7073 | 433.4906 | 360.738 | 352.1378
2226.7073 | 1971.7073 | 360.7811 | 352.2706 | 433.5121 | 2226.7073 | 433.5121 | 360.7811 | 352.2706
2227.7073 | 1972.7073 | 360.9241 | 352.4033 | 433.6405 | 2227.7073 | 433.6405 | 360.9241 | 352.4033
2228.7073 | 1973.7073 | 361.0517 | 352.5473 | 433.6458 | 2228.7073 | 433.6458 | 361.0517 | 352.5473
2229.7073 | 1974.7073 | 361.1759 | 352.681 | 433.5314 | 2229.7073 | 433.5314 | 361.1759 | 352.681
2230.7073 | 1975.7073 | 361.2931 | 352.8093 | 433.3748 | 2230.7073 | 433.3748 | 361.2931 | 352.8093
2231.7073 | 1976.7073 | 361.3874 | 352.9469 | 433.2961 | 2231.7073 | 433.2961 | 361.3874 | 352.9469
2232.7073 | 1977.7073 | 361.5627 | 353.0851 | 433.3425 | 2232.7073 | 433.3425 | 361.5627 | 353.0851
2233.7073 | 1978.7073 | 361.6813 | 353.2239 | 433.3589 | 2233.7073 | 433.3589 | 361.6813 | 353.2239
2234.7073 | 1979.7073 | 361.8132 | 353.3587 | 433.4172 | 2234.7073 | 433.4172 | 361.8132 | 353.3587
2235.7073 | 1980.7073 | 361.9663 | 353.4935 | 433.4207 | 2235.7073 | 433.4207 | 361.9663 | 353.4935
2236.7073 | 1981.7073 | 362.0968 | 353.6229 | 433.5901 | 2236.7073 | 433.5901 | 362.0968 | 353.6229
2237.7073 | 1982.7073 | 362.2183 | 353.7495 | 433.6269 | 2237.7073 | 433.6269 | 362.2183 | 353.7495
2238.7073 | 1983.7073 | 362.3453 | 353.8764 | 433.6428 | 2238.7073 | 433.6428 | 362.3453 | 353.8764
2239.7073 | 1984.7073 | 362.4467 | 354.0116 | 433.6229 | 2239.7073 | 433.6229 | 362.4467 | 354.0116
2240.7073 | 1985.7073 | 362.0987 | 354.1456 | 433.6281 | 2240.7073 | 433.6281 | 362.0987 | 354.1456
2241.7073 | 1986.7073 | 362.3271 | 354.2746 | 433.7392 | 2241.7073 | 433.7392 | 362.3271 | 354.2746
2242.7073 | 1987.7073 | 362.5179 | 354.3967 | 433.8344 | 2242.7073 | 433.8344 | 362.5179 | 354.3967
2243.7073 | 1988.7073 | 362.676 | 354.5297 | 433.9433 | 2243.7073 | 433.9433 | 362.676 | 354.5297
2244.7073 | 1989.7073 | 362.8279 | 354.6593 | 433.7968 | 2244.7073 | 433.7968 | 362.8279 | 354.6593
2245.7073 | 1990.7073 | 362.99 | 354.7772 | 433.8229 | 2245.7073 | 433.8229 | 362.99 | 354.7772
2246.7073 | 1991.7073 | 363.1353 | 354.9143 | 433.6689 | 2246.7073 | 433.6689 | 363.1353 | 354.9143
2247.7073 | 1992.7073 | 363.2961 | 355.0464 | 433.6169 | 2247.7073 | 433.6169 | 363.2961 | 355.0464
2248.7073 | 1993.7073 | 363.472 | 355.1601 | 433.5865 | 2248.7073 | 433.5865 | 363.472 | 355.1601
2249.7073 | 1994.7073 | 363.608 | 355.2527 | 433.6111 | 2249.7073 | 433.6111 | 363.608 | 355.2527
2250.7073 | 1995.7073 | 363.7477 | 355.345 | 433.6654 | 2250.7073 | 433.6654 | 363.7477 | 355.345
2251.7073 | 1996.7073 | 363.9034 | 355.4474 | 433.6018 | 2251.7073 | 433.6018 | 363.9034 | 355.4474
2252.7073 | 1997.7073 | 364.0342 | 355.5475 | 433.5484 | 2252.7073 | 433.5484 | 364.0342 | 355.5475
2253.7073 | 1998.7073 | 364.1424 | 355.6082 | 433.6267 | 2253.7073 | 433.6267 | 364.1424 | 355.6082
2254.7073 | 1999.7073 | 364.2829 | 355.7235 | 433.6013 | 2254.7073 | 433.6013 | 364.2829 | 355.7235
2255.7229 | 2000.7229 | 364.3966 | 355.8475 | 433.5141 | 2255.7229 | 433.5141 | 364.3966 | 355.8475
2256.8323 | 2001.8323 | 364.5784 | 355.9947 | 433.4818 | 2256.8323 | 433.4818 | 364.5784 | 355.9947
2257.7385 | 2002.7385 | 364.7016 | 356.1045 | 433.3869 | 2257.7385 | 433.3869 | 364.7016 | 356.1045
2258.7229 | 2003.7229 | 364.7987 | 356.219 | 433.2143 | 2258.7229 | 433.2143 | 364.7987 | 356.219
2259.7073 | 2004.7073 | 364.9157 | 356.3455 | 433.152 | 2259.7073 | 433.152 | 364.9157 | 356.3455
2260.7073 | 2005.7073 | 365.0319 | 356.4698 | 433.0246 | 2260.7073 | 433.0246 | 365.0319 | 356.4698
2261.7385 | 2006.7385 | 365.1381 | 356.5829 | 433.0627 | 2261.7385 | 433.0627 | 365.1381 | 356.5829
2262.7073 | 2007.7073 | 365.228 | 356.6948 | 433.1161 | 2262.7073 | 433.1161 | 365.228 | 356.6948
2263.7073 | 2008.7073 | 365.3318 | 356.7951 | 433.0915 | 2263.7073 | 433.0915 | 365.3318 | 356.7951
2264.7073 | 2009.7073 | 365.4263 | 356.9161 | 433.1102 | 2264.7073 | 433.1102 | 365.4263 | 356.9161
2265.7073 | 2010.7073 | 365.5241 | 357.0213 | 433.1391 | 2265.7073 | 433.1391 | 365.5241 | 357.0213
2266.7073 | 2011.7073 | 365.6152 | 357.1184 | 433.0206 | 2266.7073 | 433.0206 | 365.6152 | 357.1184
2267.7073 | 2012.7073 | 365.6817 | 357.223 | 433.0723 | 2267.7073 | 433.0723 | 365.6817 | 357.223
2268.7073 | 2013.7073 | 365.7728 | 357.3367 | 433.1713 | 2268.7073 | 433.1713 | 365.7728 | 357.3367
2269.7073 | 2014.7073 | 365.852 | 357.4315 | 433.1263 | 2269.7073 | 433.1263 | 365.852 | 357.4315
2270.7073 | 2015.7073 | 365.936 | 357.5245 | 433.1196 | 2270.7073 | 433.1196 | 365.936 | 357.5245
2271.7073 | 2016.7073 | 366.0282 | 357.6329 | 433.193 | 2271.7073 | 433.193 | 366.0282 | 357.6329
2272.7073 | 2017.7073 | 366.1251 | 357.7285 | 433.4034 | 2272.7073 | 433.4034 | 366.1251 | 357.7285
2273.7073 | 2018.7073 | 366.2098 | 357.8259 | 433.4924 | 2273.7073 | 433.4924 | 366.2098 | 357.8259
2274.7073 | 2019.7073 | 366.3062 | 357.9244 | 433.4411 | 2274.7073 | 433.4411 | 366.3062 | 357.9244
2275.7073 | 2020.7073 | 366.3952 | 358.0327 | 433.4667 | 2275.7073 | 433.4667 | 366.3952 | 358.0327
2276.7073 | 2021.7073 | 366.4656 | 358.1394 | 433.4917 | 2276.7073 | 433.4917 | 366.4656 | 358.1394
2277.7073 | 2022.7073 | 366.5584 | 358.2481 | 433.5208 | 2277.7073 | 433.5208 | 366.5584 | 358.2481
2278.7073 | 2023.7073 | 366.6437 | 358.3581 | 433.5216 | 2278.7073 | 433.5216 | 366.6437 | 358.3581
2279.7073 | 2024.7073 | 366.7247 | 358.4558 | 433.5097 | 2279.7073 | 433.5097 | 366.7247 | 358.4558
2280.7073 | 2025.7073 | 366.8077 | 358.5625 | 433.5083 | 2280.7073 | 433.5083 | 366.8077 | 358.5625
2281.7073 | 2026.7073 | 366.8917 | 358.6685 | 433.6133 | 2281.7073 | 433.6133 | 366.8917 | 358.6685
2282.7073 | 2027.7073 | 366.9943 | 358.7864 | 433.667 | 2282.7073 | 433.667 | 366.9943 | 358.7864
2283.7073 | 2028.7073 | 367.0758 | 358.8999 | 433.6085 | 2283.7073 | 433.6085 | 367.0758 | 358.8999
2284.7073 | 2029.7073 | 367.1609 | 359.0089 | 433.785 | 2284.7073 | 433.785 | 367.1609 | 359.0089
2285.7073 | 2030.7073 | 367.2505 | 359.1167 | 433.7898 | 2285.7073 | 433.7898 | 367.2505 | 359.1167
2286.7073 | 2031.7073 | 367.337 | 359.234 | 433.8706 | 2286.7073 | 433.8706 | 367.337 | 359.234
2287.7073 | 2032.7073 | 367.4191 | 359.3482 | 433.9478 | 2287.7073 | 433.9478 | 367.4191 | 359.3482
2288.7698 | 2033.7698 | 367.5172 | 359.4707 | 434.181 | 2288.7698 | 434.181 | 367.5172 | 359.4707
2289.7854 | 2034.7854 | 367.6244 | 359.5851 | 434.2971 | 2289.7854 | 434.2971 | 367.6244 | 359.5851
2290.7073 | 2035.7073 | 367.7135 | 359.6775 | 434.3502 | 2290.7073 | 434.3502 | 367.7135 | 359.6775
2291.7073 | 2036.7073 | 367.8053 | 359.7942 | 434.3859 | 2291.7073 | 434.3859 | 367.8053 | 359.7942
2292.7073 | 2037.7073 | 367.9007 | 359.9191 | 434.432 | 2292.7073 | 434.432 | 367.9007 | 359.9191
2293.7073 | 2038.7073 | 367.9842 | 360.0336 | 434.3652 | 2293.7073 | 434.3652 | 367.9842 | 360.0336
2294.7073 | 2039.7073 | 368.0716 | 360.1424 | 434.2625 | 2294.7073 | 434.2625 | 368.0716 | 360.1424
2295.8323 | 2040.8323 | 368.2014 | 360.2677 | 434.2068 | 2295.8323 | 434.2068 | 368.2014 | 360.2677
2296.801 | 2041.801 | 368.2866 | 360.3732 | 434.2006 | 2296.801 | 434.2006 | 368.2866 | 360.3732
2297.7229 | 2042.7229 | 368.3946 | 360.4749 | 434.0932 | 2297.7229 | 434.0932 | 368.3946 | 360.4749
2298.7073 | 2043.7073 | 368.5022 | 360.5828 | 433.9797 | 2298.7073 | 433.9797 | 368.5022 | 360.5828
2299.7073 | 2044.7073 | 368.6003 | 360.6989 | 433.8331 | 2299.7073 | 433.8331 | 368.6003 | 360.6989
2300.7073 | 2045.7073 | 368.7059 | 360.8166 | 433.9657 | 2300.7073 | 433.9657 | 368.7059 | 360.8166
2301.7073 | 2046.7073 | 368.8245 | 360.9397 | 434.0974 | 2301.7073 | 434.0974 | 368.8245 | 360.9397
2302.7073 | 2047.7073 | 368.9222 | 361.0547 | 434.1668 | 2302.7073 | 434.1668 | 368.9222 | 361.0547
2303.7073 | 2048.7073 | 369.0142 | 361.1985 | 434.1057 | 2303.7073 | 434.1057 | 369.0142 | 361.1985
2304.7073 | 2049.7073 | 369.1055 | 361.343 | 434.0592 | 2304.7073 | 434.0592 | 369.1055 | 361.343
2305.7073 | 2050.7073 | 369.2278 | 361.4292 | 434.1221 | 2305.7073 | 434.1221 | 369.2278 | 361.4292
2306.7073 | 2051.7073 | 369.3303 | 361.5642 | 434.259 | 2306.7073 | 434.259 | 369.3303 | 361.5642
2307.7073 | 2052.7073 | 369.4464 | 361.6912 | 434.2861 | 2307.7073 | 434.2861 | 369.4464 | 361.6912
2308.7073 | 2053.7073 | 369.5614 | 361.8006 | 434.2416 | 2308.7073 | 434.2416 | 369.5614 | 361.8006
2309.7073 | 2054.7073 | 369.6617 | 361.9156 | 434.272 | 2309.7073 | 434.272 | 369.6617 | 361.9156
2310.7073 | 2055.7073 | 369.7861 | 362.0369 | 434.3724 | 2310.7073 | 434.3724 | 369.7861 | 362.0369
2311.7073 | 2056.7073 | 369.8948 | 362.1551 | 434.2579 | 2311.7073 | 434.2579 | 369.8948 | 362.1551
2312.7073 | 2057.7073 | 369.9854 | 362.2658 | 434.1935 | 2312.7073 | 434.1935 | 369.9854 | 362.2658
2313.7073 | 2058.7073 | 370.0933 | 362.367 | 434.1135 | 2313.7073 | 434.1135 | 370.0933 | 362.367
2314.7073 | 2059.7073 | 370.1952 | 362.4892 | 434.0092 | 2314.7073 | 434.0092 | 370.1952 | 362.4892
2315.7073 | 2060.7073 | 370.2804 | 362.5961 | 433.9908 | 2315.7073 | 433.9908 | 370.2804 | 362.5961
2316.7073 | 2061.7073 | 370.3907 | 362.7077 | 434.0444 | 2316.7073 | 434.0444 | 370.3907 | 362.7077
2317.7073 | 2062.7073 | 370.4792 | 362.8088 | 434.0372 | 2317.7073 | 434.0372 | 370.4792 | 362.8088
2318.7073 | 2063.7073 | 370.5715 | 362.9164 | 434.066 | 2318.7073 | 434.066 | 370.5715 | 362.9164
2319.7073 | 2064.7073 | 370.6743 | 363.0323 | 434.0719 | 2319.7073 | 434.0719 | 370.6743 | 363.0323
2320.7073 | 2065.7073 | 370.7621 | 363.1371 | 434.2063 | 2320.7073 | 434.2063 | 370.7621 | 363.1371
2321.7073 | 2066.7073 | 370.8622 | 363.2477 | 434.2349 | 2321.7073 | 434.2349 | 370.8622 | 363.2477
2322.7073 | 2067.7073 | 370.9541 | 363.3574 | 434.1984 | 2322.7073 | 434.1984 | 370.9541 | 363.3574
2323.7073 | 2068.7073 | 371.0498 | 363.4702 | 434.0919 | 2323.7073 | 434.0919 | 371.0498 | 363.4702
2324.7073 | 2069.7073 | 371.1438 | 363.5724 | 434.1167 | 2324.7073 | 434.1167 | 371.1438 | 363.5724
2325.7073 | 2070.7073 | 371.2279 | 363.6724 | 434.1953 | 2325.7073 | 434.1953 | 371.2279 | 363.6724
2326.7073 | 2071.7073 | 371.3203 | 363.772 | 434.2061 | 2326.7073 | 434.2061 | 371.3203 | 363.772
2327.7073 | 2072.7073 | 371.4269 | 363.8767 | 434.2423 | 2327.7073 | 434.2423 | 371.4269 | 363.8767
2328.7073 | 2073.7073 | 371.5032 | 363.9821 | 434.297 | 2328.7073 | 434.297 | 371.5032 | 363.9821
2329.7073 | 2074.7073 | 371.6016 | 364.0904 | 434.1354 | 2329.7073 | 434.1354 | 371.6016 | 364.0904
2330.7073 | 2075.7073 | 371.6977 | 364.1874 | 434.0115 | 2330.7073 | 434.0115 | 371.6977 | 364.1874
2331.7073 | 2076.7073 | 371.786 | 364.2869 | 433.9282 | 2331.7073 | 433.9282 | 371.786 | 364.2869
2332.7073 | 2077.7073 | 371.8738 | 364.3895 | 433.8604 | 2332.7073 | 433.8604 | 371.8738 | 364.3895
2333.7073 | 2078.7073 | 371.9669 | 364.4877 | 433.8053 | 2333.7073 | 433.8053 | 371.9669 | 364.4877
2334.7073 | 2079.7073 | 372.0529 | 364.5852 | 433.6686 | 2334.7073 | 433.6686 | 372.0529 | 364.5852
2335.7073 | 2080.7073 | 372.1674 | 364.6871 | 433.7593 | 2335.7073 | 433.7593 | 372.1674 | 364.6871
2336.7073 | 2081.7073 | 372.2693 | 364.778 | 433.8422 | 2336.7073 | 433.8422 | 372.2693 | 364.778
2337.7073 | 2082.7073 | 372.3591 | 364.8781 | 433.7183 | 2337.7073 | 433.7183 | 372.3591 | 364.8781
2338.7073 | 2083.7073 | 372.4288 | 364.9815 | 433.8263 | 2338.7073 | 433.8263 | 372.4288 | 364.9815
2339.7073 | 2084.7073 | 372.5343 | 365.072 | 433.773 | 2339.7073 | 433.773 | 372.5343 | 365.072
2340.7073 | 2085.7073 | 372.6166 | 365.1688 | 433.7087 | 2340.7073 | 433.7087 | 372.6166 | 365.1688
2341.7073 | 2086.7073 | 372.7006 | 365.2615 | 433.545 | 2341.7073 | 433.545 | 372.7006 | 365.2615
2342.7073 | 2087.7073 | 372.8027 | 365.3576 | 433.4431 | 2342.7073 | 433.4431 | 372.8027 | 365.3576
2343.7073 | 2088.7073 | 372.8677 | 365.442 | 433.4435 | 2343.7073 | 433.4435 | 372.8677 | 365.442
2344.7073 | 2089.7073 | 372.9764 | 365.5395 | 433.3112 | 2344.7073 | 433.3112 | 372.9764 | 365.5395
2345.7073 | 2090.7073 | 373.0631 | 365.6427 | 433.1886 | 2345.7073 | 433.1886 | 373.0631 | 365.6427
2346.7073 | 2091.7073 | 373.1404 | 365.7323 | 433.1495 | 2346.7073 | 433.1495 | 373.1404 | 365.7323
2347.7073 | 2092.7073 | 373.2213 | 365.8196 | 433.1151 | 2347.7073 | 433.1151 | 373.2213 | 365.8196
2348.7073 | 2093.7073 | 373.3013 | 365.9018 | 433.0617 | 2348.7073 | 433.0617 | 373.3013 | 365.9018
2349.7073 | 2094.7073 | 373.3753 | 366.0029 | 432.925 | 2349.7073 | 432.925 | 373.3753 | 366.0029
2350.7073 | 2095.7073 | 373.4618 | 366.0943 | 432.8293 | 2350.7073 | 432.8293 | 373.4618 | 366.0943
2351.7073 | 2096.7073 | 373.5497 | 366.1723 | 432.796 | 2351.7073 | 432.796 | 373.5497 | 366.1723
2352.7073 | 2097.7073 | 373.6198 | 366.2617 | 432.8977 | 2352.7073 | 432.8977 | 373.6198 | 366.2617
2353.7073 | 2098.7073 | 373.6974 | 366.3549 | 432.9714 | 2353.7073 | 432.9714 | 373.6974 | 366.3549
2354.7073 | 2099.7073 | 373.7843 | 366.4426 | 432.8581 | 2354.7073 | 432.8581 | 373.7843 | 366.4426
2355.7073 | 2100.7073 | 373.8498 | 366.5315 | 432.7914 | 2355.7073 | 432.7914 | 373.8498 | 366.5315
2356.7073 | 2101.7073 | 373.9414 | 366.6128 | 432.6488 | 2356.7073 | 432.6488 | 373.9414 | 366.6128
2357.7073 | 2102.7073 | 374.0303 | 366.6996 | 432.6353 | 2357.7073 | 432.6353 | 374.0303 | 366.6996
2358.7073 | 2103.7073 | 374.0973 | 366.7848 | 432.5519 | 2358.7073 | 432.5519 | 374.0973 | 366.7848
2359.7073 | 2104.7073 | 374.1976 | 366.8688 | 432.4913 | 2359.7073 | 432.4913 | 374.1976 | 366.8688
2360.7073 | 2105.7073 | 374.2632 | 366.9536 | 432.441 | 2360.7073 | 432.441 | 374.2632 | 366.9536
2361.7073 | 2106.7073 | 374.3549 | 367.0463 | 432.415 | 2361.7073 | 432.415 | 374.3549 | 367.0463
2362.7073 | 2107.7073 | 374.4276 | 367.13 | 432.3798 | 2362.7073 | 432.3798 | 374.4276 | 367.13
2363.7073 | 2108.7073 | 374.5263 | 367.2149 | 432.4974 | 2363.7073 | 432.4974 | 374.5263 | 367.2149
2364.7073 | 2109.7073 | 374.5897 | 367.2882 | 432.7182 | 2364.7073 | 432.7182 | 374.5897 | 367.2882
2365.7073 | 2110.7073 | 374.6943 | 367.3916 | 432.9556 | 2365.7073 | 432.9556 | 374.6943 | 367.3916
2366.7073 | 2111.7073 | 374.7731 | 367.4841 | 433.0121 | 2366.7073 | 433.0121 | 374.7731 | 367.4841
2367.7073 | 2112.7073 | 374.8695 | 367.5886 | 433.0959 | 2367.7073 | 433.0959 | 374.8695 | 367.5886
2368.7073 | 2113.7073 | 374.9479 | 367.677 | 433.2155 | 2368.7073 | 433.2155 | 374.9479 | 367.677
2369.7073 | 2114.7073 | 375.0449 | 367.7861 | 433.2125 | 2369.7073 | 433.2125 | 375.0449 | 367.7861
2370.7073 | 2115.7073 | 375.1539 | 367.8814 | 433.222 | 2370.7073 | 433.222 | 375.1539 | 367.8814
2371.7073 | 2116.7073 | 375.2421 | 367.9807 | 433.3286 | 2371.7073 | 433.3286 | 375.2421 | 367.9807
2372.7073 | 2117.7073 | 375.3527 | 368.0807 | 433.4363 | 2372.7073 | 433.4363 | 375.3527 | 368.0807
2373.7073 | 2118.7073 | 375.4379 | 368.1773 | 433.4132 | 2373.7073 | 433.4132 | 375.4379 | 368.1773
2374.7073 | 2119.7073 | 375.5367 | 368.2856 | 433.3889 | 2374.7073 | 433.3889 | 375.5367 | 368.2856
2375.7073 | 2120.7073 | 375.6308 | 368.375 | 433.4704 | 2375.7073 | 433.4704 | 375.6308 | 368.375
2376.7073 | 2121.7073 | 375.7306 | 368.4449 | 433.4219 | 2376.7073 | 433.4219 | 375.7306 | 368.4449
2377.7073 | 2122.7073 | 375.814 | 368.5498 | 433.4366 | 2377.7073 | 433.4366 | 375.814 | 368.5498
2378.7073 | 2123.7073 | 375.9224 | 368.6474 | 433.5048 | 2378.7073 | 433.5048 | 375.9224 | 368.6474
2379.7073 | 2124.7073 | 376.0164 | 368.7217 | 433.6531 | 2379.7073 | 433.6531 | 376.0164 | 368.7217
2380.7073 | 2125.7073 | 376.1204 | 368.808 | 433.5396 | 2380.7073 | 433.5396 | 376.1204 | 368.808
2381.7073 | 2126.7073 | 376.202 | 368.9005 | 433.4433 | 2381.7073 | 433.4433 | 376.202 | 368.9005
2382.7073 | 2127.7073 | 376.2989 | 368.9886 | 433.4118 | 2382.7073 | 433.4118 | 376.2989 | 368.9886
2383.7073 | 2128.7073 | 376.3648 | 369.065 | 433.4844 | 2383.7073 | 433.4844 | 376.3648 | 369.065
2384.7073 | 2129.7073 | 376.4703 | 369.1459 | 433.3779 | 2384.7073 | 433.3779 | 376.4703 | 369.1459
2385.7073 | 2130.7073 | 376.5549 | 369.2301 | 433.3862 | 2385.7073 | 433.3862 | 376.5549 | 369.2301
2386.7073 | 2131.7073 | 376.6286 | 369.3063 | 433.5697 | 2386.7073 | 433.5697 | 376.6286 | 369.3063
2387.7854 | 2132.7854 | 376.7131 | 369.3943 | 433.7068 | 2387.7854 | 433.7068 | 376.7131 | 369.3943
2388.7542 | 2133.7542 | 376.8017 | 369.4598 | 433.6668 | 2388.7542 | 433.6668 | 376.8017 | 369.4598
2389.7229 | 2134.7229 | 376.8713 | 369.5483 | 433.5785 | 2389.7229 | 433.5785 | 376.8713 | 369.5483
2390.7073 | 2135.7073 | 376.9482 | 369.6212 | 433.5002 | 2390.7073 | 433.5002 | 376.9482 | 369.6212
2391.7073 | 2136.7073 | 377.0255 | 369.6643 | 433.5572 | 2391.7073 | 433.5572 | 377.0255 | 369.6643
2392.7073 | 2137.7073 | 377.1165 | 369.7677 | 433.6259 | 2392.7073 | 433.6259 | 377.1165 | 369.7677
2393.7073 | 2138.7073 | 377.1823 | 369.8574 | 433.5863 | 2393.7073 | 433.5863 | 377.1823 | 369.8574
2394.7073 | 2139.7073 | 377.2561 | 369.9162 | 433.5936 | 2394.7073 | 433.5936 | 377.2561 | 369.9162
2395.7073 | 2140.7073 | 377.3416 | 369.9929 | 433.4915 | 2395.7073 | 433.4915 | 377.3416 | 369.9929
2396.7073 | 2141.7073 | 377.4079 | 370.0753 | 433.5033 | 2396.7073 | 433.5033 | 377.4079 | 370.0753
2397.7073 | 2142.7073 | 377.4883 | 370.1524 | 433.5318 | 2397.7073 | 433.5318 | 377.4883 | 370.1524
2398.7073 | 2143.7073 | 377.5573 | 370.2201 | 433.6006 | 2398.7073 | 433.6006 | 377.5573 | 370.2201
2399.7073 | 2144.7073 | 377.6363 | 370.2869 | 433.648 | 2399.7073 | 433.648 | 377.6363 | 370.2869
2400.7073 | 2145.7073 | 377.706 | 370.3599 | 433.6078 | 2400.7073 | 433.6078 | 377.706 | 370.3599
2401.7073 | 2146.7073 | 377.79 | 370.4429 | 433.5461 | 2401.7073 | 433.5461 | 377.79 | 370.4429
2402.7073 | 2147.7073 | 377.8549 | 370.5049 | 433.3974 | 2402.7073 | 433.3974 | 377.8549 | 370.5049
2403.7073 | 2148.7073 | 377.9355 | 370.5815 | 433.4299 | 2403.7073 | 433.4299 | 377.9355 | 370.5815
2404.7073 | 2149.7073 | 378.0243 | 370.6445 | 433.4521 | 2404.7073 | 433.4521 | 378.0243 | 370.6445
2405.7073 | 2150.7073 | 378.0947 | 370.7125 | 433.4904 | 2405.7073 | 433.4904 | 378.0947 | 370.7125
2406.7073 | 2151.7073 | 378.167 | 370.7835 | 433.5287 | 2406.7073 | 433.5287 | 378.167 | 370.7835
2407.7073 | 2152.7073 | 378.2408 | 370.8463 | 433.5491 | 2407.7073 | 433.5491 | 378.2408 | 370.8463
2408.7073 | 2153.7073 | 378.3223 | 370.917 | 433.5534 | 2408.7073 | 433.5534 | 378.3223 | 370.917
2409.7073 | 2154.7073 | 378.3922 | 370.9772 | 433.41 | 2409.7073 | 433.41 | 378.3922 | 370.9772
2410.7073 | 2155.7073 | 378.4593 | 371.0498 | 433.3419 | 2410.7073 | 433.3419 | 378.4593 | 371.0498
2411.7073 | 2156.7073 | 378.5438 | 371.1147 | 433.3812 | 2411.7073 | 433.3812 | 378.5438 | 371.1147
2412.7073 | 2157.7073 | 378.5993 | 371.1745 | 433.2984 | 2412.7073 | 433.2984 | 378.5993 | 371.1745
2413.7073 | 2158.7073 | 378.6841 | 371.2395 | 433.1387 | 2413.7073 | 433.1387 | 378.6841 | 371.2395
2414.7073 | 2159.7073 | 378.7599 | 371.2934 | 432.9697 | 2414.7073 | 432.9697 | 378.7599 | 371.2934
2415.7073 | 2160.7073 | 378.8295 | 371.3633 | 432.7727 | 2415.7073 | 432.7727 | 378.8295 | 371.3633
2416.7073 | 2161.7073 | 378.8927 | 371.4125 | 432.8353 | 2416.7073 | 432.8353 | 378.8927 | 371.4125
2417.7073 | 2162.7073 | 378.981 | 371.4535 | 432.7922 | 2417.7073 | 432.7922 | 378.981 | 371.4535
2418.7073 | 2163.7073 | 379.0582 | 371.4948 | 432.6371 | 2418.7073 | 432.6371 | 379.0582 | 371.4948
2419.7073 | 2164.7073 | 379.1231 | 371.5367 | 432.6241 | 2419.7073 | 432.6241 | 379.1231 | 371.5367
2420.7073 | 2165.7073 | 379.204 | 371.5829 | 432.6293 | 2420.7073 | 432.6293 | 379.204 | 371.5829
2421.7073 | 2166.7073 | 379.2547 | 371.6369 | 432.5823 | 2421.7073 | 432.5823 | 379.2547 | 371.6369
2422.7073 | 2167.7073 | 379.3366 | 371.6855 | 432.5977 | 2422.7073 | 432.5977 | 379.3366 | 371.6855
2423.7073 | 2168.7073 | 379.4056 | 371.7383 | 432.6397 | 2423.7073 | 432.6397 | 379.4056 | 371.7383
2424.7073 | 2169.7073 | 379.4616 | 371.791 | 432.7265 | 2424.7073 | 432.7265 | 379.4616 | 371.791
2425.7073 | 2170.7073 | 379.5447 | 371.8478 | 432.7751 | 2425.7073 | 432.7751 | 379.5447 | 371.8478
2426.7073 | 2171.7073 | 379.6056 | 371.8995 | 432.8231 | 2426.7073 | 432.8231 | 379.6056 | 371.8995
2427.7073 | 2172.7073 | 379.6658 | 371.9529 | 432.9521 | 2427.7073 | 432.9521 | 379.6658 | 371.9529
2428.7073 | 2173.7073 | 379.7341 | 371.9996 | 433.0482 | 2428.7073 | 433.0482 | 379.7341 | 371.9996
2429.7073 | 2174.7073 | 379.7847 | 372.0565 | 433.2165 | 2429.7073 | 433.2165 | 379.7847 | 372.0565
2430.7073 | 2175.7073 | 379.8576 | 372.1089 | 433.2069 | 2430.7073 | 433.2069 | 379.8576 | 372.1089
2431.7073 | 2176.7073 | 379.9192 | 372.1581 | 433.2055 | 2431.7073 | 433.2055 | 379.9192 | 372.1581
2432.7073 | 2177.7073 | 379.9822 | 372.2116 | 433.2092 | 2432.7073 | 433.2092 | 379.9822 | 372.2116
2433.7073 | 2178.7073 | 380.0322 | 372.2603 | 433.1786 | 2433.7073 | 433.1786 | 380.0322 | 372.2603
2434.7073 | 2179.7073 | 380.0939 | 372.3133 | 433.2257 | 2434.7073 | 433.2257 | 380.0939 | 372.3133
2435.7073 | 2180.7073 | 380.1598 | 372.3547 | 433.2087 | 2435.7073 | 433.2087 | 380.1598 | 372.3547
2436.7073 | 2181.7073 | 380.2134 | 372.3955 | 433.1663 | 2436.7073 | 433.1663 | 380.2134 | 372.3955
2437.7073 | 2182.7073 | 380.2632 | 372.4544 | 433.1269 | 2437.7073 | 433.1269 | 380.2632 | 372.4544
2438.7073 | 2183.7073 | 380.3413 | 372.4971 | 433.0638 | 2438.7073 | 433.0638 | 380.3413 | 372.4971
2439.7073 | 2184.7073 | 380.3763 | 372.5422 | 432.9821 | 2439.7073 | 432.9821 | 380.3763 | 372.5422
2440.7073 | 2185.7073 | 380.4476 | 372.599 | 432.849 | 2440.7073 | 432.849 | 380.4476 | 372.599
2441.7073 | 2186.7073 | 380.496 | 372.6475 | 432.9644 | 2441.7073 | 432.9644 | 380.496 | 372.6475
2442.7073 | 2187.7073 | 380.554 | 372.7015 | 433.0091 | 2442.7073 | 433.0091 | 380.554 | 372.7015
2443.7073 | 2188.7073 | 380.6161 | 372.7224 | 433.0896 | 2443.7073 | 433.0896 | 380.6161 | 372.7224
2444.8635 | 2189.8635 | 380.6874 | 372.8033 | 433.2131 | 2444.8635 | 433.2131 | 380.6874 | 372.8033
2445.7698 | 2190.7698 | 380.7412 | 372.8261 | 433.2203 | 2445.7698 | 433.2203 | 380.7412 | 372.8261
2446.7385 | 2191.7385 | 380.7962 | 372.8807 | 433.1434 | 2446.7385 | 433.1434 | 380.7962 | 372.8807
2447.7073 | 2192.7073 | 380.8525 | 372.9164 | 433.0669 | 2447.7073 | 433.0669 | 380.8525 | 372.9164
2448.7073 | 2193.7073 | 380.9242 | 372.9576 | 433.0422 | 2448.7073 | 433.0422 | 380.9242 | 372.9576
2449.7073 | 2194.7073 | 380.9802 | 373.0096 | 433.1384 | 2449.7073 | 433.1384 | 380.9802 | 373.0096
2450.7073 | 2195.7073 | 381.0461 | 373.0497 | 433.1813 | 2450.7073 | 433.1813 | 381.0461 | 373.0497
2451.7073 | 2196.7073 | 381.095 | 373.0975 | 433.1976 | 2451.7073 | 433.1976 | 381.095 | 373.0975
2452.7073 | 2197.7073 | 381.1658 | 373.1375 | 433.2807 | 2452.7073 | 433.2807 | 381.1658 | 373.1375
2453.7073 | 2198.7073 | 381.2065 | 373.1807 | 433.3304 | 2453.7073 | 433.3304 | 381.2065 | 373.1807
2454.7073 | 2199.7073 | 381.286 | 373.2318 | 433.4222 | 2454.7073 | 433.4222 | 381.286 | 373.2318
2455.7073 | 2200.7073 | 381.3426 | 373.2716 | 433.4283 | 2455.7073 | 433.4283 | 381.3426 | 373.2716
2456.7073 | 2201.7073 | 381.4081 | 373.3122 | 433.4401 | 2456.7073 | 433.4401 | 381.4081 | 373.3122
2457.7073 | 2202.7073 | 381.4645 | 373.3551 | 433.3853 | 2457.7073 | 433.3853 | 381.4645 | 373.3551
2458.7073 | 2203.7073 | 381.5253 | 373.4017 | 433.4346 | 2458.7073 | 433.4346 | 381.5253 | 373.4017
2459.7073 | 2204.7073 | 381.5764 | 373.4463 | 433.3433 | 2459.7073 | 433.3433 | 381.5764 | 373.4463
2460.7073 | 2205.7073 | 381.6444 | 373.4851 | 433.3281 | 2460.7073 | 433.3281 | 381.6444 | 373.4851
2461.7073 | 2206.7073 | 381.7041 | 373.529 | 433.4256 | 2461.7073 | 433.4256 | 381.7041 | 373.529
2462.7073 | 2207.7073 | 381.7632 | 373.5734 | 433.4675 | 2462.7073 | 433.4675 | 381.7632 | 373.5734
2463.7073 | 2208.7073 | 381.8209 | 373.6269 | 433.5431 | 2463.7073 | 433.5431 | 381.8209 | 373.6269
2464.7073 | 2209.7073 | 381.8886 | 373.6563 | 433.4692 | 2464.7073 | 433.4692 | 381.8886 | 373.6563
2465.7073 | 2210.7073 | 381.9304 | 373.697 | 433.4557 | 2465.7073 | 433.4557 | 381.9304 | 373.697
2466.7073 | 2211.7073 | 382.0031 | 373.7395 | 433.4321 | 2466.7073 | 433.4321 | 382.0031 | 373.7395
2467.7073 | 2212.7073 | 382.0659 | 373.7751 | 433.4233 | 2467.7073 | 433.4233 | 382.0659 | 373.7751
2468.7073 | 2213.7073 | 382.1167 | 373.825 | 433.5058 | 2468.7073 | 433.5058 | 382.1167 | 373.825
2469.7073 | 2214.7073 | 382.1696 | 373.8578 | 433.4493 | 2469.7073 | 433.4493 | 382.1696 | 373.8578
2470.7073 | 2215.7073 | 382.2282 | 373.8986 | 433.4411 | 2470.7073 | 433.4411 | 382.2282 | 373.8986
2471.7073 | 2216.7073 | 382.2858 | 373.9322 | 433.4596 | 2471.7073 | 433.4596 | 382.2858 | 373.9322
2472.7073 | 2217.7073 | 382.3397 | 373.9703 | 433.4068 | 2472.7073 | 433.4068 | 382.3397 | 373.9703
2473.7073 | 2218.7073 | 382.406 | 374.0058 | 433.2522 | 2473.7073 | 433.2522 | 382.406 | 374.0058
2474.7073 | 2219.7073 | 382.4586 | 374.0522 | 433.3315 | 2474.7073 | 433.3315 | 382.4586 | 374.0522
2475.7073 | 2220.7073 | 382.5196 | 374.0976 | 433.3901 | 2475.7073 | 433.3901 | 382.5196 | 374.0976
2476.7073 | 2221.7073 | 382.5682 | 374.1295 | 433.376 | 2476.7073 | 433.376 | 382.5682 | 374.1295
2477.7073 | 2222.7073 | 382.6246 | 374.1689 | 433.4265 | 2477.7073 | 433.4265 | 382.6246 | 374.1689
2478.7073 | 2223.7073 | 382.6873 | 374.2024 | 433.5505 | 2478.7073 | 433.5505 | 382.6873 | 374.2024
2479.7073 | 2224.7073 | 382.7407 | 374.2475 | 433.5967 | 2479.7073 | 433.5967 | 382.7407 | 374.2475
2480.7073 | 2225.7073 | 382.7814 | 374.2767 | 433.5253 | 2480.7073 | 433.5253 | 382.7814 | 374.2767
2481.7073 | 2226.7073 | 382.8345 | 374.3149 | 433.5286 | 2481.7073 | 433.5286 | 382.8345 | 374.3149
2482.7073 | 2227.7073 | 382.9006 | 374.3473 | 433.5192 | 2482.7073 | 433.5192 | 382.9006 | 374.3473
2483.7073 | 2228.7073 | 382.9566 | 374.3884 | 433.4636 | 2483.7073 | 433.4636 | 382.9566 | 374.3884
2484.7073 | 2229.7073 | 383.0132 | 374.418 | 433.4907 | 2484.7073 | 433.4907 | 383.0132 | 374.418
2485.7073 | 2230.7073 | 383.0765 | 374.4619 | 433.5376 | 2485.7073 | 433.5376 | 383.0765 | 374.4619
2486.7073 | 2231.7073 | 383.1237 | 374.4913 | 433.5266 | 2486.7073 | 433.5266 | 383.1237 | 374.4913
2487.7073 | 2232.7073 | 383.1698 | 374.5279 | 433.5299 | 2487.7073 | 433.5299 | 383.1698 | 374.5279
2488.7073 | 2233.7073 | 383.2204 | 374.5555 | 433.5291 | 2488.7073 | 433.5291 | 383.2204 | 374.5555
2489.7073 | 2234.7073 | 383.2976 | 374.5903 | 433.5098 | 2489.7073 | 433.5098 | 383.2976 | 374.5903
2490.7073 | 2235.7073 | 383.3499 | 374.6172 | 433.5592 | 2490.7073 | 433.5592 | 383.3499 | 374.6172
2491.7073 | 2236.7073 | 383.3881 | 374.6473 | 433.5462 | 2491.7073 | 433.5462 | 383.3881 | 374.6473
2492.7073 | 2237.7073 | 383.4387 | 374.6881 | 433.5859 | 2492.7073 | 433.5859 | 383.4387 | 374.6881
2493.7073 | 2238.7073 | 383.5067 | 374.7126 | 433.5628 | 2493.7073 | 433.5628 | 383.5067 | 374.7126
2494.7073 | 2239.7073 | 383.5535 | 374.7425 | 433.6045 | 2494.7073 | 433.6045 | 383.5535 | 374.7425
2495.7073 | 2240.7073 | 383.5943 | 374.7721 | 433.5669 | 2495.7073 | 433.5669 | 383.5943 | 374.7721
2496.7073 | 2241.7073 | 383.659 | 374.807 | 433.5799 | 2496.7073 | 433.5799 | 383.659 | 374.807
2497.7073 | 2242.7073 | 383.7193 | 374.8374 | 433.7418 | 2497.7073 | 433.7418 | 383.7193 | 374.8374
2498.7073 | 2243.7073 | 383.7832 | 374.8749 | 433.6402 | 2498.7073 | 433.6402 | 383.7832 | 374.8749
2499.7073 | 2244.7073 | 383.8251 | 374.901 | 433.5959 | 2499.7073 | 433.5959 | 383.8251 | 374.901
2500.7073 | 2245.7073 | 383.8688 | 374.9314 | 433.5505 | 2500.7073 | 433.5505 | 383.8688 | 374.9314
2501.7073 | 2246.7073 | 383.9346 | 374.9662 | 433.444 | 2501.7073 | 433.444 | 383.9346 | 374.9662
2502.7073 | 2247.7073 | 383.9858 | 374.9936 | 433.3316 | 2502.7073 | 433.3316 | 383.9858 | 374.9936
2503.7073 | 2248.7073 | 384.0299 | 375.0187 | 433.2664 | 2503.7073 | 433.2664 | 384.0299 | 375.0187
2504.7073 | 2249.7073 | 384.0917 | 375.0559 | 433.1543 | 2504.7073 | 433.1543 | 384.0917 | 375.0559
2505.7073 | 2250.7073 | 384.1425 | 375.087 | 433.0089 | 2505.7073 | 433.0089 | 384.1425 | 375.087
2506.7073 | 2251.7073 | 384.1983 | 375.1186 | 432.9094 | 2506.7073 | 432.9094 | 384.1983 | 375.1186
2507.7073 | 2252.7073 | 384.2444 | 375.151 | 432.9916 | 2507.7073 | 432.9916 | 384.2444 | 375.151
2508.7385 | 2253.7385 | 384.3031 | 375.1839 | 433.0616 | 2508.7385 | 433.0616 | 384.3031 | 375.1839
2509.7073 | 2254.7073 | 384.3491 | 375.2066 | 432.9944 | 2509.7073 | 432.9944 | 384.3491 | 375.2066
2510.7229 | 2255.7229 | 384.4015 | 375.2319 | 433.0408 | 2510.7229 | 433.0408 | 384.4015 | 375.2319
2511.7073 | 2256.7073 | 384.4419 | 375.2607 | 432.9244 | 2511.7073 | 432.9244 | 384.4419 | 375.2607
2512.7073 | 2257.7073 | 384.4993 | 375.2858 | 432.829 | 2512.7073 | 432.829 | 384.4993 | 375.2858
2513.7073 | 2258.7073 | 384.545 | 375.3104 | 432.8619 | 2513.7073 | 432.8619 | 384.545 | 375.3104
2514.7073 | 2259.7073 | 384.6037 | 375.3492 | 432.9546 | 2514.7073 | 432.9546 | 384.6037 | 375.3492
2515.7073 | 2260.7073 | 384.6581 | 375.3796 | 432.9432 | 2515.7073 | 432.9432 | 384.6581 | 375.3796
2516.7073 | 2261.7073 | 384.7031 | 375.3955 | 432.8658 | 2516.7073 | 432.8658 | 384.7031 | 375.3955
2517.7073 | 2262.7073 | 384.7491 | 375.4299 | 432.7637 | 2517.7073 | 432.7637 | 384.7491 | 375.4299
2518.7073 | 2263.7073 | 384.8032 | 375.4508 | 432.7601 | 2518.7073 | 432.7601 | 384.8032 | 375.4508
2519.7073 | 2264.7073 | 384.84 | 375.477 | 432.6943 | 2519.7073 | 432.6943 | 384.84 | 375.477
2520.7073 | 2265.7073 | 384.8935 | 375.4963 | 432.5781 | 2520.7073 | 432.5781 | 384.8935 | 375.4963
2521.7073 | 2266.7073 | 384.954 | 375.527 | 432.6266 | 2521.7073 | 432.6266 | 384.954 | 375.527
2522.7073 | 2267.7073 | 384.9915 | 375.565 | 432.7687 | 2522.7073 | 432.7687 | 384.9915 | 375.565
2523.7073 | 2268.7073 | 385.0446 | 375.5939 | 432.8921 | 2523.7073 | 432.8921 | 385.0446 | 375.5939
2524.7073 | 2269.7073 | 385.1036 | 375.613 | 432.9923 | 2524.7073 | 432.9923 | 385.1036 | 375.613
2525.7073 | 2270.7073 | 385.1469 | 375.6403 | 433.1225 | 2525.7073 | 433.1225 | 385.1469 | 375.6403
2526.7073 | 2271.7073 | 385.1875 | 375.6664 | 433.1421 | 2526.7073 | 433.1421 | 385.1875 | 375.6664
2527.8167 | 2272.8167 | 385.2408 | 375.6903 | 433.0257 | 2527.8167 | 433.0257 | 385.2408 | 375.6903
2528.8167 | 2273.8167 | 385.2905 | 375.7251 | 432.9395 | 2528.8167 | 432.9395 | 385.2905 | 375.7251
2529.8167 | 2274.8167 | 385.3338 | 375.749 | 432.8002 | 2529.8167 | 432.8002 | 385.3338 | 375.749
2530.7229 | 2275.7229 | 385.3813 | 375.7837 | 432.7623 | 2530.7229 | 432.7623 | 385.3813 | 375.7837
2531.7073 | 2276.7073 | 385.4259 | 375.8027 | 432.7534 | 2531.7073 | 432.7534 | 385.4259 | 375.8027
2532.7073 | 2277.7073 | 385.4646 | 375.8288 | 432.7535 | 2532.7073 | 432.7535 | 385.4646 | 375.8288
2533.7073 | 2278.7073 | 385.513 | 375.8561 | 432.792 | 2533.7073 | 432.792 | 385.513 | 375.8561
2534.7073 | 2279.7073 | 385.5566 | 375.8874 | 432.7713 | 2534.7073 | 432.7713 | 385.5566 | 375.8874
2535.7073 | 2280.7073 | 385.6201 | 375.9205 | 432.7383 | 2535.7073 | 432.7383 | 385.6201 | 375.9205
2536.7073 | 2281.7073 | 385.6476 | 375.9444 | 432.8144 | 2536.7073 | 432.8144 | 385.6476 | 375.9444
2537.7073 | 2282.7073 | 385.7021 | 375.9691 | 432.9853 | 2537.7073 | 432.9853 | 385.7021 | 375.9691
2538.7073 | 2283.7073 | 385.745 | 375.9928 | 433.0819 | 2538.7073 | 433.0819 | 385.745 | 375.9928
2539.7073 | 2284.7073 | 385.7871 | 376.0249 | 433.2 | 2539.7073 | 433.2 | 385.7871 | 376.0249
2540.7073 | 2285.7073 | 385.8337 | 376.0464 | 433.4052 | 2540.7073 | 433.4052 | 385.8337 | 376.0464
2541.7073 | 2286.7073 | 385.8755 | 376.0772 | 433.5273 | 2541.7073 | 433.5273 | 385.8755 | 376.0772
2542.7073 | 2287.7073 | 385.9242 | 376.1021 | 433.5192 | 2542.7073 | 433.5192 | 385.9242 | 376.1021
2543.7073 | 2288.7073 | 385.9606 | 376.1277 | 433.5208 | 2543.7073 | 433.5208 | 385.9606 | 376.1277
2544.7073 | 2289.7073 | 386.0085 | 376.1635 | 433.57 | 2544.7073 | 433.57 | 386.0085 | 376.1635
2545.7073 | 2290.7073 | 386.0585 | 376.1766 | 433.63 | 2545.7073 | 433.63 | 386.0585 | 376.1766
2546.7073 | 2291.7073 | 386.1082 | 376.2007 | 433.6221 | 2546.7073 | 433.6221 | 386.1082 | 376.2007
2547.7073 | 2292.7073 | 386.1687 | 376.2257 | 433.6845 | 2547.7073 | 433.6845 | 386.1687 | 376.2257
2548.7073 | 2293.7073 | 386.2067 | 376.2533 | 433.7345 | 2548.7073 | 433.7345 | 386.2067 | 376.2533
2549.7073 | 2294.7073 | 386.2504 | 376.2742 | 433.8015 | 2549.7073 | 433.8015 | 386.2504 | 376.2742
2550.7073 | 2295.7073 | 386.2922 | 376.304 | 433.7604 | 2550.7073 | 433.7604 | 386.2922 | 376.304
2551.7073 | 2296.7073 | 386.357 | 376.3265 | 433.7741 | 2551.7073 | 433.7741 | 386.357 | 376.3265
2552.7073 | 2297.7073 | 386.3957 | 376.3469 | 433.7592 | 2552.7073 | 433.7592 | 386.3957 | 376.3469
2553.7542 | 2298.7542 | 386.445 | 376.3774 | 433.8536 | 2553.7542 | 433.8536 | 386.445 | 376.3774
2554.7698 | 2299.7698 | 386.4833 | 376.4083 | 433.8533 | 2554.7698 | 433.8533 | 386.4833 | 376.4083
2555.7073 | 2300.7073 | 386.5244 | 376.4295 | 433.8808 | 2555.7073 | 433.8808 | 386.5244 | 376.4295
2556.7073 | 2301.7073 | 386.5657 | 376.4611 | 433.727 | 2556.7073 | 433.727 | 386.5657 | 376.4611
2557.7385 | 2302.7385 | 386.6116 | 376.4819 | 433.6747 | 2557.7385 | 433.6747 | 386.6116 | 376.4819
2558.7073 | 2303.7073 | 386.6595 | 376.5059 | 433.6765 | 2558.7073 | 433.6765 | 386.6595 | 376.5059
2559.7073 | 2304.7073 | 386.7075 | 376.534 | 433.4746 | 2559.7073 | 433.4746 | 386.7075 | 376.534
2560.7229 | 2305.7229 | 386.7594 | 376.5619 | 433.3514 | 2560.7229 | 433.3514 | 386.7594 | 376.5619
2561.7073 | 2306.7073 | 386.7717 | 376.5804 | 433.2466 | 2561.7073 | 433.2466 | 386.7717 | 376.5804
2562.7073 | 2307.7073 | 386.8492 | 376.6018 | 433.2262 | 2562.7073 | 433.2262 | 386.8492 | 376.6018
2563.7073 | 2308.7073 | 386.8875 | 376.6306 | 433.1797 | 2563.7073 | 433.1797 | 386.8875 | 376.6306
2564.7073 | 2309.7073 | 386.9434 | 376.6591 | 433.1323 | 2564.7073 | 433.1323 | 386.9434 | 376.6591
2565.7073 | 2310.7073 | 386.9861 | 376.6742 | 433.1075 | 2565.7073 | 433.1075 | 386.9861 | 376.6742
2566.7073 | 2311.7073 | 387.0353 | 376.6961 | 433.073 | 2566.7073 | 433.073 | 387.0353 | 376.6961
2567.7073 | 2312.7073 | 387.0839 | 376.7364 | 433.1381 | 2567.7073 | 433.1381 | 387.0839 | 376.7364
2568.7073 | 2313.7073 | 387.1321 | 376.7665 | 433.1298 | 2568.7073 | 433.1298 | 387.1321 | 376.7665
2569.7073 | 2314.7073 | 387.1739 | 376.7866 | 433.0608 | 2569.7073 | 433.0608 | 387.1739 | 376.7866
2570.7073 | 2315.7073 | 387.2186 | 376.8049 | 433.0069 | 2570.7073 | 433.0069 | 387.2186 | 376.8049
2571.7073 | 2316.7073 | 387.2591 | 376.8382 | 433.0159 | 2571.7073 | 433.0159 | 387.2591 | 376.8382
2572.7073 | 2317.7073 | 387.3225 | 376.8631 | 432.9149 | 2572.7073 | 432.9149 | 387.3225 | 376.8631
2573.7073 | 2318.7073 | 387.3633 | 376.8879 | 432.7977 | 2573.7073 | 432.7977 | 387.3633 | 376.8879
2574.7073 | 2319.7073 | 387.4016 | 376.9087 | 432.775 | 2574.7073 | 432.775 | 387.4016 | 376.9087
2575.7073 | 2320.7073 | 387.4501 | 376.9387 | 432.8993 | 2575.7073 | 432.8993 | 387.4501 | 376.9387
2576.7073 | 2321.7073 | 387.5006 | 376.9612 | 432.8701 | 2576.7073 | 432.8701 | 387.5006 | 376.9612
2577.7073 | 2322.7073 | 387.5484 | 376.9736 | 432.9282 | 2577.7073 | 432.9282 | 387.5484 | 376.9736
2578.7073 | 2323.7073 | 387.5984 | 377.0027 | 432.8299 | 2578.7073 | 432.8299 | 387.5984 | 377.0027
2579.7073 | 2324.7073 | 387.6305 | 377.026 | 432.7959 | 2579.7073 | 432.7959 | 387.6305 | 377.026
2580.7073 | 2325.7073 | 387.6847 | 377.047 | 432.7262 | 2580.7073 | 432.7262 | 387.6847 | 377.047
2581.7073 | 2326.7073 | 387.7068 | 377.0698 | 432.8548 | 2581.7073 | 432.8548 | 387.7068 | 377.0698
2582.7073 | 2327.7073 | 387.763 | 377.0925 | 432.9197 | 2582.7073 | 432.9197 | 387.763 | 377.0925
2583.7073 | 2328.7073 | 387.8162 | 377.1086 | 432.818 | 2583.7073 | 432.818 | 387.8162 | 377.1086
2584.7073 | 2329.7073 | 387.8661 | 377.1366 | 432.6918 | 2584.7073 | 432.6918 | 387.8661 | 377.1366
2585.7073 | 2330.7073 | 387.9032 | 377.1545 | 432.7189 | 2585.7073 | 432.7189 | 387.9032 | 377.1545
2586.7073 | 2331.7073 | 387.9459 | 377.1762 | 432.7268 | 2586.7073 | 432.7268 | 387.9459 | 377.1762
2587.801 | 2332.801 | 387.9966 | 377.1913 | 432.7963 | 2587.801 | 432.7963 | 387.9966 | 377.1913
2588.7542 | 2333.7542 | 388.0265 | 377.2163 | 432.945 | 2588.7542 | 432.945 | 388.0265 | 377.2163
2589.7854 | 2334.7854 | 388.0831 | 377.2412 | 433.1514 | 2589.7854 | 433.1514 | 388.0831 | 377.2412
2590.7073 | 2335.7073 | 388.1222 | 377.2552 | 433.1767 | 2590.7073 | 433.1767 | 388.1222 | 377.2552
2591.7073 | 2336.7073 | 388.151 | 377.2707 | 433.142 | 2591.7073 | 433.142 | 388.151 | 377.2707
2592.7073 | 2337.7073 | 388.1953 | 377.2835 | 433.0852 | 2592.7073 | 433.0852 | 388.1953 | 377.2835
2593.7073 | 2338.7073 | 388.2464 | 377.3002 | 433.1439 | 2593.7073 | 433.1439 | 388.2464 | 377.3002
2594.7073 | 2339.7073 | 388.2918 | 377.3333 | 433.1904 | 2594.7073 | 433.1904 | 388.2918 | 377.3333
2595.7073 | 2340.7073 | 388.3182 | 377.3579 | 433.1875 | 2595.7073 | 433.1875 | 388.3182 | 377.3579
2596.7073 | 2341.7073 | 388.3637 | 377.3567 | 433.3397 | 2596.7073 | 433.3397 | 388.3637 | 377.3567
2597.7073 | 2342.7073 | 388.404 | 377.3835 | 433.3812 | 2597.7073 | 433.3812 | 388.404 | 377.3835
2598.7073 | 2343.7073 | 388.4479 | 377.4082 | 433.3225 | 2598.7073 | 433.3225 | 388.4479 | 377.4082
2599.7073 | 2344.7073 | 388.453 | 377.4245 | 433.259 | 2599.7073 | 433.259 | 388.453 | 377.4245
2600.7073 | 2345.7073 | 388.5236 | 377.4419 | 433.2173 | 2600.7073 | 433.2173 | 388.5236 | 377.4419
2601.7073 | 2346.7073 | 388.5705 | 377.456 | 433.1468 | 2601.7073 | 433.1468 | 388.5705 | 377.456
2602.7073 | 2347.7073 | 388.5982 | 377.4781 | 433.2723 | 2602.7073 | 433.2723 | 388.5982 | 377.4781
2603.7073 | 2348.7073 | 388.6409 | 377.4954 | 433.3074 | 2603.7073 | 433.3074 | 388.6409 | 377.4954
2604.7073 | 2349.7073 | 388.6792 | 377.5127 | 433.319 | 2604.7073 | 433.319 | 388.6792 | 377.5127
2605.7073 | 2350.7073 | 388.7364 | 377.5255 | 433.3514 | 2605.7073 | 433.3514 | 388.7364 | 377.5255
2606.7073 | 2351.7073 | 388.7659 | 377.5295 | 433.4998 | 2606.7073 | 433.4998 | 388.7659 | 377.5295
2607.7073 | 2352.7073 | 388.7885 | 377.5551 | 433.5385 | 2607.7073 | 433.5385 | 388.7885 | 377.5551
2608.7073 | 2353.7073 | 388.8472 | 377.5676 | 433.3446 | 2608.7073 | 433.3446 | 388.8472 | 377.5676
2609.7073 | 2354.7073 | 388.8875 | 377.5883 | 433.3213 | 2609.7073 | 433.3213 | 388.8875 | 377.5883
2610.7073 | 2355.7073 | 388.9179 | 377.5997 | 433.3346 | 2610.7073 | 433.3346 | 388.9179 | 377.5997
2611.7073 | 2356.7073 | 388.9783 | 377.6237 | 433.3042 | 2611.7073 | 433.3042 | 388.9783 | 377.6237
2612.7229 | 2357.7229 | 389.0208 | 377.6386 | 433.3675 | 2612.7229 | 433.3675 | 389.0208 | 377.6386
2613.7542 | 2358.7542 | 389.0578 | 377.6423 | 433.3916 | 2613.7542 | 433.3916 | 389.0578 | 377.6423
2614.7385 | 2359.7385 | 389.0867 | 377.6611 | 433.413 | 2614.7385 | 433.413 | 389.0867 | 377.6611
2615.7073 | 2360.7073 | 389.1288 | 377.6785 | 433.4793 | 2615.7073 | 433.4793 | 389.1288 | 377.6785
2616.7073 | 2361.7073 | 389.175 | 377.6828 | 433.3363 | 2616.7073 | 433.3363 | 389.175 | 377.6828
2617.7073 | 2362.7073 | 389.2081 | 377.6976 | 433.21 | 2617.7073 | 433.21 | 389.2081 | 377.6976
2618.7073 | 2363.7073 | 389.2422 | 377.7177 | 433.2745 | 2618.7073 | 433.2745 | 389.2422 | 377.7177
2619.7073 | 2364.7073 | 389.2937 | 377.7347 | 433.3164 | 2619.7073 | 433.3164 | 389.2937 | 377.7347
2620.7073 | 2365.7073 | 389.3262 | 377.7457 | 433.225 | 2620.7073 | 433.225 | 389.3262 | 377.7457
2621.7073 | 2366.7073 | 389.3653 | 377.7517 | 433.1617 | 2621.7073 | 433.1617 | 389.3653 | 377.7517
2622.7073 | 2367.7073 | 389.4138 | 377.774 | 433.2561 | 2622.7073 | 433.2561 | 389.4138 | 377.774
2623.7073 | 2368.7073 | 389.442 | 377.7972 | 433.2969 | 2623.7073 | 433.2969 | 389.442 | 377.7972
2624.7073 | 2369.7073 | 389.463 | 377.8124 | 433.2664 | 2624.7073 | 433.2664 | 389.463 | 377.8124
2625.7073 | 2370.7073 | 389.5236 | 377.8237 | 433.2004 | 2625.7073 | 433.2004 | 389.5236 | 377.8237
2626.7073 | 2371.7073 | 389.5679 | 377.8427 | 433.1867 | 2626.7073 | 433.1867 | 389.5679 | 377.8427
2627.7073 | 2372.7073 | 389.6028 | 377.86 | 433.1283 | 2627.7073 | 433.1283 | 389.6028 | 377.86
2628.7073 | 2373.7073 | 389.6424 | 377.8767 | 432.9868 | 2628.7073 | 432.9868 | 389.6424 | 377.8767
2629.7073 | 2374.7073 | 389.6621 | 377.8849 | 433.0444 | 2629.7073 | 433.0444 | 389.6621 | 377.8849
2630.7073 | 2375.7073 | 389.7212 | 377.9092 | 433.0801 | 2630.7073 | 433.0801 | 389.7212 | 377.9092
2631.7073 | 2376.7073 | 389.7488 | 377.9273 | 433.1178 | 2631.7073 | 433.1178 | 389.7488 | 377.9273
2632.7073 | 2377.7073 | 389.791 | 377.9417 | 433.5419 | 2632.7073 | 433.5419 | 389.791 | 377.9417
2633.7073 | 2378.7073 | 389.8367 | 377.9537 | 434.7397 | 2633.7073 | 434.7397 | 389.8367 | 377.9537
2634.7073 | 2379.7073 | 389.858 | 377.9739 | 436.5939 | 2634.7073 | 436.5939 | 389.858 | 377.9739
2635.7073 | 2380.7073 | 389.8996 | 377.9929 | 439.0634 | 2635.7073 | 439.0634 | 389.8996 | 377.9929
2636.7073 | 2381.7073 | 389.9467 | 378.0029 | 442.0954 | 2636.7073 | 442.0954 | 389.9467 | 378.0029
2637.7073 | 2382.7073 | 389.9661 | 378.0178 | 445.2311 | 2637.7073 | 445.2311 | 389.9661 | 378.0178
2638.7073 | 2383.7073 | 390.0191 | 378.0362 | 448.4305 | 2638.7073 | 448.4305 | 390.0191 | 378.0362
2639.7073 | 2384.7073 | 390.0638 | 378.0519 | 451.5217 | 2639.7073 | 451.5217 | 390.0638 | 378.0519
2640.7073 | 2385.7073 | 390.1168 | 378.0702 | 454.5399 | 2640.7073 | 454.5399 | 390.1168 | 378.0702
2641.7073 | 2386.7073 | 390.1594 | 378.0844 | 457.2389 | 2641.7073 | 457.2389 | 390.1594 | 378.0844
2642.7073 | 2387.7073 | 390.2149 | 378.0986 | 459.5033 | 2642.7073 | 459.5033 | 390.2149 | 378.0986
2643.7073 | 2388.7073 | 390.2442 | 378.1203 | 461.3413 | 2643.7073 | 461.3413 | 390.2442 | 378.1203
2644.7073 | 2389.7073 | 390.3157 | 378.1368 | 462.8966 | 2644.7073 | 462.8966 | 390.3157 | 378.1368
2645.7073 | 2390.7073 | 390.3727 | 378.1551 | 464.3577 | 2645.7073 | 464.3577 | 390.3727 | 378.1551
2646.7073 | 2391.7073 | 390.4525 | 378.2165 | 465.4357 | 2646.7073 | 465.4357 | 390.4525 | 378.2165
2647.7073 | 2392.7073 | 390.5104 | 378.3662 | 466.3157 | 2647.7073 | 466.3157 | 390.5104 | 378.3662
2648.7073 | 2393.7073 | 390.5945 | 378.4796 | 467.0746 | 2648.7073 | 467.0746 | 390.5945 | 378.4796
2649.7073 | 2394.7073 | 390.6718 | 378.5752 | 467.4556 | 2649.7073 | 467.4556 | 390.6718 | 378.5752
2650.7073 | 2395.7073 | 390.7543 | 378.666 | 467.8088 | 2650.7073 | 467.8088 | 390.7543 | 378.666
2651.7073 | 2396.7073 | 390.8406 | 378.7443 | 468.0326 | 2651.7073 | 468.0326 | 390.8406 | 378.7443
2652.7073 | 2397.7073 | 390.9316 | 378.8376 | 468.2221 | 2652.7073 | 468.2221 | 390.9316 | 378.8376
2653.7073 | 2398.7073 | 391.0309 | 378.9209 | 468.2543 | 2653.7073 | 468.2543 | 391.0309 | 378.9209
2654.7073 | 2399.7073 | 391.1324 | 379.0002 | 468.391 | 2654.7073 | 468.391 | 391.1324 | 379.0002
2655.7073 | 2400.7073 | 391.2434 | 379.0996 | 468.3791 | 2655.7073 | 468.3791 | 391.2434 | 379.0996
2656.7073 | 2401.7073 | 391.3485 | 379.1798 | 468.2851 | 2656.7073 | 468.2851 | 391.3485 | 379.1798
2657.7073 | 2402.7073 | 391.454 | 379.2664 | 468.2205 | 2657.7073 | 468.2205 | 391.454 | 379.2664
2658.7073 | 2403.7073 | 391.5571 | 379.3643 | 468.2063 | 2658.7073 | 468.2063 | 391.5571 | 379.3643
2659.7073 | 2404.7073 | 391.665 | 379.4579 | 468.1378 | 2659.7073 | 468.1378 | 391.665 | 379.4579
2660.7073 | 2405.7073 | 391.7995 | 379.5611 | 467.9734 | 2660.7073 | 467.9734 | 391.7995 | 379.5611
2661.7073 | 2406.7073 | 391.9083 | 379.6545 | 467.7374 | 2661.7073 | 467.7374 | 391.9083 | 379.6545
2662.7073 | 2407.7073 | 392.0248 | 379.7611 | 467.5665 | 2662.7073 | 467.5665 | 392.0248 | 379.7611
2663.7073 | 2408.7073 | 392.1501 | 379.863 | 467.4578 | 2663.7073 | 467.4578 | 392.1501 | 379.863
2664.7073 | 2409.7073 | 392.2416 | 379.9706 | 467.2908 | 2664.7073 | 467.2908 | 392.2416 | 379.9706
2665.7073 | 2410.7073 | 392.3953 | 380.0822 | 467.1997 | 2665.7073 | 467.1997 | 392.3953 | 380.0822
2666.7073 | 2411.7073 | 392.513 | 380.1904 | 467.0372 | 2666.7073 | 467.0372 | 392.513 | 380.1904
2667.7073 | 2412.7073 | 392.6441 | 380.3004 | 467.1407 | 2667.7073 | 467.1407 | 392.6441 | 380.3004
2668.7073 | 2413.7073 | 392.7736 | 380.4114 | 467.2421 | 2668.7073 | 467.2421 | 392.7736 | 380.4114
2669.7073 | 2414.7073 | 392.9869 | 380.5294 | 467.3663 | 2669.7073 | 467.3663 | 392.9869 | 380.5294
2670.7073 | 2415.7073 | 393.177 | 380.6464 | 467.5345 | 2670.7073 | 467.5345 | 393.177 | 380.6464
2671.7073 | 2416.7073 | 393.3823 | 380.7663 | 467.6273 | 2671.7073 | 467.6273 | 393.3823 | 380.7663
2672.7073 | 2417.7073 | 393.6085 | 380.9155 | 467.9966 | 2672.7073 | 467.9966 | 393.6085 | 380.9155
2673.7073 | 2418.7073 | 393.9009 | 381.1069 | 468.5561 | 2673.7073 | 468.5561 | 393.9009 | 381.1069
2674.7073 | 2419.7073 | 394.2253 | 381.3261 | 468.865 | 2674.7073 | 468.865 | 394.2253 | 381.3261
2675.7073 | 2420.7073 | 394.6537 | 381.5999 | 469.1522 | 2675.7073 | 469.1522 | 394.6537 | 381.5999
2676.7073 | 2421.7073 | 395.1848 | 381.8042 | 469.4539 | 2676.7073 | 469.4539 | 395.1848 | 381.8042
2677.7073 | 2422.7073 | 395.8296 | 382.013 | 469.8355 | 2677.7073 | 469.8355 | 395.8296 | 382.013
2678.7073 | 2423.7073 | 396.5383 | 382.1837 | 470.189 | 2678.7073 | 470.189 | 396.5383 | 382.1837
2679.7073 | 2424.7073 | 397.4265 | 382.3859 | 470.4484 | 2679.7073 | 470.4484 | 397.4265 | 382.3859
2680.7073 | 2425.7073 | 398.2295 | 382.5903 | 470.6851 | 2680.7073 | 470.6851 | 398.2295 | 382.5903
2681.7073 | 2426.7073 | 399.0477 | 382.8288 | 470.9325 | 2681.7073 | 470.9325 | 399.0477 | 382.8288
2682.7073 | 2427.7073 | 399.9147 | 383.1268 | 471.1171 | 2682.7073 | 471.1171 | 399.9147 | 383.1268
2683.7073 | 2428.7073 | 400.9126 | 383.4763 | 471.2604 | 2683.7073 | 471.2604 | 400.9126 | 383.4763
2684.7073 | 2429.7073 | 402.135 | 383.8868 | 471.4115 | 2684.7073 | 471.4115 | 402.135 | 383.8868
2685.7073 | 2430.7073 | 403.5025 | 384.3471 | 471.464 | 2685.7073 | 471.464 | 403.5025 | 384.3471
2686.7073 | 2431.7073 | 404.92 | 384.8673 | 471.569 | 2686.7073 | 471.569 | 404.92 | 384.8673
2687.7073 | 2432.7073 | 406.5851 | 385.4503 | 471.7328 | 2687.7073 | 471.7328 | 406.5851 | 385.4503
2688.7073 | 2433.7073 | 408.6812 | 386.0524 | 471.8945 | 2688.7073 | 471.8945 | 408.6812 | 386.0524
2689.7073 | 2434.7073 | 411.0429 | 386.7027 | 471.9889 | 2689.7073 | 471.9889 | 411.0429 | 386.7027
2690.7073 | 2435.7073 | 413.3138 | 387.4094 | 472.0175 | 2690.7073 | 472.0175 | 413.3138 | 387.4094
2691.7073 | 2436.7073 | 415.4337 | 388.1063 | 471.9458 | 2691.7073 | 471.9458 | 415.4337 | 388.1063
2692.7073 | 2437.7073 | 417.5385 | 388.9411 | 471.8508 | 2692.7073 | 471.8508 | 417.5385 | 388.9411
2693.7073 | 2438.7073 | 419.4354 | 389.825 | 471.7403 | 2693.7073 | 471.7403 | 419.4354 | 389.825
2694.7073 | 2439.7073 | 420.9352 | 390.6809 | 471.7438 | 2694.7073 | 471.7438 | 420.9352 | 390.6809
2695.7073 | 2440.7073 | 420.8792 | 391.5547 | 471.8666 | 2695.7073 | 471.8666 | 420.8792 | 391.5547
2696.7073 | 2441.7073 | 420.9114 | 392.3852 | 471.8794 | 2696.7073 | 471.8794 | 420.9114 | 392.3852
2697.7073 | 2442.7073 | 420.945 | 393.2466 | 471.8254 | 2697.7073 | 471.8254 | 420.945 | 393.2466
2698.7073 | 2443.7073 | 420.8861 | 394.0991 | 471.8617 | 2698.7073 | 471.8617 | 420.8861 | 394.0991
2699.7073 | 2444.7073 | 421.1014 | 394.9699 | 471.6932 | 2699.7073 | 471.6932 | 421.1014 | 394.9699
2700.7073 | 2445.7073 | 421.8444 | 395.8611 | 471.6507 | 2700.7073 | 471.6507 | 421.8444 | 395.8611
2701.7073 | 2446.7073 | 422.0352 | 396.7607 | 471.8425 | 2701.7073 | 471.8425 | 422.0352 | 396.7607
2702.7073 | 2447.7073 | 422.4281 | 397.7111 | 472.0307 | 2702.7073 | 472.0307 | 422.4281 | 397.7111
2703.7073 | 2448.7073 | 423.1193 | 398.6945 | 472.3261 | 2703.7073 | 472.3261 | 423.1193 | 398.6945
2704.7073 | 2449.7073 | 423.9375 | 399.6575 | 472.3599 | 2704.7073 | 472.3599 | 423.9375 | 399.6575
2705.7073 | 2450.7073 | 424.673 | 400.5925 | 472.4604 | 2705.7073 | 472.4604 | 424.673 | 400.5925
2706.7073 | 2451.7073 | 425.4877 | 401.5933 | 472.5895 | 2706.7073 | 472.5895 | 425.4877 | 401.5933
2707.7073 | 2452.7073 | 426.3077 | 402.5304 | 472.6602 | 2707.7073 | 472.6602 | 426.3077 | 402.5304
2708.7073 | 2453.7073 | 427.1568 | 403.5006 | 472.6604 | 2708.7073 | 472.6604 | 427.1568 | 403.5006
2709.7073 | 2454.7073 | 427.9696 | 404.4765 | 472.6326 | 2709.7073 | 472.6326 | 427.9696 | 404.4765
2710.7073 | 2455.7073 | 428.8623 | 405.4861 | 472.7034 | 2710.7073 | 472.7034 | 428.8623 | 405.4861
2711.7073 | 2456.7073 | 429.677 | 406.424 | 472.5117 | 2711.7073 | 472.5117 | 429.677 | 406.424
2712.7073 | 2457.7073 | 430.4468 | 407.294 | 472.2156 | 2712.7073 | 472.2156 | 430.4468 | 407.294
2713.7073 | 2458.7073 | 431.2417 | 408.1922 | 471.9883 | 2713.7073 | 471.9883 | 431.2417 | 408.1922
2714.7073 | 2459.7073 | 431.9121 | 409.0547 | 471.8326 | 2714.7073 | 471.8326 | 431.9121 | 409.0547
2715.7073 | 2460.7073 | 432.5671 | 409.9851 | 471.5776 | 2715.7073 | 471.5776 | 432.5671 | 409.9851
2716.7073 | 2461.7073 | 433.1693 | 410.8327 | 471.4628 | 2716.7073 | 471.4628 | 433.1693 | 410.8327
2717.7073 | 2462.7073 | 433.725 | 411.6812 | 471.3401 | 2717.7073 | 471.3401 | 433.725 | 411.6812
2718.7073 | 2463.7073 | 434.323 | 412.5765 | 471.0905 | 2718.7073 | 471.0905 | 434.323 | 412.5765
2719.7073 | 2464.7073 | 434.9821 | 413.4826 | 470.9271 | 2719.7073 | 470.9271 | 434.9821 | 413.4826
2720.7073 | 2465.7073 | 435.5898 | 414.3286 | 470.4416 | 2720.7073 | 470.4416 | 435.5898 | 414.3286
2721.7073 | 2466.7073 | 436.1511 | 415.14 | 469.9123 | 2721.7073 | 469.9123 | 436.1511 | 415.14
2722.7073 | 2467.7073 | 436.6999 | 416.0484 | 469.6623 | 2722.7073 | 469.6623 | 436.6999 | 416.0484
2723.7073 | 2468.7073 | 437.2846 | 416.859 | 469.3734 | 2723.7073 | 469.3734 | 437.2846 | 416.859
2724.7073 | 2469.7073 | 437.8328 | 417.6581 | 469.0514 | 2724.7073 | 469.0514 | 437.8328 | 417.6581
2725.7073 | 2470.7073 | 438.3478 | 418.4318 | 468.9295 | 2725.7073 | 468.9295 | 438.3478 | 418.4318
2726.7073 | 2471.7073 | 438.865 | 419.2917 | 468.7554 | 2726.7073 | 468.7554 | 438.865 | 419.2917
2727.7073 | 2472.7073 | 439.3724 | 420.0907 | 468.5601 | 2727.7073 | 468.5601 | 439.3724 | 420.0907
2728.7073 | 2473.7073 | 439.8895 | 420.8965 | 468.1719 | 2728.7073 | 468.1719 | 439.8895 | 420.8965
2729.7073 | 2474.7073 | 440.4632 | 421.7125 | 467.7976 | 2729.7073 | 467.7976 | 440.4632 | 421.7125
2730.7073 | 2475.7073 | 440.9528 | 422.4401 | 467.5382 | 2730.7073 | 467.5382 | 440.9528 | 422.4401
2731.7073 | 2476.7073 | 441.4814 | 423.1996 | 467.7044 | 2731.7073 | 467.7044 | 441.4814 | 423.1996
2732.7073 | 2477.7073 | 441.9942 | 423.9332 | 467.5753 | 2732.7073 | 467.5753 | 441.9942 | 423.9332
2733.7073 | 2478.7073 | 442.4741 | 424.6305 | 467.377 | 2733.7073 | 467.377 | 442.4741 | 424.6305
2734.7073 | 2479.7073 | 443.0106 | 425.4065 | 467.3561 | 2734.7073 | 467.3561 | 443.0106 | 425.4065
2735.7073 | 2480.7073 | 443.5056 | 426.1529 | 467.3244 | 2735.7073 | 467.3244 | 443.5056 | 426.1529
2736.7073 | 2481.7073 | 444.043 | 426.9713 | 467.4665 | 2736.7073 | 467.4665 | 444.043 | 426.9713
2737.7073 | 2482.7073 | 444.5783 | 427.6242 | 467.4294 | 2737.7073 | 467.4294 | 444.5783 | 427.6242
2738.7073 | 2483.7073 | 445.2086 | 428.3413 | 467.3115 | 2738.7073 | 467.3115 | 445.2086 | 428.3413
2739.7073 | 2484.7073 | 445.8564 | 429.0573 | 467.2171 | 2739.7073 | 467.2171 | 445.8564 | 429.0573
2740.7073 | 2485.7073 | 446.5096 | 429.8418 | 467.126 | 2740.7073 | 467.126 | 446.5096 | 429.8418
2741.7073 | 2486.7073 | 447.1795 | 430.6104 | 467.2222 | 2741.7073 | 467.2222 | 447.1795 | 430.6104
2742.7073 | 2487.7073 | 447.8911 | 431.3686 | 467.1325 | 2742.7073 | 467.1325 | 447.8911 | 431.3686
2743.7073 | 2488.7073 | 448.5804 | 432.1158 | 467.3001 | 2743.7073 | 467.3001 | 448.5804 | 432.1158
2744.7073 | 2489.7073 | 449.3029 | 432.8857 | 467.3261 | 2744.7073 | 467.3261 | 449.3029 | 432.8857
2745.7073 | 2490.7073 | 450.0385 | 433.641 | 467.4065 | 2745.7073 | 467.4065 | 450.0385 | 433.641
2746.7073 | 2491.7073 | 450.7276 | 434.4351 | 467.4882 | 2746.7073 | 467.4882 | 450.7276 | 434.4351
2747.7073 | 2492.7073 | 451.4365 | 435.16 | 467.5013 | 2747.7073 | 467.5013 | 451.4365 | 435.16
2748.7073 | 2493.7073 | 452.1189 | 435.8943 | 467.3401 | 2748.7073 | 467.3401 | 452.1189 | 435.8943
2749.7073 | 2494.7073 | 452.7603 | 436.6324 | 467.3096 | 2749.7073 | 467.3096 | 452.7603 | 436.6324
2750.7073 | 2495.7073 | 453.4039 | 437.3612 | 467.2342 | 2750.7073 | 467.2342 | 453.4039 | 437.3612
2751.7073 | 2496.7073 | 454.1125 | 438.1716 | 467.3275 | 2751.7073 | 467.3275 | 454.1125 | 438.1716
2752.7073 | 2497.7073 | 454.6811 | 438.9253 | 467.3471 | 2752.7073 | 467.3471 | 454.6811 | 438.9253
2753.7073 | 2498.7073 | 455.3597 | 439.6315 | 467.3702 | 2753.7073 | 467.3702 | 455.3597 | 439.6315
2754.7073 | 2499.7073 | 455.965 | 440.3032 | 467.5213 | 2754.7073 | 467.5213 | 455.965 | 440.3032
2755.7073 | 2500.7073 | 456.6767 | 440.9391 | 467.6526 | 2755.7073 | 467.6526 | 456.6767 | 440.9391
2756.7073 | 2501.7073 | 457.3301 | 441.5157 | 467.7917 | 2756.7073 | 467.7917 | 457.3301 | 441.5157
2757.7073 | 2502.7073 | 457.9894 | 442.1059 | 468.0724 | 2757.7073 | 468.0724 | 457.9894 | 442.1059
2758.7073 | 2503.7073 | 458.6505 | 442.6851 | 468.122 | 2758.7073 | 468.122 | 458.6505 | 442.6851
2759.7073 | 2504.7073 | 459.3561 | 443.276 | 468.1917 | 2759.7073 | 468.1917 | 459.3561 | 443.276
2760.7073 | 2505.7073 | 459.9894 | 443.863 | 468.2445 | 2760.7073 | 468.2445 | 459.9894 | 443.863
2761.7073 | 2506.7073 | 460.6051 | 444.4431 | 468.1828 | 2761.7073 | 468.1828 | 460.6051 | 444.4431
2762.7073 | 2507.7073 | 461.2148 | 445.084 | 468.3074 | 2762.7073 | 468.3074 | 461.2148 | 445.084
2763.7073 | 2508.7073 | 461.8547 | 445.6892 | 468.2316 | 2763.7073 | 468.2316 | 461.8547 | 445.6892
2764.7073 | 2509.7073 | 462.4407 | 446.3187 | 468.3126 | 2764.7073 | 468.3126 | 462.4407 | 446.3187
2765.7073 | 2510.7073 | 463.0211 | 446.9403 | 468.4081 | 2765.7073 | 468.4081 | 463.0211 | 446.9403
2766.7073 | 2511.7073 | 463.6423 | 447.6217 | 468.6851 | 2766.7073 | 468.6851 | 463.6423 | 447.6217
2767.7073 | 2512.7073 | 464.183 | 448.1971 | 468.63 | 2767.7073 | 468.63 | 464.183 | 448.1971
2768.7073 | 2513.7073 | 464.6897 | 448.7433 | 468.5051 | 2768.7073 | 468.5051 | 464.6897 | 448.7433
2769.7073 | 2514.7073 | 465.2606 | 449.2955 | 468.4802 | 2769.7073 | 468.4802 | 465.2606 | 449.2955
2770.7073 | 2515.7073 | 465.8554 | 449.8989 | 468.335 | 2770.7073 | 468.335 | 465.8554 | 449.8989
2771.7073 | 2516.7073 | 466.3398 | 450.4488 | 468.2919 | 2771.7073 | 468.2919 | 466.3398 | 450.4488
2772.7073 | 2517.7073 | 466.9655 | 451.0458 | 468.4101 | 2772.7073 | 468.4101 | 466.9655 | 451.0458
2773.7073 | 2518.7073 | 467.593 | 451.7624 | 468.3259 | 2773.7073 | 468.3259 | 467.593 | 451.7624
2774.7073 | 2519.7073 | 468.0388 | 452.2303 | 468.3654 | 2774.7073 | 468.3654 | 468.0388 | 452.2303
2775.7073 | 2520.7073 | 468.4996 | 452.8186 | 468.3122 | 2775.7073 | 468.3122 | 468.4996 | 452.8186
2776.7073 | 2521.7073 | 468.9846 | 453.3634 | 468.1706 | 2776.7073 | 468.1706 | 468.9846 | 453.3634
2777.7073 | 2522.7073 | 469.3865 | 453.9803 | 468.0904 | 2777.7073 | 468.0904 | 469.3865 | 453.9803
2778.7073 | 2523.7073 | 469.7884 | 454.4838 | 468.0779 | 2778.7073 | 468.0779 | 469.7884 | 454.4838
2779.7073 | 2524.7073 | 470.2741 | 454.9618 | 468.1453 | 2779.7073 | 468.1453 | 470.2741 | 454.9618
2780.7073 | 2525.7073 | 470.6896 | 455.581 | 468.3259 | 2780.7073 | 468.3259 | 470.6896 | 455.581
2781.7073 | 2526.7073 | 471.1026 | 456.0951 | 468.5209 | 2781.7073 | 468.5209 | 471.1026 | 456.0951
2782.7073 | 2527.7073 | 471.4481 | 456.6874 | 468.6983 | 2782.7073 | 468.6983 | 471.4481 | 456.6874
2783.7073 | 2528.7073 | 471.8918 | 457.1597 | 468.9071 | 2783.7073 | 468.9071 | 471.8918 | 457.1597
2784.7073 | 2529.7073 | 472.241 | 457.6697 | 469.1827 | 2784.7073 | 469.1827 | 472.241 | 457.6697
2785.7073 | 2530.7073 | 472.6224 | 458.1008 | 469.3471 | 2785.7073 | 469.3471 | 472.6224 | 458.1008
2786.7073 | 2531.7073 | 472.9839 | 458.4552 | 469.4208 | 2786.7073 | 469.4208 | 472.9839 | 458.4552
2787.7073 | 2532.7073 | 473.3994 | 458.8516 | 469.4707 | 2787.7073 | 469.4707 | 473.3994 | 458.8516
2788.7073 | 2533.7073 | 473.7007 | 459.3191 | 469.6378 | 2788.7073 | 469.6378 | 473.7007 | 459.3191
2789.7073 | 2534.7073 | 474.1333 | 459.7201 | 469.7018 | 2789.7073 | 469.7018 | 474.1333 | 459.7201
2790.7073 | 2535.7073 | 474.5026 | 460.0671 | 469.5772 | 2790.7073 | 469.5772 | 474.5026 | 460.0671
2791.7073 | 2536.7073 | 474.7878 | 460.4462 | 469.3788 | 2791.7073 | 469.3788 | 474.7878 | 460.4462
2792.7073 | 2537.7073 | 475.012 | 460.6625 | 469.1146 | 2792.7073 | 469.1146 | 475.012 | 460.6625
2793.7073 | 2538.7073 | 475.4281 | 460.9647 | 468.9594 | 2793.7073 | 468.9594 | 475.4281 | 460.9647
2794.7073 | 2539.7073 | 475.684 | 461.2042 | 468.9357 | 2794.7073 | 468.9357 | 475.684 | 461.2042
2795.7073 | 2540.7073 | 475.9553 | 461.434 | 468.9259 | 2795.7073 | 468.9259 | 475.9553 | 461.434
2796.7073 | 2541.7073 | 476.1659 | 461.6563 | 469.1212 | 2796.7073 | 469.1212 | 476.1659 | 461.6563
2797.7073 | 2542.7073 | 476.2477 | 461.8163 | 469.27 | 2797.7073 | 469.27 | 476.2477 | 461.8163
2798.7073 | 2543.7073 | 476.3676 | 462.0347 | 469.4961 | 2798.7073 | 469.4961 | 476.3676 | 462.0347
2799.7073 | 2544.7073 | 476.6615 | 462.2285 | 469.5977 | 2799.7073 | 469.5977 | 476.6615 | 462.2285
2800.7073 | 2545.7073 | 476.7333 | 462.4041 | 469.6076 | 2800.7073 | 469.6076 | 476.7333 | 462.4041
2801.7073 | 2546.7073 | 476.9828 | 462.5879 | 469.4463 | 2801.7073 | 469.4463 | 476.9828 | 462.5879
2802.7073 | 2547.7073 | 477.0438 | 462.8268 | 469.1758 | 2802.7073 | 469.1758 | 477.0438 | 462.8268
2803.7073 | 2548.7073 | 477.1261 | 463.0626 | 469.0698 | 2803.7073 | 469.0698 | 477.1261 | 463.0626
2804.7073 | 2549.7073 | 477.1917 | 463.0303 | 469.1223 | 2804.7073 | 469.1223 | 477.1917 | 463.0303
2805.7073 | 2550.7073 | 477.1711 | 463.0196 | 469.1458 | 2805.7073 | 469.1458 | 477.1711 | 463.0196
2806.7073 | 2551.7073 | 477.2783 | 463.1879 | 469.0555 | 2806.7073 | 469.0555 | 477.2783 | 463.1879
2807.7073 | 2552.7073 | 477.3216 | 463.2741 | 468.9156 | 2807.7073 | 468.9156 | 477.3216 | 463.2741
2808.7073 | 2553.7073 | 477.3084 | 463.1639 | 468.9488 | 2808.7073 | 468.9488 | 477.3084 | 463.1639
2809.7073 | 2554.7073 | 477.3325 | 463.3543 | 468.9572 | 2809.7073 | 468.9572 | 477.3325 | 463.3543
2810.7073 | 2555.7073 | 477.3362 | 463.3799 | 469.0658 | 2810.7073 | 469.0658 | 477.3362 | 463.3799
2811.7073 | 2556.7073 | 477.2951 | 463.4885 | 469.1994 | 2811.7073 | 469.1994 | 477.2951 | 463.4885
2812.7073 | 2557.7073 | 477.3064 | 463.5609 | 469.2919 | 2812.7073 | 469.2919 | 477.3064 | 463.5609
2813.7073 | 2558.7073 | 477.2837 | 463.582 | 469.3911 | 2813.7073 | 469.3911 | 477.2837 | 463.582
2814.7073 | 2559.7073 | 477.3634 | 463.8159 | 469.6361 | 2814.7073 | 469.6361 | 477.3634 | 463.8159
2815.7073 | 2560.7073 | 477.3482 | 463.9684 | 469.5823 | 2815.7073 | 469.5823 | 477.3482 | 463.9684
2816.7073 | 2561.7073 | 477.3616 | 464.0811 | 469.5008 | 2816.7073 | 469.5008 | 477.3616 | 464.0811
2817.7073 | 2562.7073 | 477.2174 | 464.1946 | 469.6487 | 2817.7073 | 469.6487 | 477.2174 | 464.1946
2818.7073 | 2563.7073 | 477.3648 | 464.5508 | 469.8184 | 2818.7073 | 469.8184 | 477.3648 | 464.5508
2819.7073 | 2564.7073 | 477.3699 | 464.7517 | 469.8685 | 2819.7073 | 469.8685 | 477.3699 | 464.7517
2820.7073 | 2565.7073 | 477.2901 | 464.7894 | 469.8804 | 2820.7073 | 469.8804 | 477.2901 | 464.7894
2821.7073 | 2566.7073 | 477.225 | 464.9688 | 469.9106 | 2821.7073 | 469.9106 | 477.225 | 464.9688
2822.7073 | 2567.7073 | 477.3839 | 465.3973 | 469.803 | 2822.7073 | 469.803 | 477.3839 | 465.3973
2823.7073 | 2568.7073 | 477.36 | 465.6381 | 469.6482 | 2823.7073 | 469.6482 | 477.36 | 465.6381
2824.7073 | 2569.7073 | 477.3561 | 466.0049 | 469.43 | 2824.7073 | 469.43 | 477.3561 | 466.0049
2825.7073 | 2570.7073 | 477.5225 | 466.3748 | 469.1884 | 2825.7073 | 469.1884 | 477.5225 | 466.3748
2826.7073 | 2571.7073 | 477.4371 | 466.5839 | 468.954 | 2826.7073 | 468.954 | 477.4371 | 466.5839
2827.7073 | 2572.7073 | 477.5797 | 467.0068 | 468.9462 | 2827.7073 | 468.9462 | 477.5797 | 467.0068
2828.7073 | 2573.7073 | 477.5712 | 467.6499 | 468.9781 | 2828.7073 | 468.9781 | 477.5712 | 467.6499
2829.7073 | 2574.7073 | 477.6299 | 468.3298 | 468.8251 | 2829.7073 | 468.8251 | 477.6299 | 468.3298
2830.7073 | 2575.7073 | 477.6241 | 468.8265 | 468.6166 | 2830.7073 | 468.6166 | 477.6241 | 468.8265
2831.7073 | 2576.7073 | 477.7281 | 469.5013 | 468.4464 | 2831.7073 | 468.4464 | 477.7281 | 469.5013
2832.7073 | 2577.7073 | 477.786 | 470.1807 | 468.3154 | 2832.7073 | 468.3154 | 477.786 | 470.1807
2833.7073 | 2578.7073 | 477.8465 | 470.9044 | 468.1662 | 2833.7073 | 468.1662 | 477.8465 | 470.9044
2834.7073 | 2579.7073 | 477.8307 | 471.4145 | 468.345 | 2834.7073 | 468.345 | 477.8307 | 471.4145
2835.7073 | 2580.7073 | 477.8822 | 472.0803 | 468.3729 | 2835.7073 | 468.3729 | 477.8822 | 472.0803
2836.7073 | 2581.7073 | 478.0051 | 472.8217 | 468.1134 | 2836.7073 | 468.1134 | 478.0051 | 472.8217
2837.7073 | 2582.7073 | 478.0404 | 473.453 | 467.7138 | 2837.7073 | 467.7138 | 478.0404 | 473.453
2838.7073 | 2583.7073 | 478.1736 | 473.9185 | 467.7537 | 2838.7073 | 467.7537 | 478.1736 | 473.9185
2839.7073 | 2584.7073 | 478.3835 | 474.8013 | 467.6572 | 2839.7073 | 467.6572 | 478.3835 | 474.8013
2840.7073 | 2585.7073 | 478.5358 | 475.3968 | 467.366 | 2840.7073 | 467.366 | 478.5358 | 475.3968
2841.7073 | 2586.7073 | 478.6389 | 476.4154 | 467.1268 | 2841.7073 | 467.1268 | 478.6389 | 476.4154
2842.7073 | 2587.7073 | 478.7866 | 476.8043 | 466.9812 | 2842.7073 | 466.9812 | 478.7866 | 476.8043
2843.7073 | 2588.7073 | 478.8081 | 477.6277 | 466.794 | 2843.7073 | 466.794 | 478.8081 | 477.6277
2844.7073 | 2589.7073 | 479.0382 | 478.5666 | 466.754 | 2844.7073 | 466.754 | 479.0382 | 478.5666
2845.7073 | 2590.7073 | 479.1611 | 479.1843 | 466.6264 | 2845.7073 | 466.6264 | 479.1611 | 479.1843
2846.7073 | 2591.7073 | 479.4152 | 479.2983 | 466.49 | 2846.7073 | 466.49 | 479.4152 | 479.2983
2847.7073 | 2592.7073 | 479.515 | 479.6878 | 466.4015 | 2847.7073 | 466.4015 | 479.515 | 479.6878
2848.7073 | 2593.7073 | 479.6852 | 480.0645 | 466.2529 | 2848.7073 | 466.2529 | 479.6852 | 480.0645
2849.7073 | 2594.7073 | 479.9229 | 480.4655 | 466.0469 | 2849.7073 | 466.0469 | 479.9229 | 480.4655
2850.7073 | 2595.7073 | 479.9496 | 481.3915 | 465.9781 | 2850.7073 | 465.9781 | 479.9496 | 481.3915
2851.7073 | 2596.7073 | 480.3791 | 481.616 | 465.8226 | 2851.7073 | 465.8226 | 480.3791 | 481.616
2852.7073 | 2597.7073 | 480.601 | 482.1843 | 465.6826 | 2852.7073 | 465.6826 | 480.601 | 482.1843
2853.7073 | 2598.7073 | 480.7501 | 482.4905 | 465.4785 | 2853.7073 | 465.4785 | 480.7501 | 482.4905
2854.7073 | 2599.7073 | 480.6508 | 482.0879 | 465.3355 | 2854.7073 | 465.3355 | 480.6508 | 482.0879
2855.7073 | 2600.7073 | 480.5622 | 482.8793 | 465.2244 | 2855.7073 | 465.2244 | 480.5622 | 482.8793
2856.7073 | 2601.7073 | 480.721 | 482.0161 | 465.1172 | 2856.7073 | 465.1172 | 480.721 | 482.0161
2857.7073 | 2602.7073 | 480.6447 | 481.8024 | 465.1029 | 2857.7073 | 465.1029 | 480.6447 | 481.8024
2858.7073 | 2603.7073 | 480.5216 | 481.4183 | 465.0512 | 2858.7073 | 465.0512 | 480.5216 | 481.4183
2859.7073 | 2604.7073 | 480.5563 | 481.6891 | 464.9267 | 2859.7073 | 464.9267 | 480.5563 | 481.6891
2860.7073 | 2605.7073 | 480.7744 | 480.9308 | 464.9711 | 2860.7073 | 464.9711 | 480.7744 | 480.9308
2861.7073 | 2606.7073 | 480.8961 | 480.9222 | 464.9882 | 2861.7073 | 464.9882 | 480.8961 | 480.9222
2862.7073 | 2607.7073 | 480.9025 | 481.1928 | 465.1104 | 2862.7073 | 465.1104 | 480.9025 | 481.1928
2863.7073 | 2608.7073 | 480.8347 | 480.874 | 465.1457 | 2863.7073 | 465.1457 | 480.8347 | 480.874
2864.7073 | 2609.7073 | 480.8551 | 480.8046 | 465.203 | 2864.7073 | 465.203 | 480.8551 | 480.8046
2865.7073 | 2610.7073 | 480.9756 | 481.0075 | 465.2934 | 2865.7073 | 465.2934 | 480.9756 | 481.0075
2866.7073 | 2611.7073 | 480.9872 | 480.789 | 465.3988 | 2866.7073 | 465.3988 | 480.9872 | 480.789
2867.7073 | 2612.7073 | 481.0548 | 480.8375 | 465.5321 | 2867.7073 | 465.5321 | 481.0548 | 480.8375
2868.7073 | 2613.7073 | 481.1448 | 481.6599 | 465.587 | 2868.7073 | 465.587 | 481.1448 | 481.6599
2869.7073 | 2614.7073 | 481.1505 | 481.6164 | 465.586 | 2869.7073 | 465.586 | 481.1505 | 481.6164
2870.7073 | 2615.7073 | 481.5044 | 480.7512 | 465.6732 | 2870.7073 | 465.6732 | 481.5044 | 480.7512
2871.7073 | 2616.7073 | 481.8247 | 480.8493 | 465.9391 | 2871.7073 | 465.9391 | 481.8247 | 480.8493
2872.7073 | 2617.7073 | 481.9022 | 481.0631 | 466.2158 | 2872.7073 | 466.2158 | 481.9022 | 481.0631
2873.7073 | 2618.7073 | 482.2499 | 480.5112 | 466.1447 | 2873.7073 | 466.1447 | 482.2499 | 480.5112
2874.7073 | 2619.7073 | 482.4383 | 480.9645 | 466.1796 | 2874.7073 | 466.1796 | 482.4383 | 480.9645
2875.7073 | 2620.7073 | 482.7088 | 480.5834 | 466.1492 | 2875.7073 | 466.1492 | 482.7088 | 480.5834
2876.7073 | 2621.7073 | 482.9931 | 480.508 | 466.0425 | 2876.7073 | 466.0425 | 482.9931 | 480.508
2877.7073 | 2622.7073 | 483.3989 | 479.8666 | 466.0283 | 2877.7073 | 466.0283 | 483.3989 | 479.8666
2878.7073 | 2623.7073 | 483.6917 | 479.7446 | 465.9733 | 2878.7073 | 465.9733 | 483.6917 | 479.7446
2879.7073 | 2624.7073 | 483.966 | 479.6538 | 465.8645 | 2879.7073 | 465.8645 | 483.966 | 479.6538
2880.7073 | 2625.7073 | 484.159 | 479.4512 | 465.8762 | 2880.7073 | 465.8762 | 484.159 | 479.4512
2881.7073 | 2626.7073 | 484.5053 | 479.433 | 465.8719 | 2881.7073 | 465.8719 | 484.5053 | 479.433
2882.7073 | 2627.7073 | 484.808 | 479.4243 | 465.8966 | 2882.7073 | 465.8966 | 484.808 | 479.4243
2883.7073 | 2628.7073 | 485.1597 | 479.8289 | 465.862 | 2883.7073 | 465.862 | 485.1597 | 479.8289
2884.7073 | 2629.7073 | 485.4351 | 479.7467 | 465.834 | 2884.7073 | 465.834 | 485.4351 | 479.7467
2885.7073 | 2630.7073 | 485.7559 | 479.6262 | 465.8802 | 2885.7073 | 465.8802 | 485.7559 | 479.6262
2886.7073 | 2631.7073 | 486.5292 | 479.112 | 466.0392 | 2886.7073 | 466.0392 | 486.5292 | 479.112
2887.7073 | 2632.7073 | 487.0326 | 479.4216 | 466.0501 | 2887.7073 | 466.0501 | 487.0326 | 479.4216
2888.7073 | 2633.7073 | 487.8258 | 479.4283 | 466.2314 | 2888.7073 | 466.2314 | 487.8258 | 479.4283
2889.7073 | 2634.7073 | 488.2015 | 479.2301 | 466.3065 | 2889.7073 | 466.3065 | 488.2015 | 479.2301
2890.7073 | 2635.7073 | 488.3967 | 479.159 | 466.4077 | 2890.7073 | 466.4077 | 488.3967 | 479.159
2891.7073 | 2636.7073 | 488.5785 | 479.5485 | 466.3264 | 2891.7073 | 466.3264 | 488.5785 | 479.5485
2892.7073 | 2637.7073 | 488.8657 | 479.9195 | 466.191 | 2892.7073 | 466.191 | 488.8657 | 479.9195
2893.7073 | 2638.7073 | 489.0872 | 480.0292 | 466.1652 | 2893.7073 | 466.1652 | 489.0872 | 480.0292
2894.7073 | 2639.7073 | 489.2435 | 480.0265 | 466.0638 | 2894.7073 | 466.0638 | 489.2435 | 480.0265
2895.7073 | 2640.7073 | 489.6311 | 480.1349 | 465.9534 | 2895.7073 | 465.9534 | 489.6311 | 480.1349
2896.7073 | 2641.7073 | 490.0175 | 480.2476 | 465.9128 | 2896.7073 | 465.9128 | 490.0175 | 480.2476
2897.7073 | 2642.7073 | 490.562 | 480.013 | 465.8694 | 2897.7073 | 465.8694 | 490.562 | 480.013
2898.7073 | 2643.7073 | 490.7702 | 479.8711 | 465.8346 | 2898.7073 | 465.8346 | 490.7702 | 479.8711
2899.7073 | 2644.7073 | 491.2113 | 479.6529 | 465.8172 | 2899.7073 | 465.8172 | 491.2113 | 479.6529
2900.7073 | 2645.7073 | 491.3418 | 479.4263 | 465.739 | 2900.7073 | 465.739 | 491.3418 | 479.4263
2901.7073 | 2646.7073 | 491.4984 | 479.3055 | 465.6215 | 2901.7073 | 465.6215 | 491.4984 | 479.3055
2902.7073 | 2647.7073 | 491.7259 | 479.0537 | 465.5677 | 2902.7073 | 465.5677 | 491.7259 | 479.0537
2903.7073 | 2648.7073 | 491.8214 | 479.1911 | 465.4292 | 2903.7073 | 465.4292 | 491.8214 | 479.1911
2904.7073 | 2649.7073 | 492.1933 | 478.9703 | 465.2994 | 2904.7073 | 465.2994 | 492.1933 | 478.9703
2905.7073 | 2650.7073 | 492.5822 | 478.9385 | 465.1632 | 2905.7073 | 465.1632 | 492.5822 | 478.9385
2906.7073 | 2651.7073 | 492.4404 | 479.2171 | 465.0418 | 2906.7073 | 465.0418 | 492.4404 | 479.2171
2907.7073 | 2652.7073 | 492.5159 | 479.3574 | 464.9341 | 2907.7073 | 464.9341 | 492.5159 | 479.3574
2908.7073 | 2653.7073 | 492.9089 | 479.4246 | 464.8234 | 2908.7073 | 464.8234 | 492.9089 | 479.4246
2909.7073 | 2654.7073 | 493.2435 | 479.4858 | 464.6667 | 2909.7073 | 464.6667 | 493.2435 | 479.4858
2910.7073 | 2655.7073 | 493.3993 | 479.3562 | 464.5596 | 2910.7073 | 464.5596 | 493.3993 | 479.3562
2911.7073 | 2656.7073 | 493.5153 | 479.1258 | 464.4138 | 2911.7073 | 464.4138 | 493.5153 | 479.1258
2912.7073 | 2657.7073 | 493.6709 | 478.7802 | 464.3329 | 2912.7073 | 464.3329 | 493.6709 | 478.7802
2913.7073 | 2658.7073 | 493.893 | 478.6038 | 464.2245 | 2913.7073 | 464.2245 | 493.893 | 478.6038
2914.7073 | 2659.7073 | 494.082 | 478.6766 | 464.1004 | 2914.7073 | 464.1004 | 494.082 | 478.6766
2915.7073 | 2660.7073 | 494.3287 | 478.9376 | 463.9814 | 2915.7073 | 463.9814 | 494.3287 | 478.9376
2916.7073 | 2661.7073 | 494.5205 | 478.6523 | 463.8019 | 2916.7073 | 463.8019 | 494.5205 | 478.6523
2917.7073 | 2662.7073 | 494.6786 | 478.7781 | 463.5472 | 2917.7073 | 463.5472 | 494.6786 | 478.7781
2918.7073 | 2663.7073 | 494.9634 | 479.1491 | 463.4651 | 2918.7073 | 463.4651 | 494.9634 | 479.1491
2919.7073 | 2664.7073 | 495.2609 | 479.484 | 463.351 | 2919.7073 | 463.351 | 495.2609 | 479.484
2920.7073 | 2665.7073 | 495.4798 | 479.5712 | 463.1736 | 2920.7073 | 463.1736 | 495.4798 | 479.5712
2921.7073 | 2666.7073 | 496.5294 | 479.842 | 463.0179 | 2921.7073 | 463.0179 | 496.5294 | 479.842
2922.7073 | 2667.7073 | 497.0449 | 480.2098 | 462.9614 | 2922.7073 | 462.9614 | 497.0449 | 480.2098
2923.7073 | 2668.7073 | 497.2337 | 480.7541 | 462.9007 | 2923.7073 | 462.9007 | 497.2337 | 480.7541
2924.7073 | 2669.7073 | 497.6098 | 480.7083 | 462.825 | 2924.7073 | 462.825 | 497.6098 | 480.7083
2925.7073 | 2670.7073 | 497.8462 | 480.9353 | 462.7414 | 2925.7073 | 462.7414 | 497.8462 | 480.9353
2926.7073 | 2671.7073 | 497.7435 | 481.0621 | 462.6651 | 2926.7073 | 462.6651 | 497.7435 | 481.0621
2927.7073 | 2672.7073 | 498.0411 | 481.6277 | 462.6307 | 2927.7073 | 462.6307 | 498.0411 | 481.6277
2928.7073 | 2673.7073 | 498.5936 | 481.2397 | 462.5879 | 2928.7073 | 462.5879 | 498.5936 | 481.2397
2929.7073 | 2674.7073 | 498.6955 | 481.6397 | 462.6524 | 2929.7073 | 462.6524 | 498.6955 | 481.6397
2930.7073 | 2675.7073 | 498.623 | 481.7192 | 462.7413 | 2930.7073 | 462.7413 | 498.623 | 481.7192
2931.7073 | 2676.7073 | 498.6871 | 481.8864 | 462.8569 | 2931.7073 | 462.8569 | 498.6871 | 481.8864
2932.7073 | 2677.7073 | 498.6513 | 482.0792 | 463.0564 | 2932.7073 | 463.0564 | 498.6513 | 482.0792
2933.7073 | 2678.7073 | 498.8803 | 482.2785 | 463.1978 | 2933.7073 | 463.1978 | 498.8803 | 482.2785
2934.7073 | 2679.7073 | 498.8776 | 481.9445 | 463.2969 | 2934.7073 | 463.2969 | 498.8776 | 481.9445
2935.7073 | 2680.7073 | 499.1577 | 481.2788 | 463.3707 | 2935.7073 | 463.3707 | 499.1577 | 481.2788
2936.7073 | 2681.7073 | 499.1583 | 480.4657 | 463.4042 | 2936.7073 | 463.4042 | 499.1583 | 480.4657
2937.7073 | 2682.7073 | 498.9599 | 480.2085 | 463.4594 | 2937.7073 | 463.4594 | 498.9599 | 480.2085
2938.7073 | 2683.7073 | 499.1134 | 480.1723 | 463.5832 | 2938.7073 | 463.5832 | 499.1134 | 480.1723
2939.7073 | 2684.7073 | 499.2168 | 480.724 | 463.6798 | 2939.7073 | 463.6798 | 499.2168 | 480.724
2940.7073 | 2685.7073 | 499.4524 | 480.6005 | 463.7241 | 2940.7073 | 463.7241 | 499.4524 | 480.6005
2941.7073 | 2686.7073 | 499.2745 | 480.5682 | 463.8222 | 2941.7073 | 463.8222 | 499.2745 | 480.5682
2942.7073 | 2687.7073 | 499.8535 | 480.751 | 463.9716 | 2942.7073 | 463.9716 | 499.8535 | 480.751
2943.7073 | 2688.7073 | 499.5061 | 481.5045 | 464.0602 | 2943.7073 | 464.0602 | 499.5061 | 481.5045
2944.7073 | 2689.7073 | 499.9029 | 480.4575 | 464.0033 | 2944.7073 | 464.0033 | 499.9029 | 480.4575
2945.7073 | 2690.7073 | 499.8554 | 480.5285 | 463.9835 | 2945.7073 | 463.9835 | 499.8554 | 480.5285
2946.7073 | 2691.7073 | 499.9766 | 481.5278 | 464.0714 | 2946.7073 | 464.0714 | 499.9766 | 481.5278
2947.7073 | 2692.7073 | 499.9572 | 481.6785 | 464.177 | 2947.7073 | 464.177 | 499.9572 | 481.6785
2948.7073 | 2693.7073 | 500.031 | 481.6505 | 464.1964 | 2948.7073 | 464.1964 | 500.031 | 481.6505
2949.7073 | 2694.7073 | 500.1974 | 481.8628 | 464.2189 | 2949.7073 | 464.2189 | 500.1974 | 481.8628
2950.7073 | 2695.7073 | 500.1685 | 481.6613 | 464.2905 | 2950.7073 | 464.2905 | 500.1685 | 481.6613
2951.7073 | 2696.7073 | 500.1601 | 481.9206 | 464.3592 | 2951.7073 | 464.3592 | 500.1601 | 481.9206
2952.7073 | 2697.7073 | 500.4005 | 481.6265 | 464.4577 | 2952.7073 | 464.4577 | 500.4005 | 481.6265
2953.7073 | 2698.7073 | 500.5132 | 481.7251 | 464.6211 | 2953.7073 | 464.6211 | 500.5132 | 481.7251
2954.7073 | 2699.7073 | 500.919 | 482.0402 | 464.7626 | 2954.7073 | 464.7626 | 500.919 | 482.0402
2955.7073 | 2700.7073 | 500.8478 | 481.738 | 464.7393 | 2955.7073 | 464.7393 | 500.8478 | 481.738
2956.7073 | 2701.7073 | 500.9542 | 481.5662 | 464.6735 | 2956.7073 | 464.6735 | 500.9542 | 481.5662
2957.7073 | 2702.7073 | 501.0746 | 481.3459 | 464.4979 | 2957.7073 | 464.4979 | 501.0746 | 481.3459
2958.7073 | 2703.7073 | 501.1929 | 481.533 | 464.3774 | 2958.7073 | 464.3774 | 501.1929 | 481.533
2959.7073 | 2704.7073 | 501.2593 | 482.0928 | 464.3797 | 2959.7073 | 464.3797 | 501.2593 | 482.0928
2960.7073 | 2705.7073 | 501.4962 | 481.3706 | 464.4128 | 2960.7073 | 464.4128 | 501.4962 | 481.3706
2961.7073 | 2706.7073 | 501.688 | 481.4305 | 464.408 | 2961.7073 | 464.408 | 501.688 | 481.4305
2962.7073 | 2707.7073 | 501.6562 | 482.0855 | 464.3758 | 2962.7073 | 464.3758 | 501.6562 | 482.0855
2963.7073 | 2708.7073 | 502.0094 | 482.4766 | 464.4631 | 2963.7073 | 464.4631 | 502.0094 | 482.4766
2964.7073 | 2709.7073 | 502.1721 | 483.0305 | 464.5073 | 2964.7073 | 464.5073 | 502.1721 | 483.0305
2965.7073 | 2710.7073 | 502.3869 | 483.3227 | 464.5218 | 2965.7073 | 464.5218 | 502.3869 | 483.3227
2966.7073 | 2711.7073 | 502.8617 | 483.092 | 464.5375 | 2966.7073 | 464.5375 | 502.8617 | 483.092
2967.7073 | 2712.7073 | 502.8903 | 482.9294 | 464.5198 | 2967.7073 | 464.5198 | 502.8903 | 482.9294
2968.7073 | 2713.7073 | 503.0219 | 483.5673 | 464.5552 | 2968.7073 | 464.5552 | 503.0219 | 483.5673
2969.7073 | 2714.7073 | 503.4055 | 483.9216 | 464.6418 | 2969.7073 | 464.6418 | 503.4055 | 483.9216
2970.7073 | 2715.7073 | 503.3719 | 484.5781 | 464.6901 | 2970.7073 | 464.6901 | 503.3719 | 484.5781
2971.7073 | 2716.7073 | 503.6044 | 484.9388 | 464.7222 | 2971.7073 | 464.7222 | 503.6044 | 484.9388
2972.7073 | 2717.7073 | 503.9066 | 485.4053 | 464.8506 | 2972.7073 | 464.8506 | 503.9066 | 485.4053
2973.7073 | 2718.7073 | 504.113 | 485.4644 | 464.907 | 2973.7073 | 464.907 | 504.113 | 485.4644
2974.7073 | 2719.7073 | 503.5565 | 485.5183 | 465.0281 | 2974.7073 | 465.0281 | 503.5565 | 485.5183
2975.7073 | 2720.7073 | 503.6247 | 485.5771 | 465.0191 | 2975.7073 | 465.0191 | 503.6247 | 485.5771
2976.7073 | 2721.7073 | 503.8014 | 485.8466 | 465.0641 | 2976.7073 | 465.0641 | 503.8014 | 485.8466
2977.7073 | 2722.7073 | 503.9539 | 486.2613 | 465.1717 | 2977.7073 | 465.1717 | 503.9539 | 486.2613
2978.7073 | 2723.7073 | 504.2531 | 486.6311 | 465.1028 | 2978.7073 | 465.1028 | 504.2531 | 486.6311
2979.7073 | 2724.7073 | 504.3525 | 486.8069 | 465.0463 | 2979.7073 | 465.0463 | 504.3525 | 486.8069
2980.7073 | 2725.7073 | 504.748 | 487.466 | 465.0283 | 2980.7073 | 465.0283 | 504.748 | 487.466
2981.7073 | 2726.7073 | 504.8816 | 487.5202 | 465.0302 | 2981.7073 | 465.0302 | 504.8816 | 487.5202
2982.7073 | 2727.7073 | 505.1008 | 488.5079 | 465.0146 | 2982.7073 | 465.0146 | 505.1008 | 488.5079
2983.7073 | 2728.7073 | 504.6459 | 488.4329 | 465.078 | 2983.7073 | 465.078 | 504.6459 | 488.4329
2984.7073 | 2729.7073 | 504.852 | 488.7256 | 465.0807 | 2984.7073 | 465.0807 | 504.852 | 488.7256
2985.7073 | 2730.7073 | 504.7567 | 489.1238 | 465.1611 | 2985.7073 | 465.1611 | 504.7567 | 489.1238
2986.7073 | 2731.7073 | 505.0073 | 489.5098 | 465.2858 | 2986.7073 | 465.2858 | 505.0073 | 489.5098
2987.7073 | 2732.7073 | 505.3273 | 489.9372 | 465.3267 | 2987.7073 | 465.3267 | 505.3273 | 489.9372
2988.7073 | 2733.7073 | 505.0537 | 490.01 | 465.3877 | 2988.7073 | 465.3877 | 505.0537 | 490.01
2989.7073 | 2734.7073 | 504.9027 | 490.4572 | 465.4532 | 2989.7073 | 465.4532 | 504.9027 | 490.4572
2990.7073 | 2735.7073 | 504.8775 | 491.2667 | 465.4357 | 2990.7073 | 465.4357 | 504.8775 | 491.2667
2991.7073 | 2736.7073 | 504.7137 | 491.2802 | 465.4502 | 2991.7073 | 465.4502 | 504.7137 | 491.2802
2992.7073 | 2737.7073 | 504.9207 | 491.392 | 465.4976 | 2992.7073 | 465.4976 | 504.9207 | 491.392
2993.7073 | 2738.7073 | 504.638 | 491.6535 | 465.5653 | 2993.7073 | 465.5653 | 504.638 | 491.6535
2994.7073 | 2739.7073 | 504.7523 | 492.0895 | 465.5712 | 2994.7073 | 465.5712 | 504.7523 | 492.0895
2995.7073 | 2740.7073 | 504.6782 | 492.4698 | 465.6112 | 2995.7073 | 465.6112 | 504.6782 | 492.4698
2996.7073 | 2741.7073 | 504.8541 | 492.596 | 465.6844 | 2996.7073 | 465.6844 | 504.8541 | 492.596
2997.7073 | 2742.7073 | 504.947 | 493.2607 | 465.7623 | 2997.7073 | 465.7623 | 504.947 | 493.2607
2998.7073 | 2743.7073 | 505.0493 | 493.8653 | 465.8517 | 2998.7073 | 465.8517 | 505.0493 | 493.8653
2999.7073 | 2744.7073 | 505.4026 | 494.0339 | 465.9732 | 2999.7073 | 465.9732 | 505.4026 | 494.0339
3000.7073 | 2745.7073 | 505.345 | 494.4866 | 465.9999 | 3000.7073 | 465.9999 | 505.345 | 494.4866
3001.7073 | 2746.7073 | 505.5137 | 494.8439 | 466.1161 | 3001.7073 | 466.1161 | 505.5137 | 494.8439
3002.7073 | 2747.7073 | 505.6763 | 495.1451 | 466.1902 | 3002.7073 | 466.1902 | 505.6763 | 495.1451
3003.7073 | 2748.7073 | 505.8967 | 495.5342 | 466.2112 | 3003.7073 | 466.2112 | 505.8967 | 495.5342
3004.7073 | 2749.7073 | 506.1764 | 495.6729 | 466.3452 | 3004.7073 | 466.3452 | 506.1764 | 495.6729
3005.7073 | 2750.7073 | 506.4584 | 495.6386 | 466.4876 | 3005.7073 | 466.4876 | 506.4584 | 495.6386
3006.7073 | 2751.7073 | 506.5475 | 495.792 | 466.5877 | 3006.7073 | 466.5877 | 506.5475 | 495.792
3007.7073 | 2752.7073 | 506.6622 | 496.3017 | 466.6248 | 3007.7073 | 466.6248 | 506.6622 | 496.3017
3008.7073 | 2753.7073 | 506.533 | 496.4677 | 466.6575 | 3008.7073 | 466.6575 | 506.533 | 496.4677
3009.7073 | 2754.7073 | 506.5805 | 496.8592 | 466.7157 | 3009.7073 | 466.7157 | 506.5805 | 496.8592
3010.7073 | 2755.7073 | 506.4278 | 497.0762 | 466.8131 | 3010.7073 | 466.8131 | 506.4278 | 497.0762
3011.7073 | 2756.7073 | 506.6431 | 496.7218 | 466.8539 | 3011.7073 | 466.8539 | 506.6431 | 496.7218
3012.7073 | 2757.7073 | 506.8775 | 496.7822 | 466.8471 | 3012.7073 | 466.8471 | 506.8775 | 496.7822
3013.7073 | 2758.7073 | 506.8093 | 496.6191 | 466.8872 | 3013.7073 | 466.8872 | 506.8093 | 496.6191
3014.7073 | 2759.7073 | 507.072 | 496.709 | 467.002 | 3014.7073 | 467.002 | 507.072 | 496.709
3015.7073 | 2760.7073 | 507.2281 | 497.1179 | 467.0854 | 3015.7073 | 467.0854 | 507.2281 | 497.1179
3016.7073 | 2761.7073 | 507.4424 | 497.8198 | 467.1656 | 3016.7073 | 467.1656 | 507.4424 | 497.8198
3017.7073 | 2762.7073 | 507.7219 | 497.9769 | 467.1126 | 3017.7073 | 467.1126 | 507.7219 | 497.9769
3018.7073 | 2763.7073 | 507.8331 | 498.5342 | 466.961 | 3018.7073 | 466.961 | 507.8331 | 498.5342
3019.7073 | 2764.7073 | 507.8357 | 498.7436 | 466.9702 | 3019.7073 | 466.9702 | 507.8357 | 498.7436
3020.7073 | 2765.7073 | 507.8908 | 498.7563 | 466.9719 | 3020.7073 | 466.9719 | 507.8908 | 498.7563
3021.7073 | 2766.7073 | 508.0933 | 499.0098 | 466.8932 | 3021.7073 | 466.8932 | 508.0933 | 499.0098
3022.7073 | 2767.7073 | 508.3241 | 499.285 | 466.9683 | 3022.7073 | 466.9683 | 508.3241 | 499.285
3023.7073 | 2768.7073 | 508.5873 | 499.91 | 466.9919 | 3023.7073 | 466.9919 | 508.5873 | 499.91
3024.7073 | 2769.7073 | 508.6401 | 499.9908 | 467.0539 | 3024.7073 | 467.0539 | 508.6401 | 499.9908
3025.7073 | 2770.7073 | 508.883 | 500.2642 | 467.0837 | 3025.7073 | 467.0837 | 508.883 | 500.2642
3026.7073 | 2771.7073 | 509.1179 | 500.1773 | 467.0088 | 3026.7073 | 467.0088 | 509.1179 | 500.1773
3027.7073 | 2772.7073 | 509.3643 | 499.9563 | 466.9115 | 3027.7073 | 466.9115 | 509.3643 | 499.9563
3028.7073 | 2773.7073 | 509.4725 | 499.5228 | 466.8897 | 3028.7073 | 466.8897 | 509.4725 | 499.5228
3029.7073 | 2774.7073 | 509.9448 | 500.5167 | 466.9928 | 3029.7073 | 466.9928 | 509.9448 | 500.5167
3030.7073 | 2775.7073 | 510.323 | 499.9337 | 467.0252 | 3030.7073 | 467.0252 | 510.323 | 499.9337
3031.7073 | 2776.7073 | 510.4448 | 499.2948 | 467.0639 | 3031.7073 | 467.0639 | 510.4448 | 499.2948
3032.7073 | 2777.7073 | 511.0983 | 503.4239 | 467.1084 | 3032.7073 | 467.1084 | 511.0983 | 503.4239
3033.7073 | 2778.7073 | 511.2761 | 504.3242 | 467.1395 | 3033.7073 | 467.1395 | 511.2761 | 504.3242
3034.7073 | 2779.7073 | 511.3504 | 502.1326 | 467.1955 | 3034.7073 | 467.1955 | 511.3504 | 502.1326
3035.7073 | 2780.7073 | 511.4938 | 502.1065 | 467.2436 | 3035.7073 | 467.2436 | 511.4938 | 502.1065
3036.7073 | 2781.7073 | 511.7105 | 502.2087 | 467.3182 | 3036.7073 | 467.3182 | 511.7105 | 502.2087
3037.7073 | 2782.7073 | 511.7013 | 502.3127 | 467.3572 | 3037.7073 | 467.3572 | 511.7013 | 502.3127
3038.7073 | 2783.7073 | 511.919 | 502.6911 | 467.3697 | 3038.7073 | 467.3697 | 511.919 | 502.6911
3039.7073 | 2784.7073 | 511.9353 | 502.727 | 467.4254 | 3039.7073 | 467.4254 | 511.9353 | 502.727
3040.7073 | 2785.7073 | 512.1306 | 502.992 | 467.5025 | 3040.7073 | 467.5025 | 512.1306 | 502.992
3041.7073 | 2786.7073 | 512.3916 | 502.4965 | 467.5365 | 3041.7073 | 467.5365 | 512.3916 | 502.4965
3042.7073 | 2787.7073 | 512.5521 | 502.6754 | 467.6042 | 3042.7073 | 467.6042 | 512.5521 | 502.6754
3043.7073 | 2788.7073 | 512.5644 | 502.9647 | 467.5391 | 3043.7073 | 467.5391 | 512.5644 | 502.9647
3044.7073 | 2789.7073 | 512.5343 | 502.6068 | 467.396 | 3044.7073 | 467.396 | 512.5343 | 502.6068
3045.7073 | 2790.7073 | 512.8565 | 502.1628 | 467.2197 | 3045.7073 | 467.2197 | 512.8565 | 502.1628
3046.7073 | 2791.7073 | 513.1185 | 501.7715 | 467.1597 | 3046.7073 | 467.1597 | 513.1185 | 501.7715
3047.7073 | 2792.7073 | 513.3219 | 501.864 | 467.093 | 3047.7073 | 467.093 | 513.3219 | 501.864
3048.7073 | 2793.7073 | 513.4884 | 501.5911 | 467.0451 | 3048.7073 | 467.0451 | 513.4884 | 501.5911
3049.7073 | 2794.7073 | 513.6471 | 501.5009 | 466.896 | 3049.7073 | 466.896 | 513.6471 | 501.5009
3050.7073 | 2795.7073 | 513.5252 | 501.8364 | 466.8093 | 3050.7073 | 466.8093 | 513.5252 | 501.8364
3051.7073 | 2796.7073 | 513.6328 | 502.2128 | 466.7034 | 3051.7073 | 466.7034 | 513.6328 | 502.2128
3052.7073 | 2797.7073 | 513.828 | 502.2253 | 466.5209 | 3052.7073 | 466.5209 | 513.828 | 502.2253
3053.7073 | 2798.7073 | 513.7941 | 503.07 | 466.3421 | 3053.7073 | 466.3421 | 513.7941 | 503.07
3054.7073 | 2799.7073 | 514.0366 | 503.2803 | 466.1429 | 3054.7073 | 466.1429 | 514.0366 | 503.2803
3055.7073 | 2800.7073 | 514.244 | 503.5755 | 465.9847 | 3055.7073 | 465.9847 | 514.244 | 503.5755
3056.7073 | 2801.7073 | 514.5777 | 503.779 | 465.8747 | 3056.7073 | 465.8747 | 514.5777 | 503.779
3057.7073 | 2802.7073 | 514.897 | 504.2334 | 465.7003 | 3057.7073 | 465.7003 | 514.897 | 504.2334
3058.7073 | 2803.7073 | 514.9276 | 505.021 | 465.485 | 3058.7073 | 465.485 | 514.9276 | 505.021
3059.7073 | 2804.7073 | 515.1093 | 505.0092 | 465.3456 | 3059.7073 | 465.3456 | 515.1093 | 505.0092
3060.7073 | 2805.7073 | 515.46 | 505.6115 | 465.2496 | 3060.7073 | 465.2496 | 515.46 | 505.6115
3061.7073 | 2806.7073 | 515.671 | 505.2934 | 465.1111 | 3061.7073 | 465.1111 | 515.671 | 505.2934
3062.7073 | 2807.7073 | 515.9845 | 505.7882 | 464.9918 | 3062.7073 | 464.9918 | 515.9845 | 505.7882
3063.7073 | 2808.7073 | 516.2275 | 505.8084 | 464.8986 | 3063.7073 | 464.8986 | 516.2275 | 505.8084
3064.7073 | 2809.7073 | 516.4652 | 506.173 | 464.8562 | 3064.7073 | 464.8562 | 516.4652 | 506.173
3065.7073 | 2810.7073 | 516.7698 | 506.49 | 464.9025 | 3065.7073 | 464.9025 | 516.7698 | 506.49
3066.7073 | 2811.7073 | 517.0748 | 506.4142 | 464.7679 | 3066.7073 | 464.7679 | 517.0748 | 506.4142
3067.7073 | 2812.7073 | 517.6137 | 506.7772 | 464.7359 | 3067.7073 | 464.7359 | 517.6137 | 506.7772
3068.7073 | 2813.7073 | 517.8699 | 507.3334 | 464.6135 | 3068.7073 | 464.6135 | 517.8699 | 507.3334
3069.7073 | 2814.7073 | 518.0185 | 507.6753 | 464.5496 | 3069.7073 | 464.5496 | 518.0185 | 507.6753
3070.7073 | 2815.7073 | 518.2951 | 508.2248 | 464.5666 | 3070.7073 | 464.5666 | 518.2951 | 508.2248
3071.7073 | 2816.7073 | 518.3479 | 508.439 | 464.5444 | 3071.7073 | 464.5444 | 518.3479 | 508.439
3072.7073 | 2817.7073 | 518.5631 | 508.8087 | 464.5224 | 3072.7073 | 464.5224 | 518.5631 | 508.8087
3073.7073 | 2818.7073 | 518.7341 | 508.9804 | 464.5149 | 3073.7073 | 464.5149 | 518.7341 | 508.9804
3074.7073 | 2819.7073 | 518.9484 | 508.7317 | 464.4887 | 3074.7073 | 464.4887 | 518.9484 | 508.7317
3075.7073 | 2820.7073 | 519.1918 | 509.0108 | 464.396 | 3075.7073 | 464.396 | 519.1918 | 509.0108
3076.7073 | 2821.7073 | 519.5312 | 509.0566 | 464.3073 | 3076.7073 | 464.3073 | 519.5312 | 509.0566
3077.7073 | 2822.7073 | 519.8843 | 509.5778 | 464.1969 | 3077.7073 | 464.1969 | 519.8843 | 509.5778
3078.7073 | 2823.7073 | 520.1124 | 510.0704 | 464.0763 | 3078.7073 | 464.0763 | 520.1124 | 510.0704
3079.7073 | 2824.7073 | 520.4783 | 510.5813 | 463.8161 | 3079.7073 | 463.8161 | 520.4783 | 510.5813
3080.7073 | 2825.7073 | 520.9512 | 510.5526 | 463.5479 | 3080.7073 | 463.5479 | 520.9512 | 510.5526
3081.7073 | 2826.7073 | 521.3425 | 510.7214 | 463.3054 | 3081.7073 | 463.3054 | 521.3425 | 510.7214
3082.7073 | 2827.7073 | 521.7465 | 511.2382 | 462.9938 | 3082.7073 | 462.9938 | 521.7465 | 511.2382
3083.7073 | 2828.7073 | 522.1581 | 511.8752 | 462.6743 | 3083.7073 | 462.6743 | 522.1581 | 511.8752
3084.7073 | 2829.7073 | 522.4256 | 511.7727 | 462.299 | 3084.7073 | 462.299 | 522.4256 | 511.7727
3085.7073 | 2830.7073 | 522.7252 | 511.8733 | 461.9135 | 3085.7073 | 461.9135 | 522.7252 | 511.8733
3086.7073 | 2831.7073 | 522.9842 | 511.8649 | 461.6637 | 3086.7073 | 461.6637 | 522.9842 | 511.8649
3087.7073 | 2832.7073 | 523.2915 | 512.266 | 461.3604 | 3087.7073 | 461.3604 | 523.2915 | 512.266
3088.7073 | 2833.7073 | 523.5278 | 512.5276 | 461.0855 | 3088.7073 | 461.0855 | 523.5278 | 512.5276
3089.7073 | 2834.7073 | 523.7521 | 512.5635 | 460.6937 | 3089.7073 | 460.6937 | 523.7521 | 512.5635
3090.7073 | 2835.7073 | 523.9913 | 512.8984 | 460.2946 | 3090.7073 | 460.2946 | 523.9913 | 512.8984
3091.7073 | 2836.7073 | 524.2791 | 513.0546 | 459.9156 | 3091.7073 | 459.9156 | 524.2791 | 513.0546
3092.7073 | 2837.7073 | 524.65 | 513.0121 | 459.5838 | 3092.7073 | 459.5838 | 524.65 | 513.0121
3093.7073 | 2838.7073 | 524.9524 | 513.8483 | 459.2642 | 3093.7073 | 459.2642 | 524.9524 | 513.8483
3094.7073 | 2839.7073 | 525.3006 | 513.6372 | 458.8503 | 3094.7073 | 458.8503 | 525.3006 | 513.6372
3095.7073 | 2840.7073 | 525.739 | 513.6041 | 458.445 | 3095.7073 | 458.445 | 525.739 | 513.6041
3096.7073 | 2841.7073 | 526.0304 | 513.4105 | 458.0642 | 3096.7073 | 458.0642 | 526.0304 | 513.4105
3097.7073 | 2842.7073 | 526.3458 | 513.7386 | 457.7323 | 3097.7073 | 457.7323 | 526.3458 | 513.7386
3098.7073 | 2843.7073 | 526.5051 | 513.7142 | 457.3393 | 3098.7073 | 457.3393 | 526.5051 | 513.7142
3099.7073 | 2844.7073 | 526.7489 | 513.7334 | 457.0475 | 3099.7073 | 457.0475 | 526.7489 | 513.7334
3100.7073 | 2845.7073 | 526.9788 | 513.5919 | 456.6935 | 3100.7073 | 456.6935 | 526.9788 | 513.5919
3101.7073 | 2846.7073 | 527.1865 | 513.3735 | 456.3529 | 3101.7073 | 456.3529 | 527.1865 | 513.3735
3102.7073 | 2847.7073 | 527.3625 | 513.282 | 455.9861 | 3102.7073 | 455.9861 | 527.3625 | 513.282
3103.7073 | 2848.7073 | 527.6663 | 513.4362 | 455.5869 | 3103.7073 | 455.5869 | 527.6663 | 513.4362
3104.7073 | 2849.7073 | 527.7599 | 513.0519 | 455.1754 | 3104.7073 | 455.1754 | 527.7599 | 513.0519
3105.7073 | 2850.7073 | 527.8796 | 513.0706 | 454.7063 | 3105.7073 | 454.7063 | 527.8796 | 513.0706
3106.7073 | 2851.7073 | 527.966 | 512.9937 | 454.2367 | 3106.7073 | 454.2367 | 527.966 | 512.9937
3107.7073 | 2852.7073 | 528.1626 | 512.5657 | 453.8321 | 3107.7073 | 453.8321 | 528.1626 | 512.5657
3108.7073 | 2853.7073 | 528.4385 | 512.9919 | 453.4311 | 3108.7073 | 453.4311 | 528.4385 | 512.9919
3109.7073 | 2854.7073 | 528.6471 | 513.0271 | 453.0966 | 3109.7073 | 453.0966 | 528.6471 | 513.0271
3110.7073 | 2855.7073 | 528.8476 | 513.2335 | 452.7316 | 3110.7073 | 452.7316 | 528.8476 | 513.2335
3111.7073 | 2856.7073 | 529.0475 | 513.2796 | 452.3934 | 3111.7073 | 452.3934 | 529.0475 | 513.2796
3112.7073 | 2857.7073 | 529.2793 | 513.0196 | 452.0416 | 3112.7073 | 452.0416 | 529.2793 | 513.0196
3113.7073 | 2858.7073 | 529.6629 | 513.323 | 451.5943 | 3113.7073 | 451.5943 | 529.6629 | 513.323
3114.7073 | 2859.7073 | 529.7625 | 513.0706 | 451.1635 | 3114.7073 | 451.1635 | 529.7625 | 513.0706
3115.7073 | 2860.7073 | 529.9365 | 512.9713 | 450.7832 | 3115.7073 | 450.7832 | 529.9365 | 512.9713
3116.7073 | 2861.7073 | 530.068 | 512.9994 | 450.4971 | 3116.7073 | 450.4971 | 530.068 | 512.9994
3117.7073 | 2862.7073 | 530.253 | 512.5533 | 450.0901 | 3117.7073 | 450.0901 | 530.253 | 512.5533
3118.7073 | 2863.7073 | 530.4035 | 512.4573 | 449.7476 | 3118.7073 | 449.7476 | 530.4035 | 512.4573
3119.7073 | 2864.7073 | 530.7517 | 512.4512 | 449.4194 | 3119.7073 | 449.4194 | 530.7517 | 512.4512
3120.7073 | 2865.7073 | 530.9807 | 512.402 | 449.1109 | 3120.7073 | 449.1109 | 530.9807 | 512.402
3121.7073 | 2866.7073 | 531.178 | 512.6756 | 448.6402 | 3121.7073 | 448.6402 | 531.178 | 512.6756
3122.7073 | 2867.7073 | 531.4278 | 512.6514 | 448.2113 | 3122.7073 | 448.2113 | 531.4278 | 512.6514
3123.7073 | 2868.7073 | 531.5824 | 512.4867 | 447.8085 | 3123.7073 | 447.8085 | 531.5824 | 512.4867
3124.7073 | 2869.7073 | 531.7833 | 512.3214 | 447.3548 | 3124.7073 | 447.3548 | 531.7833 | 512.3214
3125.7073 | 2870.7073 | 532.061 | 512.1398 | 446.9211 | 3125.7073 | 446.9211 | 532.061 | 512.1398
3126.7073 | 2871.7073 | 532.2686 | 512.3644 | 446.5498 | 3126.7073 | 446.5498 | 532.2686 | 512.3644
3127.7073 | 2872.7073 | 532.4689 | 512.2272 | 446.0852 | 3127.7073 | 446.0852 | 532.4689 | 512.2272
3128.7073 | 2873.7073 | 532.6259 | 512.322 | 445.6596 | 3128.7073 | 445.6596 | 532.6259 | 512.322
3129.7073 | 2874.7073 | 532.8046 | 512.2767 | 445.2249 | 3129.7073 | 445.2249 | 532.8046 | 512.2767
3130.7073 | 2875.7073 | 533.0479 | 512.2577 | 444.7545 | 3130.7073 | 444.7545 | 533.0479 | 512.2577
3131.7073 | 2876.7073 | 533.27 | 512.2791 | 444.1578 | 3131.7073 | 444.1578 | 533.27 | 512.2791
3132.7073 | 2877.7073 | 533.4839 | 512.2819 | 443.6519 | 3132.7073 | 443.6519 | 533.4839 | 512.2819
3133.7073 | 2878.7073 | 533.5067 | 512.278 | 443.112 | 3133.7073 | 443.112 | 533.5067 | 512.278
3134.7073 | 2879.7073 | 533.6144 | 512.2447 | 442.6464 | 3134.7073 | 442.6464 | 533.6144 | 512.2447
3135.7073 | 2880.7073 | 533.6378 | 512.026 | 442.2613 | 3135.7073 | 442.2613 | 533.6378 | 512.026
3136.7073 | 2881.7073 | 533.765 | 511.9072 | 441.8022 | 3136.7073 | 441.8022 | 533.765 | 511.9072
3137.7073 | 2882.7073 | 533.8357 | 511.7939 | 441.325 | 3137.7073 | 441.325 | 533.8357 | 511.7939
3138.7073 | 2883.7073 | 534.0527 | 511.731 | 440.8306 | 3138.7073 | 440.8306 | 534.0527 | 511.731
3139.7073 | 2884.7073 | 534.2074 | 511.7382 | 440.4081 | 3139.7073 | 440.4081 | 534.2074 | 511.7382
3140.7073 | 2885.7073 | 534.2539 | 511.7704 | 439.986 | 3140.7073 | 439.986 | 534.2539 | 511.7704
3141.7073 | 2886.7073 | 534.3471 | 511.7468 | 439.6479 | 3141.7073 | 439.6479 | 534.3471 | 511.7468
3142.7073 | 2887.7073 | 534.4661 | 511.6599 | 439.2471 | 3142.7073 | 439.2471 | 534.4661 | 511.6599
3143.7073 | 2888.7073 | 534.562 | 511.7889 | 438.8201 | 3143.7073 | 438.8201 | 534.562 | 511.7889
3144.7073 | 2889.7073 | 534.5944 | 511.9898 | 438.4382 | 3144.7073 | 438.4382 | 534.5944 | 511.9898
3145.7073 | 2890.7073 | 534.726 | 512.0306 | 438.0286 | 3145.7073 | 438.0286 | 534.726 | 512.0306
3146.7073 | 2891.7073 | 534.7302 | 511.9937 | 437.5921 | 3146.7073 | 437.5921 | 534.7302 | 511.9937
3147.7073 | 2892.7073 | 534.6377 | 512.1836 | 437.0856 | 3147.7073 | 437.0856 | 534.6377 | 512.1836
3148.7073 | 2893.7073 | 534.6618 | 512.26 | 436.5761 | 3148.7073 | 436.5761 | 534.6618 | 512.26
3149.7073 | 2894.7073 | 534.796 | 512.3254 | 436.0907 | 3149.7073 | 436.0907 | 534.796 | 512.3254
3150.7073 | 2895.7073 | 534.8339 | 512.4105 | 435.605 | 3150.7073 | 435.605 | 534.8339 | 512.4105
3151.7073 | 2896.7073 | 534.9574 | 512.3861 | 435.1525 | 3151.7073 | 435.1525 | 534.9574 | 512.3861
3152.7073 | 2897.7073 | 535.0917 | 512.6375 | 434.7537 | 3152.7073 | 434.7537 | 535.0917 | 512.6375
3153.7073 | 2898.7073 | 535.1809 | 512.8139 | 434.3673 | 3153.7073 | 434.3673 | 535.1809 | 512.8139
3154.7073 | 2899.7073 | 535.3075 | 512.9669 | 433.9162 | 3154.7073 | 433.9162 | 535.3075 | 512.9669
3155.7073 | 2900.7073 | 535.3328 | 513.0766 | 433.4685 | 3155.7073 | 433.4685 | 535.3328 | 513.0766
3156.7073 | 2901.7073 | 535.4869 | 513.1925 | 433.0352 | 3156.7073 | 433.0352 | 535.4869 | 513.1925
3157.7073 | 2902.7073 | 535.5829 | 513.3706 | 432.5331 | 3157.7073 | 432.5331 | 535.5829 | 513.3706
3158.7073 | 2903.7073 | 535.6516 | 513.5136 | 432.0653 | 3158.7073 | 432.0653 | 535.6516 | 513.5136
3159.7073 | 2904.7073 | 535.8103 | 513.6414 | 431.6681 | 3159.7073 | 431.6681 | 535.8103 | 513.6414
3160.7073 | 2905.7073 | 535.834 | 513.8183 | 431.2565 | 3160.7073 | 431.2565 | 535.834 | 513.8183
3161.7073 | 2906.7073 | 535.8682 | 513.8534 | 430.8152 | 3161.7073 | 430.8152 | 535.8682 | 513.8534
3162.7073 | 2907.7073 | 535.9135 | 514.1133 | 430.3542 | 3162.7073 | 430.3542 | 535.9135 | 514.1133
3163.7073 | 2908.7073 | 535.9237 | 514.3152 | 429.8272 | 3163.7073 | 429.8272 | 535.9237 | 514.3152
3164.7073 | 2909.7073 | 535.778 | 514.5225 | 429.3042 | 3164.7073 | 429.3042 | 535.778 | 514.5225
3165.7073 | 2910.7073 | 535.7245 | 514.8003 | 428.8529 | 3165.7073 | 428.8529 | 535.7245 | 514.8003
3166.7073 | 2911.7073 | 535.7504 | 514.9547 | 428.3854 | 3166.7073 | 428.3854 | 535.7504 | 514.9547
3167.7073 | 2912.7073 | 535.6839 | 515.1232 | 427.9637 | 3167.7073 | 427.9637 | 535.6839 | 515.1232
3168.7073 | 2913.7073 | 535.7792 | 515.3903 | 427.4792 | 3168.7073 | 427.4792 | 535.7792 | 515.3903
3169.7073 | 2914.7073 | 535.8905 | 515.6549 | 426.992 | 3169.7073 | 426.992 | 535.8905 | 515.6549
3170.7073 | 2915.7073 | 535.8763 | 515.7456 | 426.504 | 3170.7073 | 426.504 | 535.8763 | 515.7456
3171.7073 | 2916.7073 | 535.93 | 516.0053 | 426.0743 | 3171.7073 | 426.0743 | 535.93 | 516.0053
3172.7073 | 2917.7073 | 536.04 | 516.0989 | 425.5706 | 3172.7073 | 425.5706 | 536.04 | 516.0989
3173.7073 | 2918.7073 | 536.1765 | 516.3513 | 425.0949 | 3173.7073 | 425.0949 | 536.1765 | 516.3513
3174.7073 | 2919.7073 | 536.1551 | 516.6158 | 424.6294 | 3174.7073 | 424.6294 | 536.1551 | 516.6158
3175.7073 | 2920.7073 | 536.2417 | 516.8337 | 424.1817 | 3175.7073 | 424.1817 | 536.2417 | 516.8337
3176.7073 | 2921.7073 | 536.3527 | 516.8319 | 423.8117 | 3176.7073 | 423.8117 | 536.3527 | 516.8319
3177.7073 | 2922.7073 | 536.4415 | 517.0765 | 423.3872 | 3177.7073 | 423.3872 | 536.4415 | 517.0765
3178.7073 | 2923.7073 | 536.4837 | 517.2817 | 422.9679 | 3178.7073 | 422.9679 | 536.4837 | 517.2817
3179.7073 | 2924.7073 | 536.5462 | 517.4862 | 422.6052 | 3179.7073 | 422.6052 | 536.5462 | 517.4862
3180.7073 | 2925.7073 | 536.5675 | 517.5799 | 422.1799 | 3180.7073 | 422.1799 | 536.5675 | 517.5799
3181.7073 | 2926.7073 | 536.5637 | 517.8194 | 421.7094 | 3181.7073 | 421.7094 | 536.5637 | 517.8194
3182.7073 | 2927.7073 | 536.4694 | 517.7721 | 421.2587 | 3182.7073 | 421.2587 | 536.4694 | 517.7721
3183.7073 | 2928.7073 | 536.4763 | 517.9406 | 420.8276 | 3183.7073 | 420.8276 | 536.4763 | 517.9406
3184.7073 | 2929.7073 | 536.4301 | 518.0359 | 420.3541 | 3184.7073 | 420.3541 | 536.4301 | 518.0359
3185.7073 | 2930.7073 | 536.3794 | 518.0502 | 419.9504 | 3185.7073 | 419.9504 | 536.3794 | 518.0502
3186.7073 | 2931.7073 | 536.3484 | 518.0498 | 419.4488 | 3186.7073 | 419.4488 | 536.3484 | 518.0498
3187.7073 | 2932.7073 | 536.2808 | 518.2535 | 418.9756 | 3187.7073 | 418.9756 | 536.2808 | 518.2535
3188.7073 | 2933.7073 | 536.2357 | 518.2998 | 418.5173 | 3188.7073 | 418.5173 | 536.2357 | 518.2998
3189.7073 | 2934.7073 | 536.1942 | 518.3102 | 418.0465 | 3189.7073 | 418.0465 | 536.1942 | 518.3102
3190.7073 | 2935.7073 | 536.0784 | 518.3106 | 417.5175 | 3190.7073 | 417.5175 | 536.0784 | 518.3106
3191.7073 | 2936.7073 | 536.0032 | 518.1705 | 417.0021 | 3191.7073 | 417.0021 | 536.0032 | 518.1705
3192.7073 | 2937.7073 | 535.9178 | 518.265 | 416.6049 | 3192.7073 | 416.6049 | 535.9178 | 518.265
3193.7073 | 2938.7073 | 535.8543 | 518.2271 | 416.162 | 3193.7073 | 416.162 | 535.8543 | 518.2271
3194.7073 | 2939.7073 | 535.7514 | 518.1678 | 415.668 | 3194.7073 | 415.668 | 535.7514 | 518.1678
3195.7073 | 2940.7073 | 535.5693 | 518.1594 | 415.1794 | 3195.7073 | 415.1794 | 535.5693 | 518.1594
3196.7073 | 2941.7073 | 535.475 | 517.9754 | 414.7504 | 3196.7073 | 414.7504 | 535.475 | 517.9754
3197.7073 | 2942.7073 | 535.3574 | 517.8553 | 414.3174 | 3197.7073 | 414.3174 | 535.3574 | 517.8553
3198.7073 | 2943.7073 | 535.1783 | 517.9092 | 413.8883 | 3198.7073 | 413.8883 | 535.1783 | 517.9092
3199.7073 | 2944.7073 | 535.093 | 517.8502 | 413.4949 | 3199.7073 | 413.4949 | 535.093 | 517.8502
3200.7073 | 2945.7073 | 534.9693 | 517.8682 | 413.064 | 3200.7073 | 413.064 | 534.9693 | 517.8682
3201.7073 | 2946.7073 | 534.8514 | 517.6682 | 412.6667 | 3201.7073 | 412.6667 | 534.8514 | 517.6682
3202.7073 | 2947.7073 | 534.7106 | 517.5834 | 412.2265 | 3202.7073 | 412.2265 | 534.7106 | 517.5834
3203.7073 | 2948.7073 | 534.5863 | 517.6163 | 411.7927 | 3203.7073 | 411.7927 | 534.5863 | 517.6163
3204.7073 | 2949.7073 | 534.4579 | 517.6159 | 411.302 | 3204.7073 | 411.302 | 534.4579 | 517.6159
3205.7073 | 2950.7073 | 534.3228 | 517.7515 | 410.8294 | 3205.7073 | 410.8294 | 534.3228 | 517.7515
3206.7073 | 2951.7073 | 534.2776 | 517.6182 | 410.4166 | 3206.7073 | 410.4166 | 534.2776 | 517.6182
3207.8635 | 2952.8635 | 534.1233 | 516.9998 | 409.9469 | 3207.8635 | 409.9469 | 534.1233 | 516.9998
3208.7229 | 2953.7229 | 534.0475 | 517.5167 | 409.5505 | 3208.7229 | 409.5505 | 534.0475 | 517.5167
3209.7073 | 2954.7073 | 533.8976 | 517.3552 | 409.0151 | 3209.7073 | 409.0151 | 533.8976 | 517.3552
3210.7073 | 2955.7073 | 533.8544 | 517.2994 | 408.5578 | 3210.7073 | 408.5578 | 533.8544 | 517.2994
3211.7073 | 2956.7073 | 533.7391 | 517.2548 | 408.1478 | 3211.7073 | 408.1478 | 533.7391 | 517.2548
3212.7073 | 2957.7073 | 533.6555 | 517.0789 | 407.6695 | 3212.7073 | 407.6695 | 533.6555 | 517.0789
3213.7073 | 2958.7073 | 533.6208 | 517.1021 | 407.2385 | 3213.7073 | 407.2385 | 533.6208 | 517.1021
3214.7073 | 2959.7073 | 533.4541 | 516.9917 | 406.8705 | 3214.7073 | 406.8705 | 533.4541 | 516.9917
3215.7073 | 2960.7073 | 533.4297 | 516.906 | 406.4785 | 3215.7073 | 406.4785 | 533.4297 | 516.906
3216.7073 | 2961.7073 | 533.4081 | 516.7271 | 406.0005 | 3216.7073 | 406.0005 | 533.4081 | 516.7271
3217.7073 | 2962.7073 | 533.303 | 516.601 | 405.5409 | 3217.7073 | 405.5409 | 533.303 | 516.601
3218.7073 | 2963.7073 | 533.2811 | 516.8536 | 405.1224 | 3218.7073 | 405.1224 | 533.2811 | 516.8536
3219.7073 | 2964.7073 | 533.2424 | 516.649 | 404.6899 | 3219.7073 | 404.6899 | 533.2424 | 516.649
3220.7073 | 2965.7073 | 533.163 | 516.6697 | 404.2911 | 3220.7073 | 404.2911 | 533.163 | 516.6697
3221.7385 | 2966.7385 | 533.0264 | 515.8235 | 403.8763 | 3221.7385 | 403.8763 | 533.0264 | 515.8235
3222.7229 | 2967.7229 | 532.9602 | 515.8522 | 403.4602 | 3222.7229 | 403.4602 | 532.9602 | 515.8522
3223.7073 | 2968.7073 | 532.9432 | 516.57 | 402.9888 | 3223.7073 | 402.9888 | 532.9432 | 516.57
3224.7073 | 2969.7073 | 532.8857 | 516.5765 | 402.5125 | 3224.7073 | 402.5125 | 532.8857 | 516.5765
3225.7073 | 2970.7073 | 532.8358 | 516.5624 | 402.0228 | 3225.7073 | 402.0228 | 532.8358 | 516.5624
3226.7073 | 2971.7073 | 532.7524 | 516.3843 | 401.6143 | 3226.7073 | 401.6143 | 532.7524 | 516.3843
3227.7073 | 2972.7073 | 532.7416 | 516.2113 | 401.2318 | 3227.7073 | 401.2318 | 532.7416 | 516.2113
3228.7073 | 2973.7073 | 532.7411 | 516.2968 | 400.8083 | 3228.7073 | 400.8083 | 532.7411 | 516.2968
3229.7073 | 2974.7073 | 532.712 | 516.1724 | 400.346 | 3229.7073 | 400.346 | 532.712 | 516.1724