## Test Conditions
DESIREE-FIRE Penlight Test Number 17 - Circuit Simulator Data Only
Test Date: | July-31-2009 | Fill in these fields - B7 and B11, time offsets for the fire time and temperature time, is critical to data processing. The rest are info only.
Nominal Test start time: | 8:14
SCDU DAQ start time | 8:14
Fire Ignition time: | 8:17
Fire time offset | 220 | This is the time in seconds after the DAQ was started that the fire was ignited
Penlight DAQ Start Time | 8:11
Fire Ignition time: | 8:17
Temp data offset | 344 | This is the time in seconds after the Penlight data logger was activated and Penlight was turned on.
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
SCDU 1 | Kerite FR-III, 3c, 6 AWG |  | Channel 3 represents the side of the thermocouple cable facing the energized cable | TC25 in the Temperature Data File
SCDU 2 | Kerite FR-III, 3c, 6 AWG |  | Channel 4 represents the side of the thermocouple cable facing the energized cable | TC25 in the Temperature Data File
Circuit Simulator Configurations and connections:
Note: Template opens with default conditions, update if alternate wiring configuration is used. |  | Circuit #1 | Circuit#2 | Circuit #3 | Circuit #4
| CPT Size: | 100 VA | 150 VA
| CPT Grounding: | NOT Grounded | NOT Grounded
| General Config. | Generic MOV | Generic MOV
| Cable Type | Kerite | Kerite
| Wiring Config: | MOV - source centered | MOV - source centered
| Circuit Path 1: | Switch Closed: Energized source. Conductor 1 | Switch Closed: Energized source.
| Circuit Path 2: | Switch open: not connected | Switch Closed: Energized source.
| Circuit Path 3: | Switch open: not connected | Switch open: not connected
| Circuit Path 4: | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation). Not used | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation). Not used
| Circuit Path 5: | Active Target: Connected to Motor Starter and connected to Red conductor. Conductor 2 | Active Target: Connected to Motor Starter and connected to Red conductor. Conductor 2
| Circuit Path 6: | Active Target: Connected to Motor Starter and connected to Wht/Blk conductor. Conductor 3 | Active Target: Connected to Motor Starter and connected to Wht/Blk conductor. Conductor 3
| Circuit Path 7: | switch open - no connection | switch open - no connection
| Circuit Path 8: | switch open - no connection | switch open - no connection
| Circuit Path 9: | switch open - no connection | switch open - no connection
A Note on Data Conversion and Accuracy:
Each of the voltage and current transducers used produces a 4-20mA signal which is routed through 477ohm precision resistors converting the signal to a nominal 2-10 VDC signal. This DC voltage signal was monitored using a National Instruments PCI-6071E data aquisition (DAQ) card. These data as recorded are presented in the "Raw Test Data" worksheet. The raw data were converted to actual values as shown on the "Converted Test Data" worksheet. The conversion is based on the fact that the 4-20 mA signal corresponds to a full scale reading on the voltage transducers of 0-300 VAC and on the current transducers of 0-5A. Nominal zero point readings for each transducer were taken in a separate test run in order to establish more accurately the zero points for current and voltage measurement. The Zero Point values are provided, and the full run is documented in a separate data file (see 'Zero Points' worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Circuit Fault Summary
Summary of Circuit Faulting Behavior for all Tested Circuits
Circuit 1 | The Kerite FR-III, 3c, 6AWG was used for Circuit 1. The initial Penlight temperature was set 430C. Swelling of the cable jacket was observed approximately eight minutes into the test. Smoldering of the cable jacket was noticed about 12 minutes after Penlight was turned on. Ignition of the cables occurred 29 minutes after Penlight was turned on. Two minutes later, Targets 5 and 6 spuriously operated. This activity occurred until a fuse trip approximately a minute and a half later.
Circuit 2 | The Kerite FR-III, 3c, 6AWG was used for Circuit 2. The initial Penlight temperature was set 430C. Swelling of the cable jacket was observed approximately eight minutes into the test. Smoldering of the cable jacket was noticed about 12 minutes after Penlight was turned on. Ignition of the cables occurred 29 minutes after Penlight was turned on. About 30 minutes into the test, Circuit 2 began experiencing voltage degradation until the fuse tripped about 2 minutes later.
Circuit 3 | Circuit 3 was not used in this test.
Circuit 4 | Circuit 4 was not used in this test.
Note: | Update this worksheet with a summary of faulting behavior for each circuit e.g.: - what was mode of first failure, - what was time of first failure, - was a spurious actuation observed, - how long did spurious actuation persist, - when did fuse blow.

## Circuit 1 Faulting
Summary of Observed Faulting Behavior for Circuit #1
Time (s) | Event | Discussion
1764 | Shorting behavior initiates | At this time, shorting behavior was observed between Target 5 and Target 6 for over one minute.
1848 | Fuse trip | The activity on Targets 5 and 6 ceased as the fuse for Circuit 1 tripped.
Summary observations
The initial Penlight temperature was set 430C. Swelling of the cable jacket was observed approximately eight minutes into the test. Smoldering of the cable jacket was noticed about 12 minutes after Penlight was turned on. Ignition of the cables occurred 29 minutes after Penlight was turned on. Two minutes later, Targets 5 and 6 spuriously operated. This activity occurred until a fuse trip approximately a minute and a half later.

## Circuit 2 Faulting
Summary of Observed Faulting Behavior for Circuit #2
Time (s) | Event | Discussion
1785 | Voltage degradation on the source conductor | At this time, the voltage on the source conductor began to degrade. This degradation lasted approximately 115 seconds before the fuse tripped.
1900 | Fuse trip | At this time, the fuse tripped for Circuit 2.
Summary Observations
The initial Penlight temperature was set 430C. Swelling of the cable jacket was observed approximately eight minutes into the test. Smoldering of the cable jacket was noticed about 12 minutes after Penlight was turned on. Ignition of the cables occurred 29 minutes after Penlight was turned on. About 30 minutes into the test, Circuit 2 began experiencing voltage degradation until the fuse tripped about 2 minutes later.

## Converted Data C1
Fire Time (s) | C1 V1 | C1 A1 | C1 V2 | C1 A2 | C1 V3 | C1 A3 | C1 V4 | C1 A4 | C1 V5 | C1 A5 | C1 V6 | C1 A6 | C1 V7 | C1 A7 | C1 V8 | C1 A8
-10 | 128.4208 | 0.0057559 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.18729 | 0.00060315 | 0.43001 | 0.00012733 | 0.47618 | -0.0013064 | 0.19792 | 0.0048701 | 0.0923 | 0.0035139
-9.8 | 128.4208 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.19559 | 0.0035139
-9.6 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.18829 | 0.0035139
-9.4 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-9.2 | 128.3248 | 0.0041567 | 0.19792 | 0.0015826 | 0.10127 | 1.6612e-05 | 0.37923 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.19792 | 0.0048701 | -0.0036512 | 0.0035139
-9 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.19792 | 0.0048701 | 0.0923 | 0.0019147
-8.8 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | -0.0013064 | 0.19792 | 0.0048701 | 0.0923 | 0.0035139
-8.6 | 128.3248 | 0.0073551 | 0.10193 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.18729 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.48581 | 0.0048701 | -0.0036512 | 0.0035139
-8.4 | 128.4208 | 0.0089549 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0054014 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.099642 | 0.0035139
-8.2 | 128.4208 | 0.0073551 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | -0.0013064 | 0.19792 | 0.0048701 | -0.0036512 | 0.0035139
-8 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.18829 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
-7.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | -0.0029056 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
-7.6 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.28424 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-7.4 | 127.9409 | 0.0057559 | 0.10193 | -0.0016164 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.33406 | 0.00012733 | 0.28424 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
-7.2 | 127.1732 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.10197 | 0.0048701 | -0.0036512 | 0.0035139
-7 | 128.0369 | 0.0057559 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | -0.0013064 | 0.29387 | 0.00647 | -0.0036512 | 0.0019147
-6.8 | 128.1329 | 0.0073551 | 0.10193 | 0.0031824 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-6.6 | 128.1329 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.003271 | -0.0036512 | 0.0035139
-6.4 | 128.3248 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.19792 | 0.0048701 | -0.0036512 | 0.0019147
-6.2 | 128.5167 | 0.010554 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-6 | 128.5167 | 0.016952 | -0.089975 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.003271 | -0.0036512 | 0.0035139
-5.8 | 128.5167 | 0.0057559 | 0.10193 | -1.6596e-05 | 0.0053144 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
-5.6 | 128.4208 | 0.0073551 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.00031555
-5.4 | 128.5167 | 0.0041567 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 7.192e-05 | 0.0923 | 0.0035139
-5.2 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.57118 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
-5 | 128.4208 | 0.0057559 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.14212 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
-4.8 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | -0.0015832 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-4.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
-4.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.28424 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-4.2 | 128.4208 | 0.0089549 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
-4 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
-3.8 | 128.3248 | 0.0057559 | 0.19792 | -1.6596e-05 | 0.19722 | 1.6612e-05 | 0.18729 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0080692 | 0.0923 | 0.0035139
-3.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-3.4 | 128.4208 | 0.0057559 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.19559 | 0.0035139
-3.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | -0.0036512 | 0.0035139
-3 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.47518 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
-2.8 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
-2.6 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.0035139
-2.4 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.66813 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
-2.2 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
-2 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.0053144 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
-1.8 | 128.4208 | 0.0057559 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
-1.6 | 128.2288 | 0.0057559 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
-1.4 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
-1.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.10197 | 0.0048701 | 0.0923 | 0.0051138
-1 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.09134 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0035139
-0.8 | 128.3248 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.526 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.19559 | 0.0051138
-0.6 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.10127 | -0.0015832 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.28424 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
-0.4 | 128.4208 | 0.0073551 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
-0.2 | 128.2288 | 0.0057559 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
0 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
0.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
0.4 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
0.6 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
0.8 | 128.1329 | 0.0073551 | 0.10193 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
1 | 128.2288 | 0.0073551 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
1.2 | 128.1329 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
1.4 | 128.2288 | 0.0057559 | 0.10193 | 0.0047816 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
1.6 | 128.1329 | 0.0041567 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
1.8 | 128.1329 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
2 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
2.2 | 128.1329 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
2.4 | 128.1329 | 0.0057559 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.28424 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
2.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.57213 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
2.8 | 128.1329 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.23811 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.18829 | 0.0051138
3 | 128.3248 | 0.0057559 | 0.10193 | 0.0015826 | 0.10127 | 0.0032156 | 0.47518 | 0.0022023 | 0.33406 | 0.0017265 | 0.57213 | 0.0002934 | 0.19792 | 0.00647 | 0.0923 | 0.0035139
3.2 | 128.2288 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.33406 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
3.4 | 128.1329 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
3.6 | 128.1329 | 0.0073551 | 0.0059762 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
3.8 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
4 | 128.1329 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.18729 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
4.2 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.38916 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
4.4 | 128.0369 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0080692 | -0.0036512 | 0.0035139
4.6 | 128.1329 | 0.0057559 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
4.8 | 128.0369 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0019147
5 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.23811 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
5.2 | 127.9409 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.10127 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | -0.0013064 | 0.19792 | 0.003271 | 0.0923 | 0.0035139
5.4 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.18829 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
5.6 | 128.1329 | 0.0073551 | 0.10193 | 0.0031824 | 0.10127 | 1.6612e-05 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
5.8 | 127.9409 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
6 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
6.2 | 128.0369 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
6.4 | 128.1329 | 0.0089549 | 0.19792 | 0.0047816 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
6.6 | 128.1329 | 0.010554 | 0.10193 | -0.0016164 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | -0.0013064 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
6.8 | 128.0369 | 0.010554 | 0.10193 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
7 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.5818 | 0.0048701 | -0.0036512 | 0.0035139
7.2 | 128.0369 | 0.012154 | 0.10193 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.19559 | 0.0051138
7.4 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
7.6 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
7.8 | 128.1329 | 0.0089549 | 0.10193 | -1.6596e-05 | -0.090676 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
8 | 128.1329 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | -0.0015832 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.19792 | 0.0048701 | 0.0923 | 0.0035139
8.2 | 128.1329 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.23811 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0019147
8.4 | 128.0369 | 0.0089549 | 0.10193 | -1.6596e-05 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | -0.0013064 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
8.6 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
8.8 | 128.1329 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | -0.0013064 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
9 | 128.1329 | 0.010554 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | -0.0014725 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
9.2 | 128.1329 | 0.010554 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.23811 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0016718 | 0.0923 | 0.0051138
9.4 | 128.0369 | 0.010554 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
9.6 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | -0.0025959 | 0.526 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
9.8 | 128.1329 | 0.010554 | 0.10193 | 0.0015826 | 0.10127 | -0.0015832 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
10 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.18829 | 0.0035139
10.2 | 128.1329 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.47618 | 0.0002934 | 0.19792 | 0.009669 | 0.0923 | 0.0035139
10.4 | 128.1329 | 0.010554 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | -0.0013064 | 0.38986 | 0.0080692 | 0.0923 | 0.0035139
10.6 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | -0.0014725 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
10.8 | 128.1329 | 0.010554 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.57213 | 0.0002934 | 0.29387 | 0.0048701 | 0.18829 | 0.0035139
11 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.23811 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.18829 | 0.0035139
11.2 | 128.1329 | 0.010554 | 0.10193 | -1.6596e-05 | 0.10127 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
11.4 | 128.1329 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.66813 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
11.6 | 128.1329 | 0.010554 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0048148 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | -0.0013064 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
11.8 | 128.0369 | 0.012154 | 0.0059762 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.0923 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0019147
12 | 128.1329 | 0.013753 | 0.10193 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.003271 | 0.18829 | 0.0051138
12.2 | 128.1329 | 0.013753 | 0.19792 | -0.0032156 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
12.4 | 128.1329 | 0.013753 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
12.6 | 128.1329 | 0.010554 | 0.0059762 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
12.8 | 128.2288 | 0.018551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
13 | 128.1329 | 0.015352 | 0.19792 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.18829 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
13.2 | 128.3248 | 0.02175 | 0.19792 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.099642 | 0.0035139
13.4 | 128.1329 | 0.013753 | 0.0059762 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
13.6 | 128.1329 | 0.013753 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.23811 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0019147
13.8 | 128.1329 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.47518 | 0.00060315 | 0.33406 | 0.0049255 | 0.38019 | 0.0034924 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
14 | 128.1329 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0066908 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
14.2 | 128.2288 | 0.012154 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0054014 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
14.4 | 128.0369 | 0.015352 | 0.10193 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.18829 | 0.0035139
14.6 | 128.1329 | 0.013753 | 0.10193 | -0.0032156 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0049255 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0019147
14.8 | 128.2288 | 0.013753 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.62195 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.099642 | 0.0051138
15 | 128.1329 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
15.2 | 128.2288 | 0.012154 | 0.10193 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
15.4 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | -0.0014725 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0019147
15.6 | 128.2288 | 0.012154 | 0.19792 | 0.0047816 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
15.8 | 128.2288 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.29154 | 0.0035139
16 | 128.2288 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
16.2 | 128.1329 | 0.013753 | 0.10193 | 0.0031824 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
16.4 | 128.2288 | 0.012154 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.099642 | 0.0019147
16.6 | 128.2288 | 0.012154 | 0.19792 | 0.0047816 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.28424 | 0.0018926 | 0.29387 | 0.0048701 | 0.18829 | 0.0019147
16.8 | 128.2288 | 0.012154 | 0.19792 | 0.0031824 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | -0.0014725 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
17 | 128.2288 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.19792 | 0.0048701 | 0.0923 | 0.0035139
17.2 | 128.2288 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
17.4 | 128.2288 | 0.012154 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
17.6 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.003271 | 0.0923 | 0.0035139
17.8 | 128.3248 | 0.012154 | 0.10193 | -0.0016164 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
18 | 128.4208 | 0.013753 | 0.10193 | -1.6596e-05 | 0.0053144 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.48581 | 0.0048701 | 0.0923 | 0.0035139
18.2 | 128.3248 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
18.4 | 128.2288 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.14212 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.003271 | 0.0923 | 0.0019147
18.6 | 128.3248 | 0.013753 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
18.8 | 128.3248 | 0.012154 | 0.10193 | -0.0032156 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.18829 | 0.00031555
19 | 128.3248 | 0.013753 | 0.19792 | -1.6596e-05 | 0.0053144 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
19.2 | 128.3248 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
19.4 | 128.2288 | 0.013753 | 0.10193 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | -0.0030717 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.18829 | 0.0035139
19.6 | 128.4208 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.011268 | 0.0923 | 0.0035139
19.8 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
20 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | -0.0014725 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
20.2 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.23811 | 0.00012733 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
20.4 | 128.5167 | 0.013753 | 0.10193 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
20.6 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.10127 | 1.6612e-05 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | -0.0013064 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
20.8 | 128.4208 | 0.012154 | 0.19792 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0019147
21 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
21.2 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.28424 | 0.0051138
21.4 | 128.4208 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.18829 | 0.0035139
21.6 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
21.8 | 128.4208 | 0.013753 | 0.10193 | -0.0016164 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
22 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.526 | 0.00012733 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
22.2 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
22.4 | 128.3248 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
22.6 | 128.4208 | 0.013753 | 0.19792 | -1.6596e-05 | 0.38916 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
22.8 | 128.5167 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
23 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.0048701 | 0.0923 | 0.0051138
23.2 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.10127 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
23.4 | 128.4208 | 0.013753 | 0.19792 | -1.6596e-05 | 0.0053144 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
23.6 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | -0.00099603 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | -0.0036512 | 0.0035139
23.8 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
24 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.28424 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
24.2 | 128.5167 | 0.013753 | 0.10193 | 0.0015826 | 0.10127 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
24.4 | 128.5167 | 0.013753 | 0.19792 | 0.0047816 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
24.6 | 128.6127 | 0.016952 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.099642 | 0.0051138
24.8 | 128.7087 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.18729 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
25 | 128.9006 | 0.013753 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
25.2 | 129.0925 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
25.4 | 129.3804 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.009669 | 0.0923 | 0.0035139
25.6 | 129.6683 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
25.8 | 129.4764 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.14212 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
26 | 129.2844 | 0.012154 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
26.2 | 128.9966 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.19559 | 0.0019147
26.4 | 128.8046 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | -0.00099603 | 0.43001 | 0.0017265 | 0.47618 | 0.0082906 | 0.38986 | 7.192e-05 | 0.0923 | 0.0051138
26.6 | 128.5167 | 0.012154 | 0.10193 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
26.8 | 128.4208 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.28424 | 0.0035139
27 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
27.2 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
27.4 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
27.6 | 128.2288 | 0.013753 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0019147
27.8 | 128.2288 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
28 | 128.1329 | 0.013753 | 0.0059762 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
28.2 | 128.1329 | 0.012154 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
28.4 | 128.1329 | 0.015352 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
28.6 | 128.1329 | 0.015352 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.00012733 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.28424 | 0.0035139
28.8 | 128.1329 | 0.013753 | 0.10193 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
29 | 128.1329 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
29.2 | 128.0369 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
29.4 | 128.1329 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0019147
29.6 | 128.0369 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
29.8 | 128.0369 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
30 | 128.0369 | 0.016952 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
30.2 | 128.1329 | 0.016952 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
30.4 | 128.1329 | 0.018551 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
30.6 | 128.1329 | 0.013753 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
30.8 | 128.0369 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
31 | 128.0369 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
31.2 | 128.0369 | 0.016952 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
31.4 | 128.0369 | 0.020151 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
31.6 | 128.2288 | 0.024949 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
31.8 | 128.2288 | 0.020151 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
32 | 128.1329 | 0.016952 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
32.2 | 128.2288 | 0.02175 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
32.4 | 128.1329 | 0.020151 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
32.6 | 128.0369 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
32.8 | 128.2288 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0035139
33 | 128.0369 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
33.2 | 128.1329 | 0.013753 | 0.0059762 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
33.4 | 127.9409 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
33.6 | 128.0369 | 0.018551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
33.8 | 128.2288 | 0.020151 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
34 | 128.1329 | 0.02175 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
34.2 | 128.0369 | 0.02335 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0035139
34.4 | 127.9409 | 0.013753 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
34.6 | 128.1329 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.18729 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.0048701 | 0.0923 | 0.0051138
34.8 | 128.0369 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
35 | 128.0369 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
35.2 | 128.1329 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
35.4 | 128.0369 | 0.013753 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
35.6 | 128.0369 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
35.8 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
36 | 128.0369 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
36.2 | 128.1329 | 0.013753 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0019147
36.4 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
36.6 | 128.1329 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
36.8 | 128.2288 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
37 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
37.2 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
37.4 | 128.4208 | 0.012154 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
37.6 | 128.3248 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
37.8 | 128.3248 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
38 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
38.2 | 128.4208 | 0.013753 | 0.10193 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
38.4 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
38.6 | 128.4208 | 0.013753 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
38.8 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
39 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0038022 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
39.2 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
39.4 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
39.6 | 128.4208 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
39.8 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0016718 | 0.0923 | 0.0051138
40 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
40.2 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
40.4 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.00060315 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
40.6 | 128.5167 | 0.013753 | 0.10193 | -1.6596e-05 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
40.8 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.23811 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
41 | 128.5167 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
41.2 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
41.4 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.23811 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
41.6 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
41.8 | 128.4208 | 0.012154 | 0.10193 | -1.6596e-05 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
42 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.18729 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.19792 | 0.003271 | 0.0923 | 0.0035139
42.2 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
42.4 | 128.4208 | 0.013753 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
42.6 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
42.8 | 128.4208 | 0.010554 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
43 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
43.2 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
43.4 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0035139
43.6 | 128.4208 | 0.02335 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0049255 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
43.8 | 128.1329 | 0.031347 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
44 | 128.9006 | 0.055339 | 0.10193 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.011324 | 0.47618 | 0.0098898 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
44.2 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 1.6612e-05 | 0.28324 | 0.00060315 | 0.43001 | 0.0065247 | 0.47618 | 0.014688 | 0.38986 | 0.003271 | -0.0036512 | 0.0035139
44.4 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0066908 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
44.6 | 128.3248 | 0.013753 | 0.19792 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
44.8 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
45 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
45.2 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
45.4 | 128.4208 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.003271 | -0.0036512 | 0.0035139
45.6 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.23811 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
45.8 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
46 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
46.2 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
46.4 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
46.6 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
46.8 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
47 | 128.2288 | 0.012154 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
47.2 | 128.2288 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.18729 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
47.4 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
47.6 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
47.8 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
48 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
48.2 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
48.4 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
48.6 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
48.8 | 128.2288 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | -0.0014725 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
49 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
49.2 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
49.4 | 128.2288 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
49.6 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.099642 | 0.0035139
49.8 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
50 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.003271 | -0.0036512 | 0.0035139
50.2 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.003271 | 0.0923 | 0.0035139
50.4 | 128.1329 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
50.6 | 128.1329 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
50.8 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.38916 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
51 | 128.1329 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
51.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
51.4 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
51.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
51.8 | 128.1329 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
52 | 128.0369 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
52.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
52.4 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
52.6 | 128.1329 | 0.0089549 | 0.10193 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
52.8 | 128.1329 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
53 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0035139
53.2 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
53.4 | 128.1329 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
53.6 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
53.8 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
54 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
54.2 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
54.4 | 128.0369 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
54.6 | 128.0369 | 0.0057559 | 0.10193 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
54.8 | 128.1329 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
55 | 128.1329 | 0.0057559 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
55.2 | 128.1329 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
55.4 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
55.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
55.8 | 128.1329 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
56 | 128.1329 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
56.2 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
56.4 | 128.1329 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
56.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.003271 | 0.0923 | 0.0035139
56.8 | 128.1329 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
57 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
57.2 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
57.4 | 128.1329 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
57.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
57.8 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
58 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
58.2 | 128.2288 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
58.4 | 128.2288 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.526 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.18829 | 0.0035139
58.6 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934 | 0.48581 | 0.0048701 | 0.0923 | 0.0035139
58.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
59 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.18829 | 0.0035139
59.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
59.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
59.6 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
59.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
60 | 128.3248 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
60.2 | 128.2288 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
60.4 | 128.3248 | 0.0057559 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.006713
60.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
60.8 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
61 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.003271 | 0.0923 | 0.0035139
61.2 | 128.3248 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.003271 | -0.0036512 | 0.0035139
61.4 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
61.6 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
61.8 | 128.6127 | 0.02175 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.19792 | 0.0048701 | -0.0036512 | 0.0051138
62 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
62.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
62.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
62.6 | 128.4208 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.003271 | 0.0923 | 0.0035139
62.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
63 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
63.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.23811 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
63.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
63.6 | 128.4208 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
63.8 | 128.4208 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
64 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
64.2 | 127.557 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.099642 | 0.0035139
64.4 | 127.4611 | 0.0089549 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
64.6 | 128.1329 | 0.0041567 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
64.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
65 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
65.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.38986 | 0.003271 | -0.0036512 | 0.0035139
65.4 | 128.5167 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
65.6 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.23811 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.099642 | 0.0035139
65.8 | 128.5167 | 0.0089549 | 0.10193 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.57213 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
66 | 128.5167 | 0.0057559 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.003271 | 0.0923 | 0.0019147
66.2 | 128.5167 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
66.4 | 128.5167 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
66.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
66.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
67 | 128.5167 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
67.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
67.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
67.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
67.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
68 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
68.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
68.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
68.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
68.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.18829 | 0.0051138
69 | 128.5167 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
69.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
69.4 | 128.4208 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
69.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
69.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
70 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
70.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
70.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
70.6 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
70.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
71 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
71.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
71.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.00060315 | 0.43001 | 0.0033264 | 0.57213 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
71.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
71.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
72 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
72.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
72.4 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.10127 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
72.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
72.8 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
73 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
73.2 | 128.4208 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
73.4 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
73.6 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
73.8 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
74 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
74.2 | 128.4208 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
74.4 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
74.6 | 128.2288 | 0.016952 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
74.8 | 128.3248 | 0.018551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
75 | 128.6127 | 0.026549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
75.2 | 128.2288 | 0.020151 | 0.10193 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
75.4 | 128.2288 | 0.026549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
75.6 | 128.4208 | 0.036146 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
75.8 | 128.7087 | 0.039345 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0081246 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
76 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.011324 | 0.66813 | 0.0082906 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
76.2 | 128.0369 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.014522 | 0.57213 | 0.0098898 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
76.4 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.014522 | 0.57213 | 0.0098898 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
76.6 | 127.749 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.014688 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
76.8 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0081246 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
77 | 128.3248 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0081246 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
77.2 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0097238 | 0.57213 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
77.4 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.012923 | 0.57213 | 0.0066908 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
77.6 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0098898 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
77.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
78 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
78.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
78.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
78.6 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
78.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | -0.0012843
79 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
79.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
79.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
79.6 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
79.8 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
80 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.19792 | 0.0048701 | 0.0923 | 0.0051138
80.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | -0.0013064 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
80.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.38916 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
80.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
80.8 | 128.2288 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
81 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.19792 | 0.00647 | 0.0923 | 0.0051138
81.2 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
81.4 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.006713
81.6 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
81.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
82 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
82.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
82.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
82.6 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
82.8 | 128.2288 | 0.0057559 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
83 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
83.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0083128
83.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
83.6 | 128.5167 | 0.0057559 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.18729 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.003271 | -0.0036512 | 0.0051138
83.8 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
84 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
84.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
84.4 | 128.2288 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
84.6 | 128.3248 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
84.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
85 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
85.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
85.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
85.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
85.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
86 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
86.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0050916 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
86.4 | 128.2288 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
86.6 | 128.3248 | 0.0073551 | 0.29387 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.526 | 0.00012733 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
86.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
87 | 128.3248 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
87.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
87.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
87.6 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
87.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
88 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
88.2 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
88.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
88.6 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
88.8 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
89 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
89.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
89.4 | 128.3248 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
89.6 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
89.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.18729 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0035139
90 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
90.2 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
90.4 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.18829 | 0.0035139
90.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
90.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
91 | 128.2288 | 0.0073551 | 0.0059762 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
91.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.006414 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
91.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
91.6 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.57213 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
91.8 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
92 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
92.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
92.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
92.6 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | -0.0013064 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
92.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
93 | 128.3248 | 0.0089549 | 0.10193 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
93.2 | 128.3248 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
93.4 | 128.2288 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.0053144 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
93.6 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
93.8 | 128.3248 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
94 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.57118 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
94.2 | 128.3248 | 0.0073551 | 0.19792 | -0.0016164 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
94.4 | 128.2288 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.18829 | 0.0051138
94.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
94.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.28424 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
95 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
95.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.62195 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
95.4 | 128.2288 | 0.0073551 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.19559 | 0.0051138
95.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
95.8 | 128.1329 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
96 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
96.2 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
96.4 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0035139
96.6 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
96.8 | 128.2288 | 0.0089549 | 0.0059762 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
97 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
97.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.00012733 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
97.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
97.6 | 128.1329 | 0.0057559 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0019147
97.8 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0035139
98 | 128.2288 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0070012 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
98.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | -0.0029056 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
98.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
98.6 | 128.2288 | 0.0089549 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.00060315 | 0.23811 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
98.8 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.011268 | 0.0923 | 0.0051138
99 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
99.2 | 128.2288 | 0.0057559 | 0.38986 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0083128
99.4 | 128.1329 | 0.0073551 | 0.38986 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
99.6 | 128.2288 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
99.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
100 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.18829 | 0.0051138
100.2 | 128.1329 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
100.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
100.6 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.009669 | 0.0923 | 0.0051138
100.8 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.23811 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
101 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
101.2 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.71795 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
101.4 | 128.2288 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
101.6 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
101.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.18729 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.48581 | 0.003271 | 0.0923 | 0.0051138
102 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
102.2 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0070012 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
102.4 | 128.2288 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | -0.0013064 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
102.6 | 128.1329 | 0.0089549 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.71795 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.19559 | 0.0035139
102.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
103 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
103.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
103.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
103.6 | 128.2288 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
103.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
104 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
104.2 | 128.1329 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
104.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
104.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
104.8 | 128.1329 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
105 | 128.2288 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0070012 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
105.2 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
105.4 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
105.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
105.8 | 128.1329 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
106 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
106.2 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
106.4 | 128.1329 | 0.0057559 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | -0.0013064 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
106.6 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
106.8 | 128.2288 | 0.0073551 | 0.0059762 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
107 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
107.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.18729 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.5818 | 0.0048701 | 0.0923 | 0.0051138
107.4 | 128.1329 | 0.0057559 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.23811 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
107.6 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
107.8 | 128.1329 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.28424 | 0.0051138
108 | 128.1329 | 0.0057559 | 0.29387 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
108.2 | 128.1329 | 0.0073551 | 0.19792 | -0.0016164 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
108.4 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
108.6 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
108.8 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
109 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
109.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.09134 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
109.4 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.38916 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
109.6 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
109.8 | 128.0369 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
110 | 128.0369 | 0.0089549 | 0.10193 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
110.2 | 128.2288 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0019147
110.4 | 128.1329 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
110.6 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.76408 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
110.8 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
111 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
111.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
111.4 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
111.6 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
111.8 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
112 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
112.2 | 128.0369 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.62195 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0019147
112.4 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
112.6 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
112.8 | 128.1329 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.28424 | 0.0051138
113 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.38916 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
113.2 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
113.4 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
113.6 | 128.1329 | 0.012154 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.0051138
113.8 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | -0.0036512 | 0.0051138
114 | 128.0369 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.47518 | 0.0022023 | 0.526 | 0.0033264 | 0.38019 | 0.0050916 | 0.19792 | 0.0048701 | 0.0923 | 0.0051138
114.2 | 128.3248 | 0.02175 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.00031555
114.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0047816 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0065247 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
114.6 | 127.9409 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
114.8 | 128.1329 | 0.0089549 | 0.10193 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.28424 | 0.0051138
115 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0066908 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
115.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
115.4 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
115.6 | 128.0369 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
115.8 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
116 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
116.2 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | -0.0013064 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
116.4 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.66813 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
116.6 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
116.8 | 128.0369 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
117 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
117.2 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
117.4 | 128.1329 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
117.6 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.10127 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.003271 | 0.0923 | 0.0051138
117.8 | 128.1329 | 0.012154 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
118 | 128.0369 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.099642 | 0.0051138
118.2 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.09134 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
118.4 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | -0.00099603 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
118.6 | 128.1329 | 0.012154 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.00031555
118.8 | 128.2288 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.00060315 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
119 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | -0.0036512 | 0.0035139
119.2 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.66813 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
119.4 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
119.6 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
119.8 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
120 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0038022 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
120.2 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
120.4 | 128.2288 | 0.013753 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
120.6 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | -0.0013064 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
120.8 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.0035139
121 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | -0.0015832 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
121.2 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
121.4 | 128.2288 | 0.013753 | 0.29387 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
121.6 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0050916 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
121.8 | 128.1329 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
122 | 128.2288 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
122.2 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
122.4 | 128.2288 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
122.6 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
122.8 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | -0.0029056 | 0.19792 | 0.0048701 | 0.0923 | 0.0051138
123 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
123.2 | 128.2288 | 0.015352 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.28424 | 0.0035139
123.4 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.18829 | 0.0051138
123.6 | 128.2288 | 0.012154 | 0.10193 | 0.0047816 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0049255 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.009912
123.8 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
124 | 128.3248 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.62195 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
124.2 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | -0.00099603 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0016718 | 0.18829 | 0.0051138
124.4 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
124.6 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0016718 | 0.18829 | 0.0035139
124.8 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.66813 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.006713
125 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
125.2 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
125.4 | 128.2288 | 0.015352 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0070012 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.5818 | 7.192e-05 | 0.18829 | 0.0051138
125.6 | 128.3248 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.18729 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.5818 | 0.0080692 | 0.0923 | 0.0051138
125.8 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.011268 | -0.0036512 | 0.0051138
126 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
126.2 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.00060315 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
126.4 | 128.3248 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.00031555
126.6 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
126.8 | 128.4208 | 0.013753 | 0.19792 | -0.0016164 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
127 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
127.2 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.10127 | -0.0015832 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
127.4 | 128.3248 | 0.013753 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
127.6 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
127.8 | 128.4208 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.5818 | 0.0048701 | 0.0923 | 0.0051138
128 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.00031555
128.2 | 128.6127 | 0.013753 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | -0.00099603 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
128.4 | 128.4208 | 0.013753 | 0.29387 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
128.6 | 128.1329 | 0.02175 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0082906 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
128.8 | 128.7087 | 0.039345 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
129 | 128.4208 | 0.015352 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0082906 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
129.2 | 128.5167 | 0.013753 | 0.0059762 | 0.0031824 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
129.4 | 128.5167 | 0.013753 | 0.10193 | 0.0031824 | 0.10127 | 0.0032156 | 0.57118 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
129.6 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.5818 | 0.00647 | 0.0923 | 0.0051138
129.8 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | -0.0189 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
130 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.017909
130.2 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
130.4 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
130.6 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.23811 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.006713
130.8 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
131 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
131.2 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
131.4 | 128.5167 | 0.015352 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | -0.0014725 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
131.6 | 128.6127 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
131.8 | 128.7087 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | -0.00099603 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.28424 | 0.0051138
132 | 128.7087 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
132.2 | 128.8046 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0048701 | 0.18829 | 0.0051138
132.4 | 129.0925 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
132.6 | 129.8603 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 1.6612e-05 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
132.8 | 129.5724 | 0.016952 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
133 | 128.9966 | 0.013753 | 0.29387 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
133.2 | 128.9006 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
133.4 | 128.7087 | 0.016952 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
133.6 | 128.8046 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.0051138
133.8 | 128.7087 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
134 | 128.6127 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
134.2 | 128.6127 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.006713
134.4 | 128.5167 | 0.013753 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
134.6 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.19559 | 0.0035139
134.8 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.23811 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
135 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
135.2 | 128.7087 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
135.4 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
135.6 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.18729 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.19792 | 0.00647 | 0.0923 | 0.0051138
135.8 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
136 | 128.5167 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
136.2 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
136.4 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
136.6 | 128.5167 | 0.015352 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
136.8 | 128.5167 | 0.015352 | 0.19792 | -1.6596e-05 | 0.48515 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.76408 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
137 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0019147
137.2 | 128.4208 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
137.4 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.0053144 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.00012733 | 0.57213 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
137.6 | 128.4208 | 0.015352 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
137.8 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
138 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
138.2 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
138.4 | 128.5167 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
138.6 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
138.8 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
139 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
139.2 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
139.4 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.57213 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
139.6 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
139.8 | 128.4208 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
140 | 128.4208 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
140.2 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
140.4 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
140.6 | 128.4208 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
140.8 | 128.4208 | 0.012154 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
141 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
141.2 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.23811 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
141.4 | 128.3248 | 0.016952 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
141.6 | 128.0369 | 0.016952 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | -0.00099603 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
141.8 | 128.4208 | 0.024949 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
142 | 127.557 | 0.026549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.19792 | 0.00647 | 0.0923 | 0.0035139
142.2 | 128.6127 | 0.061737 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.011324 | 0.47618 | 0.0050916 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
142.4 | 128.3248 | 0.013753 | 0.19792 | -0.0016164 | 0.0053144 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0081246 | 0.47618 | 0.016288 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
142.6 | 128.4208 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.09134 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
142.8 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.76408 | 0.0002934 | 0.10197 | 0.003271 | -0.0036512 | 0.0035139
143 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.01631
143.2 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
143.4 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
143.6 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | -0.00099603 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
143.8 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
144 | 128.3248 | 0.012154 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
144.2 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
144.4 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
144.6 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
144.8 | 128.2288 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0019147
145 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
145.2 | 128.2288 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
145.4 | 128.2288 | 0.010554 | 0.0059762 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0019147
145.6 | 128.2288 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.28424 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
145.8 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
146 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
146.2 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0019147
146.4 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
146.6 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.0035139
146.8 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.18829 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
147 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.0051138
147.2 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
147.4 | 128.1329 | 0.0089549 | 0.38986 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0080692 | -0.19559 | 0.006713
147.6 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0054014 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.009669 | 0.0923 | 0.0035139
147.8 | 128.0369 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
148 | 128.2288 | 0.010554 | 0.38986 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.23811 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.29154 | 0.0051138
148.2 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.18829 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
148.4 | 128.0369 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | -0.0014725 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
148.6 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
148.8 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
149 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
149.2 | 128.0369 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
149.4 | 128.0369 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
149.6 | 128.0369 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
149.8 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.0051138
150 | 128.1329 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
150.2 | 128.1329 | 0.010554 | 0.38986 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
150.4 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | -0.0036512 | 0.0051138
150.6 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
150.8 | 128.1329 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.18729 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
151 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.76408 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
151.2 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
151.4 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
151.6 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
151.8 | 128.1329 | 0.0073551 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
152 | 128.0369 | 0.0073551 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
152.2 | 128.0369 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
152.4 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.19792 | 0.003271 | 0.0923 | 0.0035139
152.6 | 128.0369 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.62195 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
152.8 | 128.1329 | 0.0089549 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.00060315 | 0.62195 | 0.00012733 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.38019 | 0.0035139
153 | 127.9409 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0080692 | 0.0923 | 0.0035139
153.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
153.4 | 128.1329 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.71795 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
153.6 | 128.0369 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 7.192e-05 | -0.0036512 | 0.0051138
153.8 | 128.0369 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.28424 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
154 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
154.2 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.57118 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
154.4 | 128.0369 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
154.6 | 127.9409 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
154.8 | 128.3248 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.62195 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.099642 | 0.006713
155 | 127.9409 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
155.2 | 128.1329 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.018197 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
155.4 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
155.6 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | -0.0036512 | 0.0051138
155.8 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.23811 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
156 | 128.0369 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.38019 | 0.0035139
156.2 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | -0.0036512 | 0.0051138
156.4 | 127.9409 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
156.6 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
156.8 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | -0.0015832 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.5818 | 0.00647 | 0.0923 | 0.0051138
157 | 128.0369 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
157.2 | 128.1329 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | -0.0036512 | 0.0035139
157.4 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
157.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
157.8 | 128.0369 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
158 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
158.2 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.0080692 | 0.0923 | 0.0051138
158.4 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.18729 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
158.6 | 128.0369 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
158.8 | 128.0369 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
159 | 128.1329 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.48515 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.28424 | -0.0013064 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
159.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.57118 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.19792 | 0.00647 | -0.0036512 | 0.0051138
159.4 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | -0.00099603 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
159.6 | 128.0369 | 0.0073551 | 0.29387 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
159.8 | 128.2288 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
160 | 128.2288 | 0.0057559 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.18829 | 0.0051138
160.2 | 128.1329 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0019147
160.4 | 128.1329 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.38019 | 0.0002934 | 0.29387 | 0.0016718 | -0.0036512 | 0.0051138
160.6 | 128.2288 | 0.0057559 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
160.8 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
161 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
161.2 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
161.4 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.00012733 | 0.28424 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
161.6 | 128.2288 | 0.0041567 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.00060315 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.0923 | 0.0035139
161.8 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | -0.0014725 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
162 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | -0.0013064 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
162.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
162.4 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
162.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
162.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0038022 | 0.33406 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.0048701 | -0.0036512 | 0.0035139
163 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
163.2 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
163.4 | 128.1329 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.18729 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
163.6 | 128.3248 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
163.8 | 128.2288 | 0.0041567 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.29387 | 0.0080692 | -0.0036512 | 0.0035139
164 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | -0.00099603 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.0035139
164.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
164.4 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0019147
164.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
164.8 | 128.2288 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
165 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
165.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0019147
165.4 | 128.2288 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0016718 | 0.0923 | 0.0051138
165.6 | 128.2288 | 0.0057559 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
165.8 | 128.2288 | 0.0057559 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.23811 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
166 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
166.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
166.4 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
166.6 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
166.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.57213 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
167 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
167.2 | 128.3248 | 0.0057559 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | -0.0036512 | 0.0035139
167.4 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.38986 | 0.009669 | -0.0036512 | 0.0035139
167.6 | 128.3248 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0083128
167.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
168 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
168.2 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.18729 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0035139
168.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | -0.0013064 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
168.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.28424 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
168.8 | 128.4208 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
169 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
169.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.003271 | -0.0036512 | 0.0051138
169.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | -0.00099603 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
169.6 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
169.8 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.18829 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
170 | 128.2288 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | -0.00099603 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
170.2 | 128.6127 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
170.4 | 128.4208 | 0.010554 | 0.10193 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.526 | 0.0049255 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
170.6 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
170.8 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
171 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
171.2 | 128.4208 | 0.015352 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
171.4 | 128.4208 | 0.02175 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0035139
171.6 | 128.4208 | 0.020151 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.18729 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.009669 | -0.0036512 | 0.0035139
171.8 | 128.5167 | 0.024949 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
172 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.00060315 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
172.2 | 128.4208 | 0.0089549 | 0.29387 | -0.0016164 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.28424 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
172.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0065247 | 0.57213 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.006713
172.6 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.38019 | 0.0050916 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
172.8 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0049255 | 0.38019 | 0.0050916 | 0.29387 | 0.00647 | -0.099642 | 0.0035139
173 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0035139
173.2 | 128.4208 | 0.0073551 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.006713
173.4 | 128.4208 | 0.0073551 | 0.19792 | 0.012779 | 0.19722 | 0.0032156 | 0.28324 | 0.0070012 | 0.43001 | 0.0081246 | 0.47618 | 0.0050916 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
173.6 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0081246 | 0.47618 | 0.0066908 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
173.8 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.18729 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0066908 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
174 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
174.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
174.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
174.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
174.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0050916 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
175 | 128.4208 | 0.0073551 | 0.29387 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0019147
175.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.10127 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.18829 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
175.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0070012 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0080692 | -0.099642 | 0.0035139
175.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
175.8 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.10127 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
176 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.19792 | 0.00647 | -0.0036512 | 0.0035139
176.2 | 128.4208 | 0.0073551 | 0.29387 | -0.0016164 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
176.4 | 128.4208 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
176.6 | 128.4208 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.19792 | 0.00647 | -0.0036512 | 0.0035139
176.8 | 128.4208 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
177 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
177.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.18829 | 0.0034924 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
177.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.0053144 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0050916 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
177.6 | 128.4208 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0035139
177.8 | 128.4208 | 0.0073551 | 0.0059762 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
178 | 128.3248 | 0.0057559 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
178.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
178.4 | 128.1329 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
178.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
178.8 | 127.4611 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | -0.099642 | 0.0035139
179 | 127.0772 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
179.2 | 127.2692 | 0.0073551 | 0.29387 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
179.4 | 127.9409 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
179.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
179.8 | 128.1329 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0080692 | -0.0036512 | 0.0051138
180 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.19792 | 0.0048701 | 0.0923 | 0.0051138
180.2 | 128.2288 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.10127 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
180.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.67775 | 0.0048701 | -0.0036512 | 0.0035139
180.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
180.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.009669 | 0.0923 | 0.0035139
181 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
181.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934 | 0.48581 | 0.00647 | -0.0036512 | 0.0035139
181.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
181.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | -0.0013064 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
181.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
182 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0083128
182.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0016718 | -0.0036512 | 0.0051138
182.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
182.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
182.8 | 128.5167 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | -0.00099603 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
183 | 128.5167 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0019147
183.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.38916 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
183.4 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0050916 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
183.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
183.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0035139
184 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0019147
184.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
184.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
184.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
184.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
185 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
185.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.57213 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
185.4 | 128.4208 | 0.0089549 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
185.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
185.8 | 128.4208 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
186 | 128.4208 | 0.0073551 | 0.10193 | -0.0016164 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
186.2 | 128.4208 | 0.0041567 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
186.4 | 128.4208 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
186.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
186.8 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
187 | 128.4208 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
187.2 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
187.4 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.18729 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
187.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
187.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
188 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.10127 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
188.2 | 128.5167 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
188.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.5818 | 0.0080692 | 0.0923 | 0.0051138
188.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
188.8 | 128.4208 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
189 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
189.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
189.4 | 128.5167 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
189.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
189.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.57118 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.10197 | 0.0048701 | 0.0923 | 0.0051138
190 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
190.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
190.4 | 128.4208 | 0.0073551 | 0.29387 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
190.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.00031555
190.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0070012 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.003271 | -0.0036512 | 0.0051138
191 | 128.4208 | 0.0057559 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0016718 | 0.0923 | 0.0051138
191.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
191.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
191.6 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
191.8 | 128.4208 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
192 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.66813 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
192.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
192.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
192.6 | 128.4208 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
192.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
193 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.62195 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
193.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | -0.099642 | 0.0035139
193.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
193.6 | 128.4208 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.18829 | 0.0035139
193.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
194 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
194.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0035139
194.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
194.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
194.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
195 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
195.2 | 128.4208 | 0.0073551 | 0.38986 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
195.4 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.18729 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
195.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
195.8 | 128.5167 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
196 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
196.2 | 128.4208 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
196.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
196.6 | 128.4208 | 0.0057559 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.18829 | 0.0051138
196.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
197 | 128.4208 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
197.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0019147
197.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
197.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0066908 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
197.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
198 | 128.4208 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
198.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
198.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
198.6 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
198.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.62195 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
199 | 128.5167 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.00031555
199.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
199.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
199.6 | 128.4208 | 0.0057559 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0035139
199.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
200 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
200.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
200.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
200.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0035139
200.8 | 128.5167 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.18729 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
201 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 1.6612e-05 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
201.2 | 128.5167 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
201.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
201.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
201.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
202 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
202.2 | 128.4208 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
202.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
202.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
202.8 | 128.4208 | 0.0073551 | 0.38986 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
203 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
203.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | -0.0036512 | 0.0051138
203.4 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.006713
203.6 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
203.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
204 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
204.2 | 128.4208 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
204.4 | 128.3248 | 0.0057559 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
204.6 | 128.4208 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
204.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0083128
205 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
205.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.28424 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
205.4 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
205.6 | 128.4208 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
205.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
206 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.28424 | 0.0051138
206.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | -0.0013064 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
206.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.19792 | 0.0080692 | 0.0923 | 0.0051138
206.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
206.8 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
207 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
207.2 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
207.4 | 128.3248 | 0.0057559 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
207.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0065247 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
207.8 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | -0.0013064 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
208 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
208.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
208.4 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
208.6 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
208.8 | 128.2288 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
209 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
209.2 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
209.4 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
209.6 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.28424 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
209.8 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
210 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
210.2 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
210.4 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
210.6 | 128.2288 | 0.016952 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
210.8 | 128.2288 | 0.016952 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.23811 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
211 | 128.3248 | 0.018551 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
211.2 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.003271 | -0.0036512 | 0.0051138
211.4 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
211.6 | 128.2288 | 0.016952 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
211.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.47518 | 0.00060315 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
212 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
212.2 | 128.2288 | 0.016952 | 0.29387 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.28424 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
212.4 | 128.2288 | 0.015352 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0035139
212.6 | 128.2288 | 0.013753 | 0.0059762 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
212.8 | 128.3248 | 0.013753 | 0.19792 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
213 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
213.2 | 128.2288 | 0.016952 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
213.4 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
213.6 | 128.2288 | 0.015352 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
213.8 | 128.2288 | 0.018551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
214 | 128.2288 | 0.015352 | 0.19792 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
214.2 | 128.1329 | 0.012154 | 0.19792 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
214.4 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
214.6 | 128.4208 | 0.013753 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0083128
214.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | -0.099642 | 0.006713
215 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
215.2 | 128.3248 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
215.4 | 128.3248 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
215.6 | 128.5167 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
215.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
216 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | -0.0013064 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
216.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
216.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
216.6 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
216.8 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
217 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
217.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
217.4 | 128.3248 | 0.0073551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.009912
217.6 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
217.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
218 | 128.3248 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
218.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.003271 | 0.18829 | 0.0051138
218.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
218.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
218.8 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
219 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
219.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
219.4 | 128.4208 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
219.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
219.8 | 128.3248 | 0.0089549 | 0.0059762 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
220 | 128.4208 | 0.0089549 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0035139
220.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
220.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.38019 | -0.0013064 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
220.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.47518 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
220.8 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
221 | 128.4208 | 0.0073551 | 0.38986 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0083128
221.2 | 128.6127 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
221.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
221.6 | 128.3248 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.003271 | 0.18829 | 0.0051138
221.8 | 128.3248 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
222 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
222.2 | 128.3248 | 0.0073551 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
222.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
222.6 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
222.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
223 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
223.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
223.4 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
223.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.099642 | 0.0051138
223.8 | 128.4208 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
224 | 128.4208 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
224.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
224.4 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
224.6 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
224.8 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
225 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
225.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
225.4 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
225.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
225.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
226 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
226.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
226.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
226.6 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
226.8 | 128.4208 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
227 | 128.3248 | 0.0073551 | 0.29387 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
227.2 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
227.4 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.18829 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
227.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 1.6612e-05 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
227.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
228 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
228.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.18729 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
228.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
228.6 | 128.3248 | 0.0073551 | 0.38986 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
228.8 | 128.4208 | 0.0089549 | 0.38986 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
229 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
229.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
229.4 | 128.4208 | 0.0057559 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
229.6 | 128.4208 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
229.8 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
230 | 128.4208 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0035139
230.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
230.4 | 128.3248 | 0.0073551 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.23811 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
230.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
230.8 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
231 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
231.2 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
231.4 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
231.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.57118 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
231.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
232 | 128.3248 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
232.2 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.19559 | 0.0051138
232.4 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
232.6 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | -0.0013064 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
232.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
233 | 128.4208 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.57118 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
233.2 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
233.4 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
233.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
233.8 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.57118 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
234 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
234.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
234.4 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
234.6 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
234.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
235 | 128.2288 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
235.2 | 128.2288 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
235.4 | 128.5167 | 0.02335 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
235.6 | 128.1329 | 0.018551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.19792 | 0.003271 | 0.0923 | 0.0051138
235.8 | 128.1329 | 0.024949 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
236 | 128.1329 | 0.031347 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
236.2 | 128.6127 | 0.044143 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
236.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.011324 | 0.57213 | 0.0098898 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
236.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.014522 | 0.66813 | 0.0098898 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
236.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
237 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
237.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.62195 | 0.014522 | 0.66813 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
237.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0098898 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
237.6 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
237.8 | 128.3248 | 0.0073551 | 0.10193 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
238 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
238.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | -0.38753 | 0.006713
238.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
238.6 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
238.8 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | -0.0036512 | 0.0051138
239 | 128.2288 | 0.0073551 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
239.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
239.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
239.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
239.8 | 128.1329 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0083128
240 | 128.1329 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
240.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
240.4 | 128.1329 | 0.0041567 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
240.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.18729 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
240.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.19792 | 0.00647 | 0.18829 | 0.0051138
241 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
241.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
241.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 1.6612e-05 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
241.6 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | -0.0013064 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
241.8 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.10127 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
242 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
242.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
242.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
242.6 | 128.0369 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
242.8 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.006713
243 | 128.1329 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
243.2 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
243.4 | 128.1329 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
243.6 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
243.8 | 128.1329 | 0.0073551 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
244 | 128.2288 | 0.0089549 | 0.10193 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.00012733 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.0923 | 0.0019147
244.2 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
244.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.0053144 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
244.6 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
244.8 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
245 | 128.1329 | 0.0057559 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | -0.0036512 | 0.0051138
245.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
245.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.0053144 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
245.6 | 128.1329 | 0.0057559 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.0923 | 0.0051138
245.8 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
246 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
246.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
246.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
246.6 | 128.1329 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
246.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 1.6612e-05 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
247 | 128.0369 | 0.0057559 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
247.2 | 128.1329 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.011268 | 0.0923 | 0.0051138
247.4 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
247.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
247.8 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
248 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
248.2 | 128.0369 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.003271 | 0.0923 | 0.0051138
248.4 | 128.3248 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
248.6 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
248.8 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
249 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
249.2 | 128.0369 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
249.4 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
249.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.0080692 | 0.0923 | 0.006713
249.8 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
250 | 128.1329 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
250.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.18729 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.5818 | 0.0048701 | 0.0923 | 0.0051138
250.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
250.6 | 128.0369 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
250.8 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.006713
251 | 128.1329 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.28424 | 0.006713
251.2 | 128.1329 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.18729 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
251.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.28424 | 0.006713
251.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
251.8 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
252 | 128.1329 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
252.2 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.10127 | 0.0016158 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
252.4 | 128.1329 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
252.6 | 128.1329 | 0.0073551 | 0.48581 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
252.8 | 128.1329 | 0.0057559 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
253 | 128.1329 | 0.0073551 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
253.2 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
253.4 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.48515 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
253.6 | 128.1329 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
253.8 | 128.2288 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
254 | 128.1329 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
254.2 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
254.4 | 128.1329 | 0.0073551 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.62195 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.38019 | 0.0035139
254.6 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
254.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
255 | 128.1329 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
255.2 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
255.4 | 127.9409 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
255.6 | 128.0369 | 0.0073551 | 0.38986 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
255.8 | 128.0369 | 0.0057559 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
256 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
256.2 | 128.1329 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
256.4 | 128.0369 | 0.0057559 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
256.6 | 128.0369 | 0.0073551 | 0.0059762 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
256.8 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
257 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
257.2 | 128.0369 | 0.0089549 | 0.19792 | -0.0016164 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
257.4 | 127.9409 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
257.6 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
257.8 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
258 | 127.9409 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
258.2 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
258.4 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
258.6 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
258.8 | 128.0369 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0035139
259 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0083128
259.2 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
259.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | -0.0014725 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
259.6 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.38019 | 0.0035139
259.8 | 127.9409 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
260 | 127.9409 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 1.6612e-05 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
260.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
260.4 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
260.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
260.8 | 128.0369 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
261 | 128.0369 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.62195 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
261.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.10197 | 0.0048701 | 0.0923 | 0.0051138
261.4 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
261.6 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.29387 | 0.0080692 | 0.0923 | 0.0035139
261.8 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.006713
262 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
262.2 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
262.4 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
262.6 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
262.8 | 128.0369 | 0.010554 | 0.19792 | -0.0016164 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
263 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
263.2 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
263.4 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
263.6 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
263.8 | 128.0369 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | -0.0036512 | 0.006713
264 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
264.2 | 128.0369 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
264.4 | 128.0369 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
264.6 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
264.8 | 127.9409 | 0.015352 | 0.29387 | 0.0015826 | 0.29321 | 1.6612e-05 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.19792 | 0.00647 | 0.0923 | 0.0051138
265 | 128.1329 | 0.010554 | 0.19792 | 0.0047816 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
265.2 | 127.8449 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
265.4 | 127.9409 | 0.0089549 | 0.19792 | 0.0063808 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
265.6 | 128.0369 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
265.8 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.10127 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | -0.0062707 | 0.28424 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
266 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.48515 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
266.2 | 128.0369 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
266.4 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
266.6 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
266.8 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
267 | 128.1329 | 0.010554 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
267.2 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.28324 | 0.0054014 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
267.4 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
267.6 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.009669 | 0.0923 | 0.0035139
267.8 | 128.0369 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
268 | 128.1329 | 0.012154 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
268.2 | 128.0369 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
268.4 | 128.0369 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
268.6 | 128.0369 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.18829 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
268.8 | 128.0369 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
269 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.10127 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
269.2 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0066908 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
269.4 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
269.6 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0019147
269.8 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
270 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.003271 | -0.0036512 | 0.0051138
270.2 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
270.4 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.23811 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
270.6 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
270.8 | 128.0369 | 0.013753 | 0.19792 | 0.0015826 | 0.38916 | 0.0016158 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.0923 | 0.0051138
271 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.76408 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
271.2 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
271.4 | 128.1329 | 0.013753 | 0.29387 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
271.6 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
271.8 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
272 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
272.2 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
272.4 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
272.6 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
272.8 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
273 | 128.1329 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
273.2 | 128.2288 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.00031555
273.4 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
273.6 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0035139
273.8 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
274 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
274.2 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.003271 | 0.28424 | 0.0035139
274.4 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
274.6 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
274.8 | 128.3248 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
275 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
275.2 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
275.4 | 128.0369 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | -0.099642 | 0.0019147
275.6 | 128.2288 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
275.8 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
276 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
276.2 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.28424 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
276.4 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
276.6 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
276.8 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.006713
277 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
277.2 | 128.2288 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
277.4 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
277.6 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
277.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.76408 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
278 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
278.2 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | -0.0013064 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
278.4 | 128.3248 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.00060315 | 0.23811 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
278.6 | 128.2288 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.00031555
278.8 | 128.3248 | 0.015352 | 0.19792 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
279 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.38916 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
279.2 | 128.3248 | 0.015352 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
279.4 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.006713
279.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.0051138
279.8 | 128.4208 | 0.015352 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
280 | 128.2288 | 0.013753 | 0.38986 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
280.2 | 128.3248 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.19792 | 0.00647 | 0.18829 | 0.0051138
280.4 | 128.3248 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.00012733 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
280.6 | 128.4208 | 0.015352 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
280.8 | 128.5167 | 0.016952 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.38019 | 0.0035139
281 | 128.3248 | 0.016952 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.009669 | 0.0923 | 0.0051138
281.2 | 127.9409 | 0.018551 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
281.4 | 128.1329 | 0.024949 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
281.6 | 128.7087 | 0.042543 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.38019 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
281.8 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0082906 | 0.10197 | 0.0048701 | 0.18829 | 0.0051138
282 | 128.4208 | 0.015352 | 0.48581 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0019147
282.2 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.47518 | 0.011799 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
282.4 | 128.4208 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0097238 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
282.6 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
282.8 | 128.4208 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
283 | 128.3248 | 0.015352 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
283.2 | 128.4208 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.19792 | 0.0048701 | 0.0923 | 0.0051138
283.4 | 128.3248 | 0.015352 | 0.19792 | 0.0015826 | 0.10127 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | -0.0013064 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
283.6 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
283.8 | 128.4208 | 0.015352 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
284 | 128.4208 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.006713
284.2 | 128.4208 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
284.4 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
284.6 | 128.4208 | 0.015352 | 0.19792 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.00012733 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
284.8 | 128.5167 | 0.015352 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
285 | 128.4208 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
285.2 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
285.4 | 128.9006 | 0.013753 | 0.19792 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
285.6 | 129.7643 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
285.8 | 129.2844 | 0.018551 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
286 | 128.9006 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
286.2 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
286.4 | 128.6127 | 0.015352 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
286.6 | 128.6127 | 0.013753 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.23811 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
286.8 | 128.5167 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0070012 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
287 | 128.5167 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.09134 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.0048701 | 0.0923 | 0.0051138
287.2 | 128.5167 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
287.4 | 128.4208 | 0.015352 | 0.29387 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
287.6 | 128.4208 | 0.015352 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
287.8 | 128.4208 | 0.015352 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
288 | 128.5167 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
288.2 | 128.5167 | 0.018551 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.00060315 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
288.4 | 128.4208 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
288.6 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
288.8 | 128.4208 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
289 | 128.4208 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
289.2 | 128.4208 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
289.4 | 128.4208 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
289.6 | 128.4208 | 0.015352 | 0.29387 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
289.8 | 128.5167 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
290 | 128.4208 | 0.015352 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0019147
290.2 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.0923 | 0.0051138
290.4 | 128.4208 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
290.6 | 128.4208 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | -0.0036512 | 0.0051138
290.8 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.28424 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
291 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.00012733 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
291.2 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
291.4 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
291.6 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
291.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.5818 | 0.0080692 | 0.0923 | 0.0051138
292 | 128.3248 | 0.013753 | 0.29387 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
292.2 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
292.4 | 128.2288 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
292.6 | 128.2288 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0019147
292.8 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
293 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
293.2 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
293.4 | 128.3248 | 0.015352 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
293.6 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0035139
293.8 | 128.2288 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.0035139
294 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
294.2 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.19792 | 0.0048701 | 0.0923 | 0.0051138
294.4 | 128.4208 | 0.024949 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
294.6 | 128.2288 | 0.034546 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.006713
294.8 | 128.4208 | 0.036146 | 0.19792 | 0.0015826 | 0.0053144 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.016122 | 0.57213 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
295 | 128.3248 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0065247 | 0.47618 | 0.0098898 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
295.2 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.57118 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
295.4 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
295.6 | 128.3248 | 0.013753 | 0.38986 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
295.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
296 | 128.3248 | 0.016952 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
296.2 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
296.4 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
296.6 | 128.3248 | 0.013753 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
296.8 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | -0.0036512 | 0.0051138
297 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
297.2 | 128.2288 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.28424 | 0.0051138
297.4 | 128.2288 | 0.012154 | 0.29387 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
297.6 | 128.2288 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 1.6612e-05 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.0048701 | 0.0923 | 0.0051138
297.8 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
298 | 128.2288 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.0051138
298.2 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
298.4 | 128.2288 | 0.012154 | 0.48581 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
298.6 | 128.2288 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
298.8 | 128.2288 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
299 | 128.2288 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.18729 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
299.2 | 128.2288 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.006713
299.4 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.0053144 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
299.6 | 128.1329 | 0.010554 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
299.8 | 128.1329 | 0.012154 | 0.10193 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0083128
300 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
300.2 | 128.0369 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0065247 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
300.4 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.28424 | 0.006713
300.6 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.19559 | 0.0035139
300.8 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
301 | 128.1329 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0016718 | 0.0923 | 0.0051138
301.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
301.4 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
301.6 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
301.8 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
302 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
302.2 | 128.1329 | 0.012154 | 0.10193 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
302.4 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
302.6 | 128.0369 | 0.010554 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
302.8 | 128.0369 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
303 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
303.2 | 128.1329 | 0.010554 | 0.19792 | 0.0063808 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
303.4 | 128.1329 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
303.6 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
303.8 | 128.1329 | 0.010554 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.38019 | 0.0035139
304 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.006713
304.2 | 128.0369 | 0.0057559 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.23811 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
304.4 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
304.6 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
304.8 | 128.0369 | 0.010554 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.18829 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
305 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.18829 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
305.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
305.4 | 128.0369 | 0.010554 | 0.48581 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
305.6 | 128.0369 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
305.8 | 127.9409 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
306 | 128.2288 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
306.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.006414 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
306.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.67775 | 0.0048701 | 0.0923 | 0.0051138
306.6 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
306.8 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.003271 | 0.18829 | 0.0051138
307 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0016158 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
307.2 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.009912
307.4 | 128.0369 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
307.6 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
307.8 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.006713
308 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.09134 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
308.2 | 128.0369 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
308.4 | 127.9409 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.009669 | 0.0923 | 0.0035139
308.6 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | -0.0036512 | 0.0035139
308.8 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.71795 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
309 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0065247 | 0.66813 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
309.2 | 128.0369 | 0.0089549 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
309.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.23811 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
309.6 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0016718 | -0.0036512 | 0.0035139
309.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.10127 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
310 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
310.2 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
310.4 | 128.1329 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
310.6 | 128.0369 | 0.010554 | 0.19792 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0035139
310.8 | 128.0369 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.00012733 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
311 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.0053144 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
311.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
311.4 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
311.6 | 128.1329 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
311.8 | 128.0369 | 0.0089549 | 0.29387 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.28424 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
312 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
312.2 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
312.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.006713
312.6 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
312.8 | 128.1329 | 0.010554 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
313 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
313.2 | 128.2288 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
313.4 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
313.6 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
313.8 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
314 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
314.2 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
314.4 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.19792 | 0.0048701 | 0.0923 | 0.0051138
314.6 | 128.1329 | 0.010554 | 0.29387 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
314.8 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
315 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.48515 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
315.2 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
315.4 | 128.1329 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
315.6 | 128.1329 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
315.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
316 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | -0.19559 | 0.0035139
316.2 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
316.4 | 128.0369 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.62195 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | -0.099642 | 0.0051138
316.6 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0083128
316.8 | 128.1329 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
317 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | -0.0013064 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
317.2 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
317.4 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
317.6 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
317.8 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.76408 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
318 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
318.2 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | -0.099642 | 0.0051138
318.4 | 128.1329 | 0.010554 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0019147
318.6 | 128.1329 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
318.8 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.38019 | 0.0035139
319 | 128.1329 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0065247 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
319.2 | 128.0369 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
319.4 | 128.1329 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | -0.0014725 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
319.6 | 128.2288 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
319.8 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | -0.0036512 | 0.0035139
320 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
320.2 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
320.4 | 128.1329 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.00031555
320.6 | 128.1329 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0019147
320.8 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
321 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | -0.00099603 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
321.2 | 128.1329 | 0.010554 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
321.4 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
321.6 | 128.0369 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
321.8 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | -0.0013064 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
322 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
322.2 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
322.4 | 128.2288 | 0.012154 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
322.6 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
322.8 | 128.2288 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
323 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
323.2 | 128.2288 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
323.4 | 128.2288 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
323.6 | 128.2288 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
323.8 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
324 | 128.2288 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
324.2 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
324.4 | 128.2288 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
324.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.48515 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
324.8 | 128.2288 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0035139
325 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
325.2 | 128.2288 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.003271 | -0.0036512 | 0.0051138
325.4 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
325.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
325.8 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
326 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
326.2 | 128.2288 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0019147
326.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.006713
326.6 | 128.3248 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
326.8 | 128.2288 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.003271 | 0.0923 | 0.0035139
327 | 128.2288 | 0.013753 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
327.2 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.28324 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
327.4 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
327.6 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.19559 | 0.0035139
327.8 | 128.2288 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0035139
328 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
328.2 | 128.3248 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0035139
328.4 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
328.6 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
328.8 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | -0.0015273 | 0.0923 | 0.0035139
329 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.19792 | 0.0016718 | -0.0036512 | 0.0051138
329.2 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.18829 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
329.4 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0035139
329.6 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0035139
329.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.23811 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.18829 | 0.0035139
330 | 128.2288 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
330.2 | 128.2288 | 0.013753 | 0.29387 | 0.0047816 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
330.4 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.00031555
330.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
330.8 | 128.2288 | 0.013753 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.18829 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
331 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 1.147 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0035139
331.2 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
331.4 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | -0.0041951 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
331.6 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
331.8 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
332 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.0923 | 0.0035139
332.2 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
332.4 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
332.6 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
332.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
333 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0016158 | 1.4349 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
333.2 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
333.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.020809 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
333.6 | 128.3248 | 0.013753 | 0.10193 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0083128
333.8 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.28424 | 0.0051138
334 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0102 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
334.2 | 128.3248 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
334.4 | 128.3248 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.33406 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
334.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
334.8 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0016718 | 0.0923 | 0.0051138
335 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.90985 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
335.2 | 128.3248 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.66813 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
335.4 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
335.6 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
335.8 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.28424 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
336 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0086004 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
336.2 | 128.3248 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
336.4 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.00060315 | 0.33406 | 0.0033264 | 0.38019 | 0.0082906 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
336.6 | 128.4208 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0082906 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
336.8 | 128.3248 | 0.013753 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0081246 | 0.47618 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
337 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
337.2 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
337.4 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0022023 | 0.33406 | 0.0081246 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
337.6 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0097238 | 0.47618 | 0.0066908 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
337.8 | 128.3248 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.57213 | 0.016288 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
338 | 128.3248 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.57213 | 0.016288 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
338.2 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0097238 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
338.4 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0097238 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.006713
338.6 | 128.3248 | 0.015352 | 0.48581 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.33406 | 0.0097238 | 0.47618 | 0.013089 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
338.8 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | -0.090676 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0098898 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
339 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.18729 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0082906 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
339.2 | 128.3248 | 0.013753 | 0.19792 | 0.01118 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0081246 | 0.47618 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
339.4 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0065247 | 0.57213 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
339.6 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0070012 | 0.43001 | 0.0081246 | 0.57213 | 0.013089 | 0.38986 | 0.0080692 | -0.0036512 | 0.0051138
339.8 | 128.3248 | 0.013753 | 0.29387 | 0.0015826 | 0.48515 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0081246 | 0.47618 | 0.0098898 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
340 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0081246 | 0.38019 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.006713
340.2 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0081246 | 0.57213 | 0.014688 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
340.4 | 128.3248 | 0.024949 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0065247 | 0.66813 | 0.016288 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
340.6 | 128.4208 | 0.015352 | 0.19792 | 0.0047816 | 0.19722 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0097238 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
340.8 | 128.3248 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.526 | 0.0081246 | 0.47618 | 0.0066908 | 0.38986 | 0.0080692 | -0.0036512 | 0.0051138
341 | 128.3248 | 0.015352 | 0.10193 | 0.0015826 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0081246 | 0.38019 | 0.01149 | 0.38986 | 0.00647 | 0.0923 | 0.006713
341.2 | 128.2288 | 0.013753 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0081246 | 0.47618 | 0.01149 | 0.38986 | 0.003271 | -0.0036512 | 0.0051138
341.4 | 127.0772 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.47618 | 0.0082906 | 0.29387 | 0.0048701 | 0.18829 | 0.0051138
341.6 | 126.8853 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0081246 | 0.57213 | 0.0082906 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
341.8 | 127.557 | 0.02175 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0081246 | 0.57213 | 0.016288 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
342 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0081246 | 0.57213 | 0.013089 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
342.2 | 128.3248 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.014688 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
342.4 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0081246 | 0.57213 | 0.013089 | 0.38986 | 0.003271 | 0.18829 | 0.0051138
342.6 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.10127 | 0.0016158 | 0.37923 | 0.0022023 | 0.43001 | 0.0081246 | 0.57213 | 0.013089 | 0.48581 | 0.00647 | 0.0923 | 0.006713
342.8 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
343 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
343.2 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
343.4 | 128.2288 | 0.013753 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
343.6 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | -0.33772 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
343.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
344 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.18729 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
344.2 | 128.2288 | 0.013753 | 0.29387 | 0.0063808 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
344.4 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
344.6 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.00012733 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
344.8 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | -0.77138 | 0.0018926 | 0.38986 | 0.003271 | -0.0036512 | 0.0051138
345 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
345.2 | 128.2288 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | -0.099642 | 0.0035139
345.4 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
345.6 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
345.8 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
346 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
346.2 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
346.4 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.099642 | 0.0035139
346.6 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | -0.0036512 | 0.006713
346.8 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
347 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.48515 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
347.2 | 128.2288 | 0.013753 | 0.29387 | -1.6596e-05 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
347.4 | 128.2288 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
347.6 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
347.8 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
348 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
348.2 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
348.4 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
348.6 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
348.8 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
349 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
349.2 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | -0.0036512 | 0.0035139
349.4 | 128.2288 | 0.013753 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
349.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
349.8 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
350 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.14212 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
350.2 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
350.4 | 128.1329 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
350.6 | 128.2288 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.18729 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
350.8 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.09134 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
351 | 128.1329 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
351.2 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
351.4 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
351.6 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
351.8 | 128.1329 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.00060315 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
352 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
352.2 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
352.4 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
352.6 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
352.8 | 128.1329 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
353 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | -0.0036512 | 0.0051138
353.2 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
353.4 | 128.1329 | 0.013753 | 0.29387 | -1.6596e-05 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
353.6 | 128.0369 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
353.8 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.48515 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
354 | 128.2288 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
354.2 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0066908 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
354.4 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
354.6 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
354.8 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
355 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
355.2 | 128.1329 | 0.012154 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
355.4 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
355.6 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.71795 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
355.8 | 128.0369 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
356 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
356.2 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.23811 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0083128
356.4 | 128.0369 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
356.6 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
356.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
357 | 128.1329 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.28424 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
357.2 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
357.4 | 127.8449 | 0.012154 | 0.10193 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
357.6 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
357.8 | 127.9409 | 0.010554 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
358 | 127.9409 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
358.2 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.18729 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.0048701 | 0.0923 | 0.0051138
358.4 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
358.6 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0083128
358.8 | 127.749 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
359 | 127.9409 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
359.2 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.57118 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
359.4 | 127.8449 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0080139 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
359.6 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.0051138
359.8 | 127.9409 | 0.010554 | 0.19792 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
360 | 127.9409 | 0.010554 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
360.2 | 127.8449 | 0.010554 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
360.4 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
360.6 | 127.9409 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
360.8 | 128.0369 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
361 | 127.8449 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0083128
361.2 | 127.9409 | 0.010554 | 0.19792 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
361.4 | 127.9409 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
361.6 | 127.9409 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.009669 | 0.0923 | 0.0051138
361.8 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | -0.0014725 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
362 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
362.2 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
362.4 | 127.9409 | 0.010554 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
362.6 | 127.749 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
362.8 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
363 | 127.8449 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.0923 | 0.0051138
363.2 | 127.8449 | 0.010554 | 0.48581 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | -0.0036512 | 0.0051138
363.4 | 127.9409 | 0.010554 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
363.6 | 127.8449 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
363.8 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
364 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0016718 | -0.0036512 | 0.0051138
364.2 | 127.9409 | 0.012154 | 0.19792 | 0.0079807 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | -0.0014725 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
364.4 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.009912
364.6 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
364.8 | 127.9409 | 0.0089549 | 0.19792 | 0.0047816 | 0.0053144 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
365 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.099642 | 0.0035139
365.2 | 127.9409 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.00031555
365.4 | 127.749 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.0048701 | 0.0923 | 0.0051138
365.6 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
365.8 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.18829 | 0.006713
366 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
366.2 | 127.9409 | 0.010554 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
366.4 | 127.749 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.011268 | 0.18829 | 0.0051138
366.6 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
366.8 | 127.8449 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0019147
367 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0035139
367.2 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.00060315 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
367.4 | 127.8449 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
367.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0065247 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
367.8 | 127.8449 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
368 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | -0.0013064 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
368.2 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.00012733 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
368.4 | 127.9409 | 0.010554 | 0.0059762 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.00012733 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
368.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
368.8 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
369 | 127.749 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
369.2 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.003271 | 0.18829 | 0.0051138
369.4 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0083128
369.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.71795 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0083128
369.8 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
370 | 127.8449 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
370.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
370.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0016718 | 0.0923 | 0.0051138
370.6 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
370.8 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
371 | 127.8449 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
371.2 | 127.9409 | 0.0089549 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
371.4 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
371.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
371.8 | 127.8449 | 0.010554 | 0.29387 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
372 | 127.8449 | 0.0057559 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
372.2 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
372.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
372.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.0053144 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
372.8 | 127.8449 | 0.0057559 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
373 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
373.2 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
373.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
373.6 | 127.9409 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
373.8 | 128.0369 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.18729 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
374 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.76408 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
374.2 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.38916 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
374.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.00012733 | 0.66813 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
374.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
374.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
375 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
375.2 | 127.9409 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
375.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
375.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
375.8 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
376 | 127.9409 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.76408 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
376.2 | 127.9409 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
376.4 | 127.9409 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.006414 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | -0.0013064 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
376.6 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.009912
376.8 | 127.9409 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
377 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | -0.0036512 | 0.006713
377.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
377.4 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
377.6 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 1.6612e-05 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.006713
377.8 | 127.9409 | 0.010554 | 0.10193 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
378 | 127.9409 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
378.2 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
378.4 | 127.9409 | 0.010554 | 0.29387 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0035139
378.6 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.10197 | 0.0048701 | 0.0923 | 0.0051138
378.8 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
379 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
379.2 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
379.4 | 127.9409 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
379.6 | 127.9409 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.00647 | 0.18829 | 0.0051138
379.8 | 127.9409 | 0.010554 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
380 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
380.2 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
380.4 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | -0.0029056 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
380.6 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
380.8 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.18729 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
381 | 128.0369 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0035139
381.2 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
381.4 | 128.0369 | 0.012154 | 0.48581 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
381.6 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.18729 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.67775 | 0.00647 | 0.0923 | 0.0051138
381.8 | 128.0369 | 0.010554 | 0.29387 | 0.0063808 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
382 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.10197 | 0.0048701 | 0.0923 | 0.0051138
382.2 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
382.4 | 127.9409 | 0.012154 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
382.6 | 127.9409 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.67775 | 0.00647 | 0.0923 | 0.0051138
382.8 | 128.0369 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
383 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
383.2 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
383.4 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
383.6 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
383.8 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.57118 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
384 | 128.0369 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
384.2 | 128.1329 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
384.4 | 128.1329 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
384.6 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
384.8 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
385 | 128.0369 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
385.2 | 128.1329 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.006713
385.4 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.0923 | 0.0051138
385.6 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
385.8 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
386 | 128.2288 | 0.015352 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
386.2 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
386.4 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
386.6 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
386.8 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.00012733 | 0.38019 | 0.0050916 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
387 | 128.1329 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | -0.0047816 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0082906 | 0.19792 | 0.0048701 | 0.0923 | 0.0051138
387.2 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.57213 | 0.014688 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
387.4 | 128.6127 | 0.056938 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.006713
387.6 | 128.1329 | 0.034546 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
387.8 | 128.4208 | 0.02335 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
388 | 128.1329 | 0.018551 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
388.2 | 128.3248 | 0.018551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
388.4 | 128.1329 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0035139
388.6 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
388.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
389 | 128.3248 | 0.015352 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.18829 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
389.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.48515 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
389.4 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.18729 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
389.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.19792 | 0.0048701 | 0.0923 | 0.0051138
389.8 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
390 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
390.2 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
390.4 | 128.2288 | 0.015352 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0019147
390.6 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
390.8 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
391 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
391.2 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
391.4 | 128.3248 | 0.013753 | 0.29387 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
391.6 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
391.8 | 128.5167 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.18729 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
392 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
392.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
392.4 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
392.6 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
392.8 | 128.3248 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
393 | 128.3248 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
393.2 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
393.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
393.6 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.0923 | 0.0051138
393.8 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
394 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.19792 | 0.00647 | 0.0923 | 0.0051138
394.2 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
394.4 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
394.6 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
394.8 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
395 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
395.2 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
395.4 | 128.3248 | 0.013753 | 0.19792 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
395.6 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
395.8 | 128.3248 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.33406 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
396 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
396.2 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | -0.0013064 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
396.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
396.6 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
396.8 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 1.6612e-05 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
397 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0016158 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
397.2 | 128.2288 | 0.016952 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.57118 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
397.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0035139
397.6 | 128.2288 | 0.015352 | 0.29387 | 0.0015826 | 0.10127 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
397.8 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
398 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.003271 | 0.0923 | 0.006713
398.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
398.4 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
398.6 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
398.8 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | -0.0036512 | 0.006713
399 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.10127 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
399.2 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.006713
399.4 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
399.6 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
399.8 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.006713
400 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
400.2 | 128.3248 | 0.013753 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
400.4 | 128.1329 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
400.6 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
400.8 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
401 | 128.1329 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
401.2 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
401.4 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
401.6 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
401.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0070012 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
402 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
402.2 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
402.4 | 128.2288 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.76408 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
402.6 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
402.8 | 128.2288 | 0.016952 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
403 | 128.3248 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0083128
403.2 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
403.4 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
403.6 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
403.8 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
404 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
404.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
404.4 | 128.2288 | 0.012154 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
404.6 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
404.8 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
405 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.67775 | 0.00647 | 0.18829 | 0.006713
405.2 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
405.4 | 128.2288 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
405.6 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
405.8 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
406 | 128.2288 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
406.2 | 128.2288 | 0.015352 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
406.4 | 128.2288 | 0.015352 | 0.29387 | 0.0063808 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
406.6 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.67775 | 0.00647 | 0.18829 | 0.006713
406.8 | 128.2288 | 0.016952 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.011268 | 0.0923 | 0.0051138
407 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
407.2 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
407.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.009912
407.6 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.66813 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
407.8 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
408 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
408.2 | 128.2288 | 0.015352 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.009912
408.4 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
408.6 | 128.2288 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
408.8 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
409 | 128.3248 | 0.015352 | 0.10193 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
409.2 | 128.2288 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
409.4 | 128.2288 | 0.015352 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
409.6 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
409.8 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
410 | 128.3248 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
410.2 | 128.2288 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
410.4 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
410.6 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
410.8 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.71795 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0035139
411 | 128.3248 | 0.016952 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.71795 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
411.2 | 128.3248 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
411.4 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
411.6 | 128.3248 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
411.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.33406 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
412 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
412.2 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
412.4 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
412.6 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
412.8 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
413 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
413.2 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.38019 | 0.0051138
413.4 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
413.6 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
413.8 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
414 | 128.3248 | 0.015352 | 0.38986 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
414.2 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
414.4 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
414.6 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
414.8 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
415 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
415.2 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0002934 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
415.4 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
415.6 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
415.8 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
416 | 128.2288 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
416.2 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.29387 | 0.0080692 | 0.28424 | 0.006713
416.4 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0019147
416.6 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
416.8 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
417 | 128.3248 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.0923 | 0.006713
417.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
417.4 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
417.6 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
417.8 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
418 | 128.2288 | 0.015352 | 0.38986 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
418.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
418.4 | 128.3248 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
418.6 | 128.3248 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
418.8 | 128.3248 | 0.016952 | 0.19792 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
419 | 128.3248 | 0.015352 | 0.38986 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0035139
419.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
419.4 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.011268 | 0.18829 | 0.006713
419.6 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
419.8 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
420 | 128.3248 | 0.016952 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
420.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
420.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
420.6 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
420.8 | 128.3248 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
421 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
421.2 | 128.3248 | 0.016952 | 0.10193 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.009912
421.4 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
421.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
421.8 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.0923 | 0.0051138
422 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
422.2 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
422.4 | 128.2288 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
422.6 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | -0.0013064 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
422.8 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.18729 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
423 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
423.2 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
423.4 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
423.6 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
423.8 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
424 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
424.2 | 128.1329 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
424.4 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
424.6 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
424.8 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
425 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
425.2 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.71795 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | -0.099642 | 0.0083128
425.4 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
425.6 | 128.2288 | 0.016952 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
425.8 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
426 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
426.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
426.4 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
426.6 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
426.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
427 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
427.2 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
427.4 | 128.2288 | 0.015352 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
427.6 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
427.8 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.18729 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
428 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
428.2 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
428.4 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
428.6 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
428.8 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.48515 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
429 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
429.2 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
429.4 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
429.6 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
429.8 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.28324 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
430 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
430.2 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
430.4 | 128.1329 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | -0.0036512 | 0.0051138
430.6 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
430.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
431 | 128.2288 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
431.2 | 128.3248 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
431.4 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
431.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
431.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.71795 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
432 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
432.2 | 128.2288 | 0.013753 | 0.19792 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
432.4 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
432.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
432.8 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
433 | 128.2288 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
433.2 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
433.4 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
433.6 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0002934 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
433.8 | 128.2288 | 0.013753 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
434 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
434.2 | 128.1329 | 0.016952 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
434.4 | 127.9409 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | -0.0036512 | 0.0035139
434.6 | 128.2288 | 0.02335 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
434.8 | 128.0369 | 0.02175 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.526 | 0.0081246 | 0.47618 | 0.0066908 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
435 | 128.1329 | 0.034546 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.00060315 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
435.2 | 128.6127 | 0.05214 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.016122 | 0.66813 | 0.01149 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
435.4 | 128.0369 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0081246 | 0.57213 | 0.014688 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
435.6 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0098898 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
435.8 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | -0.015391 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
436 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | -0.47386 | 0.00647 | 0.0923 | 0.0051138
436.2 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.19792 | 0.00647 | 0.18829 | 0.0051138
436.4 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
436.6 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
436.8 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
437 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
437.2 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
437.4 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.18829 | 0.0051138
437.6 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.0923 | 0.0035139
437.8 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0035139
438 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
438.2 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
438.4 | 128.0369 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
438.6 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
438.8 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
439 | 128.0369 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.00012733 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
439.2 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
439.4 | 128.0369 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
439.6 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.10197 | 0.0048701 | 0.0923 | 0.0051138
439.8 | 128.0369 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
440 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
440.2 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
440.4 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
440.6 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
440.8 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.48515 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
441 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
441.2 | 128.0369 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.38019 | 0.0051138
441.4 | 128.0369 | 0.010554 | 0.38986 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0065247 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
441.6 | 128.0369 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
441.8 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
442 | 127.9409 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
442.2 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
442.4 | 127.9409 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.71795 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
442.6 | 127.9409 | 0.0089549 | 0.19792 | 0.0063808 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.00012733 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
442.8 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.57118 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
443 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.18829 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
443.2 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
443.4 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.00012733 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
443.6 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
443.8 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
444 | 127.9409 | 0.010554 | 0.38986 | -1.6596e-05 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
444.2 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
444.4 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
444.6 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
444.8 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
445 | 127.8449 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
445.2 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
445.4 | 127.9409 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
445.6 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
445.8 | 127.9409 | 0.010554 | 0.19792 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
446 | 127.9409 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
446.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
446.4 | 127.9409 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
446.6 | 127.8449 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
446.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
447 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.009912
447.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
447.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
447.6 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
447.8 | 127.9409 | 0.0089549 | 0.48581 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
448 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0080139 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.006713
448.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
448.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
448.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.0080692 | 0.0923 | 0.0051138
448.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
449 | 127.8449 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
449.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
449.4 | 127.9409 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
449.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
449.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
450 | 127.8449 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
450.2 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
450.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
450.6 | 127.749 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
450.8 | 127.8449 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0086004 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
451 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
451.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
451.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
451.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.71795 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
451.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
452 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
452.2 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
452.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
452.6 | 127.749 | 0.010554 | 0.10193 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
452.8 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
453 | 127.749 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
453.2 | 127.749 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.10197 | 0.00647 | 0.18829 | 0.0051138
453.4 | 128.0369 | 0.015352 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.00031555
453.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.29387 | 0.0080692 | 0.0923 | 0.006713
453.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
454 | 127.749 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.66713 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
454.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
454.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
454.6 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | -0.0015273 | 0.18829 | 0.006713
454.8 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.009912
455 | 128.0369 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.18729 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0048701 | 0.0923 | 0.006713
455.2 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.003271 | 0.18829 | 0.0051138
455.4 | 127.8449 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
455.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
455.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
456 | 127.749 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
456.2 | 127.8449 | 0.0089549 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.009912
456.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.009912
456.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.011268 | 0.18829 | 0.0051138
456.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0019147
457 | 127.8449 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.66713 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
457.2 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
457.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
457.6 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
457.8 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.66713 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
458 | 127.9409 | 0.0073551 | 0.29387 | 0.0031824 | 0.10127 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
458.2 | 127.9409 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
458.4 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
458.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
458.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | -0.0014725 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
459 | 127.8449 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
459.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
459.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.66713 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
459.6 | 127.9409 | 0.0073551 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
459.8 | 127.749 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
460 | 127.9409 | 0.0073551 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
460.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.18729 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
460.4 | 127.9409 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
460.6 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.29387 | 0.0048701 | 0.0923 | 0.006713
460.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
461 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0065247 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
461.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
461.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0086004 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
461.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
461.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
462 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
462.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
462.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
462.6 | 127.9409 | 0.0073551 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
462.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
463 | 127.9409 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.011268 | 0.18829 | 0.0051138
463.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | -0.0036512 | 0.0051138
463.4 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
463.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
463.8 | 127.9409 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
464 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
464.2 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.009912
464.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0083128
464.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
464.8 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.006713
465 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
465.2 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
465.4 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
465.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
465.8 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
466 | 127.8449 | 0.0073551 | 0.19792 | 0.0031824 | 0.48515 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
466.2 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
466.4 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.19792 | 0.00647 | 0.18829 | 0.0051138
466.6 | 127.8449 | 0.0057559 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
466.8 | 127.8449 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
467 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
467.2 | 127.8449 | 0.0057559 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.00060315 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
467.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
467.6 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
467.8 | 127.8449 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
468 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
468.2 | 127.749 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
468.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
468.6 | 127.8449 | 0.0057559 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
468.8 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
469 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
469.2 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
469.4 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
469.6 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
469.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
470 | 127.8449 | 0.0089549 | 0.19792 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0086004 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
470.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
470.4 | 127.8449 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0019147
470.6 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
470.8 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
471 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
471.2 | 127.9409 | 0.010554 | 0.38986 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.14212 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.0035139
471.4 | 127.8449 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.009912
471.6 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
471.8 | 127.8449 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | -0.0036512 | 0.006713
472 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
472.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
472.4 | 127.9409 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
472.6 | 127.9409 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
472.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.76408 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
473 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.00060315 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
473.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.5818 | 0.00647 | 0.18829 | 0.0051138
473.4 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.28424 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
473.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
473.8 | 127.8449 | 0.0073551 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.009912
474 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
474.2 | 127.749 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.011268 | 0.18829 | 0.0051138
474.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.28424 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
474.6 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.10127 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
474.8 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.00060315 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
475 | 127.749 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
475.2 | 127.9409 | 0.0073551 | 0.19792 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
475.4 | 127.749 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
475.6 | 127.749 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.28424 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
475.8 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
476 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.011268 | 0.28424 | 0.006713
476.2 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.003271 | 0.0923 | 0.006713
476.4 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0019147
476.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
476.8 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
477 | 127.8449 | 0.0073551 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | -0.0036512 | 0.0051138
477.2 | 127.8449 | 0.0073551 | 0.0059762 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
477.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
477.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
477.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
478 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
478.2 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
478.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
478.6 | 127.749 | 0.0089549 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
478.8 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.00060315 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
479 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
479.2 | 127.653 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 1.0616 | 0.00647 | 0.18829 | 0.006713
479.4 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
479.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.76408 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
479.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
480 | 127.653 | 0.0073551 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
480.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
480.4 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
480.6 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0048701 | 0.0923 | 0.006713
480.8 | 127.749 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
481 | 127.749 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
481.2 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
481.4 | 127.749 | 0.0089549 | 0.29387 | -1.6596e-05 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
481.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.5811 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
481.8 | 127.749 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
482 | 127.749 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.00060315 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
482.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
482.4 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.19722 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | -0.0013064 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
482.6 | 127.8449 | 0.0089549 | 0.19792 | 0.0015826 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0081246 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0019147
482.8 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.48515 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
483 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | -0.0013064 | 0.29387 | 0.00647 | 0.0923 | 0.006713
483.2 | 127.8449 | 0.0057559 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
483.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
483.6 | 127.749 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
483.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0002934 | 0.48581 | 0.00647 | 0.18829 | 0.006713
484 | 127.8449 | 0.0057559 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
484.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
484.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
484.6 | 127.8449 | 0.0089549 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
484.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
485 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
485.2 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
485.4 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
485.6 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
485.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.0048701 | 0.18829 | 0.006713
486 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.48515 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
486.2 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.00060315 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.0036512 | 0.0051138
486.4 | 127.9409 | 0.010554 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
486.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
486.8 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
487 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
487.2 | 127.8449 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0002934 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
487.4 | 127.8449 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
487.6 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
487.8 | 127.8449 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
488 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.18729 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
488.2 | 127.8449 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
488.4 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
488.6 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
488.8 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
489 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.28424 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
489.2 | 127.9409 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0016718 | -0.0036512 | 0.0051138
489.4 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
489.6 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
489.8 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
490 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
490.2 | 127.9409 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
490.4 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
490.6 | 127.9409 | 0.012154 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
490.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
491 | 127.9409 | 0.012154 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.38019 | 0.0035139
491.2 | 127.9409 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.099642 | 0.0051138
491.4 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
491.6 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
491.8 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
492 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
492.2 | 128.0369 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
492.4 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
492.6 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
492.8 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
493 | 127.9409 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
493.2 | 127.9409 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0035139
493.4 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.28424 | 0.0019147
493.6 | 127.9409 | 0.010554 | 0.10193 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
493.8 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
494 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
494.2 | 127.8449 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.0080692 | 0.0923 | 0.0051138
494.4 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0083128
494.6 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
494.8 | 128.0369 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
495 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
495.2 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
495.4 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
495.6 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
495.8 | 127.9409 | 0.012154 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
496 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
496.2 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
496.4 | 128.0369 | 0.012154 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
496.6 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0065247 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.18829 | 0.006713
496.8 | 127.9409 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.28324 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
497 | 128.0369 | 0.012154 | 0.29387 | -1.6596e-05 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
497.2 | 128.0369 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
497.4 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
497.6 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
497.8 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
498 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.23811 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
498.2 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
498.4 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
498.6 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
498.8 | 128.1329 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0017265 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
499 | 128.1329 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
499.2 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
499.4 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
499.6 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
499.8 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
500 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.0923 | 0.0051138
500.2 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
500.4 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
500.6 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.006713
500.8 | 128.0369 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
501 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.19792 | 0.00647 | 0.0923 | 0.0051138
501.2 | 128.1329 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
501.4 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
501.6 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
501.8 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.00060315 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
502 | 128.1329 | 0.020151 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
502.2 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.76408 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
502.4 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
502.6 | 128.1329 | 0.015352 | 0.29387 | 0.0015826 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
502.8 | 128.1329 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
503 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0018926 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
503.2 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
503.4 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0002934 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
503.6 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0035139
503.8 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
504 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | -0.099642 | 0.006713
504.2 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
504.4 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0098898 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
504.6 | 128.0369 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0098898 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
504.8 | 128.1329 | 0.015352 | 0.38986 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0081246 | 0.57213 | 0.017887 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
505 | 128.6127 | 0.013753 | 0.19792 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.011324 | 0.66813 | 0.014688 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
505.2 | 128.6127 | 0.047342 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.016122 | 0.57213 | 0.014688 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
505.4 | 128.7087 | 0.056938 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0038022 | 0.62195 | 0.014522 | 0.57213 | 0.0082906 | 0.29387 | 0.0048701 | 0.0923 | 0.0051138
505.6 | 128.2288 | 0.048941 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.011324 | 0.47618 | 0.0082906 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
505.8 | 128.1329 | 0.034546 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
506 | 127.8449 | 0.032947 | 0.29387 | 0.0031824 | 0.38916 | 0.0016158 | 0.37923 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.006713
506.2 | 127.4611 | 0.024949 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
506.4 | 127.3651 | 0.026549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
506.6 | 127.749 | 0.02335 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
506.8 | 127.9409 | 0.020151 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.006713
507 | 128.3248 | 0.02335 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.006713
507.2 | 128.2288 | 0.026549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.011268 | 0.0923 | 0.0051138
507.4 | 127.9409 | 0.020151 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.0083128
507.6 | 128.0369 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.0035139
507.8 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.006713
508 | 128.1329 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
508.2 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
508.4 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.0035139
508.6 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
508.8 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
509 | 128.0369 | 0.012154 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
509.2 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
509.4 | 128.2288 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
509.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
509.8 | 128.1329 | 0.013753 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
510 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
510.2 | 128.2288 | 0.013753 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0019147
510.4 | 128.1329 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.66713 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.10197 | 0.0080692 | 0.18829 | 0.0051138
510.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
510.8 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
511 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.009669 | -0.099642 | 0.006713
511.2 | 128.3248 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
511.4 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
511.6 | 128.2288 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
511.8 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
512 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
512.2 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
512.4 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.28424 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
512.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
512.8 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
513 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
513.2 | 128.2288 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
513.4 | 128.2288 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
513.6 | 128.2288 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
513.8 | 128.1329 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
514 | 128.2288 | 0.013753 | 0.38986 | 0.0031824 | 0.48515 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
514.2 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | -0.099642 | 0.006713
514.4 | 128.2288 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
514.6 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
514.8 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
515 | 128.1329 | 0.015352 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
515.2 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
515.4 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
515.6 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
515.8 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
516 | 128.2288 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
516.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
516.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
516.6 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
516.8 | 128.3248 | 0.015352 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
517 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
517.2 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
517.4 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
517.6 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.006713
517.8 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | 0.28424 | 0.006713
518 | 128.3248 | 0.016952 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
518.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.10127 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
518.4 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
518.6 | 128.4208 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
518.8 | 128.3248 | 0.016952 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
519 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.00012733 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
519.2 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
519.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
519.6 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
519.8 | 128.4208 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
520 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0002934 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
520.2 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
520.4 | 129.1885 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
520.6 | 129.4764 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
520.8 | 128.6127 | 0.015352 | 0.38986 | -1.6596e-05 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
521 | 128.4208 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
521.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
521.4 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
521.6 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.10127 | 0.0016158 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
521.8 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | 0.28424 | 0.006713
522 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
522.2 | 128.1329 | 0.020151 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | -0.0036512 | 0.0051138
522.4 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
522.6 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
522.8 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
523 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.29387 | 0.0048701 | 0.18829 | 0.006713
523.2 | 128.3248 | 0.039345 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
523.4 | 127.749 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
523.6 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0080139 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
523.8 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
524 | 128.2288 | 0.013753 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
524.2 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.006713
524.4 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.10127 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
524.6 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.5811 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
524.8 | 128.1329 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0019147
525 | 127.9409 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
525.2 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.47618 | 0.0051138
525.4 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
525.6 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
525.8 | 128.0369 | 0.013753 | 0.19792 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
526 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0035139
526.2 | 128.0369 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
526.4 | 127.9409 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 1.6612e-05 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
526.6 | 128.0369 | 0.013753 | 0.19792 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
526.8 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
527 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
527.2 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | -0.0036512 | 0.0051138
527.4 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
527.6 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | -0.099642 | 0.006713
527.8 | 127.9409 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
528 | 127.9409 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
528.2 | 127.8449 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
528.4 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
528.6 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | -0.099642 | 0.0035139
528.8 | 127.8449 | 0.012154 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.19792 | 0.0080692 | 0.18829 | 0.0051138
529 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
529.2 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
529.4 | 127.9409 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.33406 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
529.6 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.29387 | 0.00647 | 0.18829 | 0.006713
529.8 | 127.8449 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
530 | 127.9409 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
530.2 | 127.8449 | 0.013753 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
530.4 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0002934 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
530.6 | 127.8449 | 0.010554 | 0.10193 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
530.8 | 127.8449 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
531 | 127.749 | 0.012154 | 0.19792 | 0.0031824 | 0.29321 | 0.0032156 | 0.57118 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
531.2 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0066908 | 0.38986 | 0.0048701 | 0.0923 | 0.0051138
531.4 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
531.6 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
531.8 | 128.0369 | 0.018551 | 0.29387 | 0.0047816 | 0.10127 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
532 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
532.2 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0035139
532.4 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.28424 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
532.6 | 127.8449 | 0.010554 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
532.8 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
533 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.19722 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.28424 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
533.2 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
533.4 | 127.749 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
533.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.38019 | 0.0051138
533.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.23811 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
534 | 127.8449 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
534.2 | 127.749 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
534.4 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.28424 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
534.6 | 127.749 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
534.8 | 127.8449 | 0.010554 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
535 | 127.8449 | 0.0089549 | 0.10193 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
535.2 | 127.749 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
535.4 | 127.749 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0016718 | 0.18829 | 0.006713
535.6 | 127.749 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
535.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
536 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
536.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
536.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
536.6 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.00060315 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.38019 | 0.006713
536.8 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.0923 | 0.0051138
537 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
537.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
537.4 | 127.9409 | 0.0073551 | 0.19792 | 0.0079807 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.00012733 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
537.6 | 127.8449 | 0.0073551 | 0.10193 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
537.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.28424 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
538 | 128.0369 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
538.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
538.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
538.6 | 128.1329 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
538.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
539 | 128.0369 | 0.0073551 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
539.2 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
539.4 | 128.0369 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
539.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
539.8 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
540 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
540.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
540.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.66713 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
540.6 | 128.0369 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
540.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
541 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
541.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
541.4 | 128.0369 | 0.0089549 | 0.10193 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
541.6 | 128.0369 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
541.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
542 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
542.2 | 128.1329 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
542.4 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.009669 | 0.18829 | 0.006713
542.6 | 128.1329 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
542.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
543 | 128.1329 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
543.2 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
543.4 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
543.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
543.8 | 128.2288 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
544 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
544.2 | 128.1329 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0019147
544.4 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
544.6 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
544.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.01149 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
545 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.5811 | 0.0048148 | 0.37923 | 0.0054014 | 0.71795 | 0.014522 | 0.66813 | 0.0082906 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
545.2 | 128.2288 | 0.0057559 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
545.4 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0081246 | 0.57213 | 0.014688 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
545.6 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.012923 | 0.57213 | 0.0098898 | 0.5818 | 0.00647 | 0.18829 | 0.006713
545.8 | 128.9006 | 0.047342 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.006713
546 | 128.1329 | 0.024949 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
546.2 | 128.4208 | 0.02335 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
546.4 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
546.6 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
546.8 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
547 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
547.2 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
547.4 | 128.4208 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
547.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
547.8 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
548 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
548.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
548.4 | 128.3248 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
548.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
548.8 | 128.2288 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
549 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
549.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
549.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
549.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.67775 | 0.00647 | 0.0923 | 0.006713
549.8 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
550 | 128.2288 | 0.0089549 | 0.10193 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
550.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
550.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
550.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
550.8 | 128.3248 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | -0.0036512 | 0.006713
551 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
551.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
551.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
551.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
551.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
552 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
552.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0035139
552.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
552.6 | 128.3248 | 0.0073551 | 0.29387 | 0.0047816 | 0.10127 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
552.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
553 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
553.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
553.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0070012 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
553.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.29387 | 0.00647 | 0.18829 | 0.006713
553.8 | 128.3248 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
554 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
554.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
554.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.0051138
554.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
554.8 | 128.2288 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
555 | 128.3248 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
555.2 | 128.2288 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | -0.0036512 | 0.0035139
555.4 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
555.6 | 128.3248 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
555.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
556 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0035139
556.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
556.4 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
556.6 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
556.8 | 128.2288 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
557 | 128.3248 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.67775 | 0.00647 | 0.18829 | 0.0051138
557.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
557.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
557.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
557.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
558 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.10197 | 0.00647 | 0.18829 | 0.0051138
558.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
558.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
558.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
558.8 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
559 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
559.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.38019 | 0.0051138
559.4 | 128.3248 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
559.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
559.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.57118 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
560 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
560.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
560.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
560.6 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
560.8 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
561 | 128.2288 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
561.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.006713
561.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
561.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
561.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0086004 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0048701 | 0.18829 | 0.0051138
562 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
562.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
562.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
562.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
562.8 | 128.2288 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
563 | 128.2288 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
563.2 | 128.3248 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
563.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.006713
563.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
563.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.0923 | 0.006713
564 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
564.2 | 128.2288 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
564.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
564.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.28424 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
564.8 | 128.2288 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
565 | 128.4208 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
565.2 | 128.2288 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
565.4 | 128.2288 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
565.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
565.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
566 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
566.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
566.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
566.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
566.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
567 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
567.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
567.4 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
567.6 | 128.3248 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
567.8 | 128.1329 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
568 | 128.3248 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.009912
568.2 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
568.4 | 128.4208 | 0.02335 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
568.6 | 128.0369 | 0.02175 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
568.8 | 128.5167 | 0.040944 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
569 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.012923 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
569.2 | 127.9409 | 0.010554 | 0.38986 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.47618 | 0.01149 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
569.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.011324 | 0.57213 | 0.0066908 | 0.5818 | 0.00647 | 0.18829 | 0.006713
569.6 | 128.2288 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | -0.29254 | 0.0054014 | 0.71795 | 0.0049255 | 0.66813 | 0.01149 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
569.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.86003 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
570 | 128.0369 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.0083128
570.2 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
570.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
570.6 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.00012733 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
570.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 1.6612e-05 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
571 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
571.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
571.4 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
571.6 | 128.1329 | 0.0089549 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
571.8 | 128.1329 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.006713
572 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
572.2 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
572.4 | 128.1329 | 0.0073551 | 0.38986 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
572.6 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
572.8 | 128.0369 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
573 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
573.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0016158 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
573.4 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
573.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
573.8 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
574 | 127.9409 | 0.0089549 | 0.38986 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
574.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
574.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
574.6 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
574.8 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
575 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
575.2 | 127.9409 | 0.0089549 | 0.0059762 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
575.4 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.23811 | 0.0033264 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
575.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
575.8 | 127.9409 | 0.013753 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
576 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.18729 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.67775 | 0.009669 | 0.18829 | 0.006713
576.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
576.4 | 127.9409 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0081246 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
576.6 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
576.8 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
577 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
577.2 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.76408 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
577.4 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.011268 | 0.28424 | 0.006713
577.6 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.0053144 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
577.8 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
578 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
578.2 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0016158 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
578.4 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
578.6 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
578.8 | 127.9409 | 0.020151 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
579 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
579.2 | 128.0369 | 0.012154 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
579.4 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.71795 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | -0.0036512 | 0.0051138
579.6 | 128.0369 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
579.8 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.29387 | 0.009669 | 0.28424 | 0.006713
580 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
580.2 | 128.1329 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
580.4 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.76408 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
580.6 | 128.0369 | 0.010554 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
580.8 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
581 | 127.9409 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
581.2 | 127.9409 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0065247 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
581.4 | 127.9409 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
581.6 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.10127 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
581.8 | 128.0369 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0035139
582 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0081246 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0019147
582.2 | 127.9409 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
582.4 | 127.8449 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
582.6 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
582.8 | 127.8449 | 0.018551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | -0.0036512 | 0.0051138
583 | 127.9409 | 0.013753 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
583.2 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
583.4 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
583.6 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.18829 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
583.8 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.19722 | 0.006414 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
584 | 128.1329 | 0.015352 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.28424 | 0.0051138
584.2 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
584.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
584.6 | 128.2288 | 0.013753 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
584.8 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0035139
585 | 128.2288 | 0.013753 | 0.38986 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
585.2 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
585.4 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
585.6 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
585.8 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.0083128
586 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
586.2 | 128.2288 | 0.013753 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
586.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.67775 | 0.0080692 | 0.18829 | 0.0051138
586.6 | 128.2288 | 0.013753 | 0.48581 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
586.8 | 128.3248 | 0.020151 | 0.19792 | -1.6596e-05 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
587 | 127.9409 | 0.02175 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.00647 | 0.28424 | 0.006713
587.2 | 128.5167 | 0.040944 | 0.48581 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
587.4 | 128.4208 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.57118 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
587.6 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
587.8 | 128.5167 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
588 | 128.3248 | 0.015352 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.33406 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
588.2 | 128.3248 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
588.4 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | 0.0923 | 0.006713
588.6 | 128.4208 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0081246 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
588.8 | 128.2288 | 0.015352 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
589 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
589.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
589.4 | 128.4208 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
589.6 | 128.6127 | 0.015352 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
589.8 | 129.0925 | 0.013753 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
590 | 129.5724 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0035139
590.2 | 128.7087 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.009912
590.4 | 128.6127 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
590.6 | 128.6127 | 0.015352 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
590.8 | 128.5167 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
591 | 128.4208 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
591.2 | 128.4208 | 0.016952 | 0.0059762 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
591.4 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
591.6 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
591.8 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0019147
592 | 128.4208 | 0.016952 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
592.2 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
592.4 | 128.4208 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
592.6 | 128.4208 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
592.8 | 128.4208 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
593 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
593.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
593.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
593.6 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
593.8 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
594 | 128.3248 | 0.015352 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
594.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
594.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
594.6 | 128.3248 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0035139
594.8 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
595 | 128.2288 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
595.2 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.006713
595.4 | 128.4208 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
595.6 | 128.2288 | 0.013753 | 0.19792 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
595.8 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.48515 | 0.0016158 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
596 | 128.3248 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
596.2 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
596.4 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.67775 | 0.00647 | 0.0923 | 0.006713
596.6 | 128.3248 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.76408 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
596.8 | 128.2288 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
597 | 128.2288 | 0.015352 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
597.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
597.4 | 128.2288 | 0.012154 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
597.6 | 128.3248 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
597.8 | 128.3248 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
598 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0082906 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
598.2 | 128.2288 | 0.02175 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
598.4 | 128.3248 | 0.020151 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
598.6 | 128.5167 | 0.039345 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
598.8 | 128.4208 | 0.055339 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.012923 | 0.57213 | 0.0082906 | 0.38986 | 0.00647 | 0.18829 | 0.006713
599 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0081246 | 0.66813 | 0.013089 | 0.38986 | 0.00647 | 0.18829 | 0.006713
599.2 | 128.2288 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.09134 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
599.4 | 128.1329 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 1.1018 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
599.6 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0016158 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0066908 | 0.5818 | 0.00647 | 0.0923 | 0.0051138
599.8 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
600 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
600.2 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0051138
600.4 | 128.1329 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0035139
600.6 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
600.8 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
601 | 128.1329 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
601.2 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
601.4 | 128.1329 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
601.6 | 128.1329 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
601.8 | 128.0369 | 0.013753 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.71795 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
602 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.5811 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
602.2 | 128.0369 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
602.4 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
602.6 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
602.8 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.67775 | 0.00647 | 0.0923 | 0.0051138
603 | 128.1329 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
603.2 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
603.4 | 128.0369 | 0.012154 | 0.38986 | -1.6596e-05 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
603.6 | 127.9409 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
603.8 | 127.749 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
604 | 127.9409 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
604.2 | 127.9409 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
604.4 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | -0.0013064 | 0.19792 | 0.00647 | 0.18829 | 0.006713
604.6 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
604.8 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
605 | 128.0369 | 0.012154 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
605.2 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
605.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
605.6 | 128.0369 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
605.8 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.67775 | 0.0080692 | 0.0923 | 0.006713
606 | 127.9409 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
606.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
606.4 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
606.6 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
606.8 | 128.0369 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
607 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
607.2 | 128.0369 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
607.4 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
607.6 | 128.0369 | 0.010554 | 0.29387 | 0.0015826 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0035139
607.8 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
608 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
608.2 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.28324 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
608.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
608.6 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
608.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
609 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
609.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
609.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.012867 | 0.0923 | 0.006713
609.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
609.8 | 127.9409 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
610 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
610.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
610.4 | 127.8449 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
610.6 | 127.9409 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
610.8 | 127.9409 | 0.0073551 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
611 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
611.2 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.009912
611.4 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
611.6 | 127.749 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
611.8 | 127.8449 | 0.013753 | 0.19792 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
612 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.0035139
612.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.57118 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
612.4 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.67775 | 0.009669 | 0.18829 | 0.006713
612.6 | 128.0369 | 0.012154 | 0.96565 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
612.8 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.66713 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
613 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
613.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.19792 | 0.0048701 | 0.18829 | 0.006713
613.4 | 127.9409 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
613.6 | 127.9409 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
613.8 | 127.9409 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
614 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.38019 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
614.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
614.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
614.6 | 127.9409 | 0.0073551 | 0.38986 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
614.8 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
615 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
615.2 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.57118 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
615.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0002934 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
615.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
615.8 | 128.0369 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
616 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
616.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
616.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
616.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
616.8 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
617 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
617.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
617.4 | 128.0369 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
617.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
617.8 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
618 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
618.2 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
618.4 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
618.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
618.8 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.18729 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
619 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
619.2 | 128.0369 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.0923 | 0.0051138
619.4 | 128.1329 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.67775 | 0.009669 | 0.18829 | 0.006713
619.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
619.8 | 128.0369 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
620 | 128.2288 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
620.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
620.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
620.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
620.8 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
621 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.00060315 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
621.2 | 128.0369 | 0.010554 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.00060315 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
621.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
621.6 | 128.0369 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
621.8 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
622 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
622.2 | 128.0369 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
622.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
622.6 | 128.0369 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.10197 | 0.0080692 | 0.18829 | 0.006713
622.8 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
623 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0083128
623.2 | 128.0369 | 0.0089549 | 0.38986 | -1.6596e-05 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
623.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
623.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
623.8 | 128.0369 | 0.0057559 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
624 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
624.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
624.4 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
624.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.09134 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
624.8 | 128.0369 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0083128
625 | 128.0369 | 0.0089549 | 0.29387 | 0.0015826 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
625.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
625.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
625.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
625.8 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
626 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
626.2 | 128.0369 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.0923 | 0.006713
626.4 | 128.1329 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
626.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0080139 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
626.8 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.10127 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
627 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
627.2 | 128.0369 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.38019 | 0.0035139
627.4 | 127.9409 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.003271 | 0.0923 | 0.006713
627.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
627.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926 | 0.5818 | 0.00647 | 0.18829 | 0.0051138
628 | 128.0369 | 0.0089549 | 0.19792 | 0.0079807 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
628.2 | 128.0369 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
628.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
628.6 | 128.1329 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 1.6612e-05 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
628.8 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
629 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
629.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
629.4 | 127.9409 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
629.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
629.8 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
630 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
630.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
630.4 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
630.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
630.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
631 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0035139
631.2 | 128.1329 | 0.0073551 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.76408 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
631.4 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
631.6 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
631.8 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.76408 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
632 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.009912
632.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
632.4 | 128.0369 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
632.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
632.8 | 128.0369 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
633 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
633.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.0923 | 0.0051138
633.4 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.19722 | 0.0032156 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
633.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.28424 | 0.0051138
633.8 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
634 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
634.2 | 128.1329 | 0.0073551 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.00012733 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
634.4 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
634.6 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
634.8 | 128.1329 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | -0.0013064 | 0.29387 | 0.00647 | 0.18829 | 0.006713
635 | 128.1329 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
635.2 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
635.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
635.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
635.8 | 128.1329 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
636 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
636.2 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
636.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
636.6 | 128.1329 | 0.0089549 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
636.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
637 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0002934 | 0.48581 | 0.00647 | 0.18829 | 0.006713
637.2 | 128.2288 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
637.4 | 128.0369 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
637.6 | 128.1329 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.00060315 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
637.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
638 | 128.1329 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
638.2 | 128.1329 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
638.4 | 128.1329 | 0.012154 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
638.6 | 128.1329 | 0.012154 | 0.29387 | 0.0047816 | 0.19722 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
638.8 | 128.0369 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.00647 | 0.18829 | 0.0051138
639 | 128.1329 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
639.2 | 128.1329 | 0.02175 | 0.10193 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.8139 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.0923 | 0.006713
639.4 | 128.4208 | 0.02335 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
639.6 | 128.0369 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
639.8 | 128.2288 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.66713 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.29387 | 0.003271 | 0.18829 | 0.006713
640 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
640.2 | 128.2288 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.48581 | 0.00647 | 0.0923 | 0.006713
640.4 | 128.2288 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
640.6 | 128.1329 | 0.0073551 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | -0.0077038 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
640.8 | 128.2288 | 0.0089549 | 0.38986 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
641 | 128.2288 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.33406 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
641.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
641.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
641.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
641.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
642 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
642.2 | 128.2288 | 0.0089549 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0083128
642.4 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
642.6 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | -0.0036512 | 0.006713
642.8 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
643 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
643.2 | 128.1329 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
643.4 | 128.1329 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
643.6 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
643.8 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
644 | 126.9813 | 0.0073551 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
644.2 | 127.0772 | 0.0073551 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
644.4 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0082906 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
644.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
644.8 | 128.0369 | 0.0073551 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
645 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
645.2 | 128.1329 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
645.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
645.6 | 128.2288 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
645.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.00012733 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
646 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
646.2 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
646.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
646.6 | 128.2288 | 0.0057559 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.38019 | 0.006713
646.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
647 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.009912
647.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
647.4 | 128.3248 | 0.0089549 | 0.48581 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
647.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
647.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
648 | 128.2288 | 0.0089549 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
648.2 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.19792 | 0.0080692 | 0.18829 | 0.0051138
648.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
648.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
648.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.10127 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
649 | 128.2288 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
649.2 | 128.2288 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
649.4 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
649.6 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
649.8 | 128.2288 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
650 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
650.2 | 128.3248 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.67775 | 0.00647 | 0.18829 | 0.006713
650.4 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
650.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
650.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
651 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
651.2 | 128.2288 | 0.0089549 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
651.4 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
651.6 | 128.2288 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.006713
651.8 | 128.2288 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
652 | 128.2288 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
652.2 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.009912
652.4 | 128.1329 | 0.013753 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
652.6 | 128.3248 | 0.02175 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
652.8 | 128.1329 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
653 | 128.1329 | 0.032947 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
653.2 | 128.8046 | 0.045742 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
653.4 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.014522 | 0.57213 | 0.0098898 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
653.6 | 128.0369 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.47618 | 0.0051138
653.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.8139 | 0.014522 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
654 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
654.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
654.4 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
654.6 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
654.8 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
655 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
655.2 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
655.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
655.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
655.8 | 128.1329 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
656 | 128.0369 | 0.0073551 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
656.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
656.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
656.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
656.8 | 128.0369 | 0.0089549 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
657 | 128.0369 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
657.2 | 127.9409 | 0.0057559 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
657.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
657.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
657.8 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.18729 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
658 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
658.2 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.011511
658.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
658.6 | 127.9409 | 0.0089549 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
658.8 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
659 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
659.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
659.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
659.6 | 127.9409 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | -0.0036512 | 0.006713
659.8 | 128.0369 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
660 | 127.9409 | 0.0073551 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
660.2 | 127.9409 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
660.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.38019 | 0.0051138
660.6 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
660.8 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
661 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
661.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
661.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
661.6 | 127.8449 | 0.0089549 | 0.48581 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
661.8 | 127.9409 | 0.010554 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
662 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
662.2 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
662.4 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
662.6 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
662.8 | 127.9409 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
663 | 127.9409 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
663.2 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
663.4 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
663.6 | 127.9409 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
663.8 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
664 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
664.2 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
664.4 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | -0.0036512 | 0.006713
664.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
664.8 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0002934 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
665 | 127.9409 | 0.012154 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
665.2 | 128.0369 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.0923 | 0.0051138
665.4 | 127.8449 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
665.6 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.67775 | 0.0080692 | 0.0923 | 0.0051138
665.8 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
666 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.38019 | 0.006713
666.2 | 127.9409 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
666.4 | 127.9409 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
666.6 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
666.8 | 127.653 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
667 | 127.8449 | 0.012154 | 0.29387 | 0.0015826 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.00647 | 0.18829 | 0.006713
667.2 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0082906 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
667.4 | 127.8449 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
667.6 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.009912
667.8 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
668 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
668.2 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
668.4 | 128.0369 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
668.6 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.003271 | -0.0036512 | 0.006713
668.8 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
669 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
669.2 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
669.4 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
669.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
669.8 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
670 | 127.749 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
670.2 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
670.4 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0016718 | 0.0923 | 0.006713
670.6 | 127.8449 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
670.8 | 128.0369 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
671 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0019147
671.2 | 127.8449 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
671.4 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.66713 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
671.6 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.011268 | 0.28424 | 0.006713
671.8 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
672 | 127.9409 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
672.2 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.47618 | 0.0051138
672.4 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
672.6 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
672.8 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
673 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
673.2 | 127.9409 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
673.4 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.66713 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
673.6 | 127.9409 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
673.8 | 127.8449 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
674 | 127.9409 | 0.013753 | 0.10193 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
674.2 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.28424 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
674.4 | 127.9409 | 0.016952 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
674.6 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
674.8 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
675 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
675.2 | 127.9409 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
675.4 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
675.6 | 128.0369 | 0.013753 | 0.38986 | 0.0015826 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
675.8 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
676 | 127.8449 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0022023 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
676.2 | 128.2288 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.18729 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
676.4 | 128.0369 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
676.6 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0035139
676.8 | 128.0369 | 0.013753 | 0.29387 | 0.0015826 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
677 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
677.2 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.66713 | 0.0070012 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
677.4 | 128.1329 | 0.013753 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.00012733 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
677.6 | 128.0369 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
677.8 | 128.0369 | 0.015352 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
678 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
678.2 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
678.4 | 128.0369 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
678.6 | 128.0369 | 0.015352 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
678.8 | 128.1329 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
679 | 128.1329 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
679.2 | 128.1329 | 0.012154 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
679.4 | 128.1329 | 0.013753 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
679.6 | 128.1329 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
679.8 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.0923 | 0.0051138
680 | 128.3248 | 0.020151 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
680.2 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
680.4 | 127.8449 | 0.02335 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
680.6 | 128.3248 | 0.040944 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
680.8 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0098898 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
681 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
681.2 | 128.1329 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.016011 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
681.4 | 128.1329 | 0.018551 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
681.6 | 128.2288 | 0.016952 | 0.29387 | 0.0015826 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0017265 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
681.8 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0048701 | 0.0923 | 0.006713
682 | 128.2288 | 0.015352 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
682.2 | 128.1329 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
682.4 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
682.6 | 128.1329 | 0.016952 | 0.29387 | 0.0079807 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
682.8 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
683 | 128.2288 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0002934 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
683.2 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
683.4 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.66713 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
683.6 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.00647 | 0.28424 | 0.006713
683.8 | 128.3248 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
684 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
684.2 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
684.4 | 128.2288 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
684.6 | 128.1329 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
684.8 | 128.4208 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
685 | 128.5167 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
685.2 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
685.4 | 128.8046 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
685.6 | 129.6683 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
685.8 | 129.1885 | 0.020151 | 0.29387 | 0.0031824 | 0.29321 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
686 | 128.7087 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
686.2 | 128.5167 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0016158 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
686.4 | 128.5167 | 0.015352 | 0.19792 | 0.0047816 | 0.10127 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
686.6 | 128.4208 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
686.8 | 128.4208 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
687 | 128.3248 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
687.2 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
687.4 | 128.2288 | 0.016952 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
687.6 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
687.8 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
688 | 128.1329 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
688.2 | 128.2288 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.28424 | 0.006713
688.4 | 128.3248 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
688.6 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
688.8 | 128.2288 | 0.015352 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
689 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
689.2 | 128.2288 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
689.4 | 128.2288 | 0.018551 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.006713
689.6 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
689.8 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
690 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.0083128
690.2 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
690.4 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
690.6 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
690.8 | 128.2288 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.66713 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
691 | 128.2288 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
691.2 | 128.3248 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
691.4 | 128.3248 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
691.6 | 128.2288 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
691.8 | 128.2288 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
692 | 128.2288 | 0.015352 | 0.29387 | 0.0015826 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
692.2 | 128.2288 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.0083128
692.4 | 128.1329 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
692.6 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.00060315 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
692.8 | 128.2288 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
693 | 128.2288 | 0.013753 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
693.2 | 128.2288 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
693.4 | 128.1329 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
693.6 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
693.8 | 128.1329 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
694 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
694.2 | 128.2288 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
694.4 | 128.1329 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.33406 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
694.6 | 128.2288 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
694.8 | 128.1329 | 0.015352 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
695 | 128.1329 | 0.015352 | 0.38986 | 0.0031824 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
695.2 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
695.4 | 128.1329 | 0.013753 | 0.29387 | 0.0063808 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
695.6 | 128.1329 | 0.013753 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
695.8 | 128.0369 | 0.013753 | 0.38986 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
696 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
696.2 | 128.2288 | 0.020151 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
696.4 | 128.2288 | 0.02335 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | -0.0036512 | 0.0051138
696.6 | 127.9409 | 0.020151 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0097238 | 0.47618 | 0.0082906 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
696.8 | 127.9409 | 0.034546 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0081246 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
697 | 128.4208 | 0.055339 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.012923 | 0.57213 | 0.0082906 | 0.38986 | 0.011268 | 0.0923 | 0.006713
697.2 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0038022 | 0.43001 | 0.0097238 | 0.57213 | 0.0082906 | 0.38986 | 0.00647 | 0.28424 | 0.006713
697.4 | 128.1329 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 1.5308 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
697.6 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
697.8 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
698 | 127.749 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
698.2 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.28424 | 0.0083128
698.4 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
698.6 | 127.8449 | 0.013753 | 0.29387 | 0.0031824 | 0.10127 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
698.8 | 127.749 | 0.015352 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
699 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
699.2 | 127.749 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
699.4 | 127.749 | 0.013753 | 0.38986 | 0.0031824 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
699.6 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
699.8 | 127.749 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.006713
700 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
700.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.23811 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
700.4 | 127.749 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0083128
700.6 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
700.8 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
701 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0019147
701.2 | 128.0369 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0048701 | 0.18829 | 0.0051138
701.4 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
701.6 | 127.9409 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
701.8 | 127.9409 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
702 | 128.0369 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
702.2 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
702.4 | 127.9409 | 0.012154 | 0.38986 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
702.6 | 128.0369 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
702.8 | 127.9409 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
703 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
703.2 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
703.4 | 128.0369 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
703.6 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
703.8 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0086004 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
704 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
704.2 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
704.4 | 127.8449 | 0.012154 | 0.48581 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.006713
704.6 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
704.8 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.28424 | 0.0051138
705 | 127.9409 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.18829 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
705.2 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
705.4 | 127.9409 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
705.6 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
705.8 | 127.9409 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
706 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
706.2 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
706.4 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
706.6 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
706.8 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
707 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
707.2 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
707.4 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
707.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0016158 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
707.8 | 127.8449 | 0.010554 | 0.29387 | 0.0079807 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
708 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
708.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0016158 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
708.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0015826 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0035139
708.6 | 127.8449 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
708.8 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
709 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.0051138
709.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
709.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
709.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
709.8 | 127.9409 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
710 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
710.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
710.4 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
710.6 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
710.8 | 127.749 | 0.012154 | 0.29387 | 0.0031824 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
711 | 127.653 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
711.2 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
711.4 | 127.8449 | 0.0089549 | 0.29387 | -0.0048148 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
711.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0015826 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
711.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
712 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.006713
712.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
712.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
712.6 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.006713
712.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
713 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.28424 | 0.006713
713.2 | 127.8449 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
713.4 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
713.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
713.8 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0019147
714 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0017265 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
714.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
714.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
714.6 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0002934 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
714.8 | 127.8449 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.23811 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
715 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.011511
715.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
715.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0019147
715.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
715.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
716 | 127.8449 | 0.0089549 | 0.58176 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
716.2 | 127.8449 | 0.0089549 | 0.19792 | -1.6596e-05 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
716.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
716.6 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
716.8 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
717 | 127.8449 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
717.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
717.4 | 127.8449 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
717.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.009912
717.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.38019 | 0.006713
718 | 127.8449 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.006713
718.2 | 127.8449 | 0.0089549 | 0.38986 | -1.6596e-05 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
718.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
718.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
718.8 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.009669 | 0.18829 | 0.006713
719 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
719.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
719.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0022023 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
719.6 | 127.9409 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
719.8 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
720 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.0051138
720.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
720.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.23811 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0035139
720.6 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
720.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
721 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.18729 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
721.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
721.4 | 127.9409 | 0.0073551 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
721.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
721.8 | 128.0369 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
722 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
722.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
722.4 | 128.0369 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
722.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.003271 | 0.18829 | 0.0051138
722.8 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
723 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.19792 | 0.00647 | 0.18829 | 0.006713
723.2 | 127.8449 | 0.016952 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.009912
723.4 | 128.3248 | 0.028148 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
723.6 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.28424 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
723.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.47618 | 0.0066908 | 0.38986 | 0.003271 | 0.0923 | 0.0051138
724 | 128.0369 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
724.2 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
724.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.28424 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
724.6 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.0048701 | 0.18829 | 0.0051138
724.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.009912
725 | 128.1329 | 0.0089549 | 0.29387 | 0.0015826 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
725.2 | 128.0369 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.00060315 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
725.4 | 127.9409 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
725.6 | 127.3651 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.28424 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
725.8 | 127.1732 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
726 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
726.2 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
726.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
726.6 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
726.8 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
727 | 128.1329 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
727.2 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
727.4 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
727.6 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
727.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
728 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
728.2 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
728.4 | 128.2288 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
728.6 | 128.2288 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
728.8 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
729 | 128.1329 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
729.2 | 128.1329 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
729.4 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0051138
729.6 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
729.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
730 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
730.2 | 127.9409 | 0.0089549 | 0.10193 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
730.4 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
730.6 | 127.9409 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
730.8 | 128.0369 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
731 | 127.8449 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
731.2 | 127.8449 | 0.029748 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
731.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.012923 | 0.57213 | 0.01149 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
731.6 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
731.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
732 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.66813 | 0.0083128
732.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.5811 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
732.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
732.6 | 127.9409 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
732.8 | 127.9409 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
733 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
733.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
733.4 | 127.9409 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
733.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
733.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.23811 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
734 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
734.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0002934 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
734.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
734.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
734.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
735 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
735.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
735.4 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
735.6 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.006713
735.8 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
736 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
736.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
736.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
736.6 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
736.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
737 | 127.8449 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | -0.0036512 | 0.0051138
737.2 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
737.4 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
737.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0022023 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.006713
737.8 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
738 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
738.2 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
738.4 | 127.8449 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.38019 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
738.6 | 127.8449 | 0.013753 | 0.38986 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
738.8 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
739 | 127.8449 | 0.016952 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.099642 | 0.0035139
739.2 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0098898 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
739.4 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.00060315 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
739.6 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.00031555
739.8 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
740 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
740.2 | 127.8449 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.011268 | 0.18829 | 0.006713
740.4 | 127.8449 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
740.6 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
740.8 | 127.8449 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
741 | 127.8449 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
741.2 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
741.4 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
741.6 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
741.8 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
742 | 128.0369 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
742.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
742.4 | 127.9409 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
742.6 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
742.8 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
743 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
743.2 | 128.0369 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
743.4 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
743.6 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.38019 | 0.006713
743.8 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.19792 | 0.0048701 | 0.18829 | 0.006713
744 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
744.2 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
744.4 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
744.6 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
744.8 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
745 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
745.2 | 128.0369 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
745.4 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.0083128
745.6 | 128.0369 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
745.8 | 128.1329 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.23811 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
746 | 128.1329 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
746.2 | 128.0369 | 0.028148 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.0083128
746.4 | 128.1329 | 0.016952 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
746.6 | 128.1329 | 0.018551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0017265 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
746.8 | 128.1329 | 0.016952 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0083128
747 | 128.2288 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.006713
747.2 | 128.1329 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.0083128
747.4 | 128.2288 | 0.018551 | 0.29387 | 0.0031824 | 0.29321 | 0.006414 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
747.6 | 128.1329 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
747.8 | 128.3248 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
748 | 129.0925 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
748.2 | 128.9966 | 0.018551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
748.4 | 128.5167 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
748.6 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.18829 | 0.006713
748.8 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
749 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
749.2 | 128.2288 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
749.4 | 128.2288 | 0.016952 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
749.6 | 128.1329 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
749.8 | 128.2288 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
750 | 128.2288 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
750.2 | 128.2288 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
750.4 | 128.1329 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
750.6 | 128.1329 | 0.016952 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
750.8 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
751 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
751.2 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
751.4 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
751.6 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0086004 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
751.8 | 128.1329 | 0.015352 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
752 | 128.1329 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
752.2 | 128.0369 | 0.013753 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
752.4 | 128.0369 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
752.6 | 127.8449 | 0.02335 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
752.8 | 128.1329 | 0.053739 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0070012 | 0.62195 | 0.012923 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
753 | 128.0369 | 0.015352 | 0.29387 | 0.0063808 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.66813 | 0.0098898 | 0.48581 | 0.00647 | 0.18829 | 0.006713
753.2 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
753.4 | 127.9409 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.0923 | 0.0083128
753.6 | 127.9409 | 0.013753 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.009912
753.8 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
754 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.0923 | 0.006713
754.2 | 127.9409 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
754.4 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
754.6 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
754.8 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
755 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
755.2 | 127.9409 | 0.013753 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
755.4 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
755.6 | 127.9409 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
755.8 | 127.9409 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
756 | 127.8449 | 0.012154 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
756.2 | 127.9409 | 0.012154 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
756.4 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
756.6 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
756.8 | 127.8449 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
757 | 127.8449 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
757.2 | 127.9409 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
757.4 | 127.9409 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
757.6 | 127.8449 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
757.8 | 127.653 | 0.012154 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
758 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0002934 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
758.2 | 127.8449 | 0.010554 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
758.4 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
758.6 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
758.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
759 | 127.749 | 0.010554 | 0.48581 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.23811 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
759.2 | 127.749 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
759.4 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
759.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0019147
759.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.006713
760 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
760.2 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
760.4 | 127.8449 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
760.6 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
760.8 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
761 | 127.653 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
761.2 | 127.749 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
761.4 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.012867 | 0.28424 | 0.006713
761.6 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
761.8 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0086004 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
762 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
762.2 | 127.653 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.28424 | 0.006713
762.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
762.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
762.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
763 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
763.2 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
763.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.28424 | 0.0018926 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
763.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
763.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
764 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0083128
764.2 | 127.8449 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
764.4 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0017265 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
764.6 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
764.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.33406 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | -0.099642 | 0.006713
765 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
765.2 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
765.4 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.011268 | 0.18829 | 0.006713
765.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
765.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
766 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.10127 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
766.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
766.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
766.6 | 127.9409 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
766.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
767 | 127.8449 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
767.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0002934 | 0.38986 | 0.00647 | 0.28424 | 0.006713
767.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
767.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.5811 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
767.8 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.23811 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
768 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
768.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
768.4 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
768.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
768.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
769 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
769.2 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
769.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0002934 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
769.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
769.8 | 127.9409 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
770 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.67775 | 0.00647 | 0.18829 | 0.006713
770.2 | 128.1329 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.28424 | 0.006713
770.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
770.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
770.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
771 | 127.9409 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
771.2 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.006713
771.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
771.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
771.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
772 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
772.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
772.4 | 127.9409 | 0.0073551 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
772.6 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
772.8 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
773 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.18729 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
773.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0016158 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
773.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0080139 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
773.6 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
773.8 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
774 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.76408 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
774.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
774.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
774.6 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0019147
774.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
775 | 127.8449 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
775.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0019147
775.4 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
775.6 | 127.9409 | 0.0089549 | 0.38986 | 0.0031824 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
775.8 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
776 | 127.9409 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
776.2 | 127.9409 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
776.4 | 127.9409 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0035139
776.6 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
776.8 | 127.8449 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
777 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.009669 | -0.0036512 | 0.006713
777.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0035139
777.4 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
777.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
777.8 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.19792 | 0.0048701 | 0.18829 | 0.006713
778 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
778.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.0083128
778.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
778.6 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
778.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.012867 | 0.18829 | 0.0051138
779 | 127.8449 | 0.0089549 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
779.2 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.009912
779.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
779.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
779.8 | 127.8449 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
780 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
780.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
780.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
780.6 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.003271 | 0.28424 | 0.006713
780.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
781 | 127.8449 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
781.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
781.4 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
781.6 | 127.9409 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
781.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
782 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
782.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
782.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0002934 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
782.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
782.8 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0022023 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.011268 | 0.28424 | 0.006713
783 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0019147
783.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0086004 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.0083128
783.4 | 127.9409 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.0051138
783.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
783.8 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
784 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
784.2 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
784.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
784.6 | 127.9409 | 0.0089549 | 0.58176 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
784.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
785 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
785.2 | 127.9409 | 0.0073551 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | -0.0036512 | 0.006713
785.4 | 127.9409 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0035139
785.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.0083128
785.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
786 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
786.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
786.4 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
786.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
786.8 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
787 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
787.2 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.47618 | 0.006713
787.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
787.6 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
787.8 | 127.9409 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
788 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
788.2 | 127.9409 | 0.020151 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0082906 | 0.29387 | 0.00647 | 0.18829 | 0.006713
788.4 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.38986 | 0.00647 | 0.0923 | 0.0051138
788.6 | 127.557 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
788.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.006713
789 | 127.9409 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
789.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
789.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.0051138
789.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0016158 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
789.8 | 127.9409 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
790 | 128.0369 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.19792 | 0.00647 | 0.18829 | 0.006713
790.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
790.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
790.6 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
790.8 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
791 | 127.9409 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
791.2 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
791.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
791.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
791.8 | 127.557 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.00647 | 0.18829 | 0.006713
792 | 126.6933 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.011268 | 0.28424 | 0.006713
792.2 | 127.2692 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.00012733 | 0.38019 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
792.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.011268 | 0.18829 | 0.0051138
792.6 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
792.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
793 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
793.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
793.4 | 128.1329 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
793.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
793.8 | 128.0369 | 0.010554 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
794 | 128.0369 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
794.2 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
794.4 | 128.0369 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
794.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
794.8 | 128.0369 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
795 | 128.0369 | 0.010554 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
795.2 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
795.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
795.6 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
795.8 | 128.0369 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
796 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
796.2 | 128.1329 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
796.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
796.6 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
796.8 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
797 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0002934 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
797.2 | 128.0369 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
797.4 | 127.9409 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
797.6 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
797.8 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
798 | 128.0369 | 0.0073551 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
798.2 | 128.0369 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
798.4 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
798.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
798.8 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
799 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
799.2 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
799.4 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
799.6 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
799.8 | 127.9409 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
800 | 128.0369 | 0.013753 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
800.2 | 128.1329 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
800.4 | 128.0369 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
800.6 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.8139 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
800.8 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
801 | 128.2288 | 0.02335 | 0.38986 | 0.0047816 | 0.29321 | 0.0016158 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
801.2 | 127.8449 | 0.020151 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
801.4 | 127.749 | 0.028148 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.29387 | 0.0080692 | 0.28424 | 0.0083128
801.6 | 128.3248 | 0.045742 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
801.8 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.014522 | 0.57213 | 0.0098898 | 0.48581 | 0.011268 | 0.28424 | 0.006713
802 | 127.3651 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0081246 | 0.66813 | 0.014688 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
802.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
802.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.011324 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.006713
802.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.01149 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
802.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | -0.0057949 | 0.526 | 0.0049255 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
803 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
803.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
803.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
803.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
803.8 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
804 | 127.9409 | 0.0089549 | 0.38986 | 0.0079807 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
804.2 | 127.9409 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
804.4 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.006713
804.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
804.8 | 127.9409 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
805 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
805.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.006713
805.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
805.6 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
805.8 | 127.9409 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
806 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.0083128
806.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
806.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
806.6 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
806.8 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
807 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.18829 | 0.006713
807.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
807.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
807.6 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
807.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
808 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
808.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
808.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
808.6 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
808.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
809 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
809.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.33406 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
809.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
809.6 | 127.8449 | 0.010554 | 0.38986 | 0.0031824 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
809.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
810 | 127.9409 | 0.0089549 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
810.2 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
810.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
810.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
810.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
811 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
811.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
811.4 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
811.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
811.8 | 128.0369 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
812 | 127.749 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
812.2 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.009613 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
812.4 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.0923 | 0.006713
812.6 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
812.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0017265 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
813 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
813.2 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.28424 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
813.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
813.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
813.8 | 127.8449 | 0.0089549 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
814 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
814.2 | 127.8449 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.012867 | 0.28424 | 0.0083128
814.4 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
814.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
814.8 | 127.749 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
815 | 127.749 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
815.2 | 127.749 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
815.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.009613 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.0083128
815.6 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
815.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.28424 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
816 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
816.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
816.4 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
816.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
816.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
817 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
817.2 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
817.4 | 127.749 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.0051138
817.6 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
817.8 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
818 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
818.2 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
818.4 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.00647 | 0.28424 | 0.006713
818.6 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
818.8 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.006713
819 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.28424 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
819.2 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
819.4 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0048701 | 0.0923 | 0.006713
819.6 | 127.9409 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
819.8 | 127.749 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
820 | 127.749 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
820.2 | 127.749 | 0.010554 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
820.4 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
820.6 | 127.8449 | 0.013753 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
820.8 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
821 | 127.653 | 0.018551 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
821.2 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
821.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
821.6 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.33406 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0035139
821.8 | 127.653 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.67775 | 0.009669 | 0.28424 | 0.006713
822 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
822.2 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
822.4 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
822.6 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
822.8 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
823 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
823.2 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
823.4 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
823.6 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
823.8 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.009613 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
824 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
824.2 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
824.4 | 127.749 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0081246 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0083128
824.6 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
824.8 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0016158 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
825 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0035139
825.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
825.4 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
825.6 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.0923 | 0.006713
825.8 | 127.8449 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
826 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.0083128
826.2 | 127.8449 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
826.4 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
826.6 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
826.8 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
827 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
827.2 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
827.4 | 127.8449 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.006713
827.6 | 127.8449 | 0.015352 | 0.48581 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
827.8 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
828 | 127.9409 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 1.6612e-05 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
828.2 | 127.9409 | 0.015352 | 0.10193 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
828.4 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
828.6 | 127.9409 | 0.013753 | 0.19792 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.8139 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
828.8 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.19722 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
829 | 127.9409 | 0.016952 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
829.2 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
829.4 | 127.9409 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
829.6 | 127.9409 | 0.015352 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.23811 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
829.8 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
830 | 127.9409 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
830.2 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | -0.0036512 | 0.006713
830.4 | 128.0369 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
830.6 | 128.0369 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
830.8 | 128.0369 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
831 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
831.2 | 128.0369 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
831.4 | 128.0369 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
831.6 | 127.9409 | 0.018551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
831.8 | 127.9409 | 0.037745 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.38019 | 0.0083128
832 | 127.9409 | 0.015352 | 1.3495 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
832.2 | 128.0369 | 0.016952 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.37923 | 0.0102 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
832.4 | 128.0369 | 0.016952 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 1.0616 | 0.0080692 | 0.28424 | 0.0051138
832.6 | 128.0369 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
832.8 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
833 | 128.1329 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
833.2 | 128.1329 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0097238 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
833.4 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
833.6 | 128.0369 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
833.8 | 128.0369 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
834 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0083128
834.2 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
834.4 | 128.2288 | 0.015352 | 0.10193 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
834.6 | 128.6127 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
834.8 | 129.5724 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
835 | 128.8046 | 0.018551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
835.2 | 128.4208 | 0.015352 | 0.29387 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
835.4 | 128.3248 | 0.015352 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
835.6 | 128.3248 | 0.016952 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
835.8 | 128.2288 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
836 | 128.1329 | 0.016952 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
836.2 | 128.1329 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
836.4 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
836.6 | 128.1329 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
836.8 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.23811 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
837 | 128.1329 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
837.2 | 128.1329 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
837.4 | 128.1329 | 0.018551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.38019 | 0.006713
837.6 | 128.1329 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
837.8 | 128.1329 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
838 | 128.1329 | 0.016952 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
838.2 | 128.1329 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
838.4 | 128.1329 | 0.015352 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
838.6 | 128.1329 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
838.8 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
839 | 128.1329 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
839.2 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
839.4 | 128.1329 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
839.6 | 128.0369 | 0.013753 | 0.38986 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
839.8 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
840 | 128.0369 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.006713
840.2 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.0923 | 0.006713
840.4 | 127.9409 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.011268 | 0.18829 | 0.006713
840.6 | 127.9409 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
840.8 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
841 | 127.9409 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.0051138
841.2 | 128.0369 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
841.4 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
841.6 | 128.0369 | 0.016952 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
841.8 | 127.749 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
842 | 128.0369 | 0.024949 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | -0.0036512 | 0.0051138
842.2 | 127.557 | 0.02175 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.011324 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
842.4 | 128.4208 | 0.055339 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.014522 | 0.66813 | 0.01149 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
842.6 | 128.0369 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
842.8 | 128.0369 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
843 | 127.9409 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.017887 | 0.48581 | 0.00647 | 0.0923 | 0.009912
843.2 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
843.4 | 127.9409 | 0.015352 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
843.6 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
843.8 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
844 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.0051138
844.2 | 127.9409 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
844.4 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
844.6 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
844.8 | 127.9409 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
845 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0048701 | 0.18829 | 0.0051138
845.2 | 127.9409 | 0.013753 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
845.4 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
845.6 | 127.8449 | 0.013753 | 0.19792 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
845.8 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
846 | 127.8449 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
846.2 | 127.9409 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
846.4 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
846.6 | 127.8449 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
846.8 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
847 | 127.749 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
847.2 | 127.8449 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.0083128
847.4 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
847.6 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
847.8 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.19792 | 0.00647 | 0.18829 | 0.006713
848 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
848.2 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.19722 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
848.4 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
848.6 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
848.8 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
849 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
849.2 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.00060315 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
849.4 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
849.6 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
849.8 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
850 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
850.2 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
850.4 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0019147
850.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
850.8 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
851 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
851.2 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
851.4 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0097238 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
851.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
851.8 | 127.8449 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
852 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
852.2 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
852.4 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
852.6 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
852.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
853 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
853.2 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
853.4 | 127.749 | 0.012154 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
853.6 | 127.8449 | 0.012154 | 0.38986 | 0.0015826 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
853.8 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
854 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | -0.099642 | 0.006713
854.2 | 127.653 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
854.4 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
854.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
854.8 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.011268 | 0.28424 | 0.006713
855 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
855.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
855.4 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
855.6 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
855.8 | 127.749 | 0.010554 | 0.38986 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.0051138
856 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
856.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
856.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0097238 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
856.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.28424 | 0.0051138
856.8 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
857 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
857.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.8139 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | -0.0036512 | 0.006713
857.4 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.28424 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
857.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
857.8 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
858 | 127.749 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
858.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
858.4 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
858.6 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
858.8 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
859 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
859.2 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
859.4 | 127.749 | 0.0089549 | 0.38986 | 0.0079807 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
859.6 | 127.557 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
859.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
860 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
860.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
860.4 | 127.749 | 0.0089549 | 0.29387 | 0.0079807 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.00012733 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
860.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
860.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
861 | 127.749 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
861.2 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
861.4 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
861.6 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.28324 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
861.8 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
862 | 127.749 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.47618 | 0.0083128
862.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
862.4 | 127.749 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.009912
862.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
862.8 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
863 | 127.8449 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
863.2 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.006713
863.4 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
863.6 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.5811 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
863.8 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
864 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
864.2 | 127.653 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.38019 | 0.0051138
864.4 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
864.6 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.18729 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
864.8 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
865 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
865.2 | 127.749 | 0.010554 | 0.38986 | 0.0079807 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
865.4 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
865.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
865.8 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.86003 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
866 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
866.2 | 127.653 | 0.0089549 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
866.4 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.67775 | 0.009669 | 0.28424 | 0.006713
866.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
866.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
867 | 127.8449 | 0.0089549 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
867.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
867.4 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
867.6 | 127.749 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
867.8 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
868 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
868.2 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
868.4 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.28424 | 0.006713
868.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
868.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
869 | 127.749 | 0.0073551 | 0.19792 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0035139
869.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
869.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
869.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
869.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
870 | 127.653 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
870.2 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.006713
870.4 | 127.749 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
870.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
870.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
871 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
871.2 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
871.4 | 127.749 | 0.010554 | 0.29387 | 0.0063808 | 0.19722 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
871.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
871.8 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0016158 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
872 | 127.8449 | 0.0057559 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
872.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
872.4 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
872.6 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
872.8 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
873 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
873.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
873.4 | 127.749 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
873.6 | 127.4611 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.006713
873.8 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
874 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
874.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
874.4 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
874.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
874.8 | 127.749 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
875 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.19792 | 0.0080692 | 0.18829 | 0.006713
875.2 | 127.8449 | 0.0089549 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | -0.0036512 | 0.0051138
875.4 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
875.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.0923 | 0.006713
875.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
876 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
876.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
876.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.009912
876.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
876.8 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
877 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0019147
877.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
877.4 | 127.8449 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0017265 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
877.6 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
877.8 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
878 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
878.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
878.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0016158 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
878.6 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
878.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
879 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
879.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
879.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
879.6 | 127.9409 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
879.8 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
880 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.011268 | 0.0923 | 0.006713
880.2 | 128.3248 | 0.028148 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.011511
880.4 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.38019 | 0.006713
880.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0097238 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
880.8 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0081246 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
881 | 127.9409 | 0.0073551 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
881.2 | 127.9409 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0035139
881.4 | 128.1329 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
881.6 | 128.1329 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
881.8 | 128.1329 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.011268 | 0.18829 | 0.006713
882 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.00647 | 0.18829 | 0.006713
882.2 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
882.4 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0016158 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0082906 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
882.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
882.8 | 127.4611 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.0923 | 0.006713
883 | 126.6933 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
883.2 | 127.653 | 0.0089549 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0097238 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
883.4 | 127.8449 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
883.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.0923 | 0.006713
883.8 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
884 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
884.2 | 128.0369 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
884.4 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.18829 | 0.0018926 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
884.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0015826 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
884.8 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0035139
885 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.00647 | 0.18829 | 0.006713
885.2 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
885.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
885.6 | 128.0369 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
885.8 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
886 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.011268 | 0.18829 | 0.006713
886.2 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
886.4 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
886.6 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
886.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
887 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
887.2 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
887.4 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
887.6 | 128.0369 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
887.8 | 128.0369 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0038022 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.29387 | 0.0080692 | 0.28424 | 0.0083128
888 | 128.1329 | 0.037745 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
888.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0097238 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
888.4 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
888.6 | 127.8449 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
888.8 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.47618 | 0.0083128
889 | 127.8449 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.0083128
889.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
889.4 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
889.6 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
889.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
890 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
890.2 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
890.4 | 127.749 | 0.0089549 | 0.29387 | 0.0095798 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0017265 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
890.6 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
890.8 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.006713
891 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
891.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
891.4 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.003271 | 0.18829 | 0.006713
891.6 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
891.8 | 127.749 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
892 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
892.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
892.4 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.66713 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.67775 | 0.009669 | 0.18829 | 0.0083128
892.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
892.8 | 127.653 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
893 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
893.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
893.4 | 127.653 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0035139
893.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
893.8 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
894 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
894.2 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
894.4 | 127.8449 | 0.020151 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
894.6 | 127.2692 | 0.012154 | 0.38986 | 0.0031824 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
894.8 | 127.653 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0038022 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.38019 | 0.006713
895 | 127.653 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0017265 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
895.2 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
895.4 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | -0.0036512 | 0.006713
895.6 | 127.749 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
895.8 | 127.749 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
896 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.19792 | 0.0080692 | 0.18829 | 0.006713
896.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0035139
896.4 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
896.6 | 127.749 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
896.8 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
897 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
897.2 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
897.4 | 127.749 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
897.6 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
897.8 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.28424 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
898 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
898.2 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
898.4 | 127.8449 | 0.015352 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
898.6 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0070012 | 0.23811 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
898.8 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.38019 | 0.0018926 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
899 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.0923 | 0.006713
899.2 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
899.4 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
899.6 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
899.8 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
900 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
900.2 | 127.9409 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
900.4 | 127.9409 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
900.6 | 128.0369 | 0.020151 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
900.8 | 127.653 | 0.02175 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
901 | 128.2288 | 0.034546 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
901.2 | 128.0369 | 0.016952 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0102 | 0.43001 | 0.0097238 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
901.4 | 128.0369 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
901.6 | 128.0369 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
901.8 | 128.1329 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
902 | 128.0369 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
902.2 | 128.1329 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.006713
902.4 | 128.0369 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
902.6 | 128.0369 | 0.015352 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
902.8 | 128.0369 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
903 | 128.2288 | 0.018551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0048701 | 0.0923 | 0.006713
903.2 | 128.8046 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
903.4 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
903.6 | 128.4208 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
903.8 | 128.2288 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
904 | 128.2288 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
904.2 | 128.0369 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
904.4 | 128.1329 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
904.6 | 128.1329 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
904.8 | 128.1329 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0018926 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
905 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
905.2 | 128.1329 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
905.4 | 128.0369 | 0.016952 | 0.19792 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
905.6 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
905.8 | 128.1329 | 0.016952 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
906 | 128.0369 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
906.2 | 128.1329 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
906.4 | 128.0369 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
906.6 | 128.0369 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
906.8 | 128.0369 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
907 | 128.0369 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
907.2 | 128.0369 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
907.4 | 128.0369 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
907.6 | 127.9409 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
907.8 | 127.9409 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
908 | 128.0369 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
908.2 | 127.9409 | 0.015352 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
908.4 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
908.6 | 128.0369 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
908.8 | 127.9409 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
909 | 127.9409 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
909.2 | 127.9409 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
909.4 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
909.6 | 128.0369 | 0.024949 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
909.8 | 127.9409 | 0.036146 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
910 | 128.3248 | 0.053739 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.016122 | 0.66813 | 0.01149 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
910.2 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
910.4 | 127.9409 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.0051138
910.6 | 127.9409 | 0.016952 | 0.38986 | 0.0031824 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
910.8 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
911 | 128.0369 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
911.2 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
911.4 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
911.6 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
911.8 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
912 | 127.9409 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
912.2 | 127.8449 | 0.013753 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0051138
912.4 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
912.6 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
912.8 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.00647 | 0.28424 | 0.006713
913 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
913.2 | 127.749 | 0.012154 | 0.29387 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
913.4 | 127.749 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
913.6 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
913.8 | 127.8449 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
914 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
914.2 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
914.4 | 127.749 | 0.013753 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
914.6 | 127.749 | 0.013753 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
914.8 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
915 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.28424 | 0.006713
915.2 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
915.4 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
915.6 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
915.8 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
916 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
916.2 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
916.4 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
916.6 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
916.8 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
917 | 127.653 | 0.015352 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0048701 | 0.0923 | 0.0051138
917.2 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.57213 | 0.0051138
917.4 | 127.653 | 0.012154 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
917.6 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.012867 | 0.18829 | 0.006713
917.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
918 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
918.2 | 127.557 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
918.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.7737 | 0.0080692 | 0.18829 | 0.0083128
918.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
918.8 | 127.653 | 0.010554 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
919 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
919.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
919.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
919.6 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.18729 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
919.8 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0048701 | 0.28424 | 0.0083128
920 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
920.2 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
920.4 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
920.6 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
920.8 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
921 | 127.653 | 0.012154 | 0.10193 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
921.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.011268 | 0.28424 | 0.0051138
921.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
921.6 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
921.8 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
922 | 127.653 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
922.2 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
922.4 | 127.653 | 0.0089549 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
922.6 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
922.8 | 127.653 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.8139 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.38019 | 0.006713
923 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
923.2 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
923.4 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
923.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
923.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
924 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
924.2 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
924.4 | 127.749 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
924.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
924.8 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
925 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
925.2 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
925.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
925.6 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
925.8 | 127.749 | 0.0089549 | 0.10193 | 0.0031824 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
926 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
926.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
926.4 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
926.6 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.67775 | 0.00647 | 0.18829 | 0.006713
926.8 | 128.0369 | 0.0073551 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
927 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
927.2 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
927.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
927.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.0083128
927.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
928 | 127.8449 | 0.010554 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
928.2 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
928.4 | 127.9409 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
928.6 | 127.9409 | 0.02335 | 0.29387 | 0.0047816 | 0.19722 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
928.8 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
929 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0097238 | 0.47618 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
929.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.0923 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
929.4 | 127.9409 | 0.010554 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
929.6 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
929.8 | 128.0369 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
930 | 127.9409 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.33406 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0051138
930.2 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
930.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
930.6 | 128.0369 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
930.8 | 127.3651 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
931 | 126.8853 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
931.2 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0035139
931.4 | 127.749 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
931.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
931.8 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.29387 | 0.0080692 | 0.18829 | 0.0051138
932 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
932.2 | 127.9409 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
932.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
932.6 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
932.8 | 128.0369 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
933 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
933.2 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
933.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.0923 | 0.006713
933.6 | 128.0369 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
933.8 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
934 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
934.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
934.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.5811 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
934.6 | 127.9409 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
934.8 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
935 | 127.557 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
935.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
935.4 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
935.6 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
935.8 | 127.9409 | 0.024949 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
936 | 127.749 | 0.034546 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.006713
936.2 | 127.8449 | 0.010554 | 0.38986 | 0.0079807 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
936.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
936.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.01149 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
936.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
937 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
937.2 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
937.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
937.6 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
937.8 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
938 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
938.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
938.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
938.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
938.8 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
939 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0016158 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
939.2 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
939.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
939.6 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0018926 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
939.8 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
940 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
940.2 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.006713
940.4 | 127.653 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
940.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
940.8 | 127.653 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.23811 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
941 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.38019 | 0.0083128
941.2 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.0923 | 0.0083128
941.4 | 127.653 | 0.010554 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
941.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
941.8 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
942 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
942.2 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
942.4 | 127.653 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
942.6 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
942.8 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
943 | 127.557 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
943.2 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
943.4 | 127.653 | 0.0057559 | 0.29387 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.0051138
943.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.011511
943.8 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
944 | 127.557 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
944.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
944.4 | 127.653 | 0.012154 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
944.6 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
944.8 | 127.557 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
945 | 127.557 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
945.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
945.4 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
945.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
945.8 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.47618 | 0.006713
946 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
946.2 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
946.4 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
946.6 | 127.4611 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
946.8 | 127.557 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
947 | 127.749 | 0.024949 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
947.2 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.38019 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
947.4 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0048701 | 0.28424 | 0.0083128
947.6 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0016158 | 0.37923 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
947.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
948 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
948.2 | 127.4611 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.19792 | 0.0080692 | 0.28424 | 0.006713
948.4 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
948.6 | 127.557 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
948.8 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0102 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
949 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
949.2 | 127.557 | 0.012154 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
949.4 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
949.6 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
949.8 | 127.653 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0019147
950 | 127.557 | 0.012154 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
950.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
950.4 | 127.653 | 0.012154 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
950.6 | 127.653 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
950.8 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.006713
951 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
951.2 | 127.653 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
951.4 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
951.6 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
951.8 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
952 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
952.2 | 127.557 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
952.4 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
952.6 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
952.8 | 127.653 | 0.013753 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
953 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
953.2 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
953.4 | 127.653 | 0.015352 | 0.38986 | 0.0031824 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
953.6 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
953.8 | 127.653 | 0.015352 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
954 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
954.2 | 127.557 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
954.4 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
954.6 | 127.653 | 0.015352 | 0.29387 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
954.8 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
955 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
955.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.009669 | 0.18829 | 0.006713
955.4 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
955.6 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
955.8 | 127.749 | 0.013753 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
956 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
956.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.00012733 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
956.4 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
956.6 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
956.8 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.011268 | 0.28424 | 0.006713
957 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
957.2 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
957.4 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.0923 | 0.006713
957.6 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
957.8 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
958 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
958.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
958.4 | 127.749 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.47618 | 0.006713
958.6 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
958.8 | 127.653 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
959 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.00012733 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
959.2 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
959.4 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
959.6 | 127.749 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
959.8 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
960 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
960.2 | 127.749 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
960.4 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
960.6 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
960.8 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.0083128
961 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.006713
961.2 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
961.4 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.47618 | 0.009912
961.6 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
961.8 | 127.749 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
962 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
962.2 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
962.4 | 127.9409 | 0.020151 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
962.6 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
962.8 | 127.4611 | 0.024949 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
963 | 127.8449 | 0.037745 | 0.38986 | 0.0047816 | 0.5811 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
963.2 | 127.557 | 0.028148 | 0.19792 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.47618 | 0.0098898 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
963.4 | 127.8449 | 0.016952 | 0.38986 | -0.0096137 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
963.6 | 127.8449 | 0.020151 | 0.38986 | 0.0047816 | 0.29321 | 0.0080139 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.0923 | 0.0083128
963.8 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0097238 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
964 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
964.2 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
964.4 | 127.8449 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.86003 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
964.6 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
964.8 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
965 | 127.8449 | 0.018551 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
965.2 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
965.4 | 127.8449 | 0.016952 | 0.19792 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
965.6 | 127.8449 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
965.8 | 127.749 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
966 | 127.8449 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
966.2 | 127.749 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
966.4 | 127.8449 | 0.016952 | 0.10193 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
966.6 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.76308 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
966.8 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
967 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
967.2 | 128.2288 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
967.4 | 128.5167 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
967.6 | 129.2844 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
967.8 | 128.8046 | 0.018551 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
968 | 128.3248 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
968.2 | 128.2288 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
968.4 | 128.1329 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
968.6 | 128.0369 | 0.016952 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
968.8 | 128.0369 | 0.016952 | 0.38986 | 0.0079807 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
969 | 127.9409 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
969.2 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
969.4 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
969.6 | 127.9409 | 0.015352 | 0.58176 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
969.8 | 127.9409 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
970 | 127.8449 | 0.015352 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
970.2 | 127.9409 | 0.016952 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
970.4 | 127.9409 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
970.6 | 128.0369 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
970.8 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.57213 | 0.0083128
971 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
971.2 | 127.9409 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
971.4 | 127.8449 | 0.016952 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
971.6 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
971.8 | 127.9409 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
972 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0048701 | 0.28424 | 0.0083128
972.2 | 128.0369 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
972.4 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
972.6 | 127.8449 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
972.8 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
973 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
973.2 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
973.4 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
973.6 | 127.8449 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
973.8 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
974 | 127.8449 | 0.018551 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
974.2 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
974.4 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0086004 | 0.33406 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
974.6 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
974.8 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
975 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
975.2 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
975.4 | 127.8449 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
975.6 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
975.8 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
976 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
976.2 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
976.4 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
976.6 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
976.8 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.009669 | 0.28424 | 0.006713
977 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
977.2 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
977.4 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
977.6 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
977.8 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.0923 | 0.006713
978 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
978.2 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
978.4 | 127.749 | 0.015352 | 0.19792 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
978.6 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
978.8 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
979 | 127.8449 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
979.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
979.4 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
979.6 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.006713
979.8 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
980 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
980.2 | 127.8449 | 0.015352 | 0.38986 | 0.0063808 | 0.19722 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
980.4 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
980.6 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
980.8 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
981 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
981.2 | 127.749 | 0.016952 | 0.38986 | 0.0015826 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
981.4 | 127.653 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
981.6 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
981.8 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
982 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
982.2 | 127.653 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
982.4 | 127.749 | 0.015352 | 0.38986 | 0.0079807 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
982.6 | 127.8449 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
982.8 | 127.557 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
983 | 127.557 | 0.020151 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
983.2 | 127.8449 | 0.024949 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.006713
983.4 | 127.8449 | 0.02335 | 0.29387 | 0.0047816 | 0.48515 | 0.009613 | 0.57118 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
983.6 | 127.3651 | 0.02335 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
983.8 | 127.749 | 0.044143 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
984 | 128.0369 | 0.045742 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.011324 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
984.2 | 128.3248 | 0.055339 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.014522 | 0.66813 | 0.0098898 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
984.4 | 127.9409 | 0.018551 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.33406 | 0.011324 | 0.66813 | 0.013089 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
984.6 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.014688 | 0.48581 | 0.00647 | 0.18829 | 0.006713
984.8 | 127.749 | 0.015352 | 0.38986 | 0.012779 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0098898 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
985 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.014411 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0082906 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
985.2 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
985.4 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
985.6 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
985.8 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.7737 | 0.0080692 | 0.18829 | 0.006713
986 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
986.2 | 127.749 | 0.015352 | 0.19792 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
986.4 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
986.6 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
986.8 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
987 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
987.2 | 127.653 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
987.4 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
987.6 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
987.8 | 127.749 | 0.013753 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
988 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
988.2 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
988.4 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
988.6 | 127.749 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
988.8 | 127.749 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0051138
989 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
989.2 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
989.4 | 127.749 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
989.6 | 127.653 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
989.8 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
990 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.0923 | 0.0051138
990.2 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
990.4 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.0923 | 0.006713
990.6 | 127.557 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
990.8 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
991 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
991.2 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
991.4 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
991.6 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
991.8 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
992 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
992.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.5811 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
992.4 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
992.6 | 127.4611 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.28424 | 0.0051138
992.8 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
993 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
993.2 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
993.4 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
993.6 | 127.653 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.23811 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
993.8 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
994 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0051138
994.2 | 127.557 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
994.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
994.6 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
994.8 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
995 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.0083128
995.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
995.4 | 127.557 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.0923 | 0.006713
995.6 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
995.8 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
996 | 127.653 | 0.012154 | 0.38986 | 0.0015826 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
996.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
996.4 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
996.6 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
996.8 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
997 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
997.2 | 127.557 | 0.012154 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
997.4 | 127.557 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
997.6 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
997.8 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.7737 | 0.009669 | 0.18829 | 0.006713
998 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.0923 | 0.0083128
998.2 | 127.557 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.28424 | 0.006713
998.4 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
998.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
998.8 | 127.557 | 0.0089549 | 0.38986 | 0.0095798 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
999 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | -0.0036512 | 0.0083128
999.2 | 127.557 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.33406 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
999.4 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
999.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
999.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1000 | 127.557 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1000.2 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
1000.4 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | -0.0036512 | 0.0051138
1000.6 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1000.8 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1001 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1001.2 | 127.557 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1001.4 | 127.4611 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1001.6 | 127.4611 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.012867 | 0.18829 | 0.006713
1001.8 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1002 | 127.4611 | 0.010554 | 0.10193 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1002.2 | 127.557 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1002.4 | 127.557 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1002.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.00647 | 0.18829 | 0.006713
1002.8 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.009669 | 0.28424 | 0.006713
1003 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
1003.2 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1003.4 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1003.6 | 127.4611 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1003.8 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1004 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1004.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1004.4 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.00647 | 0.28424 | 0.006713
1004.6 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1004.8 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1005 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
1005.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1005.4 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1005.6 | 127.557 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1005.8 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1006 | 127.557 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1006.2 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1006.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
1006.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0048701 | 0.28424 | 0.0083128
1006.8 | 127.653 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1007 | 127.557 | 0.0057559 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.0923 | 0.0083128
1007.2 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1007.4 | 127.557 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.006713
1007.6 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1007.8 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1008 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0098898 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1008.2 | 127.653 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1008.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1008.6 | 127.557 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1008.8 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1009 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1009.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1009.4 | 127.653 | 0.010554 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1009.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.009613 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1009.8 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.012867 | 0.18829 | 0.006713
1010 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1010.2 | 127.749 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1010.4 | 128.1329 | 0.028148 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1010.6 | 127.2692 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1010.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.28424 | 0.009912
1011 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0054014 | -0.33772 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
1011.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0048701 | 0.28424 | 0.006713
1011.4 | 127.8449 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1011.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1011.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1012 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.00647 | 0.18829 | 0.006713
1012.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.009912
1012.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.0923 | 0.0083128
1012.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1012.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.006713
1013 | 127.557 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1013.2 | 126.6933 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1013.4 | 126.9813 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1013.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1013.8 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.19722 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1014 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1014.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1014.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1014.6 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1014.8 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1015 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1015.2 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1015.4 | 127.749 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
1015.6 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1015.8 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1016 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1016.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1016.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1016.6 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1016.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1017 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1017.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1017.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
1017.6 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1017.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1018 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1018.2 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1018.4 | 127.9409 | 0.02335 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1018.6 | 128.4208 | 0.044143 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1018.8 | 127.0772 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.014688 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1019 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1019.2 | 127.749 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1019.4 | 127.653 | 0.010554 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1019.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1019.8 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1020 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1020.2 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1020.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1020.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0080139 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1020.8 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1021 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1021.2 | 127.557 | 0.0089549 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1021.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1021.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1021.8 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1022 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1022.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1022.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1022.6 | 127.557 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.0923 | 0.0083128
1022.8 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1023 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1023.2 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1023.4 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1023.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1023.8 | 127.3651 | 0.010554 | 0.48581 | 0.0047816 | 0.5811 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1024 | 127.557 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1024.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1024.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1024.6 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0017265 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1024.8 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1025 | 127.557 | 0.012154 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1025.2 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.011511
1025.4 | 127.557 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.0923 | 0.006713
1025.6 | 127.3651 | 0.013753 | 0.38986 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1025.8 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.19722 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1026 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1026.2 | 127.3651 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1026.4 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1026.6 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1026.8 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1027 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1027.2 | 127.4611 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1027.4 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1027.6 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1027.8 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1028 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0016158 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.0083128
1028.2 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1028.4 | 127.557 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1028.6 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.0923 | 0.006713
1028.8 | 127.557 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1029 | 127.557 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1029.2 | 127.4611 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1029.4 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0022023 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1029.6 | 127.557 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1029.8 | 127.557 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1030 | 127.557 | 0.015352 | 0.48581 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1030.2 | 127.557 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1030.4 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1030.6 | 127.557 | 0.015352 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1030.8 | 127.653 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1031 | 127.557 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.00647 | 0.18829 | 0.006713
1031.2 | 127.653 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1031.4 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1031.6 | 127.653 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1031.8 | 127.557 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1032 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1032.2 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1032.4 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.10127 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1032.6 | 127.653 | 0.013753 | 0.29387 | 0.0015826 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1032.8 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0048701 | 0.18829 | 0.0051138
1033 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.38019 | 0.0034924 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1033.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1033.4 | 127.653 | 0.012154 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.0923 | 0.0083128
1033.6 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1033.8 | 127.749 | 0.015352 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1034 | 127.653 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1034.2 | 127.749 | 0.036146 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1034.4 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1034.6 | 127.653 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1034.8 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1035 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1035.2 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1035.4 | 127.749 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1035.6 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1035.8 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1036 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1036.2 | 127.9409 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1036.4 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1036.6 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1036.8 | 128.0369 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1037 | 128.9006 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1037.2 | 128.5167 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1037.4 | 128.1329 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0022023 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1037.6 | 128.0369 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.0083128
1037.8 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1038 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1038.2 | 127.8449 | 0.015352 | 0.19792 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1038.4 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1038.6 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1038.8 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1039 | 127.9409 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1039.2 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1039.4 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1039.6 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1039.8 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1040 | 127.8449 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1040.2 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.0083128
1040.4 | 127.8449 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1040.6 | 127.8449 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1040.8 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1041 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1041.2 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1041.4 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1041.6 | 127.8449 | 0.015352 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1041.8 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
1042 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1042.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1042.4 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1042.6 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1042.8 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1043 | 127.8449 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.00647 | 0.18829 | 0.006713
1043.2 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1043.4 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0002934 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1043.6 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
1043.8 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1044 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1044.2 | 127.4611 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1044.4 | 127.4611 | 0.02175 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1044.6 | 127.9409 | 0.039345 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0097238 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1044.8 | 128.3248 | 0.040944 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.017721 | 0.66813 | 0.013089 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1045 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.43001 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1045.2 | 127.653 | 0.018551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | -0.014102 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1045.4 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1045.6 | 127.653 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1045.8 | 127.653 | 0.016952 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1046 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1046.2 | 127.653 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1046.4 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1046.6 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1046.8 | 127.557 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1047 | 127.653 | 0.013753 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1047.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1047.4 | 127.557 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1047.6 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1047.8 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
1048 | 127.557 | 0.012154 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1048.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1048.4 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
1048.6 | 127.557 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1048.8 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1049 | 127.4611 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1049.2 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1049.4 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.009669 | 0.18829 | 0.006713
1049.6 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1049.8 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1050 | 127.557 | 0.012154 | 0.38986 | 0.0015826 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1050.2 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1050.4 | 127.557 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1050.6 | 127.4611 | 0.012154 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1050.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0048701 | 0.18829 | 0.006713
1051 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1051.2 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
1051.4 | 127.4611 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1051.6 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1051.8 | 127.4611 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1052 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1052.2 | 127.4611 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0022023 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1052.4 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1052.6 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1052.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.7737 | 0.0080692 | 0.18829 | 0.006713
1053 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1053.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1053.4 | 127.4611 | 0.0089549 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1053.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1053.8 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1054 | 127.2692 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1054.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.5811 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1054.4 | 127.4611 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.43001 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1054.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.00647 | 0.18829 | 0.006713
1054.8 | 127.4611 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1055 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.009613 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1055.2 | 127.4611 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1055.4 | 127.4611 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1055.6 | 127.4611 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1055.8 | 127.2692 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1056 | 127.3651 | 0.0057559 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | -0.0036512 | 0.0051138
1056.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1056.4 | 127.3651 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1056.6 | 127.3651 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1056.8 | 127.4611 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0035139
1057 | 127.3651 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.28424 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1057.2 | 127.2692 | 0.013753 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.8139 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1057.4 | 127.3651 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.28324 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1057.6 | 127.2692 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1057.8 | 127.3651 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1058 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1058.2 | 127.3651 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
1058.4 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.28424 | 0.006713
1058.6 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1058.8 | 127.4611 | 0.0089549 | 0.29387 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
1059 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0051138
1059.2 | 127.4611 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1059.4 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1059.6 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1059.8 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.0083128
1060 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1060.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1060.4 | 127.4611 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1060.6 | 127.2692 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1060.8 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0018926 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1061 | 127.4611 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1061.2 | 127.4611 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1061.4 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1061.6 | 127.4611 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1061.8 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1062 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1062.2 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1062.4 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1062.6 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.00647 | 0.28424 | 0.0083128
1062.8 | 127.557 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1063 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.006713
1063.2 | 127.3651 | 0.0089549 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1063.4 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1063.6 | 127.4611 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1063.8 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1064 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.006713
1064.2 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.0083128
1064.4 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1064.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1064.8 | 127.3651 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1065 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1065.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1065.4 | 127.557 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0048701 | 0.38019 | 0.006713
1065.6 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1065.8 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1066 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1066.2 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1066.4 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0019147
1066.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1066.8 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0034924 | 0.29387 | 0.009669 | 0.28424 | 0.006713
1067 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1067.2 | 127.9409 | 0.028148 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1067.4 | 127.2692 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1067.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | -0.29254 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1067.8 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1068 | 127.749 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
1068.2 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.18829 | 0.006713
1068.4 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1068.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.00647 | 0.18829 | 0.006713
1068.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0048701 | 0.18829 | 0.0083128
1069 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1069.2 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.28424 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1069.4 | 127.1732 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1069.6 | 126.6933 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1069.8 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1070 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.00647 | 0.18829 | 0.006713
1070.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1070.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.0083128
1070.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.011268 | 0.0923 | 0.006713
1070.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1071 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1071.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.19722 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1071.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1071.6 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1071.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0051138
1072 | 127.749 | 0.0089549 | 0.19792 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1072.2 | 127.749 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1072.4 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1072.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1072.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1073 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1073.2 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0035139
1073.4 | 127.557 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1073.6 | 127.557 | 0.032947 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1073.8 | 126.9813 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0097238 | 0.66813 | 0.013089 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1074 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1074.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1074.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1074.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1074.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1075 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1075.2 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1075.4 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1075.6 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
1075.8 | 127.4611 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1076 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1076.2 | 127.557 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1076.4 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1076.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1076.8 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1077 | 127.4611 | 0.0089549 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
1077.2 | 127.4611 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1077.4 | 127.4611 | 0.012154 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0035139
1077.6 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1077.8 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.38019 | 0.0083128
1078 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1078.2 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1078.4 | 127.4611 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1078.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1078.8 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1079 | 127.4611 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1079.2 | 127.557 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | -0.0036512 | 0.006713
1079.4 | 127.557 | 0.012154 | 0.67775 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1079.6 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1079.8 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.0083128
1080 | 127.4611 | 0.010554 | 0.29387 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1080.2 | 127.4611 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.28324 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1080.4 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1080.6 | 127.4611 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1080.8 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.18829 | 0.0083128
1081 | 127.557 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.009669 | 0.28424 | 0.006713
1081.2 | 127.4611 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1081.4 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1081.6 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0038022 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1081.8 | 127.3651 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1082 | 127.4611 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.38986 | 0.00647 | 0.18829 | 0.006713
1082.2 | 127.557 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1082.4 | 127.4611 | 0.015352 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1082.6 | 127.557 | 0.015352 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0002934 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1082.8 | 127.4611 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1083 | 127.653 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | -0.0036512 | 0.006713
1083.2 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1083.4 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1083.6 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1083.8 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1084 | 127.653 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1084.2 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.18829 | 0.0083128
1084.4 | 127.653 | 0.018551 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1084.6 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1084.8 | 127.557 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1085 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1085.2 | 127.8449 | 0.020151 | 0.29387 | 0.0063808 | 0.38916 | 0.009613 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1085.4 | 127.749 | 0.039345 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1085.6 | 127.653 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1085.8 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1086 | 127.749 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1086.2 | 127.653 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1086.4 | 127.749 | 0.016952 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1086.6 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1086.8 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.006713
1087 | 128.0369 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.38986 | 0.011268 | 0.38019 | 0.0083128
1087.2 | 128.9966 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.18729 | 0.0038022 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1087.4 | 128.3248 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.7737 | 0.009669 | 0.28424 | 0.0083128
1087.6 | 128.0369 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1087.8 | 127.8449 | 0.018551 | 0.38986 | 0.0031824 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1088 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1088.2 | 127.749 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1088.4 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1088.6 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1088.8 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1089 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1089.2 | 127.8449 | 0.016952 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.011511
1089.4 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1089.6 | 127.749 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.0083128
1089.8 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1090 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1090.2 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1090.4 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1090.6 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1090.8 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1091 | 127.749 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1091.2 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1091.4 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1091.6 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1091.8 | 127.8449 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
1092 | 127.653 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.0083128
1092.2 | 127.4611 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.18829 | 0.006713
1092.4 | 127.653 | 0.02335 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0082906 | 0.67775 | 0.00647 | 0.18829 | 0.006713
1092.6 | 127.8449 | 0.048941 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.8139 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1092.8 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0081246 | 0.66813 | 0.014688 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1093 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1093.2 | 127.653 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.57213 | 0.006713
1093.4 | 127.557 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1093.6 | 127.557 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
1093.8 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1094 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1094.2 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1094.4 | 127.557 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
1094.6 | 127.557 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1094.8 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1095 | 127.557 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1095.2 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.19722 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1095.4 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1095.6 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
1095.8 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1096 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1096.2 | 127.3651 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.18829 | 0.006713
1096.4 | 127.557 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1096.6 | 127.3651 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1096.8 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.18729 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1097 | 127.557 | 0.013753 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.006713
1097.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1097.4 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1097.6 | 127.4611 | 0.013753 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.0923 | 0.006713
1097.8 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.011268 | 0.28424 | 0.006713
1098 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.7737 | 0.009669 | 0.28424 | 0.006713
1098.2 | 127.4611 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1098.4 | 127.4611 | 0.012154 | 0.38986 | 0.0015826 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1098.6 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1098.8 | 127.4611 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1099 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1099.2 | 127.3651 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.006713
1099.4 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1099.6 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1099.8 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1100 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1100.2 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1100.4 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1100.6 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1100.8 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
1101 | 127.3651 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1101.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0019147
1101.4 | 127.4611 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.47618 | 0.0083128
1101.6 | 127.4611 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.47618 | 0.006713
1101.8 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1102 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1102.2 | 127.1732 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.0083128
1102.4 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1102.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0038022 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1102.8 | 127.4611 | 0.010554 | 0.19792 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1103 | 127.4611 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1103.2 | 127.4611 | 0.010554 | 0.29387 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0097238 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1103.4 | 127.3651 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1103.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1103.8 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1104 | 127.3651 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1104.2 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1104.4 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1104.6 | 127.3651 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.18729 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1104.8 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1105 | 127.2692 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1105.2 | 127.1732 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1105.4 | 127.2692 | 0.013753 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1105.6 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1105.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1106 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1106.2 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1106.4 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1106.6 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1106.8 | 127.4611 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1107 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0051138
1107.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0066908 | 0.29387 | 0.0080692 | 0.28424 | 0.0083128
1107.4 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0097238 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1107.6 | 127.4611 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.017721 | 0.47618 | 0.0050916 | 0.38986 | 0.012867 | 0.28424 | 0.0083128
1107.8 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.23811 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1108 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1108.2 | 127.4611 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1108.4 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1108.6 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1108.8 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1109 | 127.3651 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1109.2 | 127.3651 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.28424 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0019147
1109.4 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.86003 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1109.6 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1109.8 | 127.4611 | 0.010554 | 0.10193 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1110 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1110.2 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0051138
1110.4 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1110.6 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1110.8 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1111 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.18729 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1111.2 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1111.4 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1111.6 | 127.3651 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1111.8 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1112 | 127.4611 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1112.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1112.4 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1112.6 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1112.8 | 127.4611 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1113 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1113.2 | 127.3651 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.47618 | 0.0051138
1113.4 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1113.6 | 127.4611 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1113.8 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1114 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1114.2 | 127.3651 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1114.4 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1114.6 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1114.8 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1115 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.28424 | 0.0083128
1115.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1115.4 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1115.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.67775 | 0.009669 | 0.18829 | 0.0083128
1115.8 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1116 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1116.2 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0017265 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1116.4 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1116.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.011213 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0018926 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1116.8 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1117 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1117.2 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1117.4 | 127.3651 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0080139 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1117.6 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1117.8 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1118 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1118.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1118.4 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1118.6 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1118.8 | 127.3651 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1119 | 127.4611 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1119.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1119.4 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1119.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.10127 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1119.8 | 127.4611 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.47618 | 0.006713
1120 | 127.4611 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1120.2 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1120.4 | 127.4611 | 0.0089549 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1120.6 | 127.4611 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1120.8 | 127.4611 | 0.0089549 | 0.29387 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.011511
1121 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1121.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1121.4 | 127.4611 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1121.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1121.8 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1122 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1122.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1122.4 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1122.6 | 127.4611 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.0923 | 0.006713
1122.8 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1123 | 127.4611 | 0.0089549 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1123.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1123.4 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1123.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1123.8 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1124 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1124.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1124.4 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1124.6 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1124.8 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1125 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1125.2 | 127.4611 | 0.0089549 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0017265 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1125.4 | 127.3651 | 0.0073551 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1125.6 | 127.3651 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1125.8 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1126 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1126.2 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1126.4 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0016158 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1126.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.28324 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1126.8 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1127 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1127.2 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1127.4 | 127.3651 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0002934 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1127.6 | 127.4611 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1127.8 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1128 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.76408 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1128.2 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1128.4 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1128.6 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1128.8 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1129 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.009912
1129.2 | 127.557 | 0.0089549 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.011511
1129.4 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1129.6 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1129.8 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.7737 | 0.0080692 | 0.28424 | 0.0083128
1130 | 127.557 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1130.2 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1130.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.006713
1130.6 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1130.8 | 127.749 | 0.0089549 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1131 | 127.749 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1131.2 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1131.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1131.6 | 127.8449 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1131.8 | 127.749 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0051138
1132 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1132.2 | 127.749 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1132.4 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.29387 | 0.009669 | 0.28424 | 0.0083128
1132.6 | 127.8449 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1132.8 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1133 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0016158 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1133.2 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1133.4 | 127.8449 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.23811 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1133.6 | 127.8449 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1133.8 | 127.8449 | 0.020151 | 0.38986 | 0.0015826 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1134 | 127.8449 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1134.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
1134.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0102 | 0.526 | 0.011324 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1134.6 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1134.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
1135 | 127.8449 | 0.0073551 | 0.29387 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1135.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.011511
1135.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
1135.6 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1135.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.19722 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1136 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1136.2 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1136.4 | 126.5974 | 0.0089549 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0019147
1136.6 | 127.1732 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1136.8 | 127.653 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1137 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0017265 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
1137.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1137.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1137.6 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1137.8 | 127.9409 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1138 | 127.9409 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1138.2 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1138.4 | 127.9409 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1138.6 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1138.8 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1139 | 127.8449 | 0.0057559 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1139.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0051138
1139.4 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1139.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1139.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1140 | 127.8449 | 0.0089549 | 0.48581 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1140.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1140.4 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.009912
1140.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1140.8 | 127.8449 | 0.010554 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1141 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1141.2 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1141.4 | 128.0369 | 0.026549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1141.6 | 128.5167 | 0.045742 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1141.8 | 127.2692 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0097238 | 0.57213 | 0.01149 | 0.7737 | 0.009669 | 0.28424 | 0.006713
1142 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0032156 | 0.47518 | 0.0070012 | 0.71795 | 0.016122 | 0.76408 | 0.01149 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1142.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1142.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1142.6 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1142.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1143 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.009613 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1143.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1143.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1143.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1143.8 | 127.653 | 0.010554 | 0.38986 | 0.0079807 | 0.19722 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1144 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1144.2 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1144.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1144.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1144.8 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1145 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1145.2 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.011213 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1145.4 | 127.653 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1145.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1145.8 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1146 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1146.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.00647 | 0.28424 | 0.0083128
1146.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1146.6 | 127.653 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | -0.0036512 | 0.0051138
1146.8 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1147 | 127.557 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1147.2 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1147.4 | 127.557 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1147.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1147.8 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1148 | 127.749 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1148.2 | 127.653 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1148.4 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1148.6 | 127.4611 | 0.012154 | 0.38986 | 0.0031824 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1148.8 | 127.557 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1149 | 127.557 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1149.2 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1149.4 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1149.6 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1149.8 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1150 | 127.557 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1150.2 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1150.4 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1150.6 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0102 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1150.8 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.006713
1151 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1151.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1151.4 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1151.6 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1151.8 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1152 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1152.2 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1152.4 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1152.6 | 127.653 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0102 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1152.8 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1153 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1153.2 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1153.4 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1153.6 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1153.8 | 127.557 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1154 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1154.2 | 127.653 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1154.4 | 127.749 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0048701 | 0.28424 | 0.006713
1154.6 | 127.653 | 0.013753 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1154.8 | 127.749 | 0.015352 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1155 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1155.2 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1155.4 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1155.6 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1155.8 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1156 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1156.2 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1156.4 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1156.6 | 127.8449 | 0.013753 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1156.8 | 127.8449 | 0.013753 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1157 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1157.2 | 127.9409 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.29387 | 0.00647 | 0.18829 | 0.0083128
1157.4 | 127.4611 | 0.02175 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1157.6 | 128.2288 | 0.040944 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1157.8 | 127.9409 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1158 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1158.2 | 127.8449 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.33406 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.66813 | 0.0083128
1158.4 | 127.8449 | 0.015352 | 0.29387 | 0.0047816 | 0.5811 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1158.6 | 127.749 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.28324 | 0.0038022 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1158.8 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1159 | 127.9409 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1159.2 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1159.4 | 127.8449 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1159.6 | 128.1329 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1159.8 | 127.9409 | 0.015352 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1160 | 128.1329 | 0.016952 | 0.38986 | 0.0047816 | 0.19722 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1160.2 | 128.7087 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1160.4 | 129.1885 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1160.6 | 128.4208 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1160.8 | 128.1329 | 0.016952 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1161 | 128.1329 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.47618 | 0.0083128
1161.2 | 128.0369 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1161.4 | 127.8449 | 0.020151 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1161.6 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.86003 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1161.8 | 127.9409 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1162 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1162.2 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1162.4 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1162.6 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0102 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.28424 | 0.0083128
1162.8 | 127.9409 | 0.018551 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1163 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1163.2 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1163.4 | 127.8449 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1163.6 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1163.8 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1164 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1164.2 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1164.4 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1164.6 | 127.8449 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1164.8 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1165 | 127.9409 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1165.2 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.28324 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1165.4 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1165.6 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1165.8 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1166 | 127.8449 | 0.016952 | 0.10193 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1166.2 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1166.4 | 127.8449 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1166.6 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0035139
1166.8 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.0923 | 0.006713
1167 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1167.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1167.4 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1167.6 | 127.653 | 0.016952 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1167.8 | 127.8449 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1168 | 127.3651 | 0.028148 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1168.2 | 127.749 | 0.053739 | 0.29387 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.012923 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1168.4 | 128.2288 | 0.048941 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.016122 | 0.66813 | 0.01149 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1168.6 | 127.653 | 0.015352 | 0.38986 | 0.0031824 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.43001 | 0.011324 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1168.8 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1169 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.29387 | 0.0080692 | 0.18829 | 0.006713
1169.2 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.66813 | 0.006713
1169.4 | 127.749 | 0.016952 | 0.48581 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1169.6 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
1169.8 | 127.749 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1170 | 127.749 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1170.2 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1170.4 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1170.6 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1170.8 | 127.653 | 0.016952 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1171 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1171.2 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1171.4 | 127.653 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0017265 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1171.6 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1171.8 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1172 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1172.2 | 127.653 | 0.013753 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1172.4 | 127.653 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1172.6 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1172.8 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.0923 | 0.006713
1173 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1173.2 | 127.653 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1173.4 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1173.6 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1173.8 | 127.653 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1174 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1174.2 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1174.4 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
1174.6 | 127.557 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1174.8 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1175 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.0083128
1175.2 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1175.4 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1175.6 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1175.8 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.18829 | 0.006713
1176 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1176.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1176.4 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1176.6 | 127.653 | 0.012154 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1176.8 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1177 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1177.2 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1177.4 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1177.6 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1177.8 | 127.653 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1178 | 127.653 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1178.2 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0016158 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1178.4 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.38019 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1178.6 | 127.557 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1178.8 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1179 | 127.653 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.0923 | 0.0083128
1179.2 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1179.4 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1179.6 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1179.8 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1180 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1180.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1180.4 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.18829 | 0.006713
1180.6 | 127.557 | 0.012154 | 0.38986 | 0.0031824 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1180.8 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1181 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1181.2 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1181.4 | 127.557 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1181.6 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1181.8 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1182 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1182.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0017265 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1182.4 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.5811 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1182.6 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1182.8 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1183 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
1183.2 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1183.4 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.28424 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1183.6 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1183.8 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.006713
1184 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1184.2 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1184.4 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1184.6 | 127.3651 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1184.8 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1185 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1185.2 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.38019 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1185.4 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1185.6 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1185.8 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1186 | 127.653 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.011511
1186.2 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1186.4 | 127.653 | 0.012154 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1186.6 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.009912
1186.8 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1187 | 127.653 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1187.2 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.19792 | 0.00647 | 0.28424 | 0.0083128
1187.4 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1187.6 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1187.8 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1188 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1188.2 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1188.4 | 127.653 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.47618 | 0.006713
1188.6 | 127.749 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1188.8 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0035139
1189 | 127.749 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1189.2 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1189.4 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1189.6 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1189.8 | 127.749 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0102 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1190 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1190.2 | 127.8449 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1190.4 | 127.749 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1190.6 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
1190.8 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1191 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1191.2 | 127.8449 | 0.015352 | 0.38986 | 0.0079807 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1191.4 | 127.8449 | 0.042543 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.01149 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1191.6 | 127.9409 | 0.02335 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0081246 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1191.8 | 127.8449 | 0.018551 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1192 | 127.9409 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
1192.2 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1192.4 | 127.8449 | 0.015352 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1192.6 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1192.8 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1193 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1193.2 | 127.9409 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1193.4 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1193.6 | 128.0369 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1193.8 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1194 | 128.0369 | 0.018551 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1194.2 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1194.4 | 128.0369 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1194.6 | 128.0369 | 0.016952 | 0.58176 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.011511
1194.8 | 128.0369 | 0.016952 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1195 | 128.0369 | 0.018551 | 0.38986 | 0.0047816 | 0.5811 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1195.2 | 128.1329 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1195.4 | 128.6127 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1195.6 | 128.9966 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
1195.8 | 128.0369 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.47618 | 0.0083128
1196 | 127.9409 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1196.2 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1196.4 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1196.6 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1196.8 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1197 | 127.8449 | 0.018551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0038022 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0051138
1197.2 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.28324 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1197.4 | 127.557 | 0.026549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1197.6 | 127.4611 | 0.02335 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1197.8 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1198 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1198.2 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1198.4 | 127.8449 | 0.018551 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1198.6 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1198.8 | 127.749 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1199 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1199.2 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.012867 | 0.28424 | 0.0083128
1199.4 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0048701 | 0.18829 | 0.006713
1199.6 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1199.8 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1200 | 127.557 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1200.2 | 127.653 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1200.4 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1200.6 | 127.653 | 0.015352 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1200.8 | 127.653 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1201 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1201.2 | 127.653 | 0.015352 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1201.4 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1201.6 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1201.8 | 127.749 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.23811 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1202 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1202.2 | 127.557 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1202.4 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1202.6 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1202.8 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1203 | 127.653 | 0.013753 | 0.48581 | 0.0015826 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1203.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1203.4 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.006713
1203.6 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1203.8 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1204 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1204.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1204.4 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1204.6 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1204.8 | 127.557 | 0.012154 | 0.29387 | 0.0079807 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1205 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1205.2 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1205.4 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1205.6 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1205.8 | 127.557 | 0.010554 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1206 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1206.2 | 127.653 | 0.02175 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1206.4 | 127.4611 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1206.6 | 127.557 | 0.013753 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1206.8 | 127.557 | 0.013753 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0017265 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1207 | 127.557 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1207.2 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1207.4 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1207.6 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1207.8 | 127.557 | 0.013753 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.57213 | 0.009912
1208 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1208.2 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1208.4 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1208.6 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1208.8 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1209 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1209.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1209.4 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1209.6 | 127.653 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.57213 | 0.0083128
1209.8 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1210 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.33406 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1210.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1210.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1210.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1210.8 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1211 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.33406 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1211.2 | 127.653 | 0.0089549 | 0.58176 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1211.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1211.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1211.8 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1212 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1212.2 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1212.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.011511
1212.6 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.28324 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1212.8 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0038022 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1213 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1213.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1213.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
1213.6 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1213.8 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1214 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1214.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1214.4 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1214.6 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1214.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1215 | 127.8449 | 0.0089549 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1215.2 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1215.4 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.012923 | 0.66813 | 0.0098898 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1215.6 | 127.749 | 0.034546 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1215.8 | 127.9409 | 0.02175 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1216 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1216.2 | 127.9409 | 0.016952 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1216.4 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1216.6 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1216.8 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1217 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1217.2 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1217.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1217.6 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1217.8 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1218 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1218.2 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1218.4 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1218.6 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1218.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1219 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1219.2 | 127.8449 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0035139
1219.4 | 127.9409 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1219.6 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1219.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1220 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1220.2 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1220.4 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1220.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1220.8 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1221 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1221.2 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1221.4 | 127.9409 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1221.6 | 127.749 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1221.8 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1222 | 127.749 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1222.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1222.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1222.6 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1222.8 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1223 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1223.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1223.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1223.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0016158 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1223.8 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1224 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1224.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1224.4 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
1224.6 | 126.8853 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1224.8 | 126.5014 | 0.0089549 | 0.29387 | 0.0095798 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1225 | 126.7893 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1225.2 | 127.2692 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1225.4 | 127.557 | 0.0089549 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1225.6 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1225.8 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1226 | 127.653 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1226.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.19722 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1226.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1226.6 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1226.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1227 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0038022 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1227.2 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1227.4 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1227.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0102 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1227.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1228 | 127.749 | 0.010554 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0019147
1228.2 | 127.8449 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1228.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1228.6 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1228.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1229 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1229.2 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1229.4 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1229.6 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0018926 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1229.8 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1230 | 127.749 | 0.010554 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1230.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.011324 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1230.4 | 127.749 | 0.0089549 | 0.58176 | 0.0063808 | 0.38916 | -0.0015832 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.011511
1230.6 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1230.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1231 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1231.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1231.4 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1231.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.009912
1231.8 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1232 | 128.0369 | 0.029748 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.43001 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1232.2 | 127.749 | 0.024949 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1232.4 | 127.749 | 0.02335 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1232.6 | 127.653 | 0.02335 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1232.8 | 127.8449 | 0.018551 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.47618 | 0.0083128
1233 | 127.557 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0048701 | 0.28424 | 0.006713
1233.2 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.33406 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1233.4 | 127.8449 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1233.6 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1233.8 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1234 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.0923 | 0.006713
1234.2 | 127.749 | 0.013753 | 0.38986 | 0.0095798 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1234.4 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1234.6 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1234.8 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1235 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1235.2 | 127.749 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1235.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
1235.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1235.8 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0038022 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1236 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1236.2 | 127.653 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1236.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1236.6 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1236.8 | 127.653 | 0.010554 | 0.29387 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1237 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1237.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1237.4 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.012867 | 0.28424 | 0.0083128
1237.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1237.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1238 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1238.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.38019 | 0.0083128
1238.4 | 127.653 | 0.012154 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1238.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1238.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1239 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
1239.2 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.012867 | 0.38019 | 0.0083128
1239.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1239.6 | 127.749 | 0.010554 | 0.10193 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1239.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1240 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1240.2 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1240.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1240.6 | 127.653 | 0.012154 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1240.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1241 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1241.2 | 127.749 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1241.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1241.6 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1241.8 | 127.749 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1242 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1242.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1242.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1242.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1242.8 | 127.653 | 0.010554 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1243 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1243.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1243.4 | 127.749 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1243.6 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.38019 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1243.8 | 127.749 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.18829 | 0.006713
1244 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1244.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1244.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1244.6 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1244.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1245 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1245.2 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1245.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1245.6 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1245.8 | 127.749 | 0.0089549 | 0.48581 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1246 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1246.2 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1246.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0102 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0048701 | 0.28424 | 0.0083128
1246.6 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1246.8 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.76308 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1247 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1247.2 | 127.653 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1247.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1247.6 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.009912
1247.8 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1248 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1248.2 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1248.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1248.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.00647 | 0.28424 | 0.0083128
1248.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1249 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1249.2 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1249.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0002934 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1249.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.28424 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1249.8 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1250 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1250.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1250.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1250.6 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
1250.8 | 127.653 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.0923 | 0.006713
1251 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1251.2 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1251.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0002934 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1251.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1251.8 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1252 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1252.2 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1252.4 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1252.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1252.8 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1253 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1253.2 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.28324 | 0.0038022 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1253.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1253.6 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1253.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1254 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1254.2 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1254.4 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1254.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.009912
1254.8 | 127.749 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1255 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1255.2 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.43001 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.0923 | 0.006713
1255.4 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1255.6 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.006713
1255.8 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1256 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1256.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1256.4 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1256.6 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1256.8 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1257 | 127.749 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1257.2 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0098898 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1257.4 | 127.653 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1257.6 | 127.8449 | 0.02175 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.0923 | 0.0083128
1257.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1258 | 127.3651 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
1258.2 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1258.4 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.011213 | 0.47518 | 0.0070012 | 0.62195 | 0.011324 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1258.6 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1258.8 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.5811 | 0.0048148 | 0.37923 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1259 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.01471
1259.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.006713
1259.4 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.28324 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1259.6 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1259.8 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1260 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1260.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1260.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1260.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1260.8 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1261 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.19722 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1261.2 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0017265 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1261.4 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1261.6 | 127.749 | 0.010554 | 0.58176 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1261.8 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1262 | 127.4611 | 0.0089549 | 0.29387 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1262.2 | 126.5974 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1262.4 | 126.6933 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1262.6 | 127.1732 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1262.8 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1263 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1263.2 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1263.4 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1263.6 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1263.8 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.0923 | 0.006713
1264 | 127.749 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1264.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
1264.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1264.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1264.8 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1265 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1265.2 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1265.4 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0051138
1265.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1265.8 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1266 | 127.9409 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1266.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1266.4 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1266.6 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1266.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1267 | 127.8449 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1267.2 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1267.4 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1267.6 | 127.8449 | 0.0073551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.006713
1267.8 | 127.8449 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.47618 | 0.006713
1268 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1268.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1268.4 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1268.6 | 127.9409 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1268.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1269 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1269.2 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1269.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1269.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1269.8 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1270 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1270.2 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1270.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1270.6 | 127.749 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1270.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1271 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1271.2 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1271.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1271.6 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1271.8 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1272 | 127.9409 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1272.2 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1272.4 | 127.653 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.28324 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1272.6 | 127.9409 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1272.8 | 127.653 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1273 | 127.653 | 0.029748 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1273.2 | 128.0369 | 0.042543 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1273.4 | 128.1329 | 0.037745 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1273.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.012923 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1273.8 | 127.4611 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.012923 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1274 | 127.2692 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.01149 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1274.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1274.4 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.014522 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1274.6 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.013089 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1274.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.013089 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1275 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1275.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1275.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1275.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1275.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.38019 | 0.0083128
1276 | 127.8449 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.66813 | 0.009912
1276.2 | 127.749 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0051138
1276.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1276.6 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1276.8 | 127.749 | 0.0073551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1277 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1277.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1277.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1277.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1277.8 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.0083128
1278 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1278.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1278.4 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1278.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1278.8 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1279 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1279.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1279.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1279.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
1279.8 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1280 | 127.749 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1280.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1280.4 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1280.6 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1280.8 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.011213 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1281 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1281.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1281.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1281.6 | 127.749 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1281.8 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1282 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1282.2 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1282.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.8139 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1282.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1282.8 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1283 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.0083128
1283.2 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1283.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1283.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1283.8 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1284 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1284.2 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1284.4 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1284.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1284.8 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1285 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1285.2 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1285.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1285.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1285.8 | 127.557 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.38019 | 0.009912
1286 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1286.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1286.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1286.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1286.8 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1287 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1287.2 | 127.557 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1287.4 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1287.6 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1287.8 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1288 | 127.4611 | 0.0089549 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1288.2 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1288.4 | 127.557 | 0.0073551 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1288.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1288.8 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1289 | 127.653 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1289.2 | 127.653 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1289.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1289.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1289.8 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1290 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.8139 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1290.2 | 127.557 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1290.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1290.6 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1290.8 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.76308 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1291 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1291.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1291.4 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1291.6 | 127.653 | 0.010554 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1291.8 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1292 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1292.2 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1292.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1292.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1292.8 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1293 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0016158 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.7737 | 0.009669 | 0.28424 | 0.0083128
1293.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1293.4 | 127.557 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1293.6 | 127.557 | 0.010554 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.0923 | 0.009912
1293.8 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1294 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.19722 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1294.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1294.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1294.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1294.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1295 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0048701 | 0.28424 | 0.0083128
1295.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1295.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1295.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1295.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.67705 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1296 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1296.2 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1296.4 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0082906 | 0.38986 | 0.00647 | 0.28424 | 0.0083128
1296.6 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.37923 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1296.8 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1297 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1297.2 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1297.4 | 127.557 | 0.0073551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1297.6 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1297.8 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.28324 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1298 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1298.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1298.4 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1298.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1298.8 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1299 | 127.557 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1299.2 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.28324 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1299.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1299.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1299.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0018926 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1300 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1300.2 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1300.4 | 127.557 | 0.010554 | 0.10193 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1300.6 | 127.557 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1300.8 | 127.557 | 0.010554 | 0.10193 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1301 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0035139
1301.2 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1301.4 | 127.653 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.47618 | 0.0083128
1301.6 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1301.8 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.47618 | 0.0083128
1302 | 127.557 | 0.0073551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1302.2 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1302.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1302.6 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1302.8 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1303 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1303.2 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1303.4 | 127.557 | 0.010554 | 0.38986 | 0.0031824 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1303.6 | 127.557 | 0.0073551 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1303.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1304 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0018926 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1304.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1304.4 | 127.557 | 0.012154 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1304.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1304.8 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1305 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1305.2 | 127.4611 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1305.4 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1305.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1305.8 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1306 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1306.2 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1306.4 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1306.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1306.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1307 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1307.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1307.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1307.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1307.8 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1308 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1308.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1308.4 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1308.6 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1308.8 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.19722 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1309 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.0923 | 0.006713
1309.2 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1309.4 | 127.557 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1309.6 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.011268 | 0.28424 | 0.0083128
1309.8 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1310 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1310.2 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.0923 | 0.0083128
1310.4 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1310.6 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1310.8 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1311 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0054014 | 0.8139 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1311.2 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1311.4 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1311.6 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.18829 | 0.009912
1311.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1312 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1312.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0098898 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1312.4 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1312.6 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1312.8 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1313 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1313.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1313.4 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1313.6 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1313.8 | 127.557 | 0.012154 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | -0.0036512 | 0.006713
1314 | 127.557 | 0.013753 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1314.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1314.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1314.6 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1314.8 | 127.557 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.011511
1315 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.38019 | 0.0083128
1315.2 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.47618 | 0.01149 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1315.4 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1315.6 | 127.4611 | 0.012154 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1315.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1316 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1316.2 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1316.4 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1316.6 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1316.8 | 127.557 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1317 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1317.2 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.67705 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1317.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0017265 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1317.6 | 127.4611 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1317.8 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1318 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1318.2 | 127.4611 | 0.012154 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1318.4 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1318.6 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1318.8 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1319 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1319.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1319.4 | 127.4611 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0033264 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1319.6 | 127.557 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1319.8 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1320 | 127.557 | 0.015352 | 0.19792 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1320.2 | 127.557 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1320.4 | 127.557 | 0.016952 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.38019 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1320.6 | 127.557 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1320.8 | 127.653 | 0.02175 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1321 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.7737 | 0.009669 | 0.28424 | 0.006713
1321.2 | 127.3651 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1321.4 | 127.2692 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.003271 | 0.28424 | 0.0083128
1321.6 | 126.9813 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.76308 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1321.8 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.009912
1322 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1322.2 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1322.4 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1322.6 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
1322.8 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0018926 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1323 | 127.557 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1323.2 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1323.4 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1323.6 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1323.8 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1324 | 127.4611 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1324.2 | 127.4611 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1324.4 | 127.4611 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1324.6 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.28324 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1324.8 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0018926 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1325 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1325.2 | 127.4611 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1325.4 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1325.6 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1325.8 | 127.4611 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1326 | 127.557 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1326.2 | 127.4611 | 0.013753 | 0.29387 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1326.4 | 127.557 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.009613 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1326.6 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1326.8 | 127.4611 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1327 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.5811 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.38019 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1327.2 | 127.3651 | 0.015352 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1327.4 | 127.3651 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1327.6 | 127.2692 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.76308 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1327.8 | 127.4611 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.011511
1328 | 127.3651 | 0.015352 | 0.38986 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1328.2 | 127.557 | 0.016952 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1328.4 | 127.3651 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1328.6 | 127.557 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1328.8 | 127.557 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1329 | 127.557 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1329.2 | 127.653 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.8139 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1329.4 | 127.557 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1329.6 | 127.653 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1329.8 | 127.557 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1330 | 127.653 | 0.016952 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1330.2 | 127.653 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1330.4 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1330.6 | 127.749 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1330.8 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0048701 | 0.18829 | 0.0083128
1331 | 127.653 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1331.2 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.66713 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1331.4 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1331.6 | 127.653 | 0.015352 | 0.48581 | 0.0031824 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1331.8 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1332 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1332.2 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1332.4 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0018926 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1332.6 | 127.8449 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.28324 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1332.8 | 127.749 | 0.016952 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1333 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1333.2 | 127.749 | 0.016952 | 0.48581 | 0.0095798 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1333.4 | 127.749 | 0.016952 | 0.58176 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1333.6 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1333.8 | 127.749 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1334 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0038022 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1334.2 | 127.749 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1334.4 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1334.6 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1334.8 | 127.8449 | 0.02175 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1335 | 127.749 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0038022 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1335.2 | 127.4611 | 0.024949 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1335.4 | 127.8449 | 0.037745 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1335.6 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1335.8 | 127.749 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.76308 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1336 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1336.2 | 127.8449 | 0.018551 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1336.4 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1336.6 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1336.8 | 127.8449 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1337 | 127.9409 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1337.2 | 127.8449 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.57213 | 0.009912
1337.4 | 127.9409 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1337.6 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1337.8 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1338 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1338.2 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1338.4 | 127.9409 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.47618 | 0.0083128
1338.6 | 128.0369 | 0.016952 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1338.8 | 128.1329 | 0.018551 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1339 | 128.2288 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1339.2 | 128.4208 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1339.4 | 128.9006 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1339.6 | 129.3804 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1339.8 | 129.0925 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0038022 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1340 | 128.8046 | 0.018551 | 0.38986 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1340.2 | 128.2288 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1340.4 | 128.2288 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1340.6 | 128.2288 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1340.8 | 128.1329 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1341 | 128.1329 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1341.2 | 128.1329 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0018926 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1341.4 | 128.0369 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1341.6 | 128.1329 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1341.8 | 128.0369 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1342 | 128.0369 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1342.2 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1342.4 | 128.0369 | 0.016952 | 0.48581 | 0.0031824 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1342.6 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1342.8 | 127.9409 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1343 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1343.2 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1343.4 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1343.6 | 127.9409 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1343.8 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1344 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.47618 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1344.2 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1344.4 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.67705 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.38019 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1344.6 | 127.9409 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1344.8 | 127.9409 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1345 | 127.9409 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.86969 | 0.0080692 | 0.28424 | 0.0083128
1345.2 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1345.4 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1345.6 | 127.9409 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1345.8 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1346 | 127.9409 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0051138
1346.2 | 127.8449 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.00647 | 0.28424 | 0.006713
1346.4 | 127.9409 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1346.6 | 127.9409 | 0.018551 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1346.8 | 127.9409 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1347 | 127.9409 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1347.2 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1347.4 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1347.6 | 127.9409 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1347.8 | 127.8449 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1348 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1348.2 | 127.9409 | 0.018551 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1348.4 | 127.8449 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1348.6 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1348.8 | 127.8449 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1349 | 127.8449 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1349.2 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1349.4 | 127.9409 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1349.6 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1349.8 | 127.9409 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1350 | 127.9409 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1350.2 | 127.8449 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1350.4 | 127.8449 | 0.016952 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1350.6 | 127.9409 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1350.8 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1351 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1351.2 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1351.4 | 127.8449 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1351.6 | 127.8449 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1351.8 | 127.8449 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1352 | 127.8449 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1352.2 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1352.4 | 127.8449 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1352.6 | 127.8449 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1352.8 | 127.8449 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1353 | 127.749 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1353.2 | 127.8449 | 0.016952 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1353.4 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1353.6 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1353.8 | 127.8449 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1354 | 127.749 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1354.2 | 127.749 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1354.4 | 127.8449 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1354.6 | 127.749 | 0.02175 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1354.8 | 127.3651 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1355 | 127.8449 | 0.055339 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1355.2 | 128.3248 | 0.039345 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0054014 | 0.71795 | 0.016122 | 0.66813 | 0.01149 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1355.4 | 127.749 | 0.016952 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1355.6 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.011324 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.006713
1355.8 | 127.8449 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1356 | 127.749 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1356.2 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1356.4 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.0051138
1356.6 | 127.749 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1356.8 | 127.749 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1357 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1357.2 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1357.4 | 127.749 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1357.6 | 127.749 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1357.8 | 127.653 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1358 | 127.653 | 0.013753 | 0.48581 | 0.0031824 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1358.2 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.37923 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1358.4 | 127.653 | 0.013753 | 0.29387 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1358.6 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1358.8 | 127.653 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0097238 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1359 | 127.653 | 0.013753 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0051138
1359.2 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.009912
1359.4 | 127.653 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1359.6 | 127.557 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1359.8 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1360 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1360.2 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1360.4 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1360.6 | 127.557 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1360.8 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1361 | 127.557 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.011511
1361.2 | 127.557 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1361.4 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.19722 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1361.6 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1361.8 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1362 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1362.2 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1362.4 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1362.6 | 127.4611 | 0.010554 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0035139
1362.8 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1363 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.8139 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1363.2 | 127.557 | 0.010554 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1363.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.28324 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1363.6 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1363.8 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1364 | 127.4611 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.47618 | 0.0083128
1364.2 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1364.4 | 127.3651 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1364.6 | 127.4611 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1364.8 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1365 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1365.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1365.4 | 127.557 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1365.6 | 127.557 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1365.8 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1366 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1366.2 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1366.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1366.6 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1366.8 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1367 | 127.557 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1367.2 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1367.4 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1367.6 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1367.8 | 127.557 | 0.010554 | 0.38986 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1368 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1368.2 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0018926 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1368.4 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0022023 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1368.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1368.8 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1369 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1369.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0017265 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1369.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1369.6 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.006713
1369.8 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1370 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1370.2 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1370.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1370.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1370.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1371 | 127.653 | 0.0057559 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1371.2 | 127.4611 | 0.0073551 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | -0.0036512 | 0.006713
1371.4 | 127.653 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1371.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1371.8 | 127.557 | 0.010554 | 0.38986 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1372 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1372.2 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1372.4 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1372.6 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.8139 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1372.8 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1373 | 127.653 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1373.2 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1373.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1373.6 | 127.653 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1373.8 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1374 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1374.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1374.4 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1374.6 | 127.653 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1374.8 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1375 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.0923 | 0.0083128
1375.2 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1375.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1375.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1375.8 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1376 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1376.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1376.4 | 127.653 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1376.6 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.011511
1376.8 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1377 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1377.2 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1377.4 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1377.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1377.8 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1378 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1378.2 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.29387 | 0.00647 | 0.28424 | 0.0083128
1378.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.29387 | 0.0080692 | 0.28424 | 0.0083128
1378.6 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.28324 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1378.8 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0002934 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1379 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1379.2 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1379.4 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1379.6 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1379.8 | 127.8449 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1380 | 127.749 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1380.2 | 128.0369 | 0.028148 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1380.4 | 127.749 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.47618 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1380.6 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1380.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1381 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0097238 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1381.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1381.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1381.6 | 127.749 | 0.012154 | 0.19792 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1381.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1382 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.003271 | 0.28424 | 0.0083128
1382.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1382.4 | 127.749 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1382.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1382.8 | 127.749 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1383 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1383.2 | 127.749 | 0.0073551 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0051138
1383.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1383.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1383.8 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1384 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1384.2 | 127.749 | 0.010554 | 0.38986 | 0.0031824 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1384.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1384.6 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1384.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1385 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1385.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1385.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1385.6 | 127.8449 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1385.8 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1386 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1386.2 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924 | 0.7737 | 0.0080692 | 0.28424 | 0.0083128
1386.4 | 127.749 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1386.6 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1386.8 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1387 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1387.2 | 127.4611 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1387.4 | 127.3651 | 0.0073551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1387.6 | 127.1732 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1387.8 | 126.9813 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.18829 | 0.0083128
1388 | 126.4054 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1388.2 | 126.5974 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.8139 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1388.4 | 126.7893 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1388.6 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1388.8 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1389 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1389.2 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1389.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.0923 | 0.0051138
1389.6 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1389.8 | 127.749 | 0.010554 | 0.38986 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1390 | 127.8449 | 0.0073551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1390.2 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0048701 | 0.28424 | 0.006713
1390.4 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1390.6 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1390.8 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0018926 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1391 | 127.9409 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0022023 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.0923 | 0.0083128
1391.2 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1391.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1391.6 | 127.8449 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1391.8 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1392 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.18829 | 0.0083128
1392.2 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1392.4 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1392.6 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1392.8 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1393 | 127.8449 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.38019 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1393.2 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1393.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1393.6 | 127.8449 | 0.010554 | 0.38986 | 0.0095798 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1393.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1394 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1394.2 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1394.4 | 127.8449 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1394.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1394.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1395 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1395.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1395.4 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1395.6 | 127.9409 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1395.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1396 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1396.2 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1396.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1396.6 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1396.8 | 127.8449 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1397 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1397.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1397.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1397.6 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1397.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1398 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1398.2 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1398.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1398.6 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1398.8 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.38019 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1399 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1399.2 | 127.749 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1399.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1399.6 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1399.8 | 127.749 | 0.010554 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1400 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1400.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1400.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1400.6 | 127.749 | 0.010554 | 0.38986 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1400.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1401 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1401.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1401.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1401.6 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1401.8 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1402 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1402.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1402.4 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1402.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1402.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1403 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1403.2 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1403.4 | 127.8449 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1403.6 | 127.8449 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1403.8 | 127.749 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1404 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1404.2 | 127.749 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1404.4 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1404.6 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1404.8 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1405 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1405.2 | 127.653 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1405.4 | 127.653 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1405.6 | 127.8449 | 0.02175 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1405.8 | 127.8449 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1406 | 127.653 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1406.2 | 127.653 | 0.02175 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1406.4 | 127.653 | 0.020151 | 0.48581 | 0.0095798 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1406.6 | 127.557 | 0.034546 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1406.8 | 128.0369 | 0.042543 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1407 | 128.3248 | 0.047342 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1407.2 | 127.8449 | 0.028148 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.33406 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1407.4 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.011324 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1407.6 | 127.0772 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1407.8 | 127.749 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1408 | 127.749 | 0.010554 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1408.2 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.014522 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1408.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1408.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1408.8 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1409 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1409.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1409.4 | 127.653 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.01149 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1409.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1409.8 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1410 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1410.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1410.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1410.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1410.8 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1411 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1411.2 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1411.4 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1411.6 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1411.8 | 127.653 | 0.010554 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1412 | 127.653 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1412.2 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1412.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1412.6 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1412.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1413 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1413.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0022023 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1413.4 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1413.6 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1413.8 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1414 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.7737 | 0.009669 | 0.38019 | 0.009912
1414.2 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1414.4 | 127.653 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1414.6 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1414.8 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1415 | 127.749 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1415.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1415.4 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1415.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1415.8 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1416 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1416.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1416.4 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1416.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1416.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1417 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1417.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.009912
1417.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1417.6 | 127.749 | 0.0089549 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1417.8 | 127.749 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1418 | 127.749 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1418.2 | 127.653 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1418.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1418.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1418.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1419 | 127.8449 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1419.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1419.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1419.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1419.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1420 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1420.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1420.4 | 127.749 | 0.0089549 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1420.6 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.0923 | 0.009912
1420.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1421 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
1421.2 | 127.653 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0038022 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1421.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1421.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1421.8 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1422 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1422.2 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1422.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1422.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.86003 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1422.8 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1423 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1423.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1423.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1423.6 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1423.8 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1424 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
1424.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1424.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.18829 | 0.006713
1424.6 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1424.8 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1425 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1425.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1425.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.18829 | 0.006713
1425.6 | 127.8449 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1425.8 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1426 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1426.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.28424 | 0.0083128
1426.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1426.6 | 127.9409 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1426.8 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1427 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
1427.2 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
1427.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.28324 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1427.6 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1427.8 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1428 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1428.2 | 127.749 | 0.012154 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1428.4 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1428.6 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1428.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1429 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1429.2 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1429.4 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1429.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1429.8 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1430 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1430.2 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1430.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.28324 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1430.6 | 127.653 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1430.8 | 127.653 | 0.0073551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1431 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1431.2 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1431.4 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1431.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1431.8 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1432 | 127.653 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1432.2 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1432.4 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1432.6 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1432.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1433 | 127.653 | 0.0089549 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.013111
1433.2 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1433.4 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1433.6 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1433.8 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1434 | 127.653 | 0.012154 | 0.38986 | 0.0079807 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1434.2 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1434.4 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1434.6 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1434.8 | 127.653 | 0.010554 | 0.38986 | 0.0031824 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1435 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1435.2 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1435.4 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1435.6 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1435.8 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1436 | 127.653 | 0.0073551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.0923 | 0.006713
1436.2 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.012867 | 0.28424 | 0.0083128
1436.4 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1436.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1436.8 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1437 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1437.2 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1437.4 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1437.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1437.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1438 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1438.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1438.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1438.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.76308 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1438.8 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1439 | 127.557 | 0.012154 | 0.38986 | 0.0079807 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1439.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1439.4 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.012867 | 0.28424 | 0.0083128
1439.6 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1439.8 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1440 | 127.557 | 0.012154 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1440.2 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.009613 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1440.4 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1440.6 | 127.653 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1440.8 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1441 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1441.2 | 127.4611 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1441.4 | 127.557 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1441.6 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1441.8 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1442 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1442.2 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1442.4 | 127.4611 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1442.6 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1442.8 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.85907 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1443 | 127.653 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1443.2 | 127.4611 | 0.016952 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0051138
1443.4 | 127.653 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1443.6 | 127.1732 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1443.8 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1444 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.96498 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1444.2 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1444.4 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1444.6 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0038022 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1444.8 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1445 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1445.2 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.011324 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1445.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1445.6 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1445.8 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1446 | 127.557 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0102 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1446.2 | 127.4611 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0022023 | 0.43001 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1446.4 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1446.6 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1446.8 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1447 | 127.749 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1447.2 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1447.4 | 127.557 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.86969 | 0.009669 | 0.28424 | 0.0083128
1447.6 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1447.8 | 127.557 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1448 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1448.2 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1448.4 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1448.6 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1448.8 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.67705 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1449 | 127.557 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1449.2 | 127.653 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1449.4 | 127.557 | 0.015352 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1449.6 | 127.557 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1449.8 | 127.557 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1450 | 127.653 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0032156 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1450.2 | 127.653 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1450.4 | 127.653 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1450.6 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1450.8 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1451 | 127.653 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1451.2 | 127.749 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1451.4 | 127.653 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1451.6 | 127.653 | 0.015352 | 0.29387 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1451.8 | 127.653 | 0.016952 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1452 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1452.2 | 127.749 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1452.4 | 127.653 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1452.6 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1452.8 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1453 | 127.749 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1453.2 | 127.653 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1453.4 | 127.653 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1453.6 | 127.653 | 0.013753 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1453.8 | 127.8449 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1454 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1454.2 | 127.749 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1454.4 | 127.749 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0038022 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1454.6 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1454.8 | 127.749 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
1455 | 127.8449 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1455.2 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1455.4 | 128.0369 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1455.6 | 127.653 | 0.02335 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.37923 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1455.8 | 127.8449 | 0.039345 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1456 | 127.8449 | 0.031347 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1456.2 | 127.8449 | 0.018551 | 0.38986 | 0.0047816 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1456.4 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1456.6 | 127.8449 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.86003 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1456.8 | 127.8449 | 0.018551 | 0.19792 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1457 | 127.8449 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1457.2 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1457.4 | 127.8449 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1457.6 | 127.9409 | 0.018551 | 0.38986 | 0.0031824 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1457.8 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1458 | 127.9409 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1458.2 | 127.9409 | 0.016952 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1458.4 | 127.9409 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.28324 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1458.6 | 127.9409 | 0.016952 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.86003 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1458.8 | 128.0369 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1459 | 128.4208 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1459.2 | 129.3804 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.0083128
1459.4 | 128.9966 | 0.018551 | 0.29387 | 0.0095798 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1459.6 | 128.3248 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1459.8 | 128.2288 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1460 | 128.1329 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1460.2 | 128.1329 | 0.018551 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1460.4 | 127.9409 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1460.6 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1460.8 | 128.0369 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1461 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1461.2 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1461.4 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1461.6 | 127.9409 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1461.8 | 128.0369 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1462 | 128.0369 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1462.2 | 128.0369 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1462.4 | 127.9409 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1462.6 | 127.9409 | 0.020151 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1462.8 | 128.0369 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1463 | 127.9409 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1463.2 | 128.0369 | 0.018551 | 0.38986 | 0.0031824 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1463.4 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.7737 | 0.009669 | 0.28424 | 0.0083128
1463.6 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1463.8 | 127.9409 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1464 | 127.9409 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1464.2 | 127.9409 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1464.4 | 127.9409 | 0.015352 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1464.6 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1464.8 | 127.9409 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1465 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1465.2 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1465.4 | 127.9409 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1465.6 | 127.8449 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1465.8 | 127.8449 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1466 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1466.2 | 127.749 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1466.4 | 127.557 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1466.6 | 127.8449 | 0.02335 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1466.8 | 128.0369 | 0.042543 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1467 | 128.3248 | 0.045742 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.014522 | 0.57213 | 0.01149 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1467.2 | 127.8449 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1467.4 | 127.749 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1467.6 | 127.8449 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0032156 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1467.8 | 127.8449 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1468 | 127.8449 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1468.2 | 127.8449 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1468.4 | 127.749 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1468.6 | 127.749 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1468.8 | 127.749 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1469 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.006713
1469.2 | 127.749 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1469.4 | 127.749 | 0.015352 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1469.6 | 127.8449 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1469.8 | 127.749 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.7737 | 0.0080692 | 0.28424 | 0.0083128
1470 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0098898 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1470.2 | 127.653 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1470.4 | 127.749 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1470.6 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0034924 | 0.7737 | 0.0080692 | 0.28424 | 0.006713
1470.8 | 127.653 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1471 | 127.653 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1471.2 | 127.653 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1471.4 | 127.653 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1471.6 | 127.653 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1471.8 | 127.653 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1472 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1472.2 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | -0.0036512 | 0.006713
1472.4 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1472.6 | 127.653 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1472.8 | 127.749 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1473 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0034924 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1473.2 | 127.557 | 0.013753 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1473.4 | 127.653 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1473.6 | 127.653 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1473.8 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1474 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1474.2 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0038022 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1474.4 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1474.6 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1474.8 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1475 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1475.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1475.4 | 127.653 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1475.6 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1475.8 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.7737 | 0.009669 | 0.28424 | 0.0083128
1476 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1476.2 | 127.4611 | 0.020151 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1476.4 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1476.6 | 127.557 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 1.1018 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1476.8 | 127.557 | 0.010554 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.009912
1477 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1477.2 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1477.4 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1477.6 | 127.3651 | 0.010554 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1477.8 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1478 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0038022 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1478.2 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1478.4 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1478.6 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0035139
1478.8 | 127.557 | 0.0089549 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1479 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1479.2 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1479.4 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1479.6 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1479.8 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1480 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1480.2 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.011511
1480.4 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1480.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1480.8 | 127.653 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1481 | 127.557 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.7737 | 0.011268 | 0.28424 | 0.0083128
1481.2 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1481.4 | 127.653 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1481.6 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1481.8 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1482 | 127.653 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1482.2 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1482.4 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1482.6 | 127.749 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1482.8 | 127.749 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1483 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1483.2 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.47618 | 0.009912
1483.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1483.6 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1483.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1484 | 127.749 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.011511
1484.2 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.57213 | 0.0083128
1484.4 | 127.749 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1484.6 | 127.9409 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1484.8 | 127.749 | 0.02335 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.011511
1485 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.38986 | 0.0080692 | 0.28424 | 0.006713
1485.2 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1485.4 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1485.6 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1485.8 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1486 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1486.2 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1486.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1486.6 | 127.8449 | 0.010554 | 0.48581 | 0.0031824 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1486.8 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.0923 | 0.006713
1487 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1487.2 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1487.4 | 127.9409 | 0.012154 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1487.6 | 127.9409 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1487.8 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1488 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1488.2 | 127.749 | 0.010554 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1488.4 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1488.6 | 126.9813 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1488.8 | 126.7893 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1489 | 127.4611 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1489.2 | 127.653 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1489.4 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1489.6 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1489.8 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1490 | 127.9409 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1490.2 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1490.4 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1490.6 | 127.9409 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1490.8 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1491 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1491.2 | 127.9409 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1491.4 | 127.9409 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1491.6 | 127.9409 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1491.8 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1492 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1492.2 | 127.9409 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1492.4 | 127.9409 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1492.6 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1492.8 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1493 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1493.2 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1493.4 | 127.9409 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1493.6 | 127.9409 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1493.8 | 127.9409 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1494 | 127.9409 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1494.2 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1494.4 | 127.9409 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1494.6 | 127.8449 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1494.8 | 127.9409 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.00647 | 0.18829 | 0.0083128
1495 | 127.9409 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1495.2 | 127.9409 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1495.4 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1495.6 | 128.0369 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1495.8 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1496 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1496.2 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1496.4 | 127.9409 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1496.6 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1496.8 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1497 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1497.2 | 127.8449 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1497.4 | 127.9409 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1497.6 | 127.8449 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1497.8 | 127.9409 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1498 | 127.8449 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1498.2 | 127.8449 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1498.4 | 128.0369 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.38986 | 0.011268 | 0.38019 | 0.0083128
1498.6 | 127.9409 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1498.8 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1499 | 127.8449 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1499.2 | 127.9409 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1499.4 | 127.9409 | 0.02335 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1499.6 | 127.8449 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1499.8 | 127.749 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1500 | 127.749 | 0.028148 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1500.2 | 128.1329 | 0.040944 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.7737 | 0.011268 | 0.28424 | 0.0083128
1500.4 | 128.5167 | 0.048941 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1500.6 | 128.1329 | 0.029748 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.57213 | 0.0098898 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1500.8 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1501 | 127.2692 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1501.2 | 127.0772 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1501.4 | 127.1732 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1501.6 | 127.749 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1501.8 | 127.749 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1502 | 127.653 | 0.010554 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1502.2 | 127.653 | 0.0089549 | 0.29387 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1502.4 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.011324 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1502.6 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.8139 | 0.012923 | 0.76408 | 0.0098898 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1502.8 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1503 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.027794 | 0.526 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1503.2 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1503.4 | 127.749 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.009912
1503.6 | 127.749 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1503.8 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1504 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1504.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1504.4 | 127.653 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.014467 | 0.38019 | 0.0083128
1504.6 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1504.8 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1505 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1505.2 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1505.4 | 127.8449 | 0.010554 | 0.38986 | 0.0079807 | 0.29321 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1505.6 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1505.8 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1506 | 127.8449 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1506.2 | 127.749 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1506.4 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1506.6 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1506.8 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1507 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1507.2 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | -0.48349 | 0.0083128
1507.4 | 127.749 | 0.0089549 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1507.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1507.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1508 | 127.8449 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1508.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.013089 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1508.4 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1508.6 | 127.9409 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1508.8 | 127.9409 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1509 | 127.8449 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1509.2 | 127.8449 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1509.4 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0065247 | 0.86003 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1509.6 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1509.8 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1510 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1510.2 | 127.8449 | 0.0089549 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.011511
1510.4 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1510.6 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1510.8 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1511 | 127.749 | 0.015352 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1511.2 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1511.4 | 127.9409 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1511.6 | 127.1732 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1511.8 | 126.9813 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1512 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1512.2 | 128.1329 | 0.039345 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.011324 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1512.4 | 128.2288 | 0.05054 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1512.6 | 127.8449 | 0.039345 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1512.8 | 128.0369 | 0.040944 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.38019 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1513 | 127.653 | 0.028148 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1513.2 | 127.4611 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.7737 | 0.011268 | 0.28424 | 0.0083128
1513.4 | 127.557 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1513.6 | 127.653 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1513.8 | 127.9409 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1514 | 127.653 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1514.2 | 127.749 | 0.02175 | 0.29387 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
1514.4 | 127.557 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1514.6 | 127.653 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1514.8 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1515 | 127.749 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1515.2 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1515.4 | 127.749 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1515.6 | 127.653 | 0.013753 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1515.8 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1516 | 127.749 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1516.2 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1516.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1516.6 | 127.749 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1516.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.86003 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1517 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1517.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1517.4 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1517.6 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1517.8 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1518 | 127.749 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1518.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1518.4 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1518.6 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1518.8 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1519 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1519.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1519.4 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1519.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.00647 | 0.38019 | 0.0083128
1519.8 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1520 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1520.2 | 127.749 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
1520.4 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.00647 | 0.28424 | 0.006713
1520.6 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1520.8 | 127.749 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1521 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1521.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1521.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1521.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1521.8 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1522 | 127.8449 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1522.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1522.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1522.6 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.0923 | 0.0083128
1522.8 | 127.749 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1523 | 127.8449 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1523.2 | 127.749 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1523.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1523.6 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1523.8 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1524 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1524.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1524.4 | 127.653 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1524.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1524.8 | 127.8449 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1525 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1525.2 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1525.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1525.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1525.8 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1526 | 127.653 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1526.2 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1526.4 | 127.749 | 0.0073551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.0923 | 0.006713
1526.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1526.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1527 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1527.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1527.4 | 127.749 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1527.6 | 127.653 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1527.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1528 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1528.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1528.4 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1528.6 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1528.8 | 127.8449 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1529 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1529.2 | 127.8449 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1529.4 | 127.749 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1529.6 | 127.749 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1529.8 | 127.749 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1530 | 127.8449 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1530.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1530.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1530.6 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.29321 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1530.8 | 127.749 | 0.010554 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1531 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1531.2 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1531.4 | 127.749 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1531.6 | 127.557 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1531.8 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1532 | 127.653 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1532.2 | 127.749 | 0.010554 | 0.38986 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1532.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1532.6 | 127.653 | 0.012154 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1532.8 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.47618 | 0.006713
1533 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1533.2 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1533.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1533.6 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1533.8 | 127.8449 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1534 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1534.2 | 127.749 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1534.4 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1534.6 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1534.8 | 127.749 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1535 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1535.2 | 127.749 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1535.4 | 127.749 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1535.6 | 127.749 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1535.8 | 127.653 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1536 | 127.749 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1536.2 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1536.4 | 127.749 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1536.6 | 127.749 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
1536.8 | 127.653 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1537 | 127.557 | 0.020151 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1537.2 | 128.2288 | 0.047342 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1537.4 | 127.557 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1537.6 | 127.4611 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0097238 | 0.66813 | 0.01149 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1537.8 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | -0.18663 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.011324 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1538 | 127.653 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1538.2 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 1.0616 | 0.009669 | 0.28424 | 0.0083128
1538.4 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1538.6 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1538.8 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1539 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1539.2 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.009912
1539.4 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1539.6 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1539.8 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1540 | 127.4611 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1540.2 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1540.4 | 127.557 | 0.010554 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1540.6 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1540.8 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.19722 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1541 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1541.2 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1541.4 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1541.6 | 127.4611 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.76308 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1541.8 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1542 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1542.2 | 127.557 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1542.4 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1542.6 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1542.8 | 127.4611 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1543 | 127.4611 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1543.2 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1543.4 | 127.3651 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1543.6 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1543.8 | 127.3651 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1544 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1544.2 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0022023 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1544.4 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0048701 | 0.18829 | 0.009912
1544.6 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1544.8 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1545 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1545.2 | 127.1732 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1545.4 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0018926 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1545.6 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1545.8 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1546 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.0083128
1546.2 | 127.4611 | 0.015352 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.86003 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1546.4 | 127.3651 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.28324 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1546.6 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1546.8 | 127.3651 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1547 | 127.4611 | 0.018551 | 0.48581 | 0.0063808 | 0.19722 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1547.2 | 127.4611 | 0.02175 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1547.4 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1547.6 | 127.3651 | 0.013753 | 0.48581 | 0.017577 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1547.8 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0035139
1548 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1548.2 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.7737 | 0.011268 | 0.28424 | 0.006713
1548.4 | 127.3651 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1548.6 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1548.8 | 127.3651 | 0.015352 | 0.29387 | 0.0095798 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1549 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1549.2 | 127.4611 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1549.4 | 127.3651 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1549.6 | 127.4611 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1549.8 | 127.4611 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0033264 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1550 | 127.3651 | 0.013753 | 0.38986 | 0.0047816 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1550.2 | 127.4611 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.7737 | 0.009669 | 0.28424 | 0.0083128
1550.4 | 127.4611 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.18829 | 0.006713
1550.6 | 127.3651 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.19792 | 0.0080692 | 0.28424 | 0.009912
1550.8 | 127.3651 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1551 | 127.4611 | 0.016952 | 0.29387 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1551.2 | 127.3651 | 0.015352 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.38019 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1551.4 | 127.4611 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1551.6 | 127.4611 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1551.8 | 127.2692 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1552 | 127.4611 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1552.2 | 127.4611 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1552.4 | 127.3651 | 0.020151 | 0.48581 | 0.0031824 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1552.6 | 127.4611 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1552.8 | 127.4611 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1553 | 127.4611 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1553.2 | 127.4611 | 0.018551 | 0.29387 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1553.4 | 127.4611 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1553.6 | 127.4611 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1553.8 | 127.4611 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1554 | 127.4611 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1554.2 | 127.4611 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1554.4 | 127.4611 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1554.6 | 127.557 | 0.016952 | 0.38986 | 0.0095798 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1554.8 | 127.557 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0098898 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1555 | 127.4611 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1555.2 | 127.749 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.012867 | 0.47618 | 0.0083128
1555.4 | 127.4611 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.7737 | 0.009669 | 0.28424 | 0.0083128
1555.6 | 127.557 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1555.8 | 127.4611 | 0.018551 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1556 | 127.4611 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.38019 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1556.2 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1556.4 | 127.3651 | 0.016952 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1556.6 | 127.557 | 0.016952 | 0.58176 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1556.8 | 127.557 | 0.031347 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1557 | 127.557 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.0923 | 0.0083128
1557.2 | 127.653 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1557.4 | 127.653 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1557.6 | 127.653 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1557.8 | 127.653 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1558 | 127.653 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1558.2 | 127.653 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1558.4 | 127.749 | 0.020151 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1558.6 | 127.749 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.00647 | 0.38019 | 0.0083128
1558.8 | 127.749 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1559 | 127.653 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1559.2 | 127.653 | 0.02175 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.66713 | 0.0022023 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1559.4 | 127.749 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1559.6 | 127.749 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1559.8 | 127.8449 | 0.018551 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1560 | 128.2288 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1560.2 | 128.9966 | 0.02175 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1560.4 | 128.2288 | 0.020151 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1560.6 | 128.0369 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1560.8 | 127.8449 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.57213 | 0.009912
1561 | 127.749 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1561.2 | 127.749 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1561.4 | 127.653 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1561.6 | 127.749 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1561.8 | 127.653 | 0.020151 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1562 | 127.653 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1562.2 | 127.653 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1562.4 | 127.653 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1562.6 | 127.653 | 0.02175 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1562.8 | 127.653 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.006713
1563 | 127.557 | 0.02175 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1563.2 | 127.653 | 0.020151 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1563.4 | 127.653 | 0.018551 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1563.6 | 127.653 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1563.8 | 127.653 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1564 | 127.557 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1564.2 | 127.653 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1564.4 | 127.653 | 0.018551 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1564.6 | 127.653 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1564.8 | 127.557 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1565 | 127.653 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1565.2 | 127.4611 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1565.4 | 127.557 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1565.6 | 127.653 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1565.8 | 127.653 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0018926 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1566 | 127.653 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1566.2 | 127.4611 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1566.4 | 127.557 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1566.6 | 127.653 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.29387 | 0.009669 | 0.18829 | 0.0083128
1566.8 | 127.3651 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1567 | 127.557 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1567.2 | 126.7893 | 0.028148 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.29387 | 0.0080692 | 0.28424 | 0.0083128
1567.4 | 127.653 | 0.05054 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.011324 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1567.6 | 127.557 | 0.020151 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1567.8 | 127.557 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1568 | 127.557 | 0.018551 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1568.2 | 127.557 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1568.4 | 127.4611 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1568.6 | 127.4611 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1568.8 | 127.4611 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1569 | 127.4611 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1569.2 | 127.4611 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1569.4 | 127.4611 | 0.018551 | 0.48581 | 0.0047816 | 0.29321 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1569.6 | 127.4611 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1569.8 | 127.3651 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1570 | 127.4611 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1570.2 | 127.4611 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1570.4 | 127.3651 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1570.6 | 127.4611 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1570.8 | 127.3651 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1571 | 127.4611 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1571.2 | 127.3651 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1571.4 | 127.3651 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.011511
1571.6 | 127.3651 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1571.8 | 127.3651 | 0.015352 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1572 | 127.3651 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1572.2 | 127.2692 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1572.4 | 127.3651 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1572.6 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1572.8 | 127.3651 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1573 | 127.2692 | 0.013753 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1573.2 | 127.2692 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1573.4 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1573.6 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1573.8 | 127.2692 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1574 | 127.2692 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1574.2 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1574.4 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1574.6 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1574.8 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1575 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1575.2 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1575.4 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1575.6 | 127.3651 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1575.8 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1576 | 127.2692 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1576.2 | 127.2692 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1576.4 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1576.6 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1576.8 | 127.2692 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1577 | 127.3651 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1577.2 | 127.0772 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1577.4 | 127.4611 | 0.020151 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1577.6 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0032156 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1577.8 | 127.2692 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1578 | 127.2692 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1578.2 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1578.4 | 127.2692 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1578.6 | 127.3651 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1578.8 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1579 | 127.2692 | 0.013753 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1579.2 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.011799 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1579.4 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1579.6 | 127.2692 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0035139
1579.8 | 127.2692 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1580 | 127.3651 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1580.2 | 127.2692 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1580.4 | 127.2692 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1580.6 | 127.2692 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1580.8 | 127.3651 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1581 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1581.2 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1581.4 | 127.2692 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1581.6 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1581.8 | 127.2692 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1582 | 127.2692 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1582.2 | 127.2692 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1582.4 | 127.4611 | 0.0073551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1582.6 | 127.2692 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1582.8 | 127.3651 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1583 | 127.3651 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1583.2 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1583.4 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1583.6 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1583.8 | 127.3651 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1584 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1584.2 | 127.3651 | 0.0089549 | 0.38986 | 0.0047816 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1584.4 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.38019 | 0.0083128
1584.6 | 127.4611 | 0.0089549 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1584.8 | 127.4611 | 0.010554 | 0.38986 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1585 | 127.4611 | 0.010554 | 0.29387 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.011511
1585.2 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.38019 | 0.009912
1585.4 | 127.3651 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1585.6 | 127.3651 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1585.8 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.009912
1586 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1586.2 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1586.4 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1586.6 | 127.557 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1586.8 | 127.4611 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1587 | 127.4611 | 0.024949 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1587.2 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1587.4 | 127.2692 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.33406 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1587.6 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.0080692 | 0.18829 | 0.006713
1587.8 | 127.557 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.00647 | 0.28424 | 0.0083128
1588 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.024064 | 0.28424 | 0.0083128
1588.2 | 127.4611 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1588.4 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1588.6 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.38986 | 0.009669 | 0.28424 | 0.006713
1588.8 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1589 | 127.653 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1589.2 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0032156 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1589.4 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1589.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1589.8 | 127.557 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1590 | 127.557 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.47618 | 0.0098898 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1590.2 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0048701 | 0.18829 | 0.0083128
1590.4 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.33406 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1590.6 | 127.2692 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1590.8 | 126.6933 | 0.010554 | 0.29387 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.8139 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.0923 | 0.0083128
1591 | 126.5014 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1591.2 | 127.0772 | 0.010554 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1591.4 | 127.1732 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1591.6 | 127.3651 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1591.8 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1592 | 127.4611 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.38019 | 0.0034924 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1592.2 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.18829 | 0.006713
1592.4 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1592.6 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1592.8 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1593 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1593.2 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1593.4 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1593.6 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1593.8 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1594 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1594.2 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1594.4 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1594.6 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1594.8 | 127.557 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1595 | 127.557 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1595.2 | 127.557 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1595.4 | 127.653 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1595.6 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1595.8 | 127.557 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1596 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1596.2 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1596.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1596.6 | 127.557 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1596.8 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.00647 | 0.38019 | 0.0083128
1597 | 127.557 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1597.2 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1597.4 | 127.557 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1597.6 | 127.557 | 0.012154 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1597.8 | 127.557 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1598 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1598.2 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1598.4 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1598.6 | 127.557 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1598.8 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1599 | 127.557 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1599.2 | 127.557 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1599.4 | 127.4611 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0034924 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1599.6 | 127.4611 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1599.8 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1600 | 127.653 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1600.2 | 127.4611 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.38986 | 0.0080692 | 0.28424 | 0.0083128
1600.4 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1600.6 | 127.557 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1600.8 | 127.557 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1601 | 127.557 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1601.2 | 127.3651 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1601.4 | 127.653 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1601.6 | 127.653 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1601.8 | 127.3651 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1602 | 128.1329 | 0.045742 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1602.2 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0097238 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1602.4 | 127.2692 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1602.6 | 126.8853 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.8139 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1602.8 | 127.4611 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.012923 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1603 | 127.3651 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.01149 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1603.2 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.011324 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1603.4 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.86003 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1603.6 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1603.8 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1604 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1604.2 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1604.4 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1604.6 | 127.3651 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
1604.8 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1605 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.38019 | 0.0083128
1605.2 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1605.4 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1605.6 | 127.3651 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1605.8 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1606 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1606.2 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1606.4 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0038022 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1606.6 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1606.8 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1607 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1607.2 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1607.4 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1607.6 | 127.2692 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1607.8 | 127.2692 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1608 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1608.2 | 127.2692 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1608.4 | 127.3651 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1608.6 | 127.2692 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1608.8 | 127.3651 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1609 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1609.2 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1609.4 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.38019 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1609.6 | 127.2692 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1609.8 | 127.2692 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1610 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1610.2 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1610.4 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1610.6 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1610.8 | 127.3651 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1611 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0034924 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1611.2 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1611.4 | 127.3651 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1611.6 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1611.8 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1612 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1612.2 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1612.4 | 127.2692 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1612.6 | 127.2692 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1612.8 | 127.1732 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1613 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1613.2 | 127.2692 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1613.4 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1613.6 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1613.8 | 127.2692 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1614 | 127.2692 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1614.2 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1614.4 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1614.6 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1614.8 | 127.2692 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1615 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.47618 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1615.2 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1615.4 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1615.6 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1615.8 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1616 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1616.2 | 127.2692 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1616.4 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1616.6 | 127.3651 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1616.8 | 127.3651 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1617 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1617.2 | 127.2692 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1617.4 | 125.9256 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1617.6 | 125.8296 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1617.8 | 126.5014 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.43001 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1618 | 127.0772 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1618.2 | 127.0772 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1618.4 | 127.1732 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1618.6 | 127.1732 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0032156 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1618.8 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1619 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1619.2 | 127.1732 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1619.4 | 127.1732 | 0.013753 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.7737 | 0.009669 | 0.28424 | 0.0083128
1619.6 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1619.8 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1620 | 127.1732 | 0.013753 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1620.2 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1620.4 | 127.1732 | 0.013753 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1620.6 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1620.8 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1621 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.0923 | 0.0083128
1621.2 | 127.1732 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1621.4 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1621.6 | 127.1732 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1621.8 | 127.0772 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1622 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1622.2 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1622.4 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1622.6 | 127.1732 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.38019 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1622.8 | 127.1732 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1623 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1623.2 | 127.1732 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1623.4 | 127.1732 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.43001 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1623.6 | 127.0772 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1623.8 | 127.1732 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.66713 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.0048701 | 0.28424 | 0.0083128
1624 | 126.9813 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1624.2 | 127.0772 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1624.4 | 127.1732 | 0.015352 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1624.6 | 127.0772 | 0.013753 | 0.38986 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.28424 | 0.0083128
1624.8 | 127.1732 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1625 | 127.0772 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.7737 | 0.009669 | 0.38019 | 0.009912
1625.2 | 127.0772 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1625.4 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1625.6 | 127.0772 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1625.8 | 127.1732 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.0923 | 0.0083128
1626 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1626.2 | 127.1732 | 0.016952 | 0.38986 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1626.4 | 127.1732 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1626.6 | 126.9813 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1626.8 | 127.0772 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1627 | 127.1732 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1627.2 | 127.1732 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1627.4 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1627.6 | 127.1732 | 0.015352 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1627.8 | 127.1732 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1628 | 127.1732 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1628.2 | 127.0772 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1628.4 | 127.1732 | 0.016952 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1628.6 | 126.9813 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1628.8 | 127.0772 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1629 | 127.0772 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1629.2 | 127.0772 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1629.4 | 127.1732 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.0083128
1629.6 | 127.0772 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1629.8 | 127.0772 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1630 | 127.0772 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1630.2 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1630.4 | 127.0772 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1630.6 | 127.0772 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1630.8 | 127.0772 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1631 | 127.0772 | 0.016952 | 0.38986 | 0.0015826 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1631.2 | 127.1732 | 0.018551 | 0.58176 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1631.4 | 127.1732 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1631.6 | 127.2692 | 0.028148 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1631.8 | 126.8853 | 0.013753 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1632 | 127.557 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1632.2 | 127.0772 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
1632.4 | 127.0772 | 0.016952 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1632.6 | 127.0772 | 0.015352 | 0.48581 | 0.0063808 | 0.67705 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1632.8 | 127.1732 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1633 | 127.1732 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1633.2 | 127.0772 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1633.4 | 127.0772 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.006713
1633.6 | 127.1732 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1633.8 | 127.0772 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.76308 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1634 | 127.0772 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1634.2 | 127.1732 | 0.015352 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1634.4 | 127.0772 | 0.020151 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1634.6 | 127.0772 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1634.8 | 127.0772 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1635 | 127.0772 | 0.018551 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1635.2 | 127.0772 | 0.018551 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1635.4 | 127.0772 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1635.6 | 127.0772 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1635.8 | 127.0772 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1636 | 127.0772 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1636.2 | 127.0772 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1636.4 | 127.0772 | 0.016952 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1636.6 | 127.0772 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1636.8 | 127.1732 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1637 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
1637.2 | 127.1732 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1637.4 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.67705 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1637.6 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1637.8 | 127.1732 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1638 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1638.2 | 127.0772 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1638.4 | 127.1732 | 0.020151 | 0.38986 | 0.0047816 | 0.5811 | 0.0032156 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1638.6 | 127.1732 | 0.018551 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1638.8 | 127.1732 | 0.020151 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1639 | 127.1732 | 0.02175 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1639.2 | 127.1732 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1639.4 | 127.1732 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1639.6 | 127.1732 | 0.020151 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1639.8 | 127.1732 | 0.020151 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1640 | 127.2692 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.009912
1640.2 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1640.4 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1640.6 | 127.1732 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1640.8 | 127.1732 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0048701 | 0.28424 | 0.0083128
1641 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1641.2 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1641.4 | 127.1732 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1641.6 | 127.2692 | 0.02175 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1641.8 | 127.2692 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1642 | 127.2692 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1642.2 | 127.1732 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1642.4 | 127.2692 | 0.020151 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1642.6 | 127.1732 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1642.8 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1643 | 127.1732 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1643.2 | 127.2692 | 0.020151 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1643.4 | 127.2692 | 0.02175 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1643.6 | 127.2692 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1643.8 | 127.2692 | 0.02175 | 0.38986 | 0.0095798 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1644 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1644.2 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1644.4 | 127.2692 | 0.020151 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1644.6 | 127.2692 | 0.02175 | 0.38986 | 0.0079807 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1644.8 | 127.2692 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1645 | 127.3651 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1645.2 | 127.3651 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1645.4 | 127.3651 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.37923 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1645.6 | 127.3651 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1645.8 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
1646 | 127.2692 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1646.2 | 126.9813 | 0.029748 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1646.4 | 127.557 | 0.045742 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1646.6 | 127.3651 | 0.02175 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1646.8 | 127.2692 | 0.02175 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1647 | 127.3651 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1647.2 | 127.3651 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1647.4 | 127.3651 | 0.02175 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0038022 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1647.6 | 127.4611 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1647.8 | 127.3651 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1648 | 127.4611 | 0.02175 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1648.2 | 127.3651 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1648.4 | 127.4611 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1648.6 | 127.557 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1648.8 | 127.557 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1649 | 127.8449 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1649.2 | 128.6127 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1649.4 | 128.3248 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1649.6 | 127.749 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1649.8 | 127.653 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1650 | 127.557 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1650.2 | 127.4611 | 0.02175 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1650.4 | 127.4611 | 0.02175 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1650.6 | 127.4611 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1650.8 | 127.4611 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1651 | 127.4611 | 0.02175 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1651.2 | 127.4611 | 0.02335 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1651.4 | 127.3651 | 0.02335 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1651.6 | 127.4611 | 0.02335 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1651.8 | 127.4611 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1652 | 127.4611 | 0.02175 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1652.2 | 127.4611 | 0.02335 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1652.4 | 127.4611 | 0.02335 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1652.6 | 127.4611 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1652.8 | 127.4611 | 0.02175 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1653 | 127.4611 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1653.2 | 127.4611 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1653.4 | 127.4611 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1653.6 | 127.3651 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1653.8 | 127.3651 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1654 | 127.4611 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1654.2 | 127.3651 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1654.4 | 127.4611 | 0.02175 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1654.6 | 127.2692 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1654.8 | 127.3651 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1655 | 127.3651 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1655.2 | 127.3651 | 0.028148 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1655.4 | 127.1732 | 0.036146 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1655.6 | 127.3651 | 0.036146 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.526 | 0.011324 | 0.66813 | 0.0082906 | 0.67775 | 0.00647 | 0.28424 | 0.0083128
1655.8 | 127.2692 | 0.02175 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1656 | 127.3651 | 0.02335 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1656.2 | 127.2692 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.013111
1656.4 | 127.3651 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1656.6 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.0923 | 0.0083128
1656.8 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1657 | 127.2692 | 0.02335 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1657.2 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1657.4 | 127.2692 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1657.6 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1657.8 | 127.3651 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1658 | 127.2692 | 0.020151 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0051138
1658.2 | 127.2692 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1658.4 | 127.2692 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1658.6 | 127.2692 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0035139
1658.8 | 127.2692 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1659 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1659.2 | 127.2692 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1659.4 | 127.2692 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1659.6 | 127.2692 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1659.8 | 127.1732 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1660 | 127.1732 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1660.2 | 127.1732 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1660.4 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1660.6 | 127.0772 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1660.8 | 127.1732 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1661 | 127.0772 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1661.2 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1661.4 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1661.6 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1661.8 | 127.0772 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1662 | 127.1732 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1662.2 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1662.4 | 127.1732 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1662.6 | 127.0772 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1662.8 | 127.0772 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1663 | 127.0772 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1663.2 | 127.1732 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1663.4 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1663.6 | 127.0772 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1663.8 | 127.1732 | 0.016952 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1664 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1664.2 | 127.1732 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.38019 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1664.4 | 127.1732 | 0.026549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1664.6 | 127.0772 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1664.8 | 127.1732 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1665 | 127.1732 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1665.2 | 127.1732 | 0.013753 | 0.48581 | 0.0079807 | 0.19722 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1665.4 | 127.1732 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1665.6 | 127.1732 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1665.8 | 127.1732 | 0.015352 | 0.48581 | 0.0047816 | 0.67705 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1666 | 127.1732 | 0.015352 | 0.48581 | 0.0095798 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1666.2 | 127.1732 | 0.013753 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1666.4 | 127.2692 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1666.6 | 127.1732 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1666.8 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1667 | 127.0772 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1667.2 | 127.1732 | 0.012154 | 0.48581 | 0.0063808 | 0.19722 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1667.4 | 127.1732 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.0083128
1667.6 | 127.1732 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1667.8 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1668 | 127.0772 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.28324 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1668.2 | 127.1732 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0102 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1668.4 | 127.1732 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.47618 | 0.009912
1668.6 | 127.1732 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1668.8 | 127.2692 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1669 | 127.2692 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1669.2 | 127.2692 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1669.4 | 127.2692 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1669.6 | 127.0772 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1669.8 | 127.2692 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1670 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1670.2 | 127.2692 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1670.4 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1670.6 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1670.8 | 127.2692 | 0.012154 | 0.38986 | 0.0079807 | 0.67705 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0034924 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1671 | 127.2692 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1671.2 | 127.2692 | 0.010554 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1671.4 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0033264 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1671.6 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1671.8 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0035139
1672 | 127.3651 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1672.2 | 127.2692 | 0.016952 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1672.4 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1672.6 | 127.653 | 0.029748 | 0.38986 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1672.8 | 126.9813 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1673 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1673.2 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.012867 | 0.28424 | 0.0083128
1673.4 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1673.6 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1673.8 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1674 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1674.2 | 127.3651 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1674.4 | 127.3651 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.67775 | 0.00647 | 0.38019 | 0.0083128
1674.6 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1674.8 | 127.3651 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1675 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1675.2 | 127.3651 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1675.4 | 127.2692 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1675.6 | 126.8853 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1675.8 | 126.1175 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1676 | 126.6933 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1676.2 | 127.1732 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1676.4 | 127.2692 | 0.010554 | 0.67775 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.011511
1676.6 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1676.8 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1677 | 127.4611 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1677.2 | 127.4611 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1677.4 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1677.6 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1677.8 | 127.3651 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1678 | 127.4611 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1678.2 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1678.4 | 127.4611 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1678.6 | 127.4611 | 0.010554 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1678.8 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1679 | 127.3651 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.00647 | 0.28424 | 0.0083128
1679.2 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1679.4 | 127.557 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1679.6 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1679.8 | 127.557 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1680 | 127.4611 | 0.012154 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1680.2 | 127.4611 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1680.4 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1680.6 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1680.8 | 127.4611 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1681 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1681.2 | 127.4611 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1681.4 | 127.4611 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0051138
1681.6 | 127.3651 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1681.8 | 127.3651 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1682 | 127.4611 | 0.016952 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1682.2 | 127.557 | 0.026549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1682.4 | 127.2692 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.38019 | 0.0083128
1682.6 | 127.0772 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1682.8 | 126.7893 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1683 | 127.3651 | 0.012154 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1683.2 | 127.2692 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1683.4 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1683.6 | 127.2692 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1683.8 | 127.1732 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1684 | 127.3651 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1684.2 | 127.3651 | 0.012154 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1684.4 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1684.6 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
1684.8 | 127.3651 | 0.012154 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1685 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1685.2 | 127.2692 | 0.013753 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1685.4 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1685.6 | 127.2692 | 0.015352 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1685.8 | 127.2692 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1686 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1686.2 | 127.2692 | 0.013753 | 0.38986 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1686.4 | 127.2692 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1686.6 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.5811 | 0.0048148 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1686.8 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1687 | 127.2692 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.38019 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1687.2 | 127.3651 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1687.4 | 127.2692 | 0.016952 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1687.6 | 127.2692 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1687.8 | 127.2692 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1688 | 127.2692 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1688.2 | 127.1732 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1688.4 | 127.2692 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1688.6 | 127.2692 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1688.8 | 127.2692 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.0083128
1689 | 127.2692 | 0.015352 | 0.48581 | 0.0063808 | 0.67705 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1689.2 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0048701 | 0.28424 | 0.009912
1689.4 | 127.1732 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.33406 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1689.6 | 127.2692 | 0.013753 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1689.8 | 127.2692 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1690 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1690.2 | 127.2692 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1690.4 | 127.2692 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1690.6 | 127.2692 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1690.8 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1691 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1691.2 | 127.2692 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1691.4 | 127.1732 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1691.6 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1691.8 | 127.0772 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1692 | 126.9813 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0018926 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1692.2 | 127.1732 | 0.018551 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1692.4 | 127.1732 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1692.6 | 127.1732 | 0.018551 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1692.8 | 127.0772 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1693 | 127.1732 | 0.015352 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.76308 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1693.2 | 126.8853 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1693.4 | 127.0772 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1693.6 | 127.2692 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1693.8 | 126.9813 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1694 | 127.1732 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1694.2 | 127.1732 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1694.4 | 127.1732 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1694.6 | 127.1732 | 0.018551 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.33406 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1694.8 | 127.1732 | 0.018551 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1695 | 127.1732 | 0.018551 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1695.2 | 127.0772 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1695.4 | 127.1732 | 0.020151 | 0.38986 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1695.6 | 127.0772 | 0.018551 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1695.8 | 127.2692 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1696 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1696.2 | 127.1732 | 0.020151 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1696.4 | 127.1732 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1696.6 | 127.1732 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1696.8 | 127.1732 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1697 | 127.1732 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1697.2 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0033264 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1697.4 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1697.6 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
1697.8 | 127.1732 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1698 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1698.2 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1698.4 | 127.1732 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.012867 | 0.28424 | 0.0083128
1698.6 | 127.2692 | 0.020151 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1698.8 | 127.1732 | 0.020151 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1699 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1699.2 | 127.1732 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1699.4 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1699.6 | 127.1732 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1699.8 | 127.2692 | 0.02335 | 0.38986 | 0.0063808 | 0.38916 | 0.0048148 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1700 | 127.1732 | 0.02175 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1700.2 | 127.2692 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1700.4 | 127.2692 | 0.02175 | 0.48581 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1700.6 | 127.2692 | 0.02335 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1700.8 | 127.2692 | 0.02335 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1701 | 127.2692 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1701.2 | 127.1732 | 0.02175 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1701.4 | 127.2692 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1701.6 | 127.2692 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1701.8 | 127.3651 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1702 | 127.2692 | 0.02175 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1702.2 | 127.1732 | 0.02175 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1702.4 | 127.2692 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1702.6 | 127.2692 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1702.8 | 127.2692 | 0.02175 | 0.29387 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1703 | 127.2692 | 0.02335 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1703.2 | 127.1732 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1703.4 | 127.3651 | 0.02175 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1703.6 | 127.3651 | 0.02175 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1703.8 | 127.3651 | 0.02335 | 0.48581 | 0.0031824 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1704 | 127.3651 | 0.02335 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1704.2 | 127.2692 | 0.024949 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1704.4 | 127.3651 | 0.024949 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1704.6 | 127.3651 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.012867 | 0.38019 | 0.0083128
1704.8 | 127.3651 | 0.018551 | 0.48581 | 0.0031824 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1705 | 127.2692 | 0.018551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1705.2 | 127.3651 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0102 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1705.4 | 127.0772 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.013111
1705.6 | 127.557 | 0.040944 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1705.8 | 127.4611 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1706 | 127.3651 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1706.2 | 127.4611 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1706.4 | 127.4611 | 0.024949 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1706.6 | 127.557 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1706.8 | 127.4611 | 0.02335 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1707 | 127.4611 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1707.2 | 127.4611 | 0.02335 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1707.4 | 127.4611 | 0.024949 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1707.6 | 127.4611 | 0.024949 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1707.8 | 127.557 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1708 | 127.557 | 0.024949 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1708.2 | 127.9409 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1708.4 | 128.9966 | 0.02335 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1708.6 | 128.1329 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1708.8 | 127.8449 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1709 | 127.8449 | 0.024949 | 0.48581 | 0.0047816 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1709.2 | 127.749 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1709.4 | 127.653 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1709.6 | 127.653 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1709.8 | 127.653 | 0.02335 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
1710 | 127.653 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1710.2 | 127.653 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1710.4 | 127.653 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1710.6 | 127.653 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1710.8 | 127.653 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1711 | 127.653 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1711.2 | 127.653 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1711.4 | 127.557 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1711.6 | 127.557 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1711.8 | 127.749 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.28324 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1712 | 127.4611 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1712.2 | 127.557 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1712.4 | 127.557 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1712.6 | 127.653 | 0.02335 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0035139
1712.8 | 127.557 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1713 | 127.557 | 0.018551 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.43001 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1713.2 | 127.557 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1713.4 | 127.557 | 0.026549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1713.6 | 127.653 | 0.056938 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1713.8 | 127.4611 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1714 | 127.4611 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0018926 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1714.2 | 127.4611 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.012867 | 0.28424 | 0.0083128
1714.4 | 127.4611 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1714.6 | 127.4611 | 0.02335 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1714.8 | 127.4611 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1715 | 127.4611 | 0.02335 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1715.2 | 127.4611 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1715.4 | 127.3651 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1715.6 | 127.4611 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.006713
1715.8 | 127.3651 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.18829 | 0.0083128
1716 | 127.3651 | 0.02175 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1716.2 | 127.3651 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1716.4 | 127.3651 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1716.6 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1716.8 | 127.3651 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1717 | 127.3651 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1717.2 | 127.2692 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1717.4 | 127.3651 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1717.6 | 127.3651 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1717.8 | 127.2692 | 0.02175 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1718 | 127.2692 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1718.2 | 127.2692 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1718.4 | 127.2692 | 0.020151 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1718.6 | 127.2692 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.33406 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1718.8 | 127.1732 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1719 | 127.2692 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.7737 | 0.011268 | 0.28424 | 0.0083128
1719.2 | 127.1732 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.29387 | 0.0080692 | 0.28424 | 0.0083128
1719.4 | 127.2692 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.009912
1719.6 | 127.2692 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1719.8 | 127.2692 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1720 | 127.3651 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1720.2 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1720.4 | 127.2692 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1720.6 | 127.2692 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1720.8 | 127.2692 | 0.018551 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1721 | 127.2692 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1721.2 | 127.2692 | 0.015352 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1721.4 | 127.2692 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1721.6 | 127.2692 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1721.8 | 127.3651 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1722 | 127.2692 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0018926 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1722.2 | 127.3651 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1722.4 | 127.3651 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1722.6 | 127.2692 | 0.016952 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0033264 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1722.8 | 127.2692 | 0.015352 | 0.38986 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1723 | 127.2692 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1723.2 | 127.3651 | 0.015352 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1723.4 | 127.2692 | 0.015352 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1723.6 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1723.8 | 127.2692 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1724 | 127.2692 | 0.015352 | 0.38986 | 0.0063808 | 0.38916 | 0.0032156 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1724.2 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1724.4 | 127.3651 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1724.6 | 127.3651 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.7737 | 0.009669 | 0.28424 | 0.0083128
1724.8 | 127.4611 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1725 | 127.4611 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1725.2 | 127.4611 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1725.4 | 127.3651 | 0.015352 | 0.48581 | 0.0063808 | 0.19722 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1725.6 | 127.4611 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1725.8 | 127.3651 | 0.018551 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1726 | 127.4611 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1726.2 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1726.4 | 127.557 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1726.6 | 127.557 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1726.8 | 127.557 | 0.024949 | 0.58176 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1727 | 127.749 | 0.032947 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0035139
1727.2 | 127.1732 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1727.4 | 127.557 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1727.6 | 127.557 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1727.8 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.0080692 | 0.18829 | 0.0083128
1728 | 127.557 | 0.012154 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1728.2 | 127.557 | 0.013753 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1728.4 | 127.557 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1728.6 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1728.8 | 127.557 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1729 | 127.557 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1729.2 | 127.4611 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1729.4 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.38019 | 0.0083128
1729.6 | 126.8853 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1729.8 | 126.4054 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1730 | 127.1732 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1730.2 | 127.3651 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1730.4 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1730.6 | 127.4611 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1730.8 | 127.557 | 0.013753 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1731 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1731.2 | 127.653 | 0.013753 | 0.38986 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.00647 | 0.47618 | 0.0083128
1731.4 | 127.4611 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1731.6 | 127.557 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1731.8 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1732 | 127.557 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1732.2 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1732.4 | 127.653 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1732.6 | 127.653 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1732.8 | 127.557 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1733 | 127.653 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1733.2 | 127.557 | 0.013753 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1733.4 | 127.557 | 0.015352 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1733.6 | 127.557 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1733.8 | 127.557 | 0.016952 | 0.48581 | 0.0063808 | 0.67705 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1734 | 127.557 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0038022 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1734.2 | 127.557 | 0.016952 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1734.4 | 127.557 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1734.6 | 127.4611 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1734.8 | 127.557 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1735 | 127.653 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1735.2 | 127.557 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1735.4 | 127.749 | 0.028148 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1735.6 | 127.557 | 0.036146 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1735.8 | 127.4611 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.011324 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1736 | 126.9813 | 0.013753 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1736.2 | 127.557 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1736.4 | 127.557 | 0.015352 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
1736.6 | 127.557 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.47618 | 0.009912
1736.8 | 127.557 | 0.015352 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1737 | 127.4611 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1737.2 | 127.4611 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1737.4 | 127.557 | 0.016952 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1737.6 | 127.4611 | 0.016952 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.47618 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1737.8 | 127.4611 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1738 | 127.4611 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1738.2 | 127.4611 | 0.016952 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1738.4 | 127.4611 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.7737 | 0.011268 | 0.38019 | 0.009912
1738.6 | 127.3651 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1738.8 | 127.4611 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.7737 | 0.011268 | 0.28424 | 0.009912
1739 | 127.3651 | 0.020151 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1739.2 | 127.4611 | 0.018551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1739.4 | 127.4611 | 0.016952 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.43001 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1739.6 | 127.3651 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1739.8 | 127.3651 | 0.018551 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1740 | 127.3651 | 0.020151 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1740.2 | 127.3651 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0051138
1740.4 | 127.3651 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1740.6 | 127.3651 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.18829 | 0.0083128
1740.8 | 127.3651 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1741 | 127.3651 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1741.2 | 127.3651 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1741.4 | 127.3651 | 0.02175 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0038022 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1741.6 | 127.2692 | 0.020151 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1741.8 | 127.1732 | 0.020151 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1742 | 127.2692 | 0.02175 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1742.2 | 127.2692 | 0.02175 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1742.4 | 127.2692 | 0.02175 | 0.29387 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1742.6 | 127.2692 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0033264 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1742.8 | 127.2692 | 0.02335 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1743 | 127.2692 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1743.2 | 127.2692 | 0.02175 | 0.38986 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1743.4 | 127.2692 | 0.02335 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1743.6 | 127.2692 | 0.02175 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1743.8 | 127.2692 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1744 | 127.3651 | 0.028148 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1744.2 | 127.2692 | 0.026549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1744.4 | 127.1732 | 0.02335 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1744.6 | 127.2692 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1744.8 | 127.2692 | 0.024949 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.43001 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1745 | 127.2692 | 0.024949 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1745.2 | 127.2692 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1745.4 | 127.2692 | 0.02335 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1745.6 | 127.2692 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0038022 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1745.8 | 127.2692 | 0.02335 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1746 | 127.2692 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1746.2 | 127.2692 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1746.4 | 127.0772 | 0.02335 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1746.6 | 127.3651 | 0.02335 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1746.8 | 127.2692 | 0.026549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.0923 | 0.006713
1747 | 127.2692 | 0.026549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1747.2 | 127.3651 | 0.026549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1747.4 | 127.3651 | 0.026549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1747.6 | 127.3651 | 0.026549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1747.8 | 127.3651 | 0.028148 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1748 | 127.3651 | 0.029748 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1748.2 | 127.3651 | 0.028148 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1748.4 | 127.3651 | 0.028148 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1748.6 | 127.3651 | 0.028148 | 0.38986 | 0.0063808 | 0.5811 | 0.0048148 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1748.8 | 127.3651 | 0.029748 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1749 | 127.3651 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1749.2 | 127.3651 | 0.029748 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1749.4 | 127.3651 | 0.028148 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1749.6 | 127.4611 | 0.028148 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1749.8 | 127.4611 | 0.028148 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1750 | 127.3651 | 0.028148 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1750.2 | 127.4611 | 0.028148 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1750.4 | 127.4611 | 0.029748 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1750.6 | 127.3651 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1750.8 | 127.4611 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1751 | 127.4611 | 0.028148 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1751.2 | 127.4611 | 0.028148 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1751.4 | 127.4611 | 0.028148 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1751.6 | 127.4611 | 0.031347 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1751.8 | 127.4611 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1752 | 127.2692 | 0.031347 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1752.2 | 127.557 | 0.029748 | 0.38986 | 0.0063808 | 0.29321 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1752.4 | 127.4611 | 0.028148 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1752.6 | 127.557 | 0.028148 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1752.8 | 127.557 | 0.026549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1753 | 127.557 | 0.026549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1753.2 | 127.653 | 0.031347 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1753.4 | 127.4611 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1753.6 | 127.557 | 0.047342 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1753.8 | 127.3651 | 0.037745 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1754 | 127.557 | 0.032947 | 0.38986 | 0.0063808 | 0.48515 | 0.0032156 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1754.2 | 127.557 | 0.031347 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1754.4 | 127.557 | 0.031347 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1754.6 | 127.653 | 0.031347 | 0.38986 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1754.8 | 127.653 | 0.031347 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1755 | 127.557 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.006713
1755.2 | 127.557 | 0.032947 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.18829 | 0.0083128
1755.4 | 127.653 | 0.031347 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1755.6 | 127.653 | 0.031347 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1755.8 | 127.653 | 0.032947 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1756 | 127.557 | 0.029748 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1756.2 | 127.653 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1756.4 | 127.653 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1756.6 | 127.653 | 0.032947 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1756.8 | 127.749 | 0.032947 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1757 | 127.749 | 0.032947 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1757.2 | 127.9409 | 0.032947 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1757.4 | 128.5167 | 0.031347 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1757.6 | 129.0925 | 0.031347 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1757.8 | 128.7087 | 0.034546 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1758 | 128.0369 | 0.031347 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1758.2 | 127.9409 | 0.031347 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1758.4 | 127.9409 | 0.029748 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1758.6 | 127.749 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.009912
1758.8 | 127.749 | 0.032947 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1759 | 127.749 | 0.032947 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1759.2 | 127.557 | 0.032947 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.38019 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1759.4 | 127.653 | 0.034546 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1759.6 | 127.653 | 0.034546 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1759.8 | 127.653 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1760 | 127.557 | 0.034546 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1760.2 | 127.557 | 0.032947 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.57213 | 0.009912
1760.4 | 127.653 | 0.034546 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1760.6 | 127.653 | 0.034546 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.012867 | 0.38019 | 0.009912
1760.8 | 127.557 | 0.037745 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1761 | 127.557 | 0.034546 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1761.2 | 127.557 | 0.034546 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1761.4 | 127.557 | 0.034546 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1761.6 | 127.557 | 0.034546 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1761.8 | 127.653 | 0.036146 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1762 | 127.653 | 0.036146 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1762.2 | 127.557 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1762.4 | 127.557 | 0.032947 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1762.6 | 127.653 | 0.034546 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1762.8 | 127.653 | 0.034546 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.43001 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1763 | 127.557 | 0.034546 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1763.2 | 127.557 | 0.034546 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.18829 | 0.0083128
1763.4 | 127.653 | 0.034546 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1763.6 | 127.557 | 0.034546 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1763.8 | 127.4611 | 0.036146 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1764 | 126.1175 | 0.1801 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1764.2 | 125.8296 | 0.22488 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1764.4 | 125.6377 | 0.23608 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1764.6 | 125.5418 | 0.25687 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1764.8 | 125.3498 | 0.26487 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1765 | 124.87 | 0.26007 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1765.2 | 125.4458 | 0.32565 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.012923 | 0.76408 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1765.4 | 125.1579 | 0.29686 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0097238 | 0.76408 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1765.6 | 124.9659 | 0.30805 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0097238 | 0.86003 | 0.013089 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1765.8 | 124.87 | 0.32725 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 1.052 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1766 | 124.678 | 0.33524 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 1.148 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1766.2 | 124.582 | 0.34804 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 1.2439 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1766.4 | 124.4861 | 0.35764 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 1.148 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1766.6 | 124.3901 | 0.36083 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 1.2439 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1766.8 | 124.3901 | 0.36883 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0054014 | 0.526 | 0.0065247 | 1.2439 | 0.01149 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1767 | 124.2942 | 0.37683 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 1.148 | 0.01149 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1767.2 | 124.1982 | 0.38323 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 1.2439 | 0.01149 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1767.4 | 124.1022 | 0.38962 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 1.2439 | 0.013089 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1767.6 | 124.0063 | 0.39762 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 1.148 | 0.014688 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1767.8 | 123.9103 | 0.40402 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 1.148 | 0.014688 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1768 | 123.9103 | 0.41042 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 1.2439 | 0.016288 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1768.2 | 123.8143 | 0.41682 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 1.2439 | 0.016288 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1768.4 | 123.7184 | 0.42321 | 0.48581 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 1.2439 | 0.017887 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1768.6 | 123.6224 | 0.43121 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 1.3399 | 0.016288 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1768.8 | 123.5264 | 0.43601 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 1.4359 | 0.016288 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1769 | 123.5264 | 0.44241 | 0.58176 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 1.3399 | 0.016288 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1769.2 | 123.4305 | 0.4504 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 1.3399 | 0.016288 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1769.4 | 123.4305 | 0.4536 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 1.2439 | 0.016288 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1769.6 | 123.3345 | 0.46 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 1.2439 | 0.017887 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1769.8 | 123.2385 | 0.4648 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 1.2439 | 0.016288 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1770 | 123.1425 | 0.4712 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 1.3399 | 0.016288 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1770.2 | 123.2385 | 0.47759 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 1.3399 | 0.016288 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1770.4 | 123.1425 | 0.48399 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 1.3399 | 0.016288 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1770.6 | 123.0466 | 0.48879 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 1.3399 | 0.017887 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1770.8 | 122.9506 | 0.49359 | 0.29387 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 1.3399 | 0.016288 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1771 | 122.9506 | 0.49999 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 1.3399 | 0.017887 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1771.2 | 122.8546 | 0.50638 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 1.3399 | 0.017887 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1771.4 | 122.7587 | 0.51278 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 1.3399 | 0.016288 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1771.6 | 122.7587 | 0.51758 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 1.3399 | 0.017887 | 0.5818 | 0.0048701 | 0.28424 | 0.006713
1771.8 | 122.6627 | 0.52558 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 1.3399 | 0.017887 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1772 | 122.5668 | 0.53358 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 1.2439 | 0.019487 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1772.2 | 122.4708 | 0.53997 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 1.4359 | 0.017887 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1772.4 | 122.3748 | 0.54637 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 1.3399 | 0.017887 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1772.6 | 122.3748 | 0.55117 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 1.3399 | 0.017887 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1772.8 | 122.2789 | 0.55597 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 1.4359 | 0.019487 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1773 | 122.3748 | 0.56077 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 1.4359 | 0.017887 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1773.2 | 122.2789 | 0.56556 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 1.3399 | 0.016288 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1773.4 | 122.0869 | 0.57036 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 1.4359 | 0.017887 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1773.6 | 122.0869 | 0.57356 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 1.4359 | 0.017887 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1773.8 | 121.991 | 0.57996 | 0.38986 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 1.4359 | 0.017887 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1774 | 122.0869 | 0.58476 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 1.4359 | 0.019487 | 0.48581 | 0.00647 | 0.28424 | 0.0083128
1774.2 | 121.991 | 0.58796 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 1.4359 | 0.019487 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1774.4 | 121.991 | 0.59435 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 1.4359 | 0.019487 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1774.6 | 121.895 | 0.59755 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0038022 | 0.71795 | 0.0065247 | 1.4359 | 0.019487 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1774.8 | 121.895 | 0.60395 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0081246 | 1.3399 | 0.019487 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1775 | 121.799 | 0.60555 | 0.38986 | 0.0095798 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.8139 | 0.0049255 | 1.3399 | 0.019487 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1775.2 | 121.703 | 0.61355 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 1.3399 | 0.019487 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1775.4 | 121.6071 | 0.61675 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 1.3399 | 0.017887 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1775.6 | 121.6071 | 0.62474 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0081246 | 1.3399 | 0.019487 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1775.8 | 121.6071 | 0.63754 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 1.4359 | 0.019487 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1776 | 121.2232 | 0.63434 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 1.4359 | 0.017887 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1776.2 | 121.6071 | 0.63594 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 1.3399 | 0.017887 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1776.4 | 121.5111 | 0.64074 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 1.4359 | 0.019487 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1776.6 | 121.4151 | 0.64554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.8139 | 0.0049255 | 1.3399 | 0.021086 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1776.8 | 121.4151 | 0.64874 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 0.28424 | 0.021086 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1777 | 121.4151 | 0.65353 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 1.4359 | 0.021086 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1777.2 | 121.3192 | 0.65833 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.8139 | 0.0065247 | 1.4359 | 0.019487 | 0.5818 | 0.009669 | -0.099642 | 0.0083128
1777.4 | 121.3192 | 0.66153 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.0049255 | 1.4359 | 0.019487 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1777.6 | 121.3192 | 0.66793 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 1.5318 | 0.019487 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1777.8 | 121.2232 | 0.67113 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 1.4359 | 0.019487 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1778 | 121.2232 | 0.67593 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 1.4359 | 0.019487 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1778.2 | 121.1273 | 0.68073 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 1.4359 | 0.019487 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1778.4 | 121.0313 | 0.68552 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.0081246 | 1.5318 | 0.021086 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1778.6 | 121.0313 | 0.68872 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 1.4359 | 0.019487 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
1778.8 | 121.0313 | 0.69192 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.8139 | 0.0065247 | 1.4359 | 0.019487 | 0.48581 | 0.012867 | 0.38019 | 0.0083128
1779 | 120.9353 | 0.69832 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 0.8139 | 0.0065247 | 1.5318 | 0.021086 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1779.2 | 120.8394 | 0.70312 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 1.5318 | 0.021086 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1779.4 | 120.9353 | 0.70632 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 1.4359 | 0.022685 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1779.6 | 120.7434 | 0.71111 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 1.5318 | 0.021086 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1779.8 | 120.8394 | 0.71591 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.8139 | 0.0065247 | 1.5318 | 0.022685 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1780 | 120.7434 | 0.71911 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.8139 | 0.0081246 | 1.5318 | 0.025884 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1780.2 | 120.7434 | 0.72391 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 1.5318 | 0.021086 | 0.5818 | 0.0080692 | 0.18829 | 0.006713
1780.4 | 120.6474 | 0.72711 | 0.48581 | 0.0047816 | 0.67705 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.0097238 | 1.3399 | 0.021086 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1780.6 | 120.6474 | 0.73031 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.8139 | 0.0081246 | 1.5318 | 0.021086 | 0.67775 | 0.0080692 | 0.28424 | 0.006713
1780.8 | 120.6474 | 0.73511 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.8139 | 0.0065247 | 1.5318 | 0.021086 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1781 | 120.6474 | 0.7415 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 1.5318 | 0.022685 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1781.2 | 120.5514 | 0.7431 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.8139 | 0.0065247 | 1.5318 | 0.019487 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1781.4 | 120.4555 | 0.7479 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.28324 | 0.0070012 | 0.8139 | 0.0065247 | 1.6278 | 0.022685 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1781.6 | 120.4555 | 0.7527 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.8139 | 0.0081246 | 1.6278 | 0.022685 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1781.8 | 120.3595 | 0.7543 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 1.6278 | 0.022685 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1782 | 120.4555 | 0.7591 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.0081246 | 1.6278 | 0.022685 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1782.2 | 120.3595 | 0.7639 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 1.5318 | 0.019487 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1782.4 | 120.3595 | 0.7687 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.8139 | 0.0065247 | 1.5318 | 0.022685 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1782.6 | 120.2635 | 0.77509 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 1.6278 | 0.022685 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1782.8 | 120.2635 | 0.77669 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.90985 | 0.0065247 | 1.6278 | 0.022685 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1783 | 120.2635 | 0.78149 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 1.6278 | 0.022685 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1783.2 | 120.1676 | 0.78469 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 1.6278 | 0.022685 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1783.4 | 120.1676 | 0.78789 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.90985 | 0.0065247 | 1.8197 | 0.024285 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1783.6 | 120.1676 | 0.77669 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.90985 | 0.0081246 | 1.7237 | 0.025884 | 0.29387 | 0.009669 | 0.28424 | 0.0083128
1783.8 | 120.2635 | 0.77989 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 1.7237 | 0.024285 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1784 | 120.1676 | 0.78469 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.90985 | 0.0065247 | 1.7237 | 0.024285 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1784.2 | 119.9756 | 0.79109 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 1.7237 | 0.024285 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1784.4 | 120.1676 | 0.79269 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.90985 | 0.0065247 | 1.7237 | 0.025884 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1784.6 | 120.0716 | 0.79589 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.90985 | 0.0049255 | 1.7237 | 0.025884 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1784.8 | 119.8797 | 0.81668 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.90985 | 0.0081246 | 1.7237 | 0.025884 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1785 | 119.8797 | 0.82308 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 0.90985 | 0.0065247 | 1.7237 | 0.024285 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1785.2 | 119.8797 | 0.82628 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 1.6278 | 0.025884 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1785.4 | 119.7837 | 0.83107 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 1.7237 | 0.024285 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1785.6 | 119.7837 | 0.83427 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.76308 | 0.0086004 | 0.90985 | 0.0065247 | 1.7237 | 0.024285 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1785.8 | 119.6877 | 0.84067 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.90985 | 0.0065247 | 1.7237 | 0.024285 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1786 | 119.6877 | 0.84547 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.90985 | 0.0065247 | 1.7237 | 0.025884 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1786.2 | 119.5918 | 0.84867 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.90985 | 0.0065247 | 1.7237 | 0.024285 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1786.4 | 119.4958 | 0.85667 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.90985 | 0.0065247 | 1.7237 | 0.024285 | 0.5818 | 0.009669 | 0.47618 | 0.006713
1786.6 | 119.5918 | 0.85827 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.90985 | 0.0065247 | 1.7237 | 0.027484 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1786.8 | 119.4958 | 0.86466 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.8139 | 0.0065247 | 1.7237 | 0.025884 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1787 | 119.3999 | 0.86786 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 1.0058 | 0.0065247 | 1.8197 | 0.027484 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1787.2 | 119.3999 | 0.87266 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 1.0058 | 0.0065247 | 1.8197 | 0.025884 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1787.4 | 119.3999 | 0.87906 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.90985 | 0.0049255 | 1.8197 | 0.027484 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1787.6 | 119.3039 | 0.88386 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.90985 | 0.0065247 | 1.7237 | 0.025884 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1787.8 | 119.3039 | 0.88706 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.90985 | 0.0065247 | 1.8197 | 0.027484 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1788 | 119.2079 | 0.89185 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.90985 | 0.0065247 | 1.8197 | 0.025884 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1788.2 | 119.2079 | 0.89665 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 1.0058 | 0.0065247 | 1.9157 | 0.027484 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1788.4 | 119.1119 | 0.90145 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 1.9157 | 0.027484 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1788.6 | 119.016 | 0.90625 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.90985 | 0.0081246 | 1.8197 | 0.027484 | 0.67775 | 0.00647 | 0.28424 | 0.006713
1788.8 | 119.016 | 0.91265 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 1.0058 | 0.0065247 | 1.9157 | 0.027484 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1789 | 119.016 | 0.91585 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 1.0058 | 0.0065247 | 1.8197 | 0.027484 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1789.2 | 118.92 | 0.92064 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 1.0058 | 0.0081246 | 2.0116 | 0.027484 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1789.4 | 118.92 | 0.92704 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.0058 | 0.0065247 | 2.0116 | 0.029083 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1789.6 | 118.824 | 0.93184 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 1.0058 | 0.0065247 | 1.9157 | 0.029083 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1789.8 | 118.824 | 0.93504 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 1.0058 | 0.0081246 | 2.0116 | 0.029083 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1790 | 118.7281 | 0.93984 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 1.0058 | 0.0081246 | 2.0116 | 0.030683 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1790.2 | 118.7281 | 0.94463 | 0.58176 | 0.0031824 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 1.0058 | 0.0081246 | 2.0116 | 0.029083 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1790.4 | 118.6321 | 0.95103 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 1.0058 | 0.011324 | 2.0116 | 0.030683 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1790.6 | 118.6321 | 0.95103 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 1.1018 | 0.0081246 | 2.0116 | 0.030683 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1790.8 | 118.6321 | 0.95743 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.0058 | 0.0081246 | 2.1076 | 0.030683 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1791 | 118.5361 | 0.96063 | 0.67775 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.90985 | 0.0081246 | 2.1076 | 0.032282 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1791.2 | 118.5361 | 0.96863 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 1.0058 | 0.0081246 | 2.1076 | 0.032282 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1791.4 | 118.4401 | 0.97343 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 1.1018 | 0.0097238 | 2.2036 | 0.032282 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1791.6 | 118.4401 | 0.97982 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 1.1018 | 0.0081246 | 2.2036 | 0.033882 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1791.8 | 118.3442 | 0.98462 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 1.0058 | 0.0097238 | 2.2036 | 0.033882 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1792 | 118.2482 | 0.98942 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.90985 | 0.0097238 | 2.2996 | 0.037081 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1792.2 | 118.2482 | 0.99582 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 1.0058 | 0.0097238 | 2.2036 | 0.037081 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1792.4 | 118.1523 | 1.0022 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 1.1018 | 0.0097238 | 2.4915 | 0.04028 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1792.6 | 118.0563 | 1.0102 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 1.1018 | 0.0097238 | 2.8754 | 0.043479 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1792.8 | 117.6724 | 1.0486 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.90985 | 0.0081246 | 5.2745 | 0.075468 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1793 | 118.1523 | 1.0054 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 1.1018 | 0.0097238 | 4.3149 | 0.06907 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1793.2 | 118.1523 | 1.0038 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 1.1018 | 0.0081246 | 2.4915 | 0.037081 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1793.4 | 118.1523 | 1.0118 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 1.1018 | 0.0097238 | 2.2036 | 0.032282 | 0.7737 | 0.011268 | 0.38019 | 0.0083128
1793.6 | 117.9603 | 1.0166 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 1.1978 | 0.011324 | 2.1076 | 0.033882 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1793.8 | 117.8644 | 1.023 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 1.1018 | 0.0097238 | 2.2996 | 0.032282 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1794 | 117.8644 | 1.031 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.1018 | 0.0097238 | 2.2036 | 0.033882 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1794.2 | 117.8644 | 1.0374 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.1018 | 0.012923 | 2.2036 | 0.035481 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1794.4 | 117.7684 | 1.0406 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.90985 | 0.011324 | 2.2996 | 0.035481 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1794.6 | 117.6724 | 1.0502 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 1.1978 | 0.011324 | 2.2996 | 0.037081 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1794.8 | 117.6724 | 1.0582 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.1018 | 0.011324 | 2.3955 | 0.03868 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1795 | 117.5765 | 1.063 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 1.1978 | 0.011324 | 2.4915 | 0.03868 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1795.2 | 117.5765 | 1.0694 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.1978 | 0.011324 | 2.5875 | 0.03868 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1795.4 | 117.4805 | 1.079 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 1.2937 | 0.012923 | 2.5875 | 0.041879 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1795.6 | 117.3845 | 1.0806 | 0.48581 | 0.0095798 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 1.2937 | 0.0081246 | 2.7794 | 0.043479 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1795.8 | 117.3845 | 1.0886 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 1.1978 | 0.011324 | 3.0673 | 0.046678 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1796 | 117.0006 | 1.119 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.1978 | 0.011324 | 4.7947 | 0.072269 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1796.2 | 116.5208 | 1.1862 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.1978 | 0.011324 | 14.8713 | 0.20662 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1796.4 | 115.4652 | 1.2869 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 1.2937 | 0.011324 | 24.7559 | 0.36657 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1796.6 | 115.2732 | 1.3077 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 1.2937 | 0.011324 | 28.3067 | 0.42255 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1796.8 | 114.9853 | 1.3429 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.1978 | 0.012923 | 31.1857 | 0.46733 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1797 | 114.6975 | 1.3781 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 1.2937 | 0.011324 | 34.1607 | 0.50892 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1797.2 | 114.1216 | 1.4437 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 1.1978 | 0.011324 | 37.8074 | 0.5665 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1797.4 | 113.7378 | 1.4725 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 1.1978 | 0.011324 | 40.6864 | 0.60649 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1797.6 | 112.97 | 1.5604 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 1.1978 | 0.011324 | 45.8687 | 0.68166 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1797.8 | 112.7781 | 1.5812 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 1.1978 | 0.012923 | 48.1719 | 0.71205 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1798 | 112.3942 | 1.618 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 1.2937 | 0.012923 | 50.3791 | 0.73924 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1798.2 | 115.1773 | 1.3205 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 54.5556 | 0.0097238 | 81.5685 | 0.29619 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1798.4 | 116.041 | 1.2197 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 66.5514 | 0.0081246 | 91.2612 | 0.11545 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1798.6 | 116.137 | 1.2181 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 67.6071 | 0.0081246 | 92.3168 | 0.10266 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1798.8 | 116.2329 | 1.2037 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 68.2789 | 0.0081246 | 92.7967 | 0.10266 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1799 | 117.1926 | 1.1094 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 70.678 | 0.0081246 | 94.2362 | 0.10586 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1799.2 | 116.3289 | 1.1957 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 68.4708 | 0.0081246 | 92.7967 | 0.10266 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1799.4 | 116.6168 | 1.1686 | 0.48581 | 0.0063808 | 0.48515 | 0.011213 | 0.57118 | 0.0070012 | 69.6224 | 0.0081246 | 93.4684 | 0.10266 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1799.6 | 116.3289 | 1.1894 | 0.48581 | 0.0063808 | 0.5811 | 0.0048148 | 0.57118 | 0.0086004 | 69.4304 | 0.0065247 | 93.3724 | 0.10426 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1799.8 | 116.2329 | 1.2085 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 69.0466 | 0.0081246 | 93.0846 | 0.10106 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1800 | 116.137 | 1.2165 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 68.8547 | 0.0065247 | 92.9886 | 0.10266 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1800.2 | 116.137 | 1.2133 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 69.2385 | 0.0081246 | 93.0846 | 0.10266 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1800.4 | 115.8491 | 1.2485 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 67.799 | 0.0081246 | 92.1249 | 0.10106 | 0.38986 | 0.009669 | 0.28424 | 0.0083128
1800.6 | 115.6571 | 1.2597 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 67.5111 | 0.0081246 | 91.9329 | 0.10106 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1800.8 | 115.6571 | 1.2709 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 67.4152 | 0.0081246 | 91.837 | 0.10106 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1801 | 115.7531 | 1.2597 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 67.6071 | 0.0081246 | 92.1249 | 0.10106 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1801.2 | 115.6571 | 1.2693 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 67.4152 | 0.0081246 | 92.0289 | 0.10106 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1801.4 | 115.6571 | 1.2789 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 67.3192 | 0.0081246 | 91.837 | 0.10106 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1801.6 | 115.5611 | 1.2885 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 67.2232 | 0.0065247 | 91.741 | 0.10266 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1801.8 | 115.3692 | 1.2949 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 67.0313 | 0.0081246 | 91.5491 | 0.099459 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1802 | 115.3692 | 1.3029 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 66.9353 | 0.0081246 | 91.3572 | 0.099459 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1802.2 | 115.2732 | 1.3125 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 66.8394 | 0.0065247 | 91.1652 | 0.099459 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1802.4 | 115.1773 | 1.3205 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 66.8394 | 0.0081246 | 91.0692 | 0.099459 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1802.6 | 115.0813 | 1.3301 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 66.7434 | 0.0065247 | 91.0692 | 0.09786 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1802.8 | 114.9853 | 1.3381 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 66.5514 | 0.0081246 | 90.8773 | 0.09786 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1803 | 114.8894 | 1.3493 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 66.5514 | 0.0081246 | 90.6854 | 0.09786 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1803.2 | 114.7934 | 1.3589 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 66.3595 | 0.0065247 | 90.5894 | 0.09786 | 0.38986 | 0.009669 | 0.28424 | 0.009912
1803.4 | 114.6975 | 1.3685 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 66.1676 | 0.0081246 | 90.4934 | 0.09786 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1803.6 | 114.6975 | 1.3781 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 66.0716 | 0.0081246 | 90.3015 | 0.09626 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1803.8 | 114.6015 | 1.3861 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 65.9756 | 0.0049255 | 90.2055 | 0.09786 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1804 | 114.4095 | 1.3941 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 65.8797 | 0.0065247 | 90.1096 | 0.09786 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1804.2 | 114.4095 | 1.4005 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 65.8797 | 0.0081246 | 90.1096 | 0.09786 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1804.4 | 114.3136 | 1.4133 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 65.8797 | 0.0081246 | 89.9176 | 0.09786 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1804.6 | 114.2176 | 1.4229 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 65.7837 | 0.0081246 | 89.8217 | 0.09786 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1804.8 | 114.2176 | 1.4309 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 65.5918 | 0.0081246 | 89.6297 | 0.09626 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1805 | 114.1216 | 1.4405 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 65.4958 | 0.0065247 | 89.4378 | 0.09626 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1805.2 | 114.0257 | 1.4501 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 65.3998 | 0.0065247 | 89.2459 | 0.09626 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1805.4 | 113.9297 | 1.4581 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 65.3998 | 0.0081246 | 89.2459 | 0.09626 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1805.6 | 113.8337 | 1.4709 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 65.3039 | 0.0065247 | 89.1499 | 0.09626 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1805.8 | 113.6418 | 1.4805 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 65.2079 | 0.0065247 | 89.0539 | 0.09626 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1806 | 113.6418 | 1.4884 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 65.2079 | 0.0065247 | 88.9579 | 0.09786 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1806.2 | 113.5458 | 1.4964 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 65.2079 | 0.0081246 | 88.766 | 0.09626 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1806.4 | 113.7378 | 1.4868 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 65.9756 | 0.0081246 | 89.3418 | 0.09626 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1806.6 | 111.9144 | 1.6612 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 63.2885 | 0.0065247 | 74.083 | 0.10746 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1806.8 | 108.0757 | 2.0834 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 13.0018 | 0.0065247 | 45.3888 | 0.5681 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1807 | 109.2273 | 1.9747 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 3.501 | 0.0081246 | 33.9688 | 0.50412 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1807.2 | 110.5708 | 1.8163 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 2.1574 | 0.0097238 | 39.151 | 0.53931 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1807.4 | 108.8434 | 1.9875 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.9655 | 0.012923 | 36.2719 | 0.54091 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1807.6 | 106.1563 | 2.2882 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 1.8695 | 0.019321 | 41.6461 | 0.62088 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1807.8 | 104.5249 | 2.4577 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 1.8695 | 0.02092 | 42.1259 | 0.62888 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1808 | 104.7168 | 2.4321 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 1.6776 | 0.02092 | 35.984 | 0.53451 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1808.2 | 102.9894 | 2.6129 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 1.6776 | 0.022519 | 39.151 | 0.58249 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1808.4 | 101.5499 | 2.7808 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 1.6776 | 0.02092 | 38.5752 | 0.5793 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1808.6 | 102.4137 | 2.6704 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.7736 | 0.022519 | 34.6405 | 0.51692 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1808.8 | 103.0854 | 2.5985 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 1.7736 | 0.022519 | 36.7518 | 0.5537 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1809 | 102.5096 | 2.6768 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.7736 | 0.024119 | 34.4486 | 0.52331 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1809.2 | 104.9088 | 2.4241 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 1.7736 | 0.022519 | 30.7059 | 0.46733 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1809.4 | 102.9894 | 2.6321 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.7736 | 0.022519 | 28.5946 | 0.43375 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1809.6 | 103.0854 | 2.6081 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 2.0615 | 0.022519 | 27.1551 | 0.40655 | 0.7737 | 0.0080692 | -0.19559 | 0.011511
1809.8 | 101.9338 | 2.7136 | 0.29387 | 0.0095798 | 0.19722 | -0.0015832 | 0.76308 | 0.0102 | 2.0615 | 0.017721 | 27.9228 | 0.42255 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1810 | 103.8532 | 2.5425 | 0.29387 | 0.0079807 | 0.38916 | 0.006414 | 0.66713 | 0.0086004 | 1.6776 | 0.02092 | 24.7559 | 0.39216 | 0.96565 | 0.011268 | 0.57213 | 0.009912
1810.2 | 105.9644 | 2.309 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 1.7736 | 0.022519 | 21.493 | 0.33458 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1810.4 | 108.7475 | 2.0099 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 1.7736 | 0.024119 | 17.6543 | 0.2738 | 0.38986 | 0.00647 | 0.47618 | 0.0083128
1810.6 | 107.4039 | 2.1538 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.28324 | 0.0086004 | 1.8695 | 0.019321 | 19.4777 | 0.29619 | 0.48581 | 0.0080692 | 0.38019 | 0.006713
1810.8 | 111.9144 | 1.6628 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 1.7736 | 0.022519 | 13.0479 | 0.20023 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1811 | 112.0103 | 1.6564 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 1.8695 | 0.024119 | 12.664 | 0.19703 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1811.2 | 111.7225 | 1.7012 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 1.7736 | 0.024119 | 13.4318 | 0.20822 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1811.4 | 112.5862 | 1.6052 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 1.8695 | 0.022519 | 12.0882 | 0.18903 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1811.6 | 114.6015 | 1.3989 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 1.8695 | 0.022519 | 9.785 | 0.15544 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1811.8 | 115.945 | 1.2469 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 1.7736 | 0.024119 | 7.6737 | 0.11865 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1812 | 115.8491 | 1.2581 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 1.8695 | 0.024119 | 7.7697 | 0.12185 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1812.2 | 115.7531 | 1.2773 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 1.8695 | 0.024119 | 7.9616 | 0.12505 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1812.4 | 115.6571 | 1.2917 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 1.9655 | 0.022519 | 8.0576 | 0.12665 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1812.6 | 115.4652 | 1.3077 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 1.9655 | 0.025718 | 8.2495 | 0.12985 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1812.8 | 115.3692 | 1.3253 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 1.9655 | 0.027318 | 8.5374 | 0.13145 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1813 | 115.0813 | 1.3413 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 1.9655 | 0.027318 | 8.7294 | 0.13305 | 0.48581 | 0.009669 | 0.47618 | 0.0083128
1813.2 | 115.0813 | 1.3573 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 2.0615 | 0.028917 | 8.6334 | 0.13465 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1813.4 | 114.8894 | 1.3701 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 2.0615 | 0.028917 | 8.7294 | 0.13625 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1813.6 | 114.7934 | 1.3829 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 2.1574 | 0.030517 | 8.9213 | 0.13785 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1813.8 | 114.6975 | 1.3989 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 2.2534 | 0.032116 | 9.0173 | 0.13945 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1814 | 114.5055 | 1.4133 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 2.1574 | 0.032116 | 9.1132 | 0.14105 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1814.2 | 114.3136 | 1.4117 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 2.2534 | 0.033716 | 9.3052 | 0.14264 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1814.4 | 114.1216 | 1.4149 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 2.3494 | 0.035315 | 9.3052 | 0.14424 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1814.6 | 113.9297 | 1.4357 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 2.3494 | 0.038514 | 9.689 | 0.14904 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1814.8 | 113.9297 | 1.4517 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 2.2534 | 0.038514 | 9.593 | 0.14904 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1815 | 113.8337 | 1.4757 | 0.48581 | 0.014378 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 2.4453 | 0.028917 | 9.689 | 0.14904 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1815.2 | 113.6418 | 1.4916 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 2.5413 | 0.030517 | 9.9769 | 0.14904 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1815.4 | 113.6418 | 1.4932 | 0.48581 | 0.0063808 | 0.29321 | 0.006414 | 0.57118 | 0.0070012 | 2.5413 | 0.036915 | 9.9769 | 0.15224 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1815.6 | 113.5458 | 1.5108 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 2.6373 | 0.036915 | 10.0729 | 0.15544 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1815.8 | 113.4499 | 1.5252 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 2.6373 | 0.036915 | 10.1689 | 0.15384 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1816 | 113.258 | 1.5412 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 2.6373 | 0.041713 | 10.3608 | 0.15864 | 0.5818 | 0.009669 | 0.28424 | 0.0051138
1816.2 | 113.066 | 1.5588 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 2.6373 | 0.038514 | 10.6487 | 0.16184 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1816.4 | 112.97 | 1.5764 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 2.8292 | 0.038514 | 10.8406 | 0.16504 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1816.6 | 112.7781 | 1.594 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 2.8292 | 0.044912 | 10.9366 | 0.16664 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1816.8 | 112.5862 | 1.6132 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 2.8292 | 0.041713 | 11.1285 | 0.16984 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1817 | 112.2982 | 1.634 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 2.9252 | 0.043313 | 11.4164 | 0.17463 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1817.2 | 112.2023 | 1.6596 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 2.9252 | 0.043313 | 11.8003 | 0.17943 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1817.4 | 111.8184 | 1.69 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 2.9252 | 0.044912 | 12.3761 | 0.18743 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1817.6 | 111.5305 | 1.73 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 2.9252 | 0.044912 | 13.2398 | 0.20023 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1817.8 | 110.9547 | 1.7923 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 3.0211 | 0.046512 | 14.7753 | 0.22422 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1818 | 110.283 | 1.8563 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 3.0211 | 0.044912 | 16.3108 | 0.24661 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1818.2 | 109.8991 | 1.8995 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 3.1171 | 0.044912 | 16.8866 | 0.25461 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1818.4 | 109.6112 | 1.9299 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 3.1171 | 0.046512 | 17.2704 | 0.261 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1818.6 | 109.2273 | 1.9683 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 3.1171 | 0.046512 | 17.6543 | 0.2658 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1818.8 | 108.9394 | 2.0019 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0070012 | 3.2131 | 0.04971 | 17.8462 | 0.269 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1819 | 108.3636 | 2.0451 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 3.2131 | 0.04971 | 18.3261 | 0.277 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1819.2 | 107.9797 | 2.0866 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 3.3091 | 0.04971 | 18.7099 | 0.2818 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1819.4 | 107.4039 | 2.1058 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 3.501 | 0.05131 | 18.614 | 0.2802 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1819.6 | 107.8838 | 1.9859 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 3.6929 | 0.056108 | 14.6793 | 0.22422 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1819.8 | 108.4596 | 1.9491 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 3.8848 | 0.060906 | 13.1438 | 0.20023 | 0.5818 | 0.009669 | 0.47618 | 0.006713
1820 | 108.9394 | 1.9651 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 3.9808 | 0.064105 | 13.0479 | 0.19863 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1820.2 | 108.9394 | 1.9795 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 4.2687 | 0.064105 | 12.9519 | 0.19543 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1820.4 | 108.6515 | 2.0099 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 4.2687 | 0.067304 | 13.1438 | 0.20023 | 0.5818 | 0.0080692 | 0.47618 | 0.0083128
1820.6 | 108.4596 | 2.0419 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 4.4606 | 0.068904 | 13.4318 | 0.20662 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1820.8 | 108.2676 | 2.0738 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 4.5566 | 0.070503 | 13.7197 | 0.20662 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1821 | 107.7878 | 2.1138 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 4.6526 | 0.072103 | 14.1035 | 0.21302 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1821.2 | 107.4999 | 2.1554 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 4.7486 | 0.075302 | 14.4874 | 0.21942 | 0.48581 | 0.0080692 | 0.47618 | 0.0083128
1821.4 | 107.116 | 2.2018 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.37923 | 0.0086004 | 4.9405 | 0.076901 | 14.9672 | 0.22582 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1821.6 | 106.5402 | 2.2514 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 5.0365 | 0.078501 | 15.3511 | 0.23221 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1821.8 | 106.0604 | 2.3074 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 5.1324 | 0.0801 | 16.0229 | 0.24021 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1822 | 105.4846 | 2.3713 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 5.3244 | 0.0817 | 16.5987 | 0.24821 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1822.2 | 104.7168 | 2.4385 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 5.6122 | 0.084898 | 17.0785 | 0.25781 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1822.4 | 104.333 | 2.4881 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 5.6122 | 0.086498 | 17.6543 | 0.2642 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1822.6 | 103.7572 | 2.5537 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 5.8042 | 0.089697 | 18.0382 | 0.2722 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1822.8 | 103.0854 | 2.6097 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 5.9961 | 0.092895 | 18.518 | 0.2786 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1823 | 102.5096 | 2.6736 | 0.67775 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 6.0921 | 0.094495 | 18.9978 | 0.285 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1823.2 | 101.454 | 2.784 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 6.476 | 0.10089 | 19.6696 | 0.29619 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1823.4 | 100.6862 | 2.8576 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 6.8598 | 0.10569 | 20.1495 | 0.30259 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1823.6 | 99.6306 | 2.9775 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 7.2437 | 0.11209 | 20.8212 | 0.31219 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1823.8 | 98.6709 | 3.0815 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 8.0114 | 0.12329 | 21.3011 | 0.32018 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1824 | 97.8072 | 3.1663 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 8.8751 | 0.13448 | 21.6849 | 0.32658 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1824.2 | 96.7516 | 3.2718 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 10.4106 | 0.15687 | 21.493 | 0.32338 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1824.4 | 95.1201 | 3.4398 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 20.0073 | 0.28803 | 21.2051 | 0.32018 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1824.6 | 92.529 | 3.7021 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 44.6709 | 0.6687 | 21.493 | 0.32178 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1824.8 | 91.6653 | 3.7965 | 0.58176 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 51.2927 | 0.75827 | 21.3011 | 0.31858 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1825 | 91.6653 | 3.7805 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 52.6362 | 0.76307 | 21.0132 | 0.31539 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1825.2 | 91.5694 | 3.7869 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 58.4902 | 0.70069 | 22.9325 | 0.12985 | 0.5818 | 0.009669 | 0.28424 | 0.011511
1825.4 | 91.3774 | 3.8141 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 60.8894 | 0.6639 | 23.5083 | 0.029083 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1825.6 | 90.9935 | 3.8524 | 0.58176 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 61.0813 | 0.6591 | 23.2204 | 0.016288 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1825.8 | 90.4177 | 3.9068 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 60.8894 | 0.6591 | 23.2204 | 0.013089 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1826 | 92.2411 | 3.7005 | 0.58176 | -1.6596e-05 | 0.48515 | 0.009613 | 0.66713 | 0.0070012 | 63.1926 | 0.6751 | 31.6655 | 0.01149 | 1.2535 | 0.009669 | 0.38019 | 0.009912
1826.2 | 93.0089 | 3.6205 | 0.48581 | 0.0063808 | 0.19722 | 0.0048148 | 0.47518 | 0.0086004 | 63.5765 | 0.6783 | 37.2316 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1826.4 | 91.4734 | 3.7901 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 60.8894 | 0.6607 | 31.8575 | 0.0098898 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1826.6 | 91.8572 | 3.7373 | 0.67775 | 0.0079807 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 61.945 | 0.6623 | 34.3526 | 0.014688 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1826.8 | 93.2967 | 3.5789 | 0.67775 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 63.6724 | 0.68309 | 39.8227 | 0.0082906 | 0.48581 | 0.009669 | 0.47618 | 0.009912
1827 | 90.9935 | 3.8285 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 61.6571 | 0.6671 | 33.4889 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1827.2 | 88.8822 | 4.0396 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 60.1216 | 0.6527 | 29.2664 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1827.4 | 87.3468 | 4.1899 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 60.0257 | 0.6511 | 27.6349 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1827.6 | 86.3871 | 4.3051 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 59.2579 | 0.63511 | 26.0994 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1827.8 | 85.2355 | 4.4075 | 0.58176 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 58.3942 | 0.63191 | 24.564 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1828 | 84.7557 | 4.465 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 58.1063 | 0.63031 | 23.9881 | 0.0066908 | 1.3495 | 0.009669 | 0.38019 | 0.009912
1828.2 | 83.9879 | 4.5178 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 57.6265 | 0.62551 | 23.5083 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1828.4 | 83.5081 | 4.5722 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 57.2426 | 0.62071 | 23.1245 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1828.6 | 83.0283 | 4.6186 | 0.58176 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 56.8587 | 0.61752 | 23.0285 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1828.8 | 82.5484 | 4.6618 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 56.4749 | 0.61272 | 22.7406 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1829 | 82.0686 | 4.7097 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 56.091 | 0.60952 | 22.7406 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1829.2 | 81.4928 | 4.7529 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 55.7071 | 0.60472 | 22.6446 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1829.4 | 81.1089 | 4.7913 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 55.4192 | 0.60472 | 22.3567 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1829.6 | 80.7251 | 4.8281 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 55.2273 | 0.59992 | 22.4527 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1829.8 | 80.3412 | 4.8617 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 55.0354 | 0.59832 | 22.4527 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1830 | 80.0533 | 4.8905 | 0.58176 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 54.7475 | 0.59512 | 22.4527 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1830.2 | 79.5734 | 4.9257 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 54.3636 | 0.59832 | 22.3567 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
1830.4 | 79.2855 | 4.9625 | 0.67775 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 54.2676 | 0.59832 | 22.2607 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1830.6 | 78.9017 | 4.9961 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 53.8838 | 0.59672 | 22.4527 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1830.8 | 78.5178 | 5.02 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 53.8838 | 0.58713 | 22.2607 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1831 | 78.3259 | 5.0344 | 0.67775 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 53.6918 | 0.58873 | 22.2607 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1831.2 | 78.1339 | 5.06 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 53.5959 | 0.59193 | 22.2607 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1831.4 | 77.6541 | 5.0872 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0054014 | 53.5959 | 0.59193 | 22.2607 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1831.6 | 77.3662 | 5.1192 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 53.308 | 0.58873 | 22.1648 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1831.8 | 76.9823 | 5.1576 | 0.67775 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0086004 | 53.0201 | 0.58873 | 21.8769 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1832 | 76.6944 | 5.1864 | 0.58176 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 52.9241 | 0.58073 | 21.9728 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1832.2 | 76.1186 | 5.2312 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 52.5402 | 0.57593 | 21.493 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1832.4 | 75.9267 | 5.2472 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 52.3483 | 0.57913 | 21.6849 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1832.6 | 75.9267 | 5.2472 | 0.67775 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 52.4443 | 0.57433 | 21.6849 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1832.8 | 75.5428 | 5.2808 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 51.9644 | 0.57113 | 21.3011 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1833 | 75.063 | 5.3191 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 52.1563 | 0.57113 | 22.2607 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1833.2 | 74.5831 | 5.3271 | 0.67775 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 50.7168 | 0.55994 | 22.6446 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1833.4 | 74.4872 | 5.3271 | 0.58176 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 52.0604 | 0.57273 | 22.4527 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1833.6 | 74.2953 | 5.3271 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 52.1563 | 0.57433 | 22.7406 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1833.8 | 74.0073 | 5.3271 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 52.1563 | 0.57433 | 23.0285 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1834 | 74.1993 | 5.3271 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 52.4443 | 0.57433 | 23.7002 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1834.2 | 74.1993 | 5.3271 | 0.67775 | 0.0031824 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 52.6362 | 0.57753 | 25.1397 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1834.4 | 78.6138 | 4.9257 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 57.3386 | 0.62551 | 34.3526 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1834.6 | 81.0129 | 4.6698 | 0.58176 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 60.1216 | 0.63991 | 39.9187 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1834.8 | 81.0129 | 4.6826 | 0.67775 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 60.1216 | 0.63831 | 40.0147 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1835 | 81.4928 | 4.6362 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 59.5459 | 0.63031 | 41.4542 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1835.2 | 81.9726 | 4.5818 | 0.67775 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 60.1216 | 0.63511 | 43.2776 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1835.4 | 81.3968 | 4.6442 | 0.58176 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 59.2579 | 0.62231 | 42.3179 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1835.6 | 83.0283 | 4.4698 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 61.6571 | 0.64791 | 46.2526 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1835.8 | 86.2911 | 4.1467 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 65.9756 | 0.68949 | 52.7783 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1836 | 88.4024 | 3.9436 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 68.7587 | 0.71668 | 57.0968 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1836.2 | 89.0742 | 3.8828 | 0.58176 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 69.8143 | 0.69109 | 58.4404 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1836.4 | 87.4427 | 4.054 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 67.703 | 0.64311 | 55.4654 | 0.261 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1836.6 | 89.65 | 3.8316 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 70.678 | 0.64311 | 59.496 | 0.20982 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1836.8 | 98.287 | 2.9456 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 83.7296 | 0.45437 | 76.4822 | 0.03868 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1837 | 96.0798 | 3.1599 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 80.9465 | 0.31842 | 71.0121 | 0.019487 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1837.2 | 96.5596 | 3.1119 | 0.67775 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0102 | 81.4264 | 0.26564 | 72.1637 | 0.016288 | 0.5818 | 0.009669 | 0.38019 | 0.013111
1837.4 | 102.9894 | 2.4625 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 90.7352 | 0.16807 | 84.7354 | 0.01149 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1837.6 | 102.8935 | 2.4785 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 90.8312 | 0.10569 | 84.4475 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1837.8 | 101.9338 | 2.5889 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 89.4876 | 0.097694 | 82.4322 | 0.01149 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1838 | 103.3733 | 2.4225 | 0.48581 | 0.0063808 | 0.38916 | 0.0048148 | 0.66713 | 0.0070012 | 91.5029 | 0.096094 | 85.3112 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1838.2 | 105.0048 | 2.2578 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 93.7102 | 0.10409 | 88.5741 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1838.4 | 108.7475 | 1.8883 | 0.48581 | 0.0095798 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 98.9884 | 0.10889 | 96.1555 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1838.6 | 108.6515 | 1.9107 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 98.7005 | 0.11049 | 95.8676 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1838.8 | 107.5959 | 2.0115 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 97.2609 | 0.11049 | 93.7563 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1839 | 107.116 | 2.0643 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.011799 | 96.3013 | 0.10889 | 92.4128 | 0.0082906 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1839.2 | 105.8684 | 2.189 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 94.5739 | 0.10569 | 89.7257 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1839.4 | 105.3886 | 2.2306 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 93.9981 | 0.10569 | 88.1902 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1839.6 | 104.237 | 2.3554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 92.2707 | 0.10249 | 85.5991 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1839.8 | 103.7572 | 2.3905 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 91.5989 | 0.10089 | 84.8314 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1840 | 102.5096 | 2.5073 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 89.7755 | 0.097694 | 82.3362 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1840.2 | 101.454 | 2.6113 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 88.24 | 0.094495 | 80.4169 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1840.4 | 100.4943 | 2.7088 | 0.58176 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 86.8965 | 0.094495 | 78.5935 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1840.6 | 98.8629 | 2.8752 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 84.9771 | 0.089697 | 76.0024 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1840.8 | 96.0798 | 3.1519 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 81.3304 | 0.19046 | 72.4516 | 0.0098898 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1841 | 94.7363 | 3.2958 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 79.8909 | 0.19526 | 70.4363 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1841.2 | 95.6959 | 3.1727 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 80.0828 | 0.22725 | 70.3403 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1841.4 | 89.9379 | 3.7549 | 0.48581 | 0.0079807 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 72.4054 | 0.68629 | 65.0621 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1841.6 | 90.1298 | 3.7421 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 72.2135 | 0.75027 | 64.2944 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1841.8 | 94.6403 | 3.2942 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 78.9312 | 0.60312 | 72.6435 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1842 | 93.2967 | 3.3998 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 79.7949 | 0.22085 | 73.1234 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1842.2 | 95.2161 | 3.2143 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 80.7546 | 0.22245 | 73.4113 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1842.4 | 93.1048 | 3.4046 | 0.58176 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 78.7393 | 0.21765 | 70.9161 | 0.01149 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1842.6 | 93.2967 | 3.4014 | 0.58176 | 0.0047816 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 76.4361 | 0.64951 | 69.3806 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1842.8 | 93.2008 | 3.4158 | 0.58176 | 0.0063808 | 0.48515 | 0.011213 | 0.57118 | 0.0086004 | 75.2845 | 0.77746 | 68.0371 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1843 | 92.529 | 3.4878 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 74.3248 | 0.77426 | 66.5976 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1843.2 | 91.7613 | 3.5485 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 73.5571 | 0.77106 | 65.5419 | 0.0082906 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1843.4 | 91.0895 | 3.6173 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 72.6933 | 0.76467 | 64.2944 | 0.0082906 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1843.6 | 90.1298 | 3.7117 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 71.3498 | 0.75187 | 62.567 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1843.8 | 89.2661 | 3.7885 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 70.3902 | 0.74547 | 61.2234 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1844 | 88.4984 | 3.8652 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 69.4304 | 0.73428 | 59.8799 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1844.2 | 87.8266 | 3.9324 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 68.5668 | 0.72788 | 58.8243 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.009912
1844.4 | 87.0589 | 3.9948 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 67.703 | 0.71988 | 57.6726 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1844.6 | 86.4831 | 4.0396 | 0.58176 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0054014 | 67.2232 | 0.71668 | 55.4654 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1844.8 | 85.1396 | 4.1931 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0102 | 65.9756 | 0.70389 | 53.642 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1845 | 81.3968 | 4.5658 | 0.67775 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 62.8087 | 0.6687 | 50.859 | 0.0066908 | 0.7737 | 0.009669 | 0.38019 | 0.0083128
1845.2 | 78.6138 | 4.8201 | 0.67775 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 60.6015 | 0.64791 | 48.8437 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1845.4 | 74.7751 | 5.1704 | 0.58176 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 57.6265 | 0.61752 | 46.2526 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1845.6 | 73.1436 | 5.3271 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 56.3789 | 0.60152 | 45.3888 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1845.8 | 72.6638 | 5.3271 | 0.67775 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 55.5152 | 0.59832 | 44.4292 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1846 | 73.5275 | 5.276 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 56.091 | 0.60312 | 44.5251 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1846.2 | 72.7598 | 5.3271 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.28324 | 0.0054014 | 55.0354 | 0.60152 | 43.2776 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1846.4 | 76.0227 | 5.0248 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 57.0507 | 0.61432 | 44.2372 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1846.6 | 80.7251 | 4.5402 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 60.3136 | 0.64951 | 46.2526 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1846.8 | 75.9267 | 5.0568 | 0.7737 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 56.5709 | 0.60472 | 43.1816 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1847 | 72.2799 | 5.3271 | 0.67775 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 53.8838 | 0.57913 | 40.8784 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1847.2 | 70.2646 | 5.3271 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 52.1563 | 0.56793 | 39.4389 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1847.4 | 67.7695 | 5.3271 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 50.333 | 0.54714 | 37.7114 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1847.6 | 10.0932 | 0.54317 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 7.8195 | 0.084898 | 6.1383 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1847.8 | 2.6077 | 0.077731 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 2.2534 | 0.025718 | 2.0116 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1848 | 1.3602 | 0.031347 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 1.2937 | 0.016122 | 1.3399 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1848.2 | 1.0723 | 0.024949 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 1.0058 | 0.014522 | 1.148 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1848.4 | 0.88032 | 0.018551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.8139 | 0.011324 | 0.86003 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1848.6 | 0.78433 | 0.016952 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.90985 | 0.011324 | 0.86003 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1848.8 | 0.68838 | 0.015352 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.8139 | 0.0097238 | 0.86003 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1849 | 0.78433 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1849.2 | 0.78433 | 0.013753 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.8139 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1849.4 | 0.68838 | 0.013753 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.8139 | 0.0097238 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1849.6 | 0.68838 | 0.013753 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0097238 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1849.8 | 0.59242 | 0.012154 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.011324 | 0.47618 | 0.0098898 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1850 | 0.59242 | 0.012154 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.47518 | 0.0102 | 0.8139 | 0.0065247 | 0.76408 | 0.0018926 | 0.67775 | 0.011268 | 0.57213 | 0.009912
1850.2 | 0.68838 | 0.013753 | 0.67775 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.66813 | 0.0034924 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1850.4 | 0.68838 | 0.012154 | 0.48581 | 0.01118 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.012923 | 0.76408 | 0.0050916 | 0.5818 | 0.0080692 | 0.57213 | 0.0083128
1850.6 | 0.49643 | 0.012154 | 0.48581 | 0.0047816 | 0.10127 | 0.006414 | 0.37923 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.011511
1850.8 | 0.68838 | 0.010554 | 0.58176 | 0.0047816 | 0.29321 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.011511
1851 | 0.68838 | 0.0073551 | 0.29387 | 0.0063808 | 0.29321 | 0.009613 | 1.051 | 0.0054014 | 0.23811 | 0.0081246 | 0.38019 | 0.0034924 | 0.7737 | 0.0080692 | 0.66813 | 0.013111
1851.2 | 0.59242 | 0.012154 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.00647 | 0.47618 | 0.009912
1851.4 | 0.59242 | 0.012154 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.37923 | 0.0070012 | 0.8139 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.006713
1851.6 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0098898 | 0.67775 | 0.00647 | 0.28424 | 0.009912
1851.8 | 0.68838 | 0.0089549 | 0.58176 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1852 | 0.68838 | 0.010554 | 0.58176 | 0.0047816 | 0.38916 | 0.0080139 | 0.47518 | 0.0102 | 0.8139 | 0.0065247 | 0.95602 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1852.2 | 0.88032 | 0.012154 | 0.19792 | 0.0031824 | 0.48515 | 0.006414 | 0.76308 | 0.0086004 | 0.71795 | 0.0033264 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.011511
1852.4 | 0.68838 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1852.6 | 0.68838 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1852.8 | 0.68838 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1853 | 0.68838 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1853.2 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1853.4 | 0.68838 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1853.6 | 0.59242 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1853.8 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 1.3495 | 0.009669 | 0.28424 | 0.009912
1854 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | -0.0036512 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1854.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1854.4 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1854.6 | 0.68838 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0034924 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1854.8 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1855 | 0.59242 | 0.013753 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1855.2 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1855.4 | 0.68838 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0017265 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1855.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1855.8 | 0.59242 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1856 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1856.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1856.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1856.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1856.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.86899 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1857 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1857.2 | 0.49643 | 0.0057559 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1857.4 | 0.59242 | 0.010554 | 0.7737 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1857.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1857.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1858 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.86003 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1858.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1858.4 | 0.78433 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1858.6 | 0.59242 | 0.0073551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0054014 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.48581 | 0.011268 | 0.28424 | 0.009912
1858.8 | 0.59242 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.38986 | 0.0080692 | 0.28424 | 0.009912
1859 | 0.59242 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.526 | 0.0081246 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1859.2 | 0.68838 | 0.0089549 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1859.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1859.6 | 0.59242 | 0.0073551 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.76308 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.012867 | 0.28424 | 0.0083128
1859.8 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1860 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.8139 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1860.2 | 0.59242 | 0.0073551 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0102 | 0.71795 | 0.0081246 | 0.76408 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1860.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1860.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1860.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.48581 | 0.011268 | 0.47618 | 0.009912
1861 | 0.59242 | 0.010554 | 0.38986 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.18829 | 0.0083128
1861.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.7737 | 0.009669 | 0.28424 | 0.009912
1861.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1861.6 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1861.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.76408 | 0.011511
1862 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1862.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1862.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.00647 | 0.38019 | 0.0083128
1862.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1862.8 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1863 | 0.59242 | 0.0073551 | 0.58176 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0098898 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1863.2 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1863.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1863.6 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1863.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1864 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1864.2 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1864.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1864.6 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1864.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1865 | 0.59242 | 0.0073551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1865.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1865.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1865.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1865.8 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1866 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.00647 | 0.38019 | 0.0083128
1866.2 | 0.49643 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1866.4 | 0.59242 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1866.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1866.8 | 0.59242 | 0.0073551 | 0.48581 | 0.0063808 | 0.29321 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.012867 | 0.28424 | 0.0083128
1867 | 0.59242 | 0.0073551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1867.2 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1867.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1867.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1867.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1868 | 0.68838 | 0.0089549 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1868.2 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.47618 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1868.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1868.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1868.8 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1869 | 0.40048 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1869.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1869.4 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1869.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1869.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.8139 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1870 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1870.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1870.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1870.6 | 0.49643 | 0.0073551 | 0.38986 | 0.0047816 | 0.38916 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1870.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0097238 | 0.38019 | 0.0098898 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1871 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1871.2 | 0.68838 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.18829 | 0.0051138
1871.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0049255 | 0.86003 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1871.6 | 0.49643 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1871.8 | 0.59242 | 0.0089549 | 0.58176 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.0080692 | 0.47618 | 0.009912
1872 | 0.59242 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0049255 | 0.76408 | 0.0050916 | 0.48581 | 0.0080692 | 0.57213 | 0.0083128
1872.2 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.011799 | 0.526 | 0.0049255 | 0.76408 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
1872.4 | 0.68838 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0102 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1872.6 | 0.59242 | 0.010554 | 0.38986 | 0.0095798 | 0.67705 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0097238 | 0.86003 | 0.0034924 | 0.48581 | 0.011268 | 0.47618 | 0.0083128
1872.8 | 0.40048 | 0.0089549 | 0.38986 | 0.0047816 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1873 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.28324 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1873.2 | 0.59242 | 0.0073551 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.66713 | 0.0102 | 0.43001 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.012867 | 0.38019 | 0.006713
1873.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.38986 | 0.009669 | 0.28424 | 0.009912
1873.6 | 0.59242 | 0.012154 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.0048701 | 0.28424 | 0.006713
1873.8 | 0.49643 | 0.0073551 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.66713 | 0.0022023 | 0.8139 | 0.0097238 | 0.57213 | 0.01149 | 0.5818 | 0.011268 | 0.28424 | 0.006713
1874 | 0.68838 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.011213 | 0.57118 | 0.011799 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1874.2 | 0.40048 | 0.0089549 | 0.29387 | 0.0047816 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0049255 | 0.76408 | 0.0034924 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1874.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0079807 | 0.38916 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.86003 | 0.0082906 | 0.5818 | 0.014467 | 0.28424 | 0.009912
1874.6 | 0.40048 | 0.0073551 | 0.48581 | 0.0047816 | 0.48515 | 0.0048148 | 0.47518 | 0.0102 | 0.43001 | 0.0081246 | 0.86003 | 0.0018926 | 0.67775 | 0.014467 | 0.47618 | 0.0051138
1874.8 | 0.59242 | 0.012154 | 0.29387 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0049255 | 0.76408 | 0.0050916 | 0.19792 | 0.011268 | 0.0923 | 0.009912
1875 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
1875.2 | 0.68838 | 0.0089549 | 0.48581 | 0.0079807 | 0.10127 | 0.009613 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.57213 | 0.009912
1875.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0097238 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1875.6 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1875.8 | 0.49643 | 0.010554 | 0.48581 | 0.0047816 | 0.29321 | 0.006414 | 0.57118 | 0.0102 | 0.43001 | 0.011324 | 0.66813 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1876 | 0.59242 | 0.012154 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.00647 | 0.28424 | 0.009912
1876.2 | 0.49643 | 0.0057559 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1876.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1876.6 | 0.49643 | 0.0073551 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.57213 | 0.009912
1876.8 | 0.40048 | 0.010554 | 0.48581 | 0.0095798 | 0.5811 | 0.0080139 | 0.57118 | 0.0038022 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1877 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1877.2 | 0.59242 | 0.012154 | 0.48581 | 0.0047816 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0097238 | 0.86003 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1877.4 | 0.68838 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0048148 | 0.76308 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1877.6 | 0.49643 | 0.0073551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0070012 | 0.8139 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1877.8 | 0.68838 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.95602 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1878 | 0.59242 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1878.2 | 0.49643 | 0.010554 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.57213 | 0.009912
1878.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
1878.6 | 0.59242 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.86969 | 0.009669 | 0.0923 | 0.009912
1878.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.011213 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.47618 | 0.0035139
1879 | 0.40048 | 0.0073551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0050916 | 0.67775 | 0.0080692 | 0.47618 | 0.009912
1879.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0048148 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1879.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0098898 | 0.86969 | 0.012867 | 0.28424 | 0.0083128
1879.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1879.8 | 0.68838 | 0.010554 | 0.48581 | 0.0031824 | 0.5811 | 0.006414 | 0.76308 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1880 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1880.2 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1880.4 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1880.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1880.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1881 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1881.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1881.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1881.6 | 0.59242 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1881.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1882 | 0.49643 | 0.010554 | 0.38986 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1882.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1882.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1882.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1882.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1883 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1883.2 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1883.4 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1883.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1883.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1884 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
1884.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1884.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1884.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1884.8 | 0.68838 | 0.010554 | 0.58176 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1885 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1885.2 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1885.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1885.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1885.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1886 | 0.59242 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1886.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1886.4 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1886.6 | 0.49643 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1886.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1887 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1887.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1887.4 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1887.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1887.8 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.57213 | 0.0083128
1888 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1888.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1888.4 | 0.68838 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1888.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1888.8 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1889 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1889.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1889.4 | 0.49643 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1889.6 | 0.59242 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1889.8 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1890 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1890.2 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1890.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1890.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1890.8 | 0.59242 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1891 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.0083128
1891.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1891.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1891.6 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1891.8 | 0.59242 | 0.0073551 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1892 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1892.2 | 0.59242 | 0.010554 | 0.29387 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1892.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1892.6 | 0.49643 | 0.010554 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1892.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.0080692 | 0.38019 | 0.009912
1893 | 0.49643 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1893.2 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1893.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1893.6 | 0.59242 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1893.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1894 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1894.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1894.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1894.6 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1894.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1895 | 0.59242 | 0.010554 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1895.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1895.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1895.6 | 0.59242 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1895.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0047816 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1896 | 0.59242 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1896.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1896.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1896.6 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1896.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1897 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1897.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1897.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1897.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1897.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1898 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.47618 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1898.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1898.4 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1898.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1898.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1899 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1899.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1899.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1899.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1899.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1900 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1900.2 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1900.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1900.6 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1900.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0054014 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
1901 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1901.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1901.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1901.6 | 0.49643 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1901.8 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1902 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1902.2 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1902.4 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1902.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1902.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1903 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1903.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.38916 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1903.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1903.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1903.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1904 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1904.2 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1904.4 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.38916 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1904.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1904.8 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1905 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1905.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1905.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1905.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1905.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1906 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
1906.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1906.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1906.6 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1906.8 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1907 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1907.2 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1907.4 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1907.6 | 0.49643 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1907.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1908 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1908.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1908.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1908.6 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1908.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1909 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1909.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1909.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1909.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.0083128
1909.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1910 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1910.2 | 0.68838 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1910.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.47618 | 0.009912
1910.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1910.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1911 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1911.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1911.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1911.6 | 0.49643 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1911.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1912 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1912.2 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1912.4 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1912.6 | 0.59242 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1912.8 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1913 | 0.49643 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1913.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1913.4 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1913.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1913.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1914 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1914.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1914.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1914.6 | 0.49643 | 0.0073551 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1914.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1915 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1915.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1915.4 | 0.49643 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1915.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.009912
1915.8 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.009912
1916 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1916.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1916.4 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1916.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1916.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1917 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1917.2 | 0.49643 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1917.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1917.6 | 0.59242 | 0.0089549 | 0.58176 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1917.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.009912
1918 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1918.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1918.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1918.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.47618 | 0.009912
1918.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1919 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1919.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1919.4 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1919.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1919.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1920 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1920.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.009912
1920.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1920.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1920.8 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1921 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1921.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1921.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1921.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1921.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1922 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1922.2 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1922.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1922.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1922.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1923 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1923.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1923.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1923.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1923.8 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1924 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1924.2 | 0.59242 | 0.0089549 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1924.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1924.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1924.8 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1925 | 0.49643 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1925.2 | 0.59242 | 0.0089549 | 0.29387 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1925.4 | 0.49643 | 0.010554 | 0.48581 | 0.012779 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.47618 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1925.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | -0.00099603 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1925.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1926 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1926.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1926.4 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1926.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.18829 | 0.0083128
1926.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1927 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1927.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1927.4 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1927.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1927.8 | 0.49643 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.006713
1928 | 0.49643 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1928.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1928.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1928.6 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.006713
1928.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1929 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1929.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1929.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1929.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1929.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1930 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1930.2 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1930.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1930.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1930.8 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1931 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1931.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1931.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1931.6 | 0.68838 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1931.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1932 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1932.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1932.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1932.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1932.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1933 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1933.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1933.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1933.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1933.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1934 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1934.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1934.4 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1934.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1934.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1935 | 0.49643 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1935.2 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1935.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1935.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1935.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1936 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.0083128
1936.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1936.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1936.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1936.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1937 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1937.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1937.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1937.6 | 0.68838 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1937.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1938 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1938.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1938.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1938.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1938.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1939 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1939.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1939.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1939.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1939.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1940 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1940.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.38986 | 0.009669 | 0.38019 | 0.0083128
1940.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1940.6 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1940.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1941 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1941.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1941.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1941.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1941.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1942 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1942.2 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1942.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1942.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1942.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1943 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1943.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1943.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1943.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1943.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1944 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1944.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1944.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1944.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1944.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1945 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1945.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1945.4 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1945.6 | 0.40048 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1945.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1946 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1946.2 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1946.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1946.6 | 0.49643 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1946.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1947 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1947.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1947.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1947.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1947.8 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1948 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1948.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1948.4 | 0.68838 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1948.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1948.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1949 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.47518 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1949.2 | 0.59242 | 0.012154 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1949.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1949.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0098898 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1949.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1950 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1950.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1950.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1950.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1950.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1951 | 0.68838 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1951.2 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1951.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1951.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1951.8 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.38916 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1952 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1952.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1952.4 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1952.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1952.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1953 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1953.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1953.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1953.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1953.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1954 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1954.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1954.4 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1954.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1954.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1955 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1955.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1955.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1955.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1955.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1956 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1956.2 | 0.49643 | 0.0073551 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1956.4 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1956.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1956.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1957 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1957.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
1957.4 | 0.49643 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1957.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1957.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1958 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1958.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1958.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1958.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1958.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1959 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1959.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1959.4 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1959.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1959.8 | 0.49643 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1960 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1960.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1960.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1960.6 | 0.49643 | 0.0089549 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1960.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1961 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1961.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1961.4 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1961.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1961.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1962 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1962.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1962.4 | 0.59242 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1962.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1962.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1963 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1963.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1963.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1963.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1963.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1964 | 0.49643 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1964.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1964.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1964.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1964.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1965 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.38019 | 0.0083128
1965.2 | 0.49643 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1965.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0049255 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1965.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1965.8 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1966 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1966.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.011511
1966.4 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1966.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1966.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1967 | 0.49643 | 0.0089549 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1967.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0095798 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1967.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1967.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1967.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1968 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1968.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1968.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1968.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.006713
1968.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.0080692 | 0.28424 | 0.0083128
1969 | 0.49643 | 0.0073551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1969.2 | 0.49643 | 0.010554 | 0.58176 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1969.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1969.6 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1969.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0050916 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1970 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1970.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.47518 | 0.0070012 | 0.526 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1970.4 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1970.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
1970.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1971 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1971.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1971.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1971.6 | 0.59242 | 0.0073551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1971.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1972 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1972.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0054014 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1972.4 | 0.59242 | 0.0073551 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1972.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1972.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1973 | 0.40048 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1973.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.006713
1973.4 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1973.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1973.8 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1974 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1974.2 | 0.49643 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1974.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1974.6 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.006713
1974.8 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1975 | 0.49643 | 0.0073551 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1975.2 | 0.59242 | 0.0089549 | 0.38986 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1975.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.28424 | 0.0083128
1975.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.006713
1975.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1976 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1976.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1976.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.47618 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1976.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1976.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1977 | 0.59242 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1977.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.009912
1977.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1977.6 | 0.68838 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1977.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1978 | 0.49643 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.006713
1978.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1978.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1978.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.28424 | 0.0083128
1978.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1979 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1979.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.006713
1979.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1979.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1979.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1980 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1980.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.0080692 | 0.38019 | 0.009912
1980.4 | 0.59242 | 0.0073551 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0102 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1980.6 | 0.59242 | 0.012154 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1980.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.38019 | 0.0083128
1981 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1981.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0049255 | 0.66813 | 0.0066908 | 0.48581 | 0.009669 | 0.28424 | 0.009912
1981.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1981.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.0083128
1981.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1982 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1982.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.48581 | 0.009669 | 0.28424 | 0.0083128
1982.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1982.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1982.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1983 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.0080692 | 0.28424 | 0.0083128
1983.2 | 0.59242 | 0.012154 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1983.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1983.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.006713
1983.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1984 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1984.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1984.4 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1984.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1984.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1985 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1985.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1985.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1985.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1985.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1986 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1986.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1986.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1986.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1986.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1987 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1987.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1987.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1987.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1987.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1988 | 0.49643 | 0.010554 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1988.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1988.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1988.6 | 0.59242 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1988.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1989 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0097238 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1989.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1989.4 | 0.59242 | 0.0089549 | 0.58176 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1989.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1989.8 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1990 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.009613 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1990.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1990.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1990.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1990.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1991 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1991.2 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1991.4 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1991.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.009613 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1991.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.009912
1992 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0097238 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1992.2 | 0.68838 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1992.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
1992.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1992.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1993 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.8139 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
1993.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1993.4 | 0.59242 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1993.6 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1993.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1994 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1994.2 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1994.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1994.6 | 0.59242 | 0.0089549 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.8139 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.28424 | 0.009912
1994.8 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.47618 | 0.0083128
1995 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1995.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1995.4 | 0.59242 | 0.010554 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.011268 | 0.38019 | 0.009912
1995.6 | 0.49643 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1995.8 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1996 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1996.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1996.4 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.009912
1996.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1996.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1997 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
1997.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
1997.4 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0081246 | 0.57213 | 0.0050916 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
1997.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1997.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.38916 | 0.0080139 | 0.57118 | 0.0086004 | 0.71795 | 0.0065247 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.28424 | 0.0083128
1998 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.38916 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1998.2 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.009912
1998.4 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.47618 | 0.009912
1998.6 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0048148 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.28424 | 0.009912
1998.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1999 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.57213 | 0.009912
1999.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
1999.4 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.76408 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
1999.6 | 0.49643 | 0.0089549 | 0.38986 | 0.0063808 | 0.5811 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.009912
1999.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2000 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2000.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2000.4 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0065247 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2000.6 | 0.49643 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2000.8 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2001 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.76408 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2001.2 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.57213 | 0.0050916 | 0.5818 | 0.011268 | 0.38019 | 0.0083128
2001.4 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.28424 | 0.0083128
2001.6 | 0.59242 | 0.0089549 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.48581 | 0.011268 | 0.38019 | 0.0083128
2001.8 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.47518 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2002 | 0.49643 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.66713 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.67775 | 0.009669 | 0.38019 | 0.0083128
2002.2 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0050916 | 0.5818 | 0.009669 | 0.28424 | 0.009912
2002.4 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.5811 | 0.006414 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.57213 | 0.0066908 | 0.67775 | 0.011268 | 0.38019 | 0.0083128
2002.6 | 0.59242 | 0.010554 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0070012 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.38986 | 0.009669 | 0.38019 | 0.0083128
2002.8 | 0.59242 | 0.0089549 | 0.38986 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2003 | 0.49643 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2003.2 | 0.59242 | 0.010554 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.57213 | 0.0050916 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2003.4 | 0.59242 | 0.010554 | 0.38986 | 0.0079807 | 0.48515 | 0.0080139 | 0.47518 | 0.0086004 | 0.62195 | 0.0065247 | 0.66813 | 0.0066908 | 0.48581 | 0.0080692 | 0.38019 | 0.0083128
2003.6 | 0.49643 | 0.0089549 | 0.48581 | 0.0047816 | 0.48515 | 0.006414 | 0.57118 | 0.0086004 | 0.526 | 0.0081246 | 0.66813 | 0.0066908 | 0.5818 | 0.009669 | 0.28424 | 0.0083128
2003.8 | 0.59242 | 0.010554 | 0.48581 | 0.0079807 | 0.48515 | 0.0080139 | 0.57118 | 0.0086004 | 0.526 | 0.0065247 | 0.66813 | 0.0066908 | 0.5818 | 0.011268 | 0.38019 | 0.009912
2004 | 0.59242 | 0.0089549 | 0.48581 | 0.0063808 | 0.48515 | 0.0080139 | 0.66713 | 0.0086004 | 0.62195 | 0.0081246 | 0.66813 | 0.0082906 | 0.5818 | 0.009669 | 0.38019 | 0.0083128
2004.2 | 2.7997 | 0.055339 | 2.789 | 0.052765 | 3.3642 | 0.052798 | 3.0663 | 0.051786 | 2.8292 | 0.05131 | 3.4511 | 0.056274 | 3.2689 | 0.054453 | 2.6834 | 0.053097
2004.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2004.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2004.8 | -73.4943 | -1.2226 | -73.6969 | -1.23 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2005 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2005.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2005.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2005.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2005.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2006 | -73.4943 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2006.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2006.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2006.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2006.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2007 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2007.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2007.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2007.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2007.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2008 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2008.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.5056 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2008.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2008.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2008.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2009 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2009.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2009.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2009.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2009.8 | -73.3983 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2219 | -73.8984 | -1.2265
2010 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2010.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2010.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2010.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2010.8 | -73.4943 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2262 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2011 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2011.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2011.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2011.6 | -73.4943 | -1.2226 | -73.6969 | -1.23 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2011.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2281 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2012 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.7065 | -1.2265
2012.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2012.4 | -73.4943 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2012.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2012.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2013 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2013.2 | -73.3983 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2013.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2013.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2013.8 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2014 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2262 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2014.2 | -73.4943 | -1.2226 | -73.6969 | -1.23 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2014.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2014.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2014.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2015 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2015.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2281 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2015.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2015.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2015.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2016 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2016.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2016.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2262 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2235 | -73.8984 | -1.2265
2016.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2016.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2017 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2017.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2017.4 | -73.4943 | -1.2226 | -73.6009 | -1.23 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2017.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2017.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2018 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2018.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2018.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2018.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.7065 | -1.2265
2018.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.5056 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2019 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2019.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2019.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2019.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2019.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2020 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2020.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2020.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2020.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2020.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2021 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2021.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.5056 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2021.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2021.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2021.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2022 | -73.3983 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2022.2 | -73.4943 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2022.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2022.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2022.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2023 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2262 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2023.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2023.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2023.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2023.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2024 | -73.4943 | -1.2226 | -73.6969 | -1.23 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2024.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2024.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2024.6 | -73.3983 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2024.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2025 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.5056 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2025.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2025.4 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2262 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2025.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2025.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2026 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2262 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2026.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2026.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2026.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2262 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2026.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2262 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2027 | -73.4943 | -1.2226 | -73.6969 | -1.23 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2027.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2027.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2027.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2027.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2028 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2028.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2028.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2028.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2028.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2029 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2029.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2029.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2029.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2029.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2030 | -73.3983 | -1.2226 | -73.6969 | -1.2316 | -73.5056 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2030.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2030.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2030.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2030.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2031 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2031.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2031.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2031.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2031.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2032 | -73.4943 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2032.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2032.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2032.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2032.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2033 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2033.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2033.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2033.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2033.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2034 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2034.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2034.4 | -73.4943 | -1.2226 | -73.6969 | -1.23 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2034.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2034.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2035 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2035.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2035.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2035.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2035.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2036 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2036.2 | -73.3983 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2036.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2036.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2036.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2037 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2037.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2037.4 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2037.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2037.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2038 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2038.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2262 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2038.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2038.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2038.8 | -73.4943 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2039 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2039.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2039.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.5056 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2039.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2039.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2235 | -73.8984 | -1.2265
2040 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2040.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2040.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2040.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2040.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.5056 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2041 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2262 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2041.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2041.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2041.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2041.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2042 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2042.2 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2042.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2042.6 | -73.3983 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2042.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2043 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2043.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2043.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2043.6 | -73.3983 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2043.8 | -73.4943 | -1.2226 | -73.6969 | -1.23 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2044 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2044.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2262 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2044.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2044.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2044.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2045 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2045.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2045.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2262 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2045.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2045.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2046 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2046.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.7065 | -1.2265
2046.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2046.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2046.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2047 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2047.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2047.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2047.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2047.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2048 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2048.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8025 | -1.2265
2048.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2048.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.5056 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2048.8 | -73.4943 | -1.2226 | -73.6969 | -1.23 | -73.5056 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2049 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2262 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2049.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2049.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2049.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2049.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2050 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2050.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2050.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2050.6 | -73.4943 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2050.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2051 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2051.2 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2051.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2051.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2051.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2052 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2052.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2052.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2052.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2052.8 | -73.4943 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2053 | -73.4943 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2053.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2053.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2053.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2053.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2054 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2299 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2054.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2054.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2054.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2249
2054.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2055 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2055.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2055.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2055.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2055.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2056 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2056.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2056.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2056.6 | -73.4943 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2056.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2057 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2057.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2057.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.5056 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2057.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2057.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2058 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2058.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2058.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2058.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2058.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2059 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2059.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2059.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2059.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2059.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2060 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.2728 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2060.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2060.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8025 | -1.2265
2060.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2060.8 | -73.4943 | -1.2226 | -73.6009 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2061 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.3226 | -1.2297 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2061.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2061.4 | -73.4943 | -1.221 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2061.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2061.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2062 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2062.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2062.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2062.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2062.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2235 | -73.8984 | -1.2265
2063 | -73.3983 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.409 | -1.2251 | -73.8984 | -1.2265
2063.2 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2063.4 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.23 | -73.4196 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2063.6 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265
2063.8 | -73.4943 | -1.2226 | -73.6969 | -1.2316 | -73.6016 | -1.2316 | -73.5155 | -1.2278 | -73.3688 | -1.2315 | -73.4186 | -1.2313 | -73.5049 | -1.2251 | -73.8984 | -1.2265

## Converted Data C2
Fire Time (s) | C2 V1 | C2 A1 | C2 V2 | C2 A2 | C2 V3 | C2 A3 | C2 V4 | C2 A4 | C2 V5 | C2 A5 | C2 V6 | C2 A6 | C2 V7 | C2 A7 | C2 V8 | C2 A8
-10 | 131.1537 | 0.0056289 | -0.0086323 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.0019319 | 0.11554 | 0.0054293 | 0.11392 | 0.0012893 | 0.25303 | -0.0065746 | 0.16505 | 7.1911e-05
-9.8 | 131.1537 | 0.0024299 | 0.087319 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0038295 | 0.20987 | 0.0044883 | 0.44497 | 0.0014227 | 0.16505 | 0.0016718
-9.6 | 131.1537 | 0.0024299 | 0.087319 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
-9.4 | 131.0577 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.075065 | 0.00033201 | 0.019589 | 0.0054293 | 0.11392 | -0.00030988 | 0.54092 | -0.00017715 | 0.16505 | 7.1911e-05
-9.2 | 131.1537 | 0.0024299 | 0.087319 | 0.0031381 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.011827 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
-9 | 131.1537 | 0.0040291 | -0.20057 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.16505 | 7.1911e-05
-8.8 | 131.1537 | 0.0024299 | -0.0086323 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.17102 | -0.0012672 | 0.21153 | 0.0038295 | 0.11392 | 0.0012893 | 0.34898 | 0.0014227 | 0.16505 | 0.00647
-8.6 | 131.1537 | -0.00076916 | -0.29653 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.21153 | 0.0054293 | 0.11392 | 0.0012893 | 0.34898 | -0.00017715 | 0.261 | 7.1911e-05
-8.4 | 131.1537 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.47751 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.11554 | 0.0038295 | 0.11392 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | -0.0015273
-8.2 | 131.1537 | 0.0024299 | 0.087319 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.17102 | 0.00033201 | -0.17235 | 0.0054293 | 0.11392 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 7.1911e-05
-8 | 131.1537 | 0.0024299 | 0.087319 | -6.0896e-05 | 0.28557 | 8.3003e-05 | 0.45891 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | -0.00017715 | 0.16505 | 0.0016718
-7.8 | 131.2496 | 0.0040291 | 0.18331 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.17102 | 0.0067301 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.54092 | 0.0014227 | 0.35695 | 0.0016718
-7.6 | 131.2496 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.45891 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | -0.00030988 | -0.034861 | 0.0014227 | 0.261 | 7.1911e-05
-7.4 | 130.9617 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.65085 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | -0.0035089 | 0.34898 | 0.0046217 | 0.261 | 0.0016718
-7.2 | 131.1537 | 0.00083003 | -0.0086323 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.30748 | 0.0054293 | 0.20987 | -0.00030988 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
-7 | 131.2496 | 0.0040291 | 0.18331 | 0.0031381 | 0.38156 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.00063108 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
-6.8 | 131.5375 | 0.0024299 | 0.087319 | 0.0015389 | 0.28557 | 8.3003e-05 | -0.11688 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0012893 | 0.44497 | 0.0014227 | 0.16505 | 7.1911e-05
-6.6 | 131.4415 | 0.0024299 | 0.18331 | 0.0015389 | 0.5735 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.16505 | 7.1911e-05
-6.4 | 131.3456 | 0.0040291 | 0.18331 | -6.0896e-05 | 0.18962 | 8.3003e-05 | 0.17102 | 0.0019319 | 0.11554 | 0.0022303 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
-6.2 | 131.2496 | 0.0024299 | 0.18331 | 0.0063372 | 0.38156 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0012893 | 0.34898 | 0.0014227 | 0.16505 | 7.1911e-05
-6 | 131.1537 | 0.0024299 | 0.087319 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0044883 | 0.44497 | 0.0014227 | 0.16505 | 0.0016718
-5.8 | 131.2496 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.11392 | 0.0012893 | 0.25303 | -0.0017763 | 0.16505 | 7.1911e-05
-5.6 | 131.1537 | 0.0072281 | 0.18331 | 0.0015389 | 0.093666 | 0.003282 | 0.17102 | 0.0019319 | 0.11554 | 0.0086283 | 0.20987 | 0.0044883 | 0.06109 | 0.0014227 | 0.16505 | 7.1911e-05
-5.4 | 131.2496 | 0.0024299 | -0.10462 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.019589 | 0.010228 | 0.30582 | 0.0092866 | 0.34898 | 0.0014227 | 0.16505 | 7.1911e-05
-5.2 | 131.1537 | 0.0040291 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.35695 | 0.0016718
-5 | 131.2496 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.003282 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.16505 | 7.1911e-05
-4.8 | 131.1537 | 0.0024299 | 0.37521 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.26697 | 0.0019319 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.069058 | 0.0016718
-4.6 | 131.0577 | 0.0056289 | 0.18331 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.21153 | 0.0038295 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | -0.12288 | 7.1911e-05
-4.4 | 130.8658 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 8.3003e-05 | -0.11688 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | -0.00017715 | 0.16505 | 0.0016718
-4.2 | 131.1537 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.34898 | 0.0014227 | 0.16505 | 7.1911e-05
-4 | 131.0577 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.075065 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 7.1911e-05
-3.8 | 131.1537 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.16505 | 7.1911e-05
-3.6 | 131.0577 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | -0.0015162 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.25303 | 0.0014227 | 0.16505 | 0.0016718
-3.4 | 131.1537 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.38156 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0044883 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
-3.2 | 131.1537 | 0.0024299 | 0.18331 | 0.004738 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0038295 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | -0.0015273
-3 | 131.0577 | 0.00083003 | -0.0086323 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.003531 | 0.11554 | 0.0038295 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.16505 | 0.0048708
-2.8 | 131.1537 | -0.0023683 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.17102 | 0.0019319 | 0.21153 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
-2.6 | 131.0577 | 0.00083003 | 0.27926 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.019589 | 0.00063108 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
-2.4 | 131.2496 | 0.00083003 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.17102 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
-2.2 | 131.2496 | 0.0040291 | 0.087319 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.075065 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.25303 | 0.0014227 | 0.261 | 7.1911e-05
-2 | 130.8658 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
-1.8 | 131.0577 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | -0.00096876 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
-1.6 | 131.0577 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.63692 | 0.0014227 | 0.261 | 0.0016718
-1.4 | 131.0577 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
-1.2 | 131.0577 | 0.00083003 | -0.10462 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.40347 | 0.0070285 | 0.20987 | 0.0012893 | 0.44497 | 0.0030219 | 0.54889 | 0.0016718
-1 | 131.0577 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.019589 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | -0.0015273
-0.8 | 130.9617 | 0.0024299 | 0.18331 | -0.0016601 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.019589 | 0.010228 | 0.20987 | -0.0019091 | 0.34898 | 0.0014227 | 0.16505 | 7.1911e-05
-0.6 | 130.9617 | 0.0024299 | -0.0086323 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | -0.00017715 | 0.16505 | 0.0016718
-0.4 | 130.9617 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.019589 | 0.010228 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.35695 | 0.0016718
-0.2 | 130.9617 | 0.0024299 | 0.087319 | -0.0032593 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.019589 | 0.00063108 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 7.1911e-05
0 | 130.8658 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | -0.076363 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.35695 | 0.0016718
0.2 | 130.9617 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.0019319 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | -0.0049754 | 0.261 | 0.0016718
0.4 | 130.9617 | -0.00076916 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | -0.0028664 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0048708
0.6 | 130.9617 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 7.1911e-05
0.8 | 130.8658 | 0.0024299 | 0.18331 | 0.0015389 | 0.18962 | 0.003282 | 0.17102 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.25303 | 0.0014227 | 0.261 | 0.0016718
1 | 130.8658 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
1.2 | 130.7698 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.019589 | 0.0038295 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
1.4 | 130.9617 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.45891 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.15708 | 0.0014227 | 0.261 | 0.0016718
1.6 | 130.8658 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0070285 | 0.40181 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 7.1911e-05
1.8 | 130.7698 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.5549 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893 | 0.25303 | 0.0014227 | 0.261 | 0.0016718
2 | 130.8658 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.0019319 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
2.2 | 130.7698 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.0019319 | 0.11554 | 0.0038295 | -0.26996 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0048708
2.4 | 130.8658 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.075065 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.25303 | 0.0014227 | 0.261 | 0.0016718
2.6 | 130.7698 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0080803 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0060882 | 0.44497 | 0.0014227 | 0.16505 | 0.0016718
2.8 | 130.7698 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.093666 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0070285 | 0.78566 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
3 | 131.0577 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.0019319 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.35695 | 0.0016718
3.2 | 130.7698 | 0.0024299 | 0.18331 | -0.0016601 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | -0.0047263
3.4 | 130.7698 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.0019319 | 0.11554 | 0.0070285 | 0.017929 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
3.6 | 130.6738 | 0.0040291 | 0.18331 | -0.0016601 | 0.47751 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0060882 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
3.8 | 130.6738 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | -0.0012672 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.16505 | 7.1911e-05
4 | 130.8658 | 0.0024299 | -0.0086323 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.26697 | 0.00033201 | -0.076363 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
4.2 | 130.6738 | 0.0056289 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.17102 | -0.0012672 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0094199 | 0.261 | 0.0016718
4.4 | 130.6738 | 0.0024299 | 0.18331 | -0.0016601 | 0.18962 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.11554 | 0.00063108 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.16505 | -0.0015273
4.6 | 130.5779 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.45891 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.15708 | 0.0014227 | 0.261 | 0.0016718
4.8 | 130.7698 | 0.0024299 | 0.18331 | -0.0016601 | -0.098276 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0038295 | -0.17401 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0048708
5 | 130.6738 | 0.0024299 | 0.18331 | 0.0015389 | 0.7654 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0060882 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
5.2 | 130.5779 | 0.00083003 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.019589 | 0.0070285 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
5.4 | 130.4819 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.0019319 | 0.019589 | 0.0054293 | 0.20987 | 0.0044883 | 0.73287 | 0.0030219 | 0.16505 | 0.0016718
5.6 | 130.5779 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | -0.020925 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.54092 | 0.0014227 | 0.261 | 0.0016718
5.8 | 130.7698 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.66945 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
6 | 130.6738 | 0.0024299 | 0.37521 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | -0.076363 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.069058 | 0.0016718
6.2 | 130.5779 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | -0.0015162 | 0.17102 | 0.00033201 | 0.019589 | 0.0054293 | 0.11392 | 0.0012893 | 0.54092 | 0.0014227 | 0.261 | 0.0016718
6.4 | 130.4819 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.82882 | 0.0014227 | 0.261 | 0.0016718
6.6 | 130.6738 | 0.00083003 | 0.18331 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.17102 | 0.0067301 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | -0.0017763 | 0.261 | 0.0016718
6.8 | 130.6738 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | -0.003116 | 0.17102 | 0.00033201 | 0.019589 | 0.0054293 | 0.30582 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
7 | 130.5779 | 0.0040291 | -0.0086323 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | -0.00017715 | 0.35695 | 7.1911e-05
7.2 | 130.5779 | 0.0024299 | 0.18331 | 0.0015389 | 0.18962 | 0.0016822 | 0.17102 | 0.00033201 | 0.019589 | 0.0038295 | -0.17401 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0048708
7.4 | 130.6738 | 0.0040291 | 0.18331 | 0.0015389 | 0.28557 | -0.0015162 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
7.6 | 130.5779 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.0067301 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
7.8 | 130.6738 | 0.0056289 | 0.18331 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.26697 | 0.003531 | 0.11554 | 0.0054293 | 0.20987 | 0.0044883 | 0.34898 | 0.0062209 | 0.261 | 0.0016718
8 | 130.6738 | 0.0024299 | 0.37521 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
8.2 | 130.5779 | 0.0024299 | 0.18331 | -0.0016601 | -0.098276 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.017929 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 7.1911e-05
8.4 | 131.0577 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.003531 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | -0.0033755 | 0.261 | 0.0016718
8.6 | 130.6738 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.0083293 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
8.8 | 130.6738 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | -0.020925 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
9 | 130.6738 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
9.2 | 130.5779 | 0.0024299 | 0.18331 | 0.0031381 | 0.28557 | -0.003116 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | -0.00030988 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
9.4 | 130.5779 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.075065 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.15708 | 0.0014227 | 0.261 | 0.0016718
9.6 | 130.5779 | 0.0040291 | 0.087319 | 0.004738 | 0.18962 | 0.0016822 | 0.17102 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0012893 | 0.34898 | 0.0014227 | -0.12288 | 0.0016718
9.8 | 130.5779 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.069058 | 0.0016718
10 | 130.6738 | 0.0024299 | 0.087319 | -0.0048591 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.34898 | 0.0014227 | 0.261 | 0.00647
10.2 | 130.5779 | 0.0040291 | 0.18331 | -0.0016601 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0022303 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.069058 | -0.0015273
10.4 | 130.6738 | 0.0040291 | 0.087319 | -0.0032593 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0086283 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.16505 | 0.00647
10.6 | 130.5779 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0048812 | 0.17102 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0060882 | 0.44497 | -0.0017763 | 0.261 | 0.0016718
10.8 | 130.7698 | 0.0040291 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.075065 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
11 | 130.6738 | 0.0040291 | 0.18331 | 0.0015389 | -0.098276 | 0.0016822 | 0.26697 | -0.0012672 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 0.0016718
11.2 | 130.5779 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.069058 | 0.0016718
11.4 | 130.6738 | 0.0040291 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0062209 | 0.261 | 0.0016718
11.6 | 130.6738 | -0.00076916 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | -0.076363 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | -0.00017715 | 0.35695 | 0.0016718
11.8 | 130.4819 | 0.0040291 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.075065 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.15708 | 0.0014227 | 0.16505 | 0.0016718
12 | 130.5779 | 0.0040291 | 0.18331 | -0.0064583 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.40181 | 0.0028892 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
12.2 | 130.4819 | 0.0056289 | 0.18331 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
12.4 | 130.5779 | 0.0040291 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.45891 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.25303 | 0.0014227 | 0.261 | 0.0016718
12.6 | 130.5779 | 0.0056289 | 0.18331 | 0.0015389 | 0.093666 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
12.8 | 130.6738 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.38156 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | -0.026893 | 0.0016718
13 | 130.6738 | 0.012026 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | -0.0012672 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | -0.00017715 | 0.261 | 0.0016718
13.2 | 130.6738 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.28557 | 8.3003e-05 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.40181 | 0.0028892 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
13.4 | 130.6738 | 0.010427 | 0.18331 | -0.0016601 | 0.38156 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0076874 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
13.6 | 130.5779 | 0.015225 | 0.18331 | 0.0015389 | 0.47751 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.11554 | 0.0086283 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
13.8 | 130.7698 | 0.024822 | 0.18331 | 0.0031381 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.011827 | 0.20987 | 0.0060882 | 0.34898 | 0.0014227 | 0.261 | 7.1911e-05
14 | 130.5779 | 0.020024 | 0.18331 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.36296 | -0.0012672 | 0.11554 | 0.015026 | 0.30582 | 0.0092866 | 0.44497 | -0.00017715 | 0.261 | 0.0016718
14.2 | 130.6738 | 0.016825 | 0.18331 | 0.0079364 | 0.28557 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.21153 | 0.019824 | 0.20987 | 0.012486 | 0.34898 | 0.0030219 | 0.16505 | 0.0016718
14.4 | 130.5779 | 0.0088273 | 0.087319 | 0.0031381 | 0.18962 | 0.0016822 | 0.26697 | 0.00033201 | 0.30748 | 0.010228 | 0.30582 | 0.015685 | 0.34898 | 0.0014227 | -0.12288 | 0.0016718
14.6 | 130.5779 | 0.0072281 | 0.087319 | -6.0896e-05 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.015026 | 0.40181 | 0.0076874 | 0.25303 | 0.0014227 | 0.16505 | 7.1911e-05
14.8 | 130.6738 | 0.0072281 | 0.18331 | 0.0031381 | 0.18962 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.30582 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
15 | 130.5779 | 0.0072281 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.40347 | 0.0054293 | 0.11392 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | -0.0015273
15.2 | 130.8658 | 0.0072281 | 0.18331 | -6.0896e-05 | 0.28557 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.25303 | 0.0014227 | 0.261 | -0.0015273
15.4 | 130.6738 | 0.0072281 | 0.18331 | 0.0015389 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.15708 | 0.0030219 | 0.261 | 0.0016718
15.6 | 130.5779 | 0.0072281 | 0.087319 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.15708 | 0.0030219 | 0.261 | 0.0016718
15.8 | 130.6738 | 0.0072281 | 0.27926 | -6.0896e-05 | 0.38156 | -0.0015162 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0060882 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
16 | 130.7698 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.075065 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892 | 0.25303 | 0.0014227 | 0.16505 | 0.0016718
16.2 | 130.4819 | 0.0072281 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
16.4 | 130.6738 | 0.0072281 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | -0.00030988 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
16.6 | 130.7698 | 0.0072281 | 0.18331 | 0.0015389 | 0.18962 | -0.0015162 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | -0.0019091 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
16.8 | 130.7698 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.17102 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
17 | 130.5779 | 0.0088273 | 0.087319 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.35695 | 0.0016718
17.2 | 130.7698 | 0.0056289 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.075065 | -0.0076652 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.35695 | 0.0016718
17.4 | 130.5779 | 0.0072281 | 0.087319 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | -0.076363 | 0.0054293 | 0.11392 | 0.0012893 | 0.34898 | 0.0014227 | 0.45294 | 0.0016718
17.6 | 130.6738 | 0.0072281 | 0.18331 | 0.0031381 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.21153 | 0.0022303 | 0.11392 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 7.1911e-05
17.8 | 130.7698 | 0.0072281 | 0.18331 | 0.0015389 | 0.18962 | -0.0047152 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
18 | 130.7698 | 0.0072281 | 0.087319 | -6.0896e-05 | 0.38156 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.74084 | 0.0016718
18.2 | 130.7698 | 0.0056289 | 0.18331 | -6.0896e-05 | 0.38156 | 8.3003e-05 | 0.075065 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0044883 | 0.44497 | -0.0033755 | 0.261 | 0.0016718
18.4 | 130.6738 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.0048812 | 0.17102 | 0.00033201 | 0.019589 | 0.0038295 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
18.6 | 130.7698 | 0.0072281 | 0.56715 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.49942 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 0.0016718
18.8 | 130.7698 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.5549 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.25303 | 0.0014227 | 0.261 | 0.0032709
19 | 130.7698 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | -0.21287 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
19.2 | 130.7698 | 0.013626 | 0.27926 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.30748 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | -0.026893 | 0.0016718
19.4 | 130.7698 | 0.0072281 | 0.18331 | 0.0015389 | 0.18962 | 0.0016822 | 0.5549 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.63692 | 0.0014227 | 0.261 | 0.0016718
19.6 | 130.8658 | 0.0088273 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.40181 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
19.8 | 130.8658 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.30582 | -0.00030988 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
20 | 130.7698 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0048812 | 0.26697 | -0.0012672 | 0.11554 | 0.0054293 | 0.20987 | -0.00030988 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
20.2 | 130.7698 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
20.4 | 130.7698 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0012893 | 0.34898 | 0.0030219 | 0.16505 | 0.0016718
20.6 | 130.7698 | 0.0056289 | 0.27926 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.003531 | 0.11554 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | -0.0031265
20.8 | 130.8658 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | -0.0035089 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
21 | 130.8658 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.25303 | 0.0014227 | 0.261 | 0.0016718
21.2 | 130.7698 | 0.0088273 | 0.18331 | -6.0896e-05 | -0.098276 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.59375 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 7.1911e-05
21.4 | 130.8658 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.019589 | 0.0086283 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
21.6 | 130.7698 | 0.0072281 | 0.087319 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.54092 | 0.0014227 | 0.261 | 0.0016718
21.8 | 130.7698 | 0.0088273 | 0.18331 | 0.0015389 | 0.093666 | 0.003282 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.63692 | 0.0014227 | 0.261 | 0.0016718
22 | 130.7698 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.47751 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.30582 | 0.0076874 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
22.2 | 130.9617 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | -0.00030988 | 0.63692 | -0.00017715 | 0.16505 | 0.0016718
22.4 | 130.7698 | 0.0088273 | 0.18331 | 0.0063372 | 0.28557 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
22.6 | 130.7698 | 0.010427 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.003531 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.25303 | 0.0046217 | 0.261 | 0.0032709
22.8 | 130.8658 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.013427 | 0.30582 | 0.0012893 | 0.44497 | 0.0014227 | 0.16505 | 0.0048708
23 | 130.8658 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.17102 | 0.0019319 | 0.30748 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
23.2 | 130.8658 | 0.0072281 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.17102 | -0.0044662 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
23.4 | 130.8658 | 0.0072281 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.0051309 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
23.6 | 130.7698 | 0.0088273 | 0.087319 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | -0.00096876 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.16505 | 0.0016718
23.8 | 130.8658 | 0.0072281 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.010228 | 0.30582 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | -0.0031265
24 | 130.8658 | 0.0088273 | 0.087319 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.64488 | 0.0016718
24.2 | 130.7698 | 0.010427 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | -0.0060654 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.069058 | 0.0016718
24.4 | 131.0577 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893 | 0.06109 | 0.0014227 | 0.261 | 0.0016718
24.6 | 130.8658 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
24.8 | 130.8658 | 0.0088273 | 0.56715 | 0.0031381 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | -0.2683 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | -0.00017715 | 0.35695 | 7.1911e-05
25 | 130.8658 | 0.0088273 | 0.37521 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.30748 | 0.0038295 | 0.11392 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.00647
25.2 | 130.8658 | 0.010427 | 0.37521 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | -0.0044662 | 0.21153 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | -0.0033755 | 0.35695 | 7.1911e-05
25.4 | 130.8658 | 0.0088273 | 0.087319 | -0.0016601 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.30582 | 0.0012893 | 0.34898 | -0.00017715 | 0.16505 | 0.0048708
25.6 | 130.7698 | 0.0088273 | 0.18331 | 0.0015389 | 0.5735 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | -0.0015273
25.8 | 130.7698 | 0.0088273 | 0.18331 | 0.0031381 | 0.18962 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.40181 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 7.1911e-05
26 | 130.4819 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | -0.0028664 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0046217 | 0.261 | 0.0016718
26.2 | 130.7698 | 0.0072281 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
26.4 | 130.6738 | 0.03122 | 0.37521 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.0019319 | 0.019589 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
26.6 | 130.4819 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | -0.0012672 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | -0.00017715 | 0.261 | 0.0016718
26.8 | 130.194 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
27 | 130.002 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.0064811 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
27.2 | 129.8101 | 0.0056289 | 0.087319 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.30748 | 0.0054293 | 0.30582 | 0.0012893 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
27.4 | 130.002 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
27.6 | 130.194 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.28557 | -0.0015162 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
27.8 | 130.2899 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.25303 | 0.0030219 | 0.261 | 0.0016718
28 | 130.3859 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0076874 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
28.2 | 130.3859 | 0.0088273 | 0.18331 | 0.0015389 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
28.4 | 130.2899 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | -0.0019091 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
28.6 | 130.4819 | 0.0088273 | 0.18331 | 0.0031381 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
28.8 | 130.4819 | 0.0088273 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | -0.076363 | 0.0070285 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
29 | 130.4819 | 0.0088273 | 0.18331 | -0.0016601 | 0.38156 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
29.2 | 130.6738 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | -0.00017715 | 0.261 | 0.0016718
29.4 | 130.4819 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.16505 | 0.0016718
29.6 | 130.4819 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.40181 | -0.0035089 | 0.44497 | 0.0014227 | 0.16505 | 0.0032709
29.8 | 130.3859 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
30 | 130.4819 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 7.1911e-05
30.2 | 130.4819 | 0.0088273 | 0.18331 | 0.004738 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
30.4 | 130.4819 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
30.6 | 130.3859 | 0.0088273 | 0.18331 | 0.0015389 | 0.18962 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.59375 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
30.8 | 130.5779 | 0.012026 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | -0.0012672 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0062209 | 0.261 | 0.0016718
31 | 130.3859 | 0.010427 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
31.2 | 130.4819 | 0.010427 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
31.4 | 130.5779 | 0.010427 | 0.18331 | 0.0031381 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0048708
31.6 | 130.3859 | 0.010427 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | -0.076363 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
31.8 | 130.4819 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | -0.0012672 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
32 | 130.5779 | 0.012026 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893 | 0.34898 | -0.0017763 | 0.35695 | 0.0016718
32.2 | 130.4819 | 0.0072281 | 0.18331 | -0.0016601 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0022303 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 7.1911e-05
32.4 | 130.4819 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893 | 0.06109 | 0.0030219 | 0.35695 | 0.0032709
32.6 | 130.4819 | 0.010427 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.261 | 0.0032709
32.8 | 130.5779 | 0.010427 | 0.18331 | -0.0016601 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.35695 | 0.0032709
33 | 130.4819 | 0.010427 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.017929 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
33.2 | 130.4819 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
33.4 | 130.4819 | 0.0072281 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.069058 | 0.0016718
33.6 | 130.4819 | 0.012026 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 7.1911e-05
33.8 | 130.4819 | 0.010427 | 0.18331 | 0.0015389 | 0.28557 | 0.003282 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
34 | 130.4819 | 0.012026 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0022303 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.00647
34.2 | 130.4819 | 0.0088273 | 0.18331 | -0.0016601 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0048708
34.4 | 130.4819 | 0.015225 | 0.18331 | 0.0015389 | 0.38156 | 0.0048812 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | -0.00030988 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
34.6 | 130.3859 | 0.012026 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0038295 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0048708
34.8 | 130.4819 | 0.023223 | 0.18331 | 0.0015389 | 0.18962 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.013427 | 0.49776 | 0.0076874 | 0.44497 | 0.0014227 | 0.261 | 7.1911e-05
35 | 130.3859 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.18962 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 0.0016718
35.2 | 130.4819 | 0.010427 | 0.087319 | 0.0015389 | 0.38156 | 0.0016822 | -0.21287 | 0.00033201 | 0.30748 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 0.0032709
35.4 | 130.4819 | 0.0088273 | 0.087319 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0070285 | 0.30582 | 0.0028892 | 0.25303 | 0.0014227 | 0.45294 | 0.0016718
35.6 | 130.4819 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.30748 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0030219 | 0.16505 | 0.0016718
35.8 | 130.3859 | 0.010427 | 0.087319 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | -0.0012672 | 0.11554 | 0.0038295 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
36 | 130.5779 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
36.2 | 130.4819 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
36.4 | 130.4819 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.35695 | 0.0016718
36.6 | 130.4819 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | -0.0012672 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
36.8 | 130.5779 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
37 | 130.5779 | 0.0088273 | 0.18331 | 0.0015389 | 0.47751 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
37.2 | 130.5779 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0062209 | 0.16505 | 0.0016718
37.4 | 130.5779 | 0.0088273 | 0.37521 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0038295 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
37.6 | 130.6738 | 0.010427 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.019589 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
37.8 | 130.7698 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.5735 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
38 | 130.7698 | 0.012026 | 0.087319 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | -0.0028664 | 0.019589 | 0.0054293 | 0.11392 | 0.0012893 | 0.34898 | 0.0014227 | 0.45294 | 0.0016718
38.2 | 130.8658 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0016718
38.4 | 130.8658 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | -0.0028664 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | -0.0017763 | 0.261 | 0.0016718
38.6 | 130.7698 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.003531 | 0.019589 | 0.0038295 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
38.8 | 130.7698 | 0.0088273 | 0.27926 | -0.0016601 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.019589 | 0.010228 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.16505 | 0.0048708
39 | 130.8658 | 0.0088273 | 0.27926 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.40181 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
39.2 | 130.7698 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
39.4 | 130.8658 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 0.0016718
39.6 | 130.7698 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0076874 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
39.8 | 130.7698 | 0.0088273 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.11392 | 0.0012893 | 0.44497 | 0.0014227 | 0.16505 | 0.0032709
40 | 130.8658 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
40.2 | 130.7698 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
40.4 | 130.8658 | 0.010427 | 0.18331 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.26697 | -0.0028664 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0046217 | 0.261 | 0.0016718
40.6 | 130.7698 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
40.8 | 130.7698 | 0.0072281 | 0.18331 | 0.0015389 | 0.18962 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.017929 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
41 | 130.7698 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.25303 | -0.00017715 | 0.261 | 0.0016718
41.2 | 130.7698 | 0.0072281 | 0.18331 | -6.0896e-05 | 0.18962 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.49776 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
41.4 | 130.7698 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.16505 | 0.0032709
41.6 | 130.6738 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | -0.0028664 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0016718
41.8 | 130.7698 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | -0.0028664 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0062209 | 0.261 | 0.0016718
42 | 130.7698 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.30582 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
42.2 | 130.7698 | 0.0056289 | 0.087319 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
42.4 | 130.7698 | 0.0072281 | 0.27926 | 0.0015389 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0016718
42.6 | 130.6738 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | -0.00017715 | 0.261 | 0.0016718
42.8 | 130.6738 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.019589 | 0.0070285 | 0.20987 | 0.0012893 | 0.25303 | 0.0030219 | 0.261 | 0.0016718
43 | 130.7698 | 0.0088273 | 0.087319 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | -0.0012672 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.069058 | 0.0016718
43.2 | 130.7698 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.003282 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | -0.00030988 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
43.4 | 130.6738 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
43.6 | 130.6738 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
43.8 | 130.6738 | 0.010427 | 0.27926 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
44 | 130.4819 | 0.010427 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | -0.0012672 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.16505 | 0.0016718
44.2 | 130.5779 | 0.012026 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.010228 | 0.30582 | 0.0044883 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
44.4 | 130.6738 | 0.020024 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
44.6 | 130.6738 | 0.023223 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0092866 | 0.54092 | -0.00017715 | 0.16505 | 0.0016718
44.8 | 130.6738 | 0.0072281 | 0.27926 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.011827 | 0.40181 | 0.017284 | 0.25303 | 0.0014227 | 0.261 | 0.0016718
45 | 130.6738 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.075065 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
45.2 | 130.6738 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.013427 | 0.30582 | 0.0012893 | 0.15708 | 0.0014227 | 0.16505 | 0.0016718
45.4 | 130.6738 | 0.0072281 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.010228 | 0.20987 | 0.0028892 | 0.34898 | -0.00017715 | 0.261 | -0.0015273
45.6 | 130.5779 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
45.8 | 130.5779 | 0.0088273 | -0.0086323 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 7.1911e-05
46 | 130.6738 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
46.2 | 130.7698 | 0.0088273 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.17102 | -0.0012672 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
46.4 | 130.5779 | 0.0088273 | 0.27926 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 7.1911e-05
46.6 | 130.5779 | 0.0072281 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.45294 | 0.0016718
46.8 | 130.6738 | 0.0072281 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
47 | 130.5779 | 0.0072281 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.35695 | 0.0016718
47.2 | 130.4819 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 7.1911e-05
47.4 | 130.6738 | 0.0072281 | 0.087319 | 0.004738 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.11554 | 0.0086283 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.16505 | 0.0048708
47.6 | 130.4819 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.075065 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | -0.00017715 | 0.261 | 0.0016718
47.8 | 130.5779 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0016718
48 | 130.3859 | 0.0056289 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
48.2 | 130.5779 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
48.4 | 130.4819 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
48.6 | 130.5779 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0046217 | 0.261 | 0.0016718
48.8 | 130.4819 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.25303 | 0.0014227 | 0.261 | 7.1911e-05
49 | 130.4819 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
49.2 | 130.3859 | 0.0072281 | 0.18331 | 0.0031381 | 0.18962 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
49.4 | 130.5779 | 0.0056289 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
49.6 | 130.4819 | 0.0056289 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
49.8 | 130.4819 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | -0.00030988 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
50 | 130.4819 | 0.0040291 | 0.18331 | -0.0016601 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
50.2 | 130.4819 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
50.4 | 130.4819 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.25303 | 0.0014227 | 0.261 | 0.0016718
50.6 | 130.3859 | 0.0056289 | 0.087319 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 7.1911e-05
50.8 | 130.3859 | 0.0056289 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0048812 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
51 | 130.3859 | 0.0056289 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 0.0032709
51.2 | 130.3859 | 0.0040291 | 0.27926 | -0.0016601 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.20987 | 0.0012893 | 0.34898 | 0.0030219 | 0.16505 | -0.0015273
51.4 | 130.3859 | 0.0040291 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | -0.076363 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
51.6 | 130.4819 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
51.8 | 130.4819 | 0.0040291 | 0.18331 | 0.0015389 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
52 | 130.3859 | 0.0040291 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.019589 | 0.0070285 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
52.2 | 130.2899 | 0.0040291 | 0.18331 | 0.0031381 | 0.18962 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0038295 | 0.30582 | 0.0044883 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
52.4 | 130.3859 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
52.6 | 130.2899 | 0.0040291 | 0.087319 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0048708
52.8 | 130.3859 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 0.0032709
53 | 130.3859 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | -0.0015273
53.2 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.63692 | 0.0030219 | 0.261 | 0.0032709
53.4 | 130.3859 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.35695 | 0.0016718
53.6 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
53.8 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0016718
54 | 130.2899 | 0.0056289 | 0.18331 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0048708
54.2 | 130.194 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.075065 | 0.00033201 | 0.019589 | 0.0086283 | 0.30582 | 0.0060882 | 0.15708 | 0.0030219 | 0.261 | 0.0032709
54.4 | 130.2899 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | -0.0015162 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.20987 | 0.0044883 | 0.54092 | 0.0014227 | 0.261 | 0.0016718
54.6 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 1.8984 | -0.0028664 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
54.8 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | -0.00017715 | 1.5086 | 7.1911e-05
55 | 130.2899 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
55.2 | 130.3859 | 0.0024299 | 0.18331 | 0.004738 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
55.4 | 130.2899 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 0.0032709
55.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | -0.0019091 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
55.8 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0016718
56 | 130.2899 | 0.00083003 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | -0.17235 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | -0.026893 | 0.0032709
56.2 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
56.4 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | -0.0015162 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
56.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
56.8 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0060882 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
57 | 130.2899 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.010228 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.35695 | 0.0032709
57.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.019589 | 0.0070285 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
57.4 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.5735 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
57.6 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.00647
57.8 | 130.3859 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 0.0016718
58 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0016718
58.2 | 130.3859 | 0.00083003 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | -0.076363 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.069058 | 0.0016718
58.4 | 130.4819 | 0.0040291 | 0.18331 | -6.0896e-05 | 0.5735 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.40181 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 7.1911e-05
58.6 | 130.4819 | 0.0024299 | 0.37521 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0016718
58.8 | 130.4819 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
59 | 130.4819 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 7.1911e-05
59.2 | 130.4819 | 0.00083003 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | -0.0028664 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.54092 | -0.00017715 | 0.261 | 0.0016718
59.4 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
59.6 | 130.4819 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | -0.00017715 | 0.35695 | 0.0032709
59.8 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
60 | 130.4819 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.16505 | 0.0032709
60.2 | 130.5779 | 0.0024299 | 0.087319 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.16505 | 0.0016718
60.4 | 130.4819 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.25303 | 0.0014227 | 0.261 | 0.0016718
60.6 | 130.5779 | 0.00083003 | 0.087319 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.35695 | 0.0016718
60.8 | 130.5779 | 0.0024299 | 0.18331 | 0.0031381 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.49776 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
61 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.35695 | 0.0048708
61.2 | 130.4819 | 0.0024299 | 0.087319 | 0.0031381 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.40181 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
61.4 | 130.5779 | 0.00083003 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
61.6 | 130.6738 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
61.8 | 130.6738 | 0.0040291 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
62 | 130.6738 | 0.0056289 | 0.18331 | -6.0896e-05 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.019589 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
62.2 | 130.4819 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.25303 | 0.0030219 | 0.261 | 0.0032709
62.4 | 130.6738 | 0.021623 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
62.6 | 130.6738 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.30582 | 0.0060882 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
62.8 | 130.6738 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.015026 | 0.30582 | 0.0076874 | 0.44497 | 0.0014227 | 0.261 | -0.0015273
63 | 130.6738 | 0.00083003 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.003531 | 0.21153 | 0.0054293 | 0.40181 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0016718
63.2 | 130.6738 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.5735 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0022303 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | -0.02392
63.4 | 130.6738 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0012893 | 0.54092 | 0.0014227 | 0.261 | 0.0016718
63.6 | 130.6738 | 0.0056289 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | -0.0028664 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.45294 | 0.0016718
63.8 | 130.7698 | 0.0024299 | 0.18331 | 0.004738 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
64 | 130.5779 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.25303 | 0.0014227 | 0.261 | 0.0016718
64.2 | 130.7698 | 0.0024299 | 0.27926 | 0.0015389 | 0.18962 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
64.4 | 130.7698 | 0.0024299 | -0.0086323 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
64.6 | 130.8658 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 7.1911e-05
64.8 | 131.6335 | 0.00083003 | 0.27926 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.36296 | -0.0012672 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.35695 | 0.0016718
65 | 130.8658 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | -0.00017715 | 0.35695 | 0.0016718
65.2 | 130.8658 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
65.4 | 130.8658 | 0.0024299 | 0.087319 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
65.6 | 130.7698 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0044883 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
65.8 | 130.5779 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
66 | 130.7698 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
66.2 | 130.7698 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
66.4 | 130.7698 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0038295 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | -0.0015273
66.6 | 130.7698 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0038295 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
66.8 | 130.6738 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | -0.00030988 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
67 | 130.7698 | 0.0024299 | 0.087319 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.40347 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
67.2 | 130.6738 | 0.0024299 | 0.27926 | 0.0015389 | 0.5735 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.49776 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
67.4 | 130.7698 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
67.6 | 130.7698 | 0.00083003 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
67.8 | 130.7698 | 0.00083003 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0014227 | 0.261 | 0.0032709
68 | 130.6738 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0051309 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893 | 0.34898 | 0.0014227 | 0.16505 | 0.0016718
68.2 | 130.7698 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
68.4 | 130.7698 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
68.6 | 130.6738 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0016718
68.8 | 130.6738 | 0.0024299 | 0.27926 | 0.0015389 | 0.18962 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
69 | 130.7698 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
69.2 | 130.5779 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.44497 | -0.00017715 | 0.261 | 0.0016718
69.4 | 130.6738 | 0.0024299 | 0.4712 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.0019319 | 0.019589 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
69.6 | 130.7698 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
69.8 | 130.7698 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 7.1911e-05
70 | 130.7698 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0016718
70.2 | 130.6738 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
70.4 | 130.6738 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
70.6 | 130.8658 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
70.8 | 130.6738 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.45294 | 0.0016718
71 | 130.6738 | 0.00083003 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0062209 | 0.35695 | 0.0032709
71.2 | 130.6738 | -0.00076916 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | -0.0028664 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 0.0032709
71.4 | 130.7698 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0012893 | 0.54092 | 0.0030219 | 0.16505 | 0.0032709
71.6 | 130.6738 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
71.8 | 130.6738 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
72 | 130.6738 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.25303 | 0.0030219 | 0.261 | 0.0016718
72.2 | 130.6738 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.45294 | 0.0016718
72.4 | 130.6738 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0062209 | 0.261 | 0.0016718
72.6 | 130.6738 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | -0.0012672 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.35695 | 0.0016718
72.8 | 130.6738 | 0.00083003 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.069058 | 0.0032709
73 | 130.6738 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0038295 | 0.20987 | 0.0012893 | 0.34898 | 0.0030219 | 0.261 | 0.00647
73.2 | 130.6738 | 0.0040291 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | -0.00017715 | 0.261 | 0.0032709
73.4 | 130.6738 | 0.0056289 | 0.18331 | 0.0015389 | 0.47751 | 0.0016822 | 0.26697 | -0.0028664 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0046217 | 0.261 | 0.0016718
73.6 | 130.5779 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.54889 | 0.0032709
73.8 | 130.6738 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
74 | 130.7698 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
74.2 | 130.6738 | 0.00083003 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
74.4 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.017929 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
74.6 | 130.5779 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
74.8 | 130.4819 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
75 | 130.6738 | 0.0040291 | 0.37521 | 0.0031381 | 0.28557 | 0.003282 | 0.26697 | 0.0019319 | -0.076363 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0048708
75.2 | 130.5779 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | -0.00017715 | 0.35695 | 0.0016718
75.4 | 130.5779 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.54889 | 0.0016718
75.6 | 130.5779 | 0.0088273 | 0.18331 | 0.0031381 | 0.28557 | 0.0016822 | 0.26697 | 0.003531 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0014227 | 0.35695 | 0.0032709
75.8 | 130.6738 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0038295 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
76 | 130.5779 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.54092 | -0.00017715 | 0.35695 | 0.0016718
76.2 | 130.5779 | 0.010427 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0016718
76.4 | 130.5779 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0086283 | 0.20987 | 0.0044883 | 0.34898 | 0.0014227 | 0.35695 | 0.0032709
76.6 | 130.5779 | 0.013626 | 0.27926 | 0.0031381 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 7.1911e-05
76.8 | 130.5779 | 0.020024 | 0.27926 | -6.0896e-05 | 0.28557 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
77 | 130.5779 | 0.020024 | 0.4712 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
77.2 | 130.4819 | 0.016825 | 0.37521 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
77.4 | 130.5779 | 0.020024 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.011827 | 0.30582 | 0.0092866 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
77.6 | 130.3859 | 0.03282 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.010228 | 0.20987 | 0.0092866 | 0.44497 | 0.0046217 | 0.261 | 0.0016718
77.8 | 130.6738 | 0.036018 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
78 | 130.7698 | 0.042416 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.011827 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.069058 | 0.0032709
78.2 | 130.6738 | 0.040817 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
78.4 | 130.2899 | 0.0024299 | 0.18331 | -0.0048591 | 0.28557 | 0.0016822 | 0.36296 | 0.0019319 | 0.11554 | 0.015026 | 0.49776 | 0.0076874 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
78.6 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.018225 | 0.30582 | 0.014085 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
78.8 | 130.194 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.010228 | 0.30582 | 0.018884 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
79 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.020483 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
79.2 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.45891 | 0.00033201 | 0.11554 | 0.010228 | 0.30582 | 0.018884 | 0.44497 | 0.0046217 | 0.261 | 0.0016718
79.4 | 130.4819 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
79.6 | 130.5779 | 0.0024299 | 0.18331 | 0.0063372 | 0.38156 | -0.0015162 | 0.36296 | 0.0019319 | 0.21153 | 0.013427 | 0.30582 | 0.0092866 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
79.8 | 130.5779 | 0.0024299 | 0.18331 | 0.004738 | 0.38156 | 0.0064811 | 0.26697 | 0.0019319 | 0.21153 | 0.016626 | 0.20987 | 0.0092866 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
80 | 130.5779 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | -0.21287 | 0.00033201 | 0.11554 | 0.0086283 | 0.40181 | 0.014085 | 0.44497 | 0.0030219 | 0.35695 | 7.1911e-05
80.2 | 130.5779 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0067301 | 0.21153 | 0.0054293 | 0.30582 | 0.0092866 | 0.44497 | 0.0046217 | 0.261 | 0.0016718
80.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 1.555 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
80.6 | 130.5779 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.11392 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
80.8 | 130.4819 | 0.0024299 | 0.18331 | 0.0063372 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.11392 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
81 | 130.4819 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | -0.038564 | 0.45294 | 0.0016718
81.2 | 130.4819 | 0.0024299 | 0.18331 | 0.004738 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
81.4 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 0.0032709
81.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | -0.0031265
81.8 | 130.4819 | 0.00083003 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | -0.014572 | 0.35695 | 0.0016718
82 | 130.6738 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0062209 | 0.54889 | 0.0016718
82.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.16505 | 0.0016718
82.4 | 130.5779 | 0.00083003 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0051309 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | -0.0017763 | 0.261 | 0.0048708
82.6 | 130.4819 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | -0.0015273
82.8 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | -0.025519
83 | 130.4819 | 0.00083003 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
83.2 | 130.4819 | 0.00083003 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.63692 | 0.0030219 | 0.35695 | 0.0032709
83.4 | 130.4819 | -0.00076916 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
83.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
83.8 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.59375 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
84 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0048708
84.2 | 130.5779 | 0.0024299 | 0.18331 | 0.0015389 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.45294 | 0.0016718
84.4 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.40181 | -0.0019091 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
84.6 | 130.5779 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0086283 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
84.8 | 130.5779 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | -0.00017715 | 0.35695 | 0.0032709
85 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.15708 | 0.0014227 | 0.35695 | 0.0032709
85.2 | 130.4819 | 0.00083003 | -0.10462 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
85.4 | 130.3859 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
85.6 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
85.8 | 130.4819 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0048708
86 | 130.3859 | 0.00083003 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.00647
86.2 | 130.5779 | 0.0024299 | 0.087319 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
86.4 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.003531 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | -0.0033755 | 0.35695 | 0.0016718
86.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
86.8 | 130.4819 | 0.00083003 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | -0.0033755 | 0.35695 | 0.0032709
87 | 130.4819 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
87.2 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
87.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
87.6 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
87.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0076874 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
88 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
88.2 | 130.3859 | 0.0024299 | -0.10462 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
88.4 | 130.4819 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
88.6 | 130.4819 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.009669
88.8 | 130.4819 | 0.0024299 | 0.4712 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.261 | 0.0016718
89 | 130.3859 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.010228 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
89.2 | 130.4819 | 0.0024299 | -0.10462 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
89.4 | 130.4819 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.18962 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | -0.078023 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
89.6 | 130.4819 | 0.0024299 | 0.18331 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
89.8 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.49942 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.069058 | 0.0032709
90 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
90.2 | 130.4819 | 0.0040291 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.36296 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.069058 | 0.0032709
90.4 | 130.2899 | 0.0024299 | 0.37521 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | -0.076363 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
90.6 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.54889 | 0.0032709
90.8 | 130.4819 | -0.0023683 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.019589 | 0.0070285 | 0.20987 | 0.0028892 | 0.54092 | 0.0030219 | 0.45294 | 0.0032709
91 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
91.2 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | -0.12288 | 0.0048708
91.4 | 130.4819 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | -0.0012672 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | -0.00017715 | 0.64488 | 0.0032709
91.6 | 130.3859 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.093666 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
91.8 | 130.4819 | 0.0024299 | 0.37521 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | -0.026893 | 0.0032709
92 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
92.2 | 130.4819 | 0.00083003 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
92.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.15708 | 0.0030219 | 0.35695 | 0.0032709
92.6 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.069058 | 0.0032709
92.8 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.54092 | 0.0014227 | 0.35695 | 0.0032709
93 | 130.4819 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
93.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
93.4 | 130.3859 | 0.00083003 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.45294 | 0.0032709
93.6 | 130.4819 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
93.8 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.069058 | 0.0032709
94 | 130.3859 | 0.0024299 | 0.18331 | -0.0016601 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.011827 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
94.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0014227 | 0.35695 | 0.0032709
94.4 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
94.6 | 130.3859 | 0.0024299 | 0.087319 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0048708
94.8 | 130.4819 | 0.0024299 | 0.37521 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | -0.026893 | 0.0048708
95 | 130.3859 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
95.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
95.4 | 130.3859 | 0.00083003 | 0.27926 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
95.6 | 130.3859 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
95.8 | 130.3859 | 0.00083003 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0067301 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | -0.0017763 | 0.35695 | 0.0032709
96 | 130.2899 | 0.00083003 | 0.18331 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.35695 | 0.0032709
96.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.11392 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
96.4 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
96.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.63692 | 0.0014227 | 0.261 | 0.0032709
96.8 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.0064811 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.25303 | 0.0030219 | 0.261 | 0.0032709
97 | 130.3859 | -0.00076916 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | -0.00017715 | 0.35695 | 0.0032709
97.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.0080803 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
97.4 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
97.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | -0.0019091 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
97.8 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
98 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
98.2 | 130.3859 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.019589 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.74084 | 0.0016718
98.4 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 8.3003e-05 | 0.45891 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | -0.00030988 | 0.73287 | 0.0014227 | 0.35695 | 0.0032709
98.6 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.30582 | 0.0092866 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
98.8 | 130.3859 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.11392 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
99 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.17102 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.73287 | 0.0014227 | 0.261 | 0.0032709
99.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | -0.0015162 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
99.4 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
99.6 | 130.3859 | 0.0024299 | 0.18331 | -6.0896e-05 | 0.66945 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0038295 | 0.68971 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
99.8 | 130.3859 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
100 | 130.3859 | 0.0024299 | 0.27926 | 0.0063372 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
100.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
100.4 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | -0.076363 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 7.1911e-05
100.6 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.011827 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
100.8 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.11392 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
101 | 130.3859 | 0.0024299 | 0.27926 | -0.0016601 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.069058 | 0.0032709
101.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
101.4 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
101.6 | 130.3859 | 0.0040291 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.11392 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0032709
101.8 | 130.3859 | 0.0024299 | 0.56715 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | -0.17235 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.45294 | 0.0016718
102 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
102.2 | 130.3859 | 0.0024299 | 0.37521 | -6.0896e-05 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
102.4 | 130.3859 | 0.00083003 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
102.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.20987 | 0.0060882 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
102.8 | 130.3859 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.261 | 0.0032709
103 | 130.2899 | 0.0024299 | 0.18331 | 0.0015389 | 0.5735 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.11392 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
103.2 | 130.2899 | 0.00083003 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | -0.17235 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
103.4 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 8.3003e-05 | 0.26697 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
103.6 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
103.8 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | -0.0015162 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.73287 | 0.0030219 | 0.35695 | 0.0032709
104 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | -0.17235 | 0.0054293 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.00647
104.2 | 130.2899 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
104.4 | 130.2899 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | -0.020925 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
104.6 | 130.2899 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.019589 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
104.8 | 130.2899 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | 0.0080803 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.49776 | -0.0019091 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
105 | 130.2899 | 0.0024299 | 0.18331 | 0.0015389 | 0.18962 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.68971 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
105.2 | 130.2899 | 0.0024299 | 0.18331 | 0.0015389 | 0.5735 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
105.4 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 7.1911e-05
105.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
105.8 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.093666 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.40181 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
106 | 130.3859 | 0.0040291 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
106.2 | 130.2899 | -0.0039682 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.40347 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.45294 | 0.0032709
106.4 | 130.2899 | 0.00083003 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | -0.0028664 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
106.6 | 130.2899 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
106.8 | 130.194 | 0.0024299 | 0.18331 | 0.0015389 | 0.28557 | -0.003116 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0016718
107 | 130.2899 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.013427 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.009669
107.2 | 130.2899 | 0.0024299 | 0.4712 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | -0.00017715 | 0.261 | 0.0016718
107.4 | 130.194 | 0.0024299 | 0.27926 | 0.0015389 | -0.002325 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
107.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
107.8 | 130.2899 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | -0.00030988 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
108 | 130.2899 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
108.2 | 130.2899 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
108.4 | 130.194 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0022303 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
108.6 | 130.2899 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | -0.00017715 | 0.35695 | 0.0016718
108.8 | 130.194 | 0.00083003 | -0.10462 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.011827 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
109 | 130.194 | 0.0024299 | 0.087319 | 0.0031381 | 0.5735 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.017929 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
109.2 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
109.4 | 130.194 | -0.00076916 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.25303 | 0.0046217 | 0.261 | 0.0032709
109.6 | 130.194 | 0.0040291 | 0.27926 | 0.0015389 | 0.5735 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
109.8 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
110 | 130.194 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.017929 | 0.0028892 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
110.2 | 130.2899 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.010886 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
110.4 | 130.2899 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | -0.0047263
110.6 | 130.194 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0078201 | 0.261 | 0.0032709
110.8 | 130.194 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.40181 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
111 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.003531 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.54092 | -0.00017715 | 0.261 | 0.0032709
111.2 | 130.098 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.17102 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.82882 | 0.0030219 | 0.261 | 0.0032709
111.4 | 130.194 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
111.6 | 130.194 | 0.0056289 | 0.66314 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
111.8 | 130.002 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.65085 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0016718
112 | 130.194 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.019589 | 0.011827 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.16505 | 0.0080692
112.2 | 130.194 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.017929 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
112.4 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | -0.17401 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
112.6 | 130.194 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
112.8 | 130.194 | 0.0056289 | 0.27926 | 0.0015389 | 0.28557 | 8.3003e-05 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
113 | 130.2899 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.25303 | 0.0014227 | 0.261 | 0.0032709
113.2 | 130.194 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | -0.00017715 | 0.261 | 0.0032709
113.4 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0028664 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
113.6 | 130.194 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.59537 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0062209 | 0.261 | 0.0016718
113.8 | 130.194 | 0.0056289 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
114 | 130.2899 | 0.0056289 | 0.087319 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | -0.076363 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.64488 | 0.0016718
114.2 | 130.194 | 0.0056289 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.075065 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
114.4 | 130.194 | 0.0072281 | 0.18331 | 0.0031381 | 0.38156 | -0.0015162 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
114.6 | 130.098 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.49942 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
114.8 | 130.194 | 0.012026 | 0.27926 | 0.0031381 | 0.47751 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
115 | 130.098 | 0.012026 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
115.2 | 130.098 | 0.012026 | 0.087319 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
115.4 | 129.8101 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 8.3003e-05 | -0.11688 | 0.0019319 | 0.21153 | 0.010228 | 0.20987 | 0.0076874 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
115.6 | 131.4415 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | -0.17235 | 0.010228 | 0.20987 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
115.8 | 130.3859 | 0.0056289 | -0.0086323 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | -0.076363 | 0.010228 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.0016718
116 | 130.194 | 0.0056289 | 0.37521 | 0.0031381 | 0.28557 | 0.003282 | 0.26697 | 0.03552 | 0.30748 | 0.0054293 | 0.20987 | 0.010886 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
116.2 | 130.2899 | 0.0056289 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | -0.0012672 | 0.019589 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
116.4 | 130.2899 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | -0.11688 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0012893 | 0.15708 | 0.0078201 | 0.261 | 0.0032709
116.6 | 130.194 | 0.0056289 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.54092 | -0.00017715 | 0.35695 | 0.0016718
116.8 | 130.194 | 0.0072281 | 0.37521 | -6.0896e-05 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
117 | 130.194 | -0.00076916 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.40347 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.45294 | 0.0032709
117.2 | 130.194 | 0.0024299 | -0.0086323 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.45294 | 0.0016718
117.4 | 130.2899 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | -0.00030988 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
117.6 | 130.2899 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.00647
117.8 | 130.194 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
118 | 130.194 | 0.0056289 | 0.27926 | 0.0015389 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | -0.17401 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
118.2 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0022303 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
118.4 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 7.1911e-05
118.6 | 130.2899 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.5549 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.35695 | 0.0032709
118.8 | 130.2899 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0048708
119 | 130.194 | 0.0056289 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
119.2 | 130.2899 | 0.0072281 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0051309 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
119.4 | 130.3859 | 0.0056289 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
119.6 | 130.194 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.003531 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
119.8 | 130.194 | 0.0056289 | 0.18331 | 0.0015389 | 0.47751 | 0.0016822 | 0.17102 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
120 | 130.2899 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.069058 | 0.0032709
120.2 | 130.2899 | 0.0056289 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.11392 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
120.4 | 130.2899 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.0048812 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
120.6 | 130.194 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
120.8 | 130.2899 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | -0.0012672 | 0.49942 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
121 | 130.194 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | -0.17235 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.00647
121.2 | 130.194 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.019589 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.54889 | 7.1911e-05
121.4 | 130.2899 | 0.0072281 | 0.18331 | 0.0031381 | 0.66945 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
121.6 | 130.2899 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.16505 | 0.0032709
121.8 | 130.2899 | 0.0072281 | 0.27926 | 0.004738 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 7.1911e-05
122 | 130.2899 | 0.0088273 | 0.18331 | 0.0031381 | 0.47751 | 0.0048812 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
122.2 | 130.2899 | 0.0072281 | -0.10462 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | -0.0012672 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | -0.0015273
122.4 | 130.2899 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.16505 | 0.0016718
122.6 | 130.3859 | 0.0072281 | 0.27926 | 0.0015389 | 0.093666 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 7.1911e-05
122.8 | 130.2899 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
123 | 130.2899 | 0.0072281 | 0.087319 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | -0.0028664 | 0.59537 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | -0.21883 | 0.0032709
123.2 | 130.2899 | 0.0072281 | 0.18331 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | -0.17401 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
123.4 | 130.3859 | 0.0072281 | 0.087319 | -6.0896e-05 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.11392 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
123.6 | 130.2899 | 0.0088273 | 0.27926 | 0.0015389 | 0.47751 | -0.0015162 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0060882 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
123.8 | 130.3859 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0067301 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
124 | 130.2899 | 0.0072281 | 0.18331 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | -0.17401 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
124.2 | 130.4819 | 0.0072281 | 0.27926 | -0.0032593 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.019589 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
124.4 | 130.3859 | 0.010427 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0051309 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.16505 | 0.0032709
124.6 | 130.3859 | 0.0072281 | 0.18331 | -6.0896e-05 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
124.8 | 130.5779 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893 | -0.13085 | 0.0014227 | 0.261 | 0.0032709
125 | 130.2899 | 0.0088273 | 0.37521 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
125.2 | 130.3859 | 0.0072281 | 0.18331 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0038295 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
125.4 | 130.3859 | 0.0072281 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.11392 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
125.6 | 130.4819 | 0.010427 | 0.18331 | -0.0016601 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 7.1911e-05
125.8 | 130.4819 | 0.0088273 | 0.18331 | 0.0079364 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.013427 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | -0.0047263
126 | 130.2899 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
126.2 | 130.3859 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.017929 | 0.0012893 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
126.4 | 130.4819 | 0.0088273 | 0.18331 | 0.0015389 | 0.47751 | -0.003116 | 0.36296 | 0.0019319 | 0.11554 | 0.0054293 | 0.40181 | -0.0051081 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
126.6 | 130.4819 | 0.0072281 | 0.27926 | -6.0896e-05 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | -0.0015273
126.8 | 130.4819 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.82882 | 0.0030219 | 0.261 | 0.0032709
127 | 130.4819 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | -0.0012672 | 0.019589 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
127.2 | 130.4819 | 0.0088273 | 0.087319 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | -0.0012672 | 0.49942 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0048708
127.4 | 130.4819 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
127.6 | 130.4819 | 0.010427 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.64488 | 0.0032709
127.8 | 130.4819 | 0.0088273 | 0.37521 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | -0.0012672 | -0.17235 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
128 | 130.4819 | 0.0072281 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
128.2 | 130.4819 | 0.0072281 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
128.4 | 130.6738 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | -0.13085 | 0.0030219 | 0.261 | 0.0032709
128.6 | 130.6738 | 0.00083003 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | -0.0060654 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | -0.00017715 | 0.35695 | 0.0032709
128.8 | 130.5779 | 0.0072281 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | -0.0028664 | 0.30748 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 7.1911e-05
129 | 130.4819 | 0.0088273 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.63692 | 0.0030219 | 0.35695 | 0.0032709
129.2 | 130.5779 | 0.012026 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
129.4 | 130.5779 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.73287 | 0.0030219 | 0.261 | 0.0032709
129.6 | 130.4819 | 0.015225 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
129.8 | 130.5779 | 0.023223 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.36296 | 0.0051309 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | -0.0049754 | 0.35695 | 0.0016718
130 | 130.3859 | 0.021623 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.003531 | 0.21153 | 0.013427 | 0.30582 | 0.0076874 | 0.44497 | 0.0062209 | 0.261 | 0.0032709
130.2 | 130.6738 | 0.010427 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | -0.076363 | 0.010228 | 0.30582 | 0.010886 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
130.4 | 130.3859 | 0.010427 | 0.18331 | 0.0015389 | 2.5888 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0076874 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
130.6 | 130.6738 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.36296 | -0.0012672 | 0.11554 | 0.0054293 | 0.30582 | 0.0044883 | 0.34898 | 0.0014227 | 0.35695 | 0.0032709
130.8 | 130.5779 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
131 | 130.5779 | 0.0088273 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.011827 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
131.2 | 130.5779 | 0.0088273 | 0.087319 | 0.0031381 | 0.28557 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 7.1911e-05
131.4 | 130.6738 | 0.0088273 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
131.6 | 130.6738 | 0.0088273 | 0.27926 | 0.0015389 | 0.18962 | -0.003116 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.73287 | 0.0030219 | 0.261 | 0.0032709
131.8 | 130.5779 | 0.0088273 | 0.18331 | 0.0031381 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.59375 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
132 | 130.5779 | 0.0088273 | 0.087319 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.45294 | 0.0016718
132.2 | 130.5779 | 0.010427 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.010228 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
132.4 | 130.5779 | 0.010427 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
132.6 | 130.5779 | 0.010427 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.003531 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
132.8 | 130.4819 | 0.0088273 | 0.18331 | 0.0031381 | 0.38156 | 0.0064811 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0012893 | 0.34898 | 0.0014227 | 0.35695 | 0.0032709
133 | 130.4819 | 0.0088273 | 0.18331 | 0.0015389 | 0.18962 | 0.0048812 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.63692 | 0.0030219 | 0.261 | 0.0032709
133.2 | 130.3859 | 0.0088273 | 0.27926 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0038295 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
133.4 | 130.002 | 0.0088273 | 0.18331 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
133.6 | 130.3859 | 0.012026 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.019589 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
133.8 | 130.4819 | 0.010427 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
134 | 130.4819 | 0.0072281 | 0.087319 | 0.0015389 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.017929 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
134.2 | 130.4819 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 8.3003e-05 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
134.4 | 130.3859 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
134.6 | 130.5779 | 0.010427 | 0.18331 | 0.0031381 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0012893 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
134.8 | 130.5779 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0048708
135 | 130.6738 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
135.2 | 130.5779 | 0.0088273 | 0.27926 | -6.0896e-05 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.013427 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
135.4 | 130.5779 | 0.0088273 | 0.37521 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
135.6 | 130.5779 | 0.012026 | 0.087319 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.019589 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
135.8 | 130.6738 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.17102 | 0.0067301 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.54889 | 0.0032709
136 | 130.6738 | 0.010427 | 0.18331 | 0.0031381 | -0.002325 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0012893 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
136.2 | 130.5779 | 0.0088273 | 0.18331 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
136.4 | 130.5779 | 0.0088273 | 0.27926 | 0.0063372 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
136.6 | 130.5779 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
136.8 | 130.8658 | 0.0088273 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.15708 | 0.0014227 | 0.261 | 0.0032709
137 | 130.5779 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
137.2 | 130.4819 | 0.0088273 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.15708 | 0.0030219 | 0.261 | 0.0016718
137.4 | 130.6738 | 0.0088273 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
137.6 | 130.5779 | 0.010427 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | -0.0012672 | 0.11554 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
137.8 | 130.5779 | 0.0088273 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | -0.0033755 | 0.261 | 0.0032709
138 | 130.5779 | 0.0088273 | 0.18331 | 0.0031381 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
138.2 | 130.6738 | 0.013626 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.54889 | 0.0032709
138.4 | 130.5779 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
138.6 | 130.5779 | 0.0088273 | 0.27926 | 0.0015389 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
138.8 | 130.5779 | 0.010427 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
139 | 130.6738 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
139.2 | 130.6738 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.075065 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.25303 | 0.0030219 | 0.261 | 0.0016718
139.4 | 130.3859 | 0.0088273 | 0.27926 | 0.0015389 | 0.28557 | 0.0016822 | 0.45891 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | -0.00017715 | 0.261 | 0.0032709
139.6 | 130.3859 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
139.8 | 130.4819 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
140 | 130.5779 | 0.0072281 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
140.2 | 130.5779 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
140.4 | 130.4819 | 0.0088273 | 0.18331 | 0.0015389 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
140.6 | 130.5779 | 0.0072281 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | -0.0031265
140.8 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.20987 | 0.0012893 | 0.44497 | 0.0046217 | 0.261 | 0.0016718
141 | 130.4819 | 0.0088273 | 0.18331 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | -0.0015273
141.2 | 130.4819 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
141.4 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | -0.0044662 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.069058 | 0.0032709
141.6 | 130.3859 | 0.0056289 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.59375 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
141.8 | 130.4819 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
142 | 130.3859 | 0.0072281 | 0.37521 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.019589 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.069058 | 0.0016718
142.2 | 130.3859 | 0.013626 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.003531 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 7.1911e-05
142.4 | 130.2899 | 0.015225 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
142.6 | 130.3859 | 0.020024 | 0.27926 | 0.004738 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.013427 | 0.30582 | 0.0060882 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
142.8 | 130.3859 | 0.03122 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.30582 | 0.010886 | 0.34898 | 0.0030219 | 0.261 | 0.00647
143 | 130.3859 | 0.039217 | 0.27926 | -6.0896e-05 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.023023 | 0.49776 | 0.012486 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
143.2 | 130.3859 | 0.0088273 | -0.10462 | 0.0031381 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.21153 | 0.015026 | 0.30582 | 0.015685 | 0.34898 | -0.0017763 | 0.261 | 0.0016718
143.4 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.075065 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0048708
143.6 | 130.3859 | 0.0072281 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
143.8 | 130.3859 | 0.0056289 | 0.18331 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0016718
144 | 130.3859 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.0016718
144.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.45294 | 0.0016718
144.4 | 130.4819 | 0.0072281 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0014227 | 0.35695 | 0.0032709
144.6 | 130.2899 | 0.0072281 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | -0.0028664 | 0.11554 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.00647
144.8 | 130.3859 | 0.0072281 | 0.27926 | 0.0031381 | 0.28557 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.40181 | -0.0019091 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
145 | 130.3859 | 0.0072281 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | -0.078023 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
145.2 | 130.2899 | 0.0040291 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | -0.0028664 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
145.4 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | -0.00030988 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
145.6 | 130.3859 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0054293 | 0.20987 | 0.0044883 | 0.54092 | 0.0014227 | 0.261 | 0.0032709
145.8 | 130.3859 | 0.0056289 | 0.18331 | -0.0032593 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
146 | 130.3859 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0046217 | 0.261 | -0.0015273
146.2 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
146.4 | 130.3859 | 0.0056289 | 0.18331 | 0.0015389 | 0.66945 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
146.6 | 130.2899 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0022303 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
146.8 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | -0.034861 | 0.0030219 | 0.261 | 0.0032709
147 | 130.194 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
147.2 | 130.194 | 0.0024299 | 0.37521 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
147.4 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
147.6 | 130.098 | 0.0056289 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
147.8 | 130.194 | 0.0056289 | 0.37521 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.00647
148 | 130.194 | 0.0056289 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0012893 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
148.2 | 130.194 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0062209 | 0.16505 | 0.0032709
148.4 | 130.3859 | 0.0056289 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.17102 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
148.6 | 130.194 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.45294 | 0.0032709
148.8 | 130.194 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.49942 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
149 | 130.194 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.16505 | 0.0032709
149.2 | 130.194 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | -0.00030988 | 0.73287 | 0.0030219 | 0.261 | 0.0016718
149.4 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.25303 | 0.0030219 | 0.261 | 0.0032709
149.6 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.17102 | -0.0028664 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 0.0032709
149.8 | 130.194 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.45891 | 0.003531 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | -0.00017715 | 0.261 | 0.0032709
150 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.093666 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
150.2 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | -0.00030988 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
150.4 | 130.098 | 0.0056289 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | -0.076363 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
150.6 | 130.194 | 0.0056289 | -0.10462 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0038295 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
150.8 | 130.194 | 0.0040291 | -0.0086323 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
151 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | -0.11688 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.54092 | 0.0014227 | 0.261 | 0.0032709
151.2 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.45294 | 0.0032709
151.4 | 130.098 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
151.6 | 130.194 | 0.0040291 | 0.18331 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.0019319 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
151.8 | 130.098 | 0.0040291 | 0.27926 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
152 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.28557 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.15708 | 0.0030219 | 0.35695 | 0.0032709
152.2 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
152.4 | 130.194 | 0.0024299 | 0.18331 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.00647
152.6 | 130.098 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.017929 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
152.8 | 130.098 | 0.0024299 | 0.27926 | 0.004738 | 0.093666 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.49776 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
153 | 130.098 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.11392 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
153.2 | 130.194 | 0.0024299 | 0.087319 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.019589 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
153.4 | 130.194 | 0.0024299 | 0.27926 | 0.0063372 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | -0.078023 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
153.6 | 130.194 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 7.1911e-05
153.8 | 130.194 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
154 | 130.002 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0094199 | 0.261 | 0.0032709
154.2 | 130.098 | 0.0024299 | 0.27926 | 0.0063372 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 7.1911e-05
154.4 | 130.098 | 0.0040291 | 0.18331 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
154.6 | 130.098 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
154.8 | 130.194 | 0.0056289 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0092866 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
155 | 130.002 | 0.0056289 | 0.37521 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 7.1911e-05
155.2 | 130.002 | 0.0056289 | 0.18331 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.011827 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
155.4 | 130.002 | 0.012026 | 0.27926 | 0.0015389 | 0.66945 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
155.6 | 130.098 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.019589 | 0.011827 | 0.20987 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
155.8 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
156 | 130.098 | 0.0024299 | 0.18331 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0092866 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
156.2 | 130.098 | 0.00083003 | 0.18331 | -6.0896e-05 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.019589 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 7.1911e-05
156.4 | 130.098 | 0.00083003 | 0.66314 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.49942 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
156.6 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
156.8 | 130.098 | 0.0024299 | 0.37521 | 0.0015389 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | -0.17235 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
157 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 8.3003e-05 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
157.2 | 130.098 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0016718
157.4 | 130.194 | 0.0024299 | 0.087319 | -0.0016601 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.59375 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
157.6 | 130.098 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
157.8 | 130.194 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.20987 | 0.0028892 | 0.25303 | 0.0030219 | 0.261 | 0.0032709
158 | 130.098 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
158.2 | 130.098 | 0.0024299 | 0.37521 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 7.1911e-05
158.4 | 130.194 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
158.6 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.66945 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
158.8 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.7654 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
159 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.011019 | 0.261 | 0.0016718
159.2 | 130.194 | 0.0040291 | -0.20057 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | -0.17235 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
159.4 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
159.6 | 129.8101 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0051309 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
159.8 | 130.194 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
160 | 130.194 | 0.0024299 | 0.18331 | 0.0079364 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
160.2 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
160.4 | 130.2899 | 0.0024299 | 0.18331 | 0.0015389 | 0.18962 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.017929 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
160.6 | 130.2899 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
160.8 | 130.2899 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | -0.076363 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0016718
161 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.68971 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
161.2 | 130.3859 | -0.0039682 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | -0.0028664 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0062209 | 0.261 | 0.0016718
161.4 | 130.194 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | 0.0030219 | 0.261 | 0.0032709
161.6 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
161.8 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.0048812 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.25303 | 0.0046217 | 0.261 | 0.0032709
162 | 130.2899 | 0.0024299 | 0.4712 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.64488 | 0.0032709
162.2 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
162.4 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
162.6 | 130.194 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | -0.0060654 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.16505 | 0.0032709
162.8 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.40347 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.74084 | 0.0032709
163 | 130.194 | 0.0024299 | -0.0086323 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0014227 | -0.12288 | 0.0032709
163.2 | 130.194 | 0.0024299 | 0.37521 | 0.0031381 | 0.18962 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
163.4 | 130.2899 | 0.00083003 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.00647
163.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.18962 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
163.8 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.18962 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
164 | 130.2899 | 0.0024299 | 0.18331 | 0.0031381 | 0.28557 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
164.2 | 130.3859 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
164.4 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
164.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.261 | 0.0016718
164.8 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | -0.0051081 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
165 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.73287 | 0.0030219 | 0.261 | 0.0032709
165.2 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
165.4 | 130.2899 | 0.0024299 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0048708
165.6 | 130.194 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.075065 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0012893 | 0.25303 | 0.0030219 | 0.261 | 0.0016718
165.8 | 130.2899 | 0.0024299 | 0.18331 | 0.0015389 | 0.7654 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0054293 | 0.20987 | 0.0060882 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
166 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.093666 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
166.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.25303 | 0.0062209 | 0.261 | 0.0032709
166.4 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.5549 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
166.6 | 130.3859 | 0.0024299 | 0.27926 | 0.004738 | 0.7654 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | -0.17401 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0016718
166.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
167 | 130.3859 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.45294 | 0.0032709
167.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.18962 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.49776 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
167.4 | 130.3859 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
167.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
167.8 | 130.3859 | 0.0024299 | 0.18331 | 0.0031381 | 0.093666 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
168 | 130.7698 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0051309 | 0.21153 | 0.0054293 | 0.20987 | 0.0044883 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
168.2 | 130.3859 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.010228 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.16505 | 0.0032709
168.4 | 130.3859 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
168.6 | 130.3859 | 0.0024299 | 0.37521 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
168.8 | 130.3859 | 0.0024299 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
169 | 130.3859 | -0.00076916 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
169.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.00647
169.4 | 130.3859 | 0.0024299 | 0.18331 | 0.0031381 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
169.6 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | -0.0060654 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
169.8 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
170 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
170.2 | 130.3859 | 0.0024299 | 0.37521 | 0.0063372 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.017929 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
170.4 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
170.6 | 130.6738 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | -0.0017763 | 0.261 | 0.0016718
170.8 | 130.3859 | 0.0024299 | -0.0086323 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | -0.12288 | 0.0032709
171 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | -0.0028664 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.25303 | 0.0062209 | 0.261 | 0.0032709
171.2 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0080803 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
171.4 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.28557 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0016718
171.6 | 130.4819 | 0.0040291 | 0.37521 | -0.0048591 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
171.8 | 130.2899 | 0.0040291 | 0.4712 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
172 | 130.5779 | 0.0056289 | 0.37521 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
172.2 | 130.4819 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.25303 | 0.0030219 | 0.35695 | 0.0032709
172.4 | 130.4819 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | -0.0028664 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0094199 | 0.261 | 0.0016718
172.6 | 130.3859 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | -0.0028664 | 0.49942 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.74084 | 0.0032709
172.8 | 130.3859 | 0.0056289 | 0.27926 | -0.0032593 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.017929 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
173 | 130.4819 | 0.0056289 | 0.37521 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 7.1911e-05
173.2 | 130.3859 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
173.4 | 130.4819 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.68971 | 0.0060882 | 0.34898 | 0.0030219 | 0.35695 | 0.0016718
173.6 | 130.3859 | 0.012026 | 0.56715 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
173.8 | 130.4819 | 0.015225 | 0.37521 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
174 | 130.5779 | 0.021623 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.010228 | 0.30582 | 0.012486 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
174.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
174.4 | 130.4819 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0076874 | 0.15708 | 0.0030219 | 0.261 | 0.0032709
174.6 | 130.4819 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.45891 | -0.0012672 | -0.076363 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
174.8 | 130.2899 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0076874 | 0.34898 | 0.0030219 | 0.35695 | 0.0016718
175 | 130.4819 | -0.0039682 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0030219 | 0.261 | 0.0016718
175.2 | 130.4819 | 0.0072281 | 0.27926 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.011827 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.16505 | 0.0016718
175.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.65085 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0092866 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
175.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.45891 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
175.8 | 130.3859 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0014227 | 0.261 | 0.0016718
176 | 130.4819 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.16505 | 0.0048708
176.2 | 130.7698 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
176.4 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892 | 0.15708 | 0.0030219 | 0.35695 | 0.0032709
176.6 | 130.4819 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
176.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.18962 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
177 | 130.7698 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.06109 | 0.0030219 | 0.261 | 0.0032709
177.2 | 130.098 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | -0.11688 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.261 | 0.0016718
177.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.54889 | 0.0032709
177.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
177.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
178 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.66945 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.59375 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
178.2 | 130.4819 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
178.4 | 130.5779 | 0.0024299 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.49776 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
178.6 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.68971 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0048708
178.8 | 130.5779 | 0.0024299 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
179 | 130.5779 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0016718
179.2 | 130.5779 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0046217 | 0.261 | 0.0032709
179.4 | 130.6738 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
179.6 | 131.1537 | 0.0040291 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
179.8 | 130.8658 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.00647
180 | 131.1537 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | -0.00017715 | 0.261 | 0.0032709
180.2 | 131.3456 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | -0.020925 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.35695 | 0.0016718
180.4 | 130.7698 | 0.0040291 | 0.087319 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | -0.0015273
180.6 | 131.0577 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.65085 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.73287 | 0.0030219 | 0.261 | 0.0032709
180.8 | 130.6738 | 0.0024299 | 0.27926 | 0.0063372 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
181 | 130.7698 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.40347 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.16505 | 0.0032709
181.2 | 130.6738 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0016718
181.4 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.73287 | 0.0030219 | 0.261 | 0.0032709
181.6 | 130.6738 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
181.8 | 130.5779 | 0.0056289 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.003531 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.16505 | 0.0032709
182 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.25303 | 0.0030219 | 0.261 | 0.0016718
182.2 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.017929 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
182.4 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0051309 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
182.6 | 130.5779 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | -0.0012672 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0014227 | 0.35695 | 0.0016718
182.8 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.5735 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
183 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0076874 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
183.2 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
183.4 | 130.5779 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0094199 | 0.35695 | 0.0016718
183.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
183.8 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.34898 | 0.0030219 | 0.16505 | 0.0032709
184 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0064811 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
184.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.17102 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.63692 | 0.0046217 | 0.261 | 0.0032709
184.4 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.66945 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
184.6 | 130.4819 | 0.0024299 | 0.087319 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.40347 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
184.8 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.63692 | 0.0030219 | 0.261 | 0.0032709
185 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.00647
185.2 | 130.6738 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.5549 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0060882 | 0.34898 | -0.00017715 | 0.35695 | 0.0032709
185.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
185.6 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.15708 | 0.0030219 | 0.261 | 0.0032709
185.8 | 130.5779 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
186 | 130.6738 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | -0.00017715 | 0.261 | 0.0032709
186.2 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | -0.078023 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
186.4 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
186.6 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
186.8 | 130.5779 | 0.0024299 | 0.18331 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
187 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.075065 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
187.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
187.4 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
187.6 | 130.5779 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.009669
187.8 | 130.6738 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | -0.17235 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
188 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | 0.003531 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
188.2 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
188.4 | 130.5779 | 0.00083003 | 0.27926 | 0.0063372 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
188.6 | 130.5779 | 0.00083003 | -0.0086323 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | -0.0012672 | 0.30748 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
188.8 | 130.5779 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
189 | 130.4819 | 0.00083003 | 0.18331 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | -0.0012672 | 0.49942 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
189.2 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
189.4 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
189.6 | 130.4819 | -0.0039682 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
189.8 | 130.5779 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.00647
190 | 130.4819 | 0.00083003 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | -0.0028664 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
190.2 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.40181 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 7.1911e-05
190.4 | 130.6738 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.34898 | -0.00017715 | 0.35695 | 0.0032709
190.6 | 130.5779 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
190.8 | 130.5779 | 0.0024299 | 0.18331 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
191 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.093666 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
191.2 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
191.4 | 130.3859 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.40347 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.64488 | 0.0032709
191.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
191.8 | 130.5779 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.017929 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
192 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
192.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
192.4 | 130.4819 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0062209 | 0.261 | 0.0032709
192.6 | 130.4819 | 0.00083003 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.017929 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
192.8 | 130.5779 | 0.0024299 | 0.4712 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
193 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | -0.00030988 | 0.34898 | 0.0014227 | 0.35695 | 0.0032709
193.2 | 130.5779 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
193.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.63692 | 0.0030219 | 0.261 | 0.0032709
193.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
193.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
194 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.003531 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
194.2 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0046217 | 0.261 | 0.0016718
194.4 | 130.4819 | -0.00076916 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
194.6 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.019589 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.54889 | 0.0048708
194.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.5549 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.261 | 0.0048708
195 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
195.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
195.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
195.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
195.8 | 130.5779 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
196 | 130.3859 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0016822 | 0.17102 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
196.2 | 130.2899 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.65085 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
196.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0014227 | 0.35695 | 0.00647
196.6 | 130.4819 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
196.8 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | -0.0017763 | 0.35695 | 0.0032709
197 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.18962 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
197.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.15708 | 0.0030219 | 0.35695 | 0.0032709
197.4 | 130.5779 | 0.0024299 | 0.37521 | 0.0031381 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
197.6 | 130.6738 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | -0.0044662 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
197.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.30748 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
198 | 130.4819 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | -0.00030988 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
198.2 | 130.5779 | 0.00083003 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | -0.00017715 | 0.261 | 0.0032709
198.4 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
198.6 | 130.5779 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
198.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
199 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
199.2 | 130.4819 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
199.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0079364 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
199.6 | 130.5779 | 0.0024299 | 0.18331 | 0.004738 | -0.002325 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
199.8 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0028664 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | -0.00017715 | 0.261 | 0.0032709
200 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
200.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0022303 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
200.4 | 130.5779 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
200.6 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.20987 | -0.0035089 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
200.8 | 130.5779 | 0.0024299 | 0.18331 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.261 | 0.00647
201 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
201.2 | 130.4819 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.49776 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
201.4 | 130.4819 | 0.00083003 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
201.6 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
201.8 | 130.6738 | 0.0056289 | 0.18331 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.54889 | 0.0032709
202 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
202.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
202.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.30748 | 0.0070285 | 0.49776 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
202.6 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.011827 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
202.8 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.47751 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.25303 | 0.0030219 | 0.261 | 0.0032709
203 | 130.4819 | 0.0040291 | 0.4712 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
203.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
203.4 | 130.4819 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
203.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.11392 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
203.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
204 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.54092 | 0.0014227 | 0.261 | 0.0032709
204.2 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
204.4 | 130.3859 | 0.0024299 | 0.37521 | 0.0015389 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
204.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.075065 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
204.8 | 130.4819 | 0.00083003 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
205 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | -0.00017715 | 0.35695 | 0.0032709
205.2 | 130.4819 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.261 | 0.0048708
205.4 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | 0.0030219 | 0.261 | 0.0032709
205.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
205.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.011827 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.54889 | 0.0016718
206 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | -0.00030988 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
206.2 | 130.4819 | 0.0024299 | 0.087319 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.45294 | 0.0032709
206.4 | 130.4819 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
206.6 | 130.4819 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0051309 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.54889 | 0.0032709
206.8 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
207 | 130.4819 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.010228 | 0.20987 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
207.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
207.4 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.093666 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0076874 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
207.6 | 130.4819 | 0.0024299 | 0.37521 | 0.0031381 | 0.5735 | 8.3003e-05 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.261 | 0.0048708
207.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
208 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
208.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | -0.0012672 | 0.21153 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | -0.0033755 | 0.261 | 0.0032709
208.4 | 130.098 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0028664 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
208.6 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
208.8 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
209 | 130.3859 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | -0.0015273
209.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | 0.0067301 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0062209 | 0.35695 | 0.0032709
209.4 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
209.6 | 130.4819 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | -0.0033755 | 0.35695 | 0.0032709
209.8 | 130.4819 | 0.0024299 | 0.37521 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
210 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
210.2 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0012893 | 0.54092 | 0.0030219 | 0.261 | 0.0048708
210.4 | 130.3859 | 0.0040291 | 0.37521 | -0.0032593 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
210.6 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | -0.00017715 | 0.35695 | 0.0032709
210.8 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
211 | 130.4819 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.261 | 0.0032709
211.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.18962 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.20987 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
211.4 | 130.3859 | 0.0040291 | 0.27926 | 0.0015389 | 0.5735 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
211.6 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.73287 | 0.0046217 | 0.261 | 0.0048708
211.8 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
212 | 130.3859 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.59375 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.00647
212.2 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
212.4 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
212.6 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
212.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
213 | 130.4819 | 0.0040291 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
213.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | -0.020925 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
213.4 | 130.3859 | 0.0024299 | 0.27926 | 0.004738 | 0.28557 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
213.6 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.49776 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
213.8 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
214 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
214.2 | 130.194 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.65085 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
214.4 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
214.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.15708 | 0.0030219 | 0.35695 | 0.0032709
214.8 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.5735 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
215 | 130.3859 | 0.0040291 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.40347 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
215.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.019589 | 0.010228 | 0.20987 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
215.4 | 130.4819 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.011827 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
215.6 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
215.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0038295 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
216 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
216.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | -0.0035089 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
216.4 | 130.3859 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | -0.0060654 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
216.6 | 130.4819 | 0.0024299 | 0.18331 | -0.0016601 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.49776 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
216.8 | 130.3859 | 0.0040291 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
217 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | -0.0012672 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
217.2 | 130.3859 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0092866 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
217.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.15708 | 0.0030219 | 0.35695 | 0.0032709
217.6 | 130.3859 | 0.0040291 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
217.8 | 130.5779 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.40347 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
218 | 130.4819 | 0.00083003 | 0.37521 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
218.2 | 130.4819 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.40181 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
218.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
218.6 | 130.3859 | 0.00083003 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
218.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
219 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
219.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.45891 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.82882 | 0.0046217 | 0.35695 | 0.0032709
219.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
219.6 | 130.4819 | 0.00083003 | -0.10462 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
219.8 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
220 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 0.0032709
220.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.5549 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
220.4 | 130.4819 | 0.0024299 | 0.4712 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0014227 | 0.45294 | 0.0048708
220.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
220.8 | 130.4819 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
221 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
221.2 | 130.4819 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.011827 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | -0.0031265
221.4 | 130.4819 | 0.0024299 | 0.18331 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
221.6 | 130.3859 | 0.0024299 | 0.27926 | 0.0079364 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.0070285 | 0.11392 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
221.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
222 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
222.2 | 130.4819 | 0.0024299 | 0.18331 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
222.4 | 130.4819 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
222.6 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0022303 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
222.8 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.075065 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.15708 | 0.0030219 | 0.35695 | 0.0048708
223 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.73287 | 0.0030219 | 0.35695 | 0.0048708
223.2 | 130.3859 | 0.00083003 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.017929 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
223.4 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.5735 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0012893 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
223.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
223.8 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
224 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
224.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.25303 | 0.0030219 | 0.35695 | 0.0032709
224.4 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
224.6 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
224.8 | 130.3859 | 0.0024299 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | -0.12288 | 0.0032709
225 | 130.4819 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
225.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | -0.003116 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
225.4 | 130.3859 | 0.0024299 | 0.4712 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
225.6 | 130.4819 | 0.00083003 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0038295 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
225.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | -0.0044662 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.069058 | 0.0032709
226 | 130.4819 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.49776 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
226.2 | 130.5779 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.25303 | 0.0030219 | 0.35695 | 0.0032709
226.4 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0051309 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0014227 | 0.35695 | 0.0048708
226.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | -0.0015162 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
226.8 | 130.4819 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
227 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | -0.034861 | 0.0030219 | 0.261 | 0.0032709
227.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
227.4 | 130.4819 | 0.0040291 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | -0.0028664 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
227.6 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.019589 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.74084 | 0.0032709
227.8 | 130.3859 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | -0.00017715 | 0.35695 | 0.0032709
228 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0022303 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
228.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
228.4 | 130.3859 | 0.0040291 | 0.37521 | 0.0031381 | 0.28557 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0086283 | 0.20987 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0016718
228.6 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0080803 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
228.8 | 130.3859 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0080803 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
229 | 130.4819 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
229.2 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
229.4 | 130.5779 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
229.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0080803 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
229.8 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
230 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
230.2 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
230.4 | 130.3859 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0044883 | 0.54092 | 0.0046217 | 0.261 | 0.0048708
230.6 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
230.8 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
231 | 130.4819 | 0.0024299 | 0.4712 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0016718
231.2 | 130.4819 | 0.00083003 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.003531 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
231.4 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
231.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
231.8 | 130.3859 | 0.0024299 | 0.37521 | -6.0896e-05 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
232 | 130.4819 | 0.00083003 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
232.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
232.4 | 130.4819 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
232.6 | 130.4819 | 0.0024299 | 0.4712 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | -0.00017715 | 0.35695 | 0.00647
232.8 | 130.3859 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.261 | 0.0048708
233 | 130.3859 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.16505 | 0.0048708
233.2 | 130.3859 | 0.0040291 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
233.4 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
233.6 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | -0.0033755 | 0.35695 | 0.0032709
233.8 | 130.3859 | 0.00083003 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0022303 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
234 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.63692 | 0.0030219 | 0.35695 | 0.0032709
234.2 | 130.3859 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
234.4 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 7.1911e-05
234.6 | 130.4819 | 0.0024299 | 0.27926 | 0.0015389 | -0.002325 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
234.8 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
235 | 130.3859 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
235.2 | 130.3859 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | -0.076363 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
235.4 | 130.5779 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0051309 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
235.6 | 130.3859 | 0.0056289 | 0.18331 | -6.0896e-05 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.0048708
235.8 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
236 | 130.3859 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.20987 | 0.0012893 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
236.2 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
236.4 | 130.4819 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
236.6 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
236.8 | 130.3859 | 0.018424 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0080692
237 | 130.4819 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.003531 | 0.21153 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
237.2 | 130.2899 | 0.020024 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.011827 | 0.49776 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
237.4 | 130.2899 | 0.026422 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.011827 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.261 | 0.00647
237.6 | 130.3859 | 0.039217 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
237.8 | 130.4819 | 0.040817 | 0.27926 | 0.0031381 | 0.28557 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.011827 | 0.30582 | 0.0076874 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
238 | 130.098 | 0.0024299 | 0.4712 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.018225 | 0.40181 | 0.012486 | 0.54092 | 0.0046217 | 0.54889 | 0.0032709
238.2 | 129.8101 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.018884 | 0.54092 | 0.0046217 | 0.261 | 0.0032709
238.4 | 130.2899 | -0.00076916 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | -0.0060654 | 0.21153 | 0.011827 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.069058 | 0.0048708
238.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.015026 | 0.40181 | 0.0092866 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
238.8 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | -0.011113 | 0.36296 | 0.00033201 | 0.21153 | 0.016626 | 0.40181 | 0.012486 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
239 | 130.3859 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.49776 | 0.014085 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
239.2 | 130.2899 | -0.0023683 | 0.27926 | 0.0031381 | 0.28557 | 0.0048812 | 0.26697 | 0.0019319 | 0.019589 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
239.4 | 130.2899 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.49776 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
239.6 | 130.2899 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0054293 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
239.8 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.25303 | 0.0046217 | 0.35695 | 0.0032709
240 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
240.2 | 130.194 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
240.4 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
240.6 | 130.2899 | 0.00083003 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | -0.026893 | 0.0048708
240.8 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.16505 | 0.0048708
241 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 0.0048708
241.2 | 130.3859 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.0016718
241.4 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.003531 | 0.30748 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
241.6 | 130.194 | 0.0024299 | 0.18331 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.019589 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
241.8 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.17102 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
242 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.25303 | 0.0046217 | 0.35695 | 0.0048708
242.2 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
242.4 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.15708 | 0.0046217 | 0.261 | 0.0048708
242.6 | 130.194 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0038295 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
242.8 | 130.2899 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
243 | 130.194 | 0.0024299 | 0.37521 | 0.0031381 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
243.2 | 130.194 | 0.0024299 | 0.18331 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
243.4 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.49776 | 0.0012893 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
243.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
243.8 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
244 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
244.2 | 130.2899 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
244.4 | 130.194 | 0.00083003 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
244.6 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.54889 | 0.0048708
244.8 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0022303 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
245 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
245.2 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.49776 | 0.0012893 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
245.4 | 130.194 | -0.00076916 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
245.6 | 130.194 | 0.0024299 | 0.4712 | 0.0031381 | 0.18962 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
245.8 | 130.2899 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0016718
246 | 130.2899 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.069058 | 0.0032709
246.2 | 130.2899 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.40347 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
246.4 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.68971 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
246.6 | 130.2899 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0054293 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.54889 | 0.0048708
246.8 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.003531 | 0.30748 | 0.0038295 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
247 | 130.2899 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.00063108 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.261 | 0.00647
247.2 | 130.194 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
247.4 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.28557 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
247.6 | 130.2899 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | -0.00017715 | 0.35695 | 0.0048708
247.8 | 130.194 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.49942 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.00647
248 | 130.194 | 0.0024299 | 0.56715 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.45294 | 0.0016718
248.2 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0016718
248.4 | 130.194 | -0.00076916 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
248.6 | 130.3859 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.261 | 0.0048708
248.8 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.40347 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
249 | 130.098 | 0.0024299 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
249.2 | 130.098 | 0.00083003 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
249.4 | 130.098 | -0.00076916 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
249.6 | 130.194 | 0.0024299 | 0.087319 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0014227 | 0.45294 | 0.0048708
249.8 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.40347 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
250 | 130.2899 | 0.00083003 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | -0.0012672 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
250.2 | 130.194 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.49942 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
250.4 | 130.2899 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.0019319 | 0.49942 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
250.6 | 130.194 | 0.00083003 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
250.8 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | -0.00030988 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
251 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.18962 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
251.2 | 130.194 | 0.0024299 | 0.18331 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0038295 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.16505 | 0.011268
251.4 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
251.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
251.8 | 130.2899 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
252 | 130.194 | 0.0024299 | 0.27926 | 0.004738 | 0.7654 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
252.2 | 130.194 | 0.00083003 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
252.4 | 130.2899 | 0.00083003 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.0048708
252.6 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
252.8 | 130.194 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
253 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
253.2 | 130.194 | 0.0024299 | 0.18331 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0038295 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
253.4 | 130.2899 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | -0.0028664 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
253.6 | 130.194 | 0.0024299 | 0.4712 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
253.8 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
254 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
254.2 | 130.2899 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | -0.11688 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0014227 | 0.45294 | 0.0048708
254.4 | 130.194 | 0.0024299 | 0.27926 | 0.0063372 | -0.002325 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.49776 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
254.6 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.49942 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
254.8 | 130.098 | -0.0039682 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
255 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
255.2 | 130.194 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.003531 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0094199 | 0.35695 | 0.0048708
255.4 | 130.194 | 0.0024299 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
255.6 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
255.8 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.49776 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
256 | 130.098 | 0.0024299 | 0.66314 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
256.2 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0038295 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
256.4 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
256.6 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0080803 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
256.8 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
257 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
257.2 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
257.4 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
257.6 | 130.098 | 0.0024299 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.019589 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | -0.026893 | 0.0048708
257.8 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.015026 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 7.1911e-05
258 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0032709
258.2 | 130.2899 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
258.4 | 130.098 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
258.6 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0028892 | 0.34898 | 0.0030219 | 0.45294 | 0.0048708
258.8 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | -0.0035089 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
259 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0012893 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
259.2 | 130.098 | 0.0024299 | 0.37521 | -6.0896e-05 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.019589 | 0.010228 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.54889 | -0.0031265
259.4 | 130.2899 | 0.0024299 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
259.6 | 130.098 | 0.0024299 | 0.27926 | 0.0063372 | 0.66945 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | -0.078023 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
259.8 | 130.098 | -0.00076916 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
260 | 130.002 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
260.2 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
260.4 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.5735 | 0.0080803 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.49776 | -0.0051081 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
260.6 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
260.8 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.66945 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
261 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
261.2 | 130.098 | 0.0024299 | 0.27926 | -0.0016601 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
261.4 | 130.002 | 0.0040291 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.16505 | 0.0032709
261.6 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.28557 | -0.003116 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.54092 | 0.0046217 | 0.261 | 0.0048708
261.8 | 130.002 | -0.0023683 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
262 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
262.2 | 130.098 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.73287 | 0.0046217 | 0.35695 | 0.0048708
262.4 | 130.098 | 0.0040291 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
262.6 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
262.8 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
263 | 130.002 | 0.0040291 | 0.27926 | 0.0015389 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
263.2 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.34898 | 0.0046217 | 0.45294 | 0.0032709
263.4 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.003531 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | -0.00017715 | 0.35695 | 0.0048708
263.6 | 130.098 | 0.0056289 | -0.10462 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 7.1911e-05
263.8 | 130.098 | 0.0056289 | 0.27926 | -6.0896e-05 | 0.66945 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.49776 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
264 | 129.9061 | 0.0040291 | 0.18331 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | -0.0028664 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0078201 | 0.35695 | 0.0032709
264.2 | 130.098 | 0.0056289 | 0.27926 | -0.0032593 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.11392 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
264.4 | 130.002 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.25303 | 0.0046217 | 0.261 | 0.0032709
264.6 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.075065 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
264.8 | 130.098 | 0.0056289 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
265 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.92481 | 0.0030219 | 0.261 | 0.0032709
265.2 | 130.002 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0067301 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.64488 | 0.0032709
265.4 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.17102 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
265.6 | 129.8101 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.003531 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
265.8 | 130.098 | 0.016825 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | -0.0017763 | 0.261 | 0.0032709
266 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.003531 | 0.21153 | 0.011827 | 0.30582 | 0.0060882 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
266.2 | 130.002 | 0.013626 | 0.27926 | 0.0031381 | 0.28557 | 0.0080803 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.73287 | 0.0046217 | 0.35695 | 0.0032709
266.4 | 129.9061 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.17102 | -0.0012672 | 0.30748 | 0.0070285 | 0.30582 | 0.0092866 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
266.6 | 130.098 | 0.0056289 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0022303 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | -0.0047263
266.8 | 130.098 | -0.00076916 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | -0.00017715 | 0.54889 | 0.0032709
267 | 130.002 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.5549 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
267.2 | 130.098 | 0.0024299 | 0.7591 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.003531 | -0.076363 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
267.4 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.66945 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.68971 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
267.6 | 130.098 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
267.8 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
268 | 130.098 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.49942 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
268.2 | 130.002 | 0.0040291 | 0.27926 | 0.0015389 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.49776 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
268.4 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
268.6 | 130.098 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
268.8 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
269 | 130.2899 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
269.2 | 130.098 | 0.0072281 | 0.56715 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | -0.00017715 | 0.35695 | 0.00647
269.4 | 130.098 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.17102 | 0.0067301 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | -0.0049754 | 0.35695 | 0.0048708
269.6 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
269.8 | 130.002 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.74084 | 0.0032709
270 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.49776 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
270.2 | 130.194 | 0.0072281 | 0.4712 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.54889 | 0.0032709
270.4 | 130.098 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.49776 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0048708
270.6 | 130.098 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
270.8 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | -0.17235 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | -0.0015273
271 | 130.194 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | -0.0033755 | 0.35695 | 0.0032709
271.2 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.49776 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
271.4 | 130.098 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
271.6 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.25303 | -0.0033755 | 0.261 | 0.0032709
271.8 | 130.3859 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
272 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
272.2 | 130.4819 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
272.4 | 130.2899 | 0.015225 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.5549 | -0.0028664 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0062209 | 0.261 | 0.0032709
272.6 | 130.5779 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.0067301 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
272.8 | 130.194 | 0.013626 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.003531 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
273 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
273.2 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
273.4 | 130.194 | 0.0088273 | 0.087319 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.261 | 0.0048708
273.6 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.7468 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
273.8 | 130.194 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 7.1911e-05
274 | 130.2899 | 0.0088273 | 0.18331 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0086283 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
274.2 | 130.2899 | 0.0072281 | 0.27926 | 0.0063372 | -0.002325 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
274.4 | 130.194 | 0.0072281 | 0.18331 | 0.0031381 | 0.5735 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.017929 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0016718
274.6 | 130.2899 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.40347 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
274.8 | 130.194 | 0.0088273 | 0.27926 | 0.0079364 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
275 | 130.194 | 0.0088273 | 0.087319 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0022303 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
275.2 | 130.098 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.261 | 0.0048708
275.4 | 130.002 | 0.0072281 | 0.37521 | 0.0015389 | 0.38156 | 0.0064811 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
275.6 | 130.098 | 0.0072281 | 0.18331 | 0.004738 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0070285 | 0.11392 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
275.8 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.54092 | -0.0033755 | 0.35695 | 0.0032709
276 | 130.098 | 0.0072281 | 0.37521 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
276.2 | 130.098 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.25303 | -0.00017715 | 0.35695 | 0.0032709
276.4 | 130.2899 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
276.6 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
276.8 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.011827 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.54889 | -0.0047263
277 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.25303 | 0.0030219 | 0.35695 | 0.0048708
277.2 | 130.194 | 0.0072281 | 0.4712 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
277.4 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0096794 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0060882 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
277.6 | 130.2899 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
277.8 | 130.2899 | 0.012026 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.16505 | 0.0032709
278 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0076874 | 0.34898 | 0.0046217 | 0.45294 | 0.0032709
278.2 | 130.2899 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.35695 | 0.0032709
278.4 | 130.194 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
278.6 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.28557 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0076874 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
278.8 | 130.3859 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
279 | 130.194 | 0.0072281 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
279.2 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
279.4 | 130.2899 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
279.6 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.11392 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
279.8 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.5735 | -0.003116 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
280 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0012893 | 0.54092 | 0.0046217 | 0.261 | 0.0032709
280.2 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
280.4 | 130.3859 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.5549 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
280.6 | 130.3859 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
280.8 | 130.3859 | 0.0072281 | 0.27926 | 0.0063372 | 0.093666 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | -0.078023 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
281 | 130.3859 | 0.0072281 | 0.27926 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
281.2 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | -0.0047152 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.25303 | 0.0030219 | 0.35695 | 0.0032709
281.4 | 130.3859 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
281.6 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0076874 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
281.8 | 130.3859 | 0.0088273 | 0.37521 | -0.0016601 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
282 | 130.4819 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
282.2 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
282.4 | 130.3859 | 0.013626 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.261 | 0.009669
282.6 | 130.2899 | 0.023223 | 0.37521 | -6.0896e-05 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.019589 | 0.015026 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.54889 | 0.011268
282.8 | 130.2899 | 0.03282 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.0019319 | 0.21153 | 0.011827 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.54889 | 0.0032709
283 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | -0.0012672 | 0.21153 | 0.010228 | 0.30582 | 0.010886 | 0.82882 | 0.0046217 | 0.35695 | 0.0048708
283.2 | 130.3859 | 0.0088273 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0038295 | 0.40181 | 0.0092866 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
283.4 | 130.194 | 0.010427 | 0.18331 | 0.0015389 | 0.47751 | 0.003282 | -0.50076 | 0.0019319 | 0.40347 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
283.6 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | -0.84575 | 0.0028892 | 0.34898 | 0.0062209 | 0.35695 | 0.0032709
283.8 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.25303 | 0.0046217 | 0.35695 | 0.0032709
284 | 130.3859 | 0.010427 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
284.2 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
284.4 | 130.4819 | 0.0088273 | 0.27926 | 0.0015389 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0012893 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
284.6 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.65085 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
284.8 | 130.4819 | 0.010427 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.019589 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
285 | 130.3859 | 0.0088273 | 0.27926 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
285.2 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.65085 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0076874 | 0.25303 | 0.0030219 | 0.35695 | 0.0032709
285.4 | 130.5779 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | -0.00030988 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
285.6 | 130.3859 | 0.012026 | 0.18331 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
285.8 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.010886 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
286 | 130.2899 | 0.0088273 | 0.27926 | 0.0015389 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | -0.0019091 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
286.2 | 130.194 | 0.0072281 | 0.66314 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.40347 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
286.4 | 129.8101 | 0.0088273 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.73287 | 0.0030219 | 0.35695 | 0.0032709
286.6 | 129.8101 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.25303 | 0.0046217 | 0.35695 | 0.0048708
286.8 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
287 | 130.2899 | 0.0072281 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0022303 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
287.2 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
287.4 | 130.4819 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
287.6 | 130.2899 | 0.0088273 | 0.37521 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
287.8 | 130.3859 | 0.012026 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
288 | 130.4819 | 0.0088273 | 0.27926 | 0.0063372 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0016718
288.2 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
288.4 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
288.6 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
288.8 | 130.4819 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.65085 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
289 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.17102 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
289.2 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
289.4 | 130.3859 | 0.0088273 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | -0.0028664 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.069058 | 0.0048708
289.6 | 130.4819 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
289.8 | 130.4819 | 0.0088273 | 0.37521 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
290 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.25303 | 0.0046217 | 0.35695 | 0.0048708
290.2 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.28557 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.49776 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
290.4 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | -0.0012672 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
290.6 | 130.4819 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.40181 | 0.0012893 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
290.8 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
291 | 130.4819 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | 0.0030219 | 0.35695 | 0.0048708
291.2 | 130.4819 | 0.012026 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.64488 | 0.0048708
291.4 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.64488 | 0.0032709
291.6 | 130.3859 | 0.0088273 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.017929 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
291.8 | 130.3859 | 0.0072281 | 0.27926 | 0.0063372 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.0016718
292 | 130.2899 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0012893 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
292.2 | 130.3859 | 0.0072281 | 0.087319 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
292.4 | 130.2899 | 0.0088273 | 0.4712 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.54889 | 0.0048708
292.6 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
292.8 | 130.3859 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
293 | 130.3859 | 0.0072281 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
293.2 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.261 | 0.0048708
293.4 | 130.3859 | 0.0072281 | 0.27926 | -0.0016601 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
293.6 | 130.3859 | 0.0072281 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.019589 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
293.8 | 130.3859 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
294 | 130.3859 | 0.0088273 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | -0.0044662 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.16505 | 0.0032709
294.2 | 130.3859 | 0.0072281 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
294.4 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
294.6 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0092866 | 0.34898 | 0.0030219 | 0.261 | 0.0048708
294.8 | 130.194 | 0.010427 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.069058 | 0.0048708
295 | 130.3859 | 0.018424 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.17102 | 0.0067301 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
295.2 | 130.194 | 0.016825 | 0.27926 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.011827 | 0.40181 | 0.0076874 | 0.34898 | 0.0030219 | 0.45294 | 0.0032709
295.4 | 130.3859 | 0.040817 | 0.27926 | 0.0031381 | 0.47751 | 0.0080803 | 0.36296 | 0.00033201 | 0.30748 | 0.015026 | 0.30582 | 0.0092866 | 0.25303 | 0.0030219 | 0.35695 | 0.0032709
295.6 | 130.2899 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.011827 | 0.30582 | 0.017284 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
295.8 | 130.2899 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
296 | 130.3859 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 1.6925 | 0.0030219 | 0.261 | 0.0032709
296.2 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
296.4 | 130.3859 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | -0.026893 | 0.0016718
296.6 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.54092 | 0.0014227 | 0.261 | 0.0032709
296.8 | 130.2899 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.11392 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
297 | 130.194 | 0.0088273 | 0.27926 | 0.0079364 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.59375 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
297.2 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
297.4 | 130.3859 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
297.6 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0038295 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
297.8 | 130.194 | 0.0072281 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0016718
298 | 130.194 | 0.0072281 | 0.087319 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0014227 | -0.026893 | 0.0016718
298.2 | 130.194 | 0.0072281 | 0.4712 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.49942 | 0.0070285 | 0.40181 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0080692
298.4 | 130.194 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
298.6 | 130.2899 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
298.8 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0014227 | 0.261 | 0.0032709
299 | 130.194 | 0.0072281 | 0.66314 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
299.2 | 130.194 | 0.0072281 | 0.087319 | 0.0031381 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
299.4 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
299.6 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0012893 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
299.8 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.010886 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
300 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
300.2 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
300.4 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.78566 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
300.6 | 130.098 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 8.3003e-05 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
300.8 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
301 | 130.194 | 0.0056289 | 0.18331 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.017929 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
301.2 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.010228 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
301.4 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
301.6 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
301.8 | 130.194 | 0.0056289 | 0.27926 | 0.0015389 | 0.093666 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
302 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0067301 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | -0.0033755 | 0.35695 | 0.0032709
302.2 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.28557 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0016718
302.4 | 130.098 | 0.0056289 | 0.27926 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.013427 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
302.6 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
302.8 | 130.194 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
303 | 130.098 | 0.0040291 | 0.27926 | 0.0015389 | 0.093666 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0012893 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
303.2 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
303.4 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.010886 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
303.6 | 129.7141 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0028664 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
303.8 | 130.098 | 0.0040291 | 0.27926 | 0.0063372 | -0.002325 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
304 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
304.2 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
304.4 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.17102 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
304.6 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
304.8 | 130.098 | 0.00083003 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.54889 | 0.0048708
305 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
305.2 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.16505 | 0.0032709
305.4 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.15708 | 0.0046217 | 0.35695 | 0.0032709
305.6 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.5735 | 0.0016822 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.11392 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
305.8 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
306 | 130.194 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.00033201 | 0.019589 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
306.2 | 130.194 | 0.0056289 | 0.087319 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
306.4 | 130.098 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
306.6 | 130.098 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.25303 | 0.0046217 | 0.35695 | 0.0032709
306.8 | 130.098 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.45891 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
307 | 130.002 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.45294 | 0.0032709
307.2 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.5549 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
307.4 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
307.6 | 130.098 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0038295 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
307.8 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.11392 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
308 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
308.2 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
308.4 | 130.098 | 0.0056289 | 0.37521 | 0.0031381 | 0.66945 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
308.6 | 130.098 | 0.0056289 | 0.4712 | -0.0016601 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
308.8 | 130.194 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
309 | 130.002 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
309.2 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | -0.002325 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
309.4 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.7654 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
309.6 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.18962 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
309.8 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.15708 | 0.0030219 | 0.35695 | 0.0032709
310 | 130.194 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.0064811 | 0.075065 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | -0.0017763 | 0.35695 | 0.0048708
310.2 | 130.098 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.64488 | 0.0032709
310.4 | 130.194 | 0.0056289 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0048708
310.6 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0078201 | 0.35695 | 0.0032709
310.8 | 130.194 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
311 | 130.2899 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0014227 | 0.35695 | 0.0048708
311.2 | 130.194 | 0.0056289 | -0.0086323 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.45294 | 0.011268
311.4 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0067301 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
311.6 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
311.8 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
312 | 130.2899 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
312.2 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.012486 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
312.4 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.28557 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.00647
312.6 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
312.8 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.0096794 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
313 | 130.194 | 0.0040291 | 0.18331 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0054293 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.00647
313.2 | 130.098 | 0.0056289 | 0.27926 | -0.0032593 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
313.4 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.019589 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
313.6 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | -0.00017715 | 0.35695 | 0.0032709
313.8 | 130.194 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
314 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.63692 | 0.0046217 | 0.261 | 0.0032709
314.2 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.7468 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0078201 | 0.35695 | 0.0032709
314.4 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
314.6 | 130.098 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.49776 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
314.8 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.45891 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
315 | 130.098 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0086283 | 0.40181 | 0.0012893 | 0.34898 | -0.0033755 | 0.35695 | 0.0032709
315.2 | 130.194 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0038295 | 0.78566 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
315.4 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.25303 | 0.0046217 | 0.35695 | 0.0032709
315.6 | 130.194 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0012893 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
315.8 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0054293 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
316 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 8.3003e-05 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
316.2 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.261 | 0.0032709
316.4 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
316.6 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
316.8 | 130.098 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.25303 | 0.0030219 | 0.35695 | 0.0048708
317 | 130.098 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
317.2 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
317.4 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0062209 | 0.35695 | 0.0032709
317.6 | 130.194 | 0.0056289 | 0.37521 | -6.0896e-05 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
317.8 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.069058 | 0.0032709
318 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.54889 | 0.0032709
318.2 | 130.194 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.11392 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
318.4 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.010886 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
318.6 | 130.2899 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.075065 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
318.8 | 130.098 | 0.0056289 | 0.27926 | 0.0063372 | -0.002325 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
319 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | -0.034861 | 0.0046217 | 0.261 | 0.0032709
319.2 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
319.4 | 130.194 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.25303 | 0.0046217 | 0.35695 | 0.0048708
319.6 | 130.194 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.11392 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
319.8 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.28557 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
320 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
320.2 | 130.194 | 0.0040291 | -0.0086323 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
320.4 | 130.194 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
320.6 | 130.194 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.34898 | 0.0030219 | 0.35695 | 0.0016718
320.8 | 130.194 | 0.0072281 | 0.37521 | -0.0016601 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.11392 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
321 | 130.194 | 0.0040291 | 0.27926 | 0.004738 | 0.7654 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
321.2 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
321.4 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.20987 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
321.6 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
321.8 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
322 | 130.2899 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.54889 | 0.0048708
322.2 | 130.194 | 0.0056289 | 0.37521 | 0.0015389 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
322.4 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
322.6 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
322.8 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.64488 | 0.0048708
323 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | -0.020925 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
323.2 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
323.4 | 130.2899 | 0.0072281 | 0.27926 | 0.004738 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
323.6 | 130.2899 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
323.8 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.66945 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
324 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
324.2 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
324.4 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
324.6 | 130.2899 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | -0.0044662 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
324.8 | 130.2899 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
325 | 130.2899 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.261 | 0.0048708
325.2 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.66945 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
325.4 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
325.6 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | -0.020925 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
325.8 | 130.2899 | 0.0072281 | 0.4712 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
326 | 130.2899 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
326.2 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
326.4 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0060882 | -0.13085 | 0.0030219 | 0.35695 | 0.0016718
326.6 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
326.8 | 130.2899 | 0.0088273 | 0.087319 | 0.0079364 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.49942 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.00647
327 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.15708 | 0.0014227 | 0.35695 | 0.0032709
327.2 | 130.194 | 0.0088273 | 0.56715 | 0.004738 | 0.38156 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.012486 | 0.44497 | 0.0014227 | 0.35695 | 0.00647
327.4 | 130.3859 | 0.0088273 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.010886 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
327.6 | 130.2899 | 0.0088273 | 0.27926 | 0.015934 | 0.38156 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.013427 | 0.30582 | 0.014085 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
327.8 | 130.3859 | -0.0071672 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.59537 | 0.013427 | 0.40181 | 0.020483 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
328 | 130.2899 | 0.023223 | 0.087319 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.019824 | 0.49776 | 0.015685 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
328.2 | 130.2899 | 0.050413 | 0.27926 | 0.0031381 | 0.38156 | 0.0080803 | 0.36296 | 0.00033201 | 0.30748 | 0.019824 | 0.40181 | 0.012486 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
328.4 | 130.098 | 0.050413 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0028664 | 0.30748 | 0.018225 | 0.40181 | 0.010886 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
328.6 | 130.098 | 0.053612 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.5549 | -0.0028664 | 0.30748 | 0.016626 | 0.40181 | 0.0092866 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
328.8 | 130.194 | 0.050413 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.013427 | 0.40181 | 0.010886 | 0.44497 | 0.0046217 | 0.35695 | -0.0015273
329 | 130.194 | 0.042416 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.013427 | 0.40181 | 0.0092866 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
329.2 | 130.194 | 0.037618 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.003531 | 0.30748 | 0.013427 | 0.40181 | 0.010886 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
329.4 | 130.098 | 0.021623 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.011827 | 0.30582 | 0.0092866 | 0.44497 | 0.0030219 | 0.35695 | 0.0080692
329.6 | 130.194 | 0.016825 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.40347 | 0.013427 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
329.8 | 130.002 | 0.020024 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.011827 | 0.40181 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
330 | 130.098 | 0.015225 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.17102 | 0.00033201 | 0.30748 | 0.013427 | 0.40181 | 0.0092866 | 0.34898 | 0.0030219 | 0.261 | 0.0048708
330.2 | 130.098 | 0.021623 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.49942 | 0.013427 | 0.40181 | 0.0076874 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
330.4 | 130.098 | 0.016825 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.26697 | 0.00033201 | 0.30748 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0030219 | 0.261 | 0.0048708
330.6 | 130.2899 | 0.016825 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.013427 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
330.8 | 130.2899 | 0.018424 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.011827 | 0.30582 | 0.0076874 | 0.34898 | -0.0033755 | 0.35695 | 0.0032709
331 | 130.2899 | 0.018424 | 0.27926 | 0.0063372 | 0.093666 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.49776 | 0.0076874 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
331.2 | 130.194 | 0.018424 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.011827 | 0.11392 | 0.0076874 | 0.44497 | 0.0030219 | 0.261 | 0.00647
331.4 | 130.098 | 0.016825 | 0.27926 | -0.0016601 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.013427 | 0.40181 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
331.6 | 130.002 | 0.016825 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.013427 | 0.40181 | 0.0092866 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
331.8 | 130.2899 | 0.020024 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.003531 | 0.21153 | 0.011827 | 0.40181 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
332 | 130.2899 | 0.016825 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.011827 | 0.40181 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
332.2 | 130.194 | 0.018424 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.30748 | 0.013427 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
332.4 | 130.2899 | 0.021623 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.011827 | 0.30582 | 0.0076874 | 0.54092 | 0.0046217 | 0.16505 | 0.0048708
332.6 | 130.2899 | 0.018424 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.40347 | 0.011827 | 0.11392 | 0.0076874 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
332.8 | 130.2899 | 0.015225 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.013427 | 0.40181 | 0.0076874 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
333 | 130.2899 | 0.013626 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.40347 | 0.011827 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
333.2 | 130.2899 | 0.018424 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.013427 | 0.59375 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
333.4 | 130.2899 | 0.018424 | 0.18331 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | -0.0012672 | 0.30748 | 0.013427 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
333.6 | 130.3859 | 0.018424 | 0.27926 | 0.004738 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.011827 | 0.49776 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
333.8 | 130.194 | 0.016825 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.010886 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
334 | 130.194 | 0.016825 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.013427 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
334.2 | 130.2899 | 0.015225 | 0.27926 | 0.004738 | 0.093666 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.013427 | 0.30582 | 0.0092866 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
334.4 | 130.2899 | 0.021623 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.011827 | 0.30582 | 0.010886 | 0.44497 | -0.00017715 | 0.261 | 0.0032709
334.6 | 130.098 | 0.020024 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.30582 | 0.0092866 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
334.8 | 130.194 | 0.018424 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0092866 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
335 | 130.194 | 0.020024 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.30748 | 0.011827 | 0.40181 | 0.010886 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
335.2 | 130.194 | 0.021623 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.075065 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
335.4 | 130.2899 | 0.016825 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.40347 | 0.013427 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
335.6 | 130.2899 | 0.020024 | 0.4712 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.011827 | 0.40181 | 0.0076874 | 0.34898 | 0.0030219 | 0.069058 | 0.0032709
335.8 | 130.098 | 0.018424 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | -0.0012672 | 0.30748 | 0.011827 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
336 | 130.194 | 0.012026 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.013427 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.0032709
336.2 | 130.3859 | 0.018424 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
336.4 | 130.2899 | 0.020024 | 0.37521 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.011827 | 0.20987 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
336.6 | 130.3859 | 0.020024 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | -0.076363 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
336.8 | 130.2899 | 0.020024 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.019589 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.069058 | 0.0048708
337 | 130.3859 | 0.018424 | 0.087319 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
337.2 | 130.3859 | 0.020024 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.20987 | 0.0076874 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
337.4 | 130.3859 | 0.018424 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
337.6 | 130.3859 | 0.016825 | 0.18331 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | -0.076363 | 0.0086283 | 0.30582 | 0.0076874 | 0.34898 | 0.0030219 | 0.261 | 0.0048708
337.8 | 130.3859 | 0.015225 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.45294 | -0.0015273
338 | 130.2899 | 0.013626 | 0.27926 | 0.004738 | 0.47751 | 0.0080803 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0060882 | 0.63692 | 0.0046217 | 0.261 | 0.0032709
338.2 | 130.194 | 0.016825 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
338.4 | 130.3859 | 0.018424 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
338.6 | 130.3859 | 0.015225 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.26697 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.25303 | 0.0030219 | 0.35695 | 0.0048708
338.8 | 130.4819 | 0.020024 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
339 | 130.3859 | 0.020024 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.11554 | 0.011827 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
339.2 | 130.3859 | 0.020024 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.011827 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
339.4 | 130.2899 | 0.018424 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
339.6 | 130.3859 | 0.016825 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.11392 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
339.8 | 130.3859 | 0.018424 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.11554 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.16505 | 0.0032709
340 | 130.3859 | 0.020024 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
340.2 | 130.2899 | 0.015225 | 0.4712 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
340.4 | 130.2899 | 0.013626 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
340.6 | 130.3859 | 0.015225 | -0.0086323 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
340.8 | 130.3859 | 0.016825 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
341 | 130.3859 | 0.015225 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
341.2 | 130.3859 | 0.015225 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.011827 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
341.4 | 129.0424 | 0.018424 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0030219 | 0.261 | 0.0048708
341.6 | 128.9464 | 0.016825 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.11392 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
341.8 | 129.6182 | 0.013626 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
342 | 130.194 | 0.013626 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
342.2 | 130.2899 | 0.012026 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
342.4 | 130.2899 | 0.015225 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.20987 | 0.0076874 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
342.6 | 130.194 | 0.016825 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0060882 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
342.8 | 130.2899 | 0.020024 | 0.27926 | 0.004738 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
343 | 130.194 | 0.016825 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | -0.0028664 | 0.21153 | 0.011827 | 0.30582 | 0.0076874 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
343.2 | 130.194 | 0.018424 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.013427 | 0.40181 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0080692
343.4 | 130.098 | 0.016825 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | -0.0028664 | 0.30748 | 0.011827 | 0.40181 | 0.0076874 | 0.44497 | -0.0017763 | 0.35695 | 0.0032709
343.6 | 130.098 | 0.018424 | 0.37521 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.013427 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
343.8 | 130.002 | 0.020024 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.013427 | 0.20987 | 0.010886 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
344 | 130.194 | 0.023223 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.013427 | 0.30582 | 0.010886 | 0.44497 | 0.0046217 | 0.261 | 7.1911e-05
344.2 | 130.098 | 0.021623 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.30582 | 0.0092866 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
344.4 | 130.002 | 0.020024 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0092866 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
344.6 | 130.098 | 0.021623 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.011827 | 0.40181 | 0.014085 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
344.8 | 130.194 | 0.03122 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0092866 | 0.44497 | 0.0030219 | 0.35695 | 0.0080692
345 | 130.194 | 0.029621 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.013427 | 0.40181 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
345.2 | 130.2899 | 0.03282 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.011827 | 0.40181 | 0.0092866 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
345.4 | 130.194 | 0.036018 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.30748 | 0.013427 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
345.6 | 130.2899 | 0.050413 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.016626 | 0.40181 | 0.0092866 | 0.44497 | 0.0030219 | 0.261 | 0.009669
345.8 | 130.194 | 0.048814 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.018225 | 0.49776 | 0.012486 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
346 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.66945 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.011827 | 0.49776 | 0.017284 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
346.2 | 130.2899 | 0.0088273 | -0.10462 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.016626 | 0.40181 | 0.012486 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
346.4 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.5735 | 0.0064811 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.010886 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
346.6 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.66945 | 0.041669 | 0.26697 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.010886 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
346.8 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
347 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | -0.0012672 | 0.21153 | -0.013764 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.16505 | 0.0048708
347.2 | 130.3859 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0062209 | 0.261 | 0.0032709
347.4 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
347.6 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.73287 | 0.0046217 | 0.16505 | 0.0032709
347.8 | 130.194 | 0.0088273 | 0.37521 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.011268
348 | 130.194 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
348.2 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.28557 | 0.0048812 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
348.4 | 130.194 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
348.6 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.011268
348.8 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0016718
349 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.0067301 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
349.2 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
349.4 | 130.194 | 0.0072281 | 0.27926 | 0.0015389 | 0.093666 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
349.6 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
349.8 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
350 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
350.2 | 130.194 | 0.0088273 | 0.4712 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0054293 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
350.4 | 130.194 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0080692
350.6 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
350.8 | 130.194 | 0.0072281 | 0.27926 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
351 | 130.002 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
351.2 | 130.194 | 0.012026 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
351.4 | 130.194 | 0.0072281 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.00063108 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
351.6 | 130.194 | 0.0072281 | 0.56715 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
351.8 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
352 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
352.2 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
352.4 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
352.6 | 130.002 | 0.0072281 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0038295 | 0.30582 | 0.0060882 | 0.34898 | 0.0030219 | 0.261 | 0.0032709
352.8 | 130.098 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | -0.0019091 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
353 | 130.098 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
353.2 | 130.194 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
353.4 | 130.098 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.16505 | 0.0032709
353.6 | 130.098 | 0.0072281 | 0.087319 | 0.0095362 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0038295 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
353.8 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.17102 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
354 | 130.098 | 0.0056289 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.013427 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
354.2 | 130.2899 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
354.4 | 130.098 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.25303 | 0.0030219 | 0.35695 | 0.0048708
354.6 | 129.9061 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | -0.0028664 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
354.8 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
355 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.11392 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
355.2 | 129.9061 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | -0.00017715 | 0.35695 | 0.0032709
355.4 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0030219 | 0.261 | 0.0048708
355.6 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
355.8 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.66945 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
356 | 130.098 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
356.2 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
356.4 | 130.194 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
356.6 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
356.8 | 130.098 | 0.0056289 | 0.37521 | -6.0896e-05 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.017929 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
357 | 130.002 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
357.2 | 130.2899 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.5549 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.261 | 0.0048708
357.4 | 129.8101 | 0.0040291 | 0.27926 | 0.0015389 | 0.66945 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
357.6 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0067301 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
357.8 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.075065 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
358 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.011827 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
358.2 | 130.002 | 0.0072281 | 0.37521 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 7.1911e-05
358.4 | 129.9061 | 0.0040291 | 0.66314 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0051309 | -0.076363 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.54889 | 0.0032709
358.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0080803 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.20987 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
358.8 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0038295 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
359 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
359.2 | 130.002 | 0.0056289 | 0.18331 | 0.0015389 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
359.4 | 130.002 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
359.6 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
359.8 | 129.9061 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.17102 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.069058 | 0.0048708
360 | 129.8101 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.30582 | 0.0060882 | 0.44497 | -0.00017715 | 0.35695 | 0.0032709
360.2 | 130.002 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | -0.0012672 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.011019 | 0.261 | 0.0032709
360.4 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
360.6 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
360.8 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
361 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.28557 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
361.2 | 130.002 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0016822 | 0.36296 | 0.003531 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
361.4 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
361.6 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | -0.0015273
361.8 | 130.002 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.7468 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
362 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.00063108 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
362.2 | 129.6182 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.5549 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
362.4 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.0083293 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
362.6 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
362.8 | 129.9061 | 0.0040291 | 0.37521 | -6.0896e-05 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.019589 | 0.015026 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | -0.0015273
363 | 129.9061 | 0.0040291 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0062209 | 0.35695 | 0.00647
363.2 | 130.002 | 0.0040291 | 0.27926 | 0.004738 | 0.5735 | 0.0048812 | 0.17102 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
363.4 | 130.002 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0016822 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
363.6 | 130.002 | 0.0040291 | 0.4712 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.11392 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
363.8 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
364 | 129.9061 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.11392 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
364.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.15708 | 0.0046217 | 0.35695 | 0.0032709
364.4 | 129.9061 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.5549 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.25303 | 0.0030219 | 0.35695 | 0.0032709
364.6 | 130.002 | 0.0056289 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.019589 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
364.8 | 129.9061 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
365 | 129.9061 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0092866 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
365.2 | 129.9061 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
365.4 | 129.9061 | 0.0040291 | 0.18331 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
365.6 | 129.9061 | 0.0056289 | 0.66314 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
365.8 | 129.9061 | 0.0056289 | 0.37521 | 0.0031381 | 0.7654 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0012893 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
366 | 129.9061 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
366.2 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.06109 | 0.0046217 | 0.35695 | 0.0048708
366.4 | 129.9061 | 0.0056289 | 0.27926 | 0.004738 | 0.66945 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
366.6 | 129.8101 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
366.8 | 129.9061 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.49776 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
367 | 130.002 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
367.2 | 130.002 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
367.4 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
367.6 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
367.8 | 130.002 | 0.0056289 | 0.18331 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.013427 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.64488 | 0.0048708
368 | 130.002 | 0.0040291 | 0.4712 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
368.2 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.84279 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | -0.00017715 | 0.261 | 0.0032709
368.4 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 8.3003e-05 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
368.6 | 129.9061 | 0.0024299 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.40347 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.261 | -0.0015273
368.8 | 129.9061 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.15708 | 0.0046217 | 0.45294 | 0.0048708
369 | 129.9061 | 0.0040291 | 0.4712 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
369.2 | 130.002 | 0.0056289 | 0.087319 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.49942 | 0.00063108 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
369.4 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
369.6 | 129.9061 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.012486 | 0.34898 | 0.0030219 | 0.45294 | 0.0032709
369.8 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.0064811 | -0.11688 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
370 | 129.7141 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
370.2 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.011827 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
370.4 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
370.6 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | -0.17401 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
370.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.019589 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.64488 | 0.0048708
371 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.261 | 0.0032709
371.2 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.7468 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
371.4 | 129.9061 | 0.00083003 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | -0.076363 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.64488 | 0.0032709
371.6 | 130.002 | -0.0023683 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.54889 | 0.0048708
371.8 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
372 | 130.002 | 0.0040291 | 0.18331 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.11392 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
372.2 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0096794 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
372.4 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.54889 | 0.0032709
372.6 | 130.002 | 0.00083003 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.069058 | 0.0048708
372.8 | 129.8101 | 0.0024299 | 0.27926 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
373 | 130.002 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.49942 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0078201 | -0.026893 | 0.0048708
373.2 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
373.4 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.17102 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
373.6 | 130.194 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
373.8 | 130.002 | 0.0024299 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | -0.0015273
374 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
374.2 | 130.002 | 0.0056289 | 0.087319 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
374.4 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.25303 | 0.0030219 | 0.261 | 0.0048708
374.6 | 130.002 | 0.0056289 | 0.37521 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
374.8 | 129.9061 | 0.0040291 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0038295 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
375 | 129.8101 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0028664 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.45294 | 0.0032709
375.2 | 129.9061 | 0.0024299 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
375.4 | 129.9061 | 0.0040291 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
375.6 | 129.9061 | 0.0056289 | 0.7591 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.003531 | -0.076363 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.45294 | 0.0032709
375.8 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.17102 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
376 | 129.9061 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | 0.0046217 | 0.261 | 0.0048708
376.2 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.28557 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.68971 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
376.4 | 129.9061 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.069058 | 0.0048708
376.6 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
376.8 | 130.2899 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
377 | 129.9061 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
377.2 | 129.9061 | 0.0056289 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.59537 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0080692
377.4 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | -0.0012672 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
377.6 | 130.002 | 0.0040291 | 0.4712 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.019589 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
377.8 | 130.002 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
378 | 130.002 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | -0.003116 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.15708 | 0.0030219 | 0.35695 | 0.0032709
378.2 | 130.002 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.68971 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
378.4 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.20987 | -0.0019091 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
378.6 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.013427 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.261 | 0.0032709
378.8 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
379 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.49776 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
379.2 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.66945 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0092866 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
379.4 | 130.098 | 0.0056289 | 0.37521 | 0.0031381 | 0.28557 | 0.0064811 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0032709
379.6 | 130.002 | 0.0056289 | 0.18331 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
379.8 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.0064811 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
380 | 130.002 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
380.2 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
380.4 | 130.002 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | -0.12288 | 0.0048708
380.6 | 130.098 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
380.8 | 130.098 | 0.0056289 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
381 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | -0.078023 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
381.2 | 130.098 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.019589 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
381.4 | 130.002 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | -0.003116 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
381.6 | 130.002 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.34898 | 0.0046217 | 0.64488 | 0.0032709
381.8 | 130.002 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.261 | 0.0032709
382 | 130.098 | 0.0056289 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0032709
382.2 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.16505 | 0.0048708
382.4 | 130.098 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0032709
382.6 | 130.098 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.16505 | 0.00647
382.8 | 130.098 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
383 | 130.098 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
383.2 | 130.194 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
383.4 | 130.098 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
383.6 | 130.194 | 0.0072281 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
383.8 | 130.194 | 0.0088273 | 0.37521 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.45294 | 0.00647
384 | 130.098 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | -0.0015162 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.63692 | 0.0030219 | 0.261 | 0.0032709
384.2 | 130.098 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.17102 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
384.4 | 130.098 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
384.6 | 130.098 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0030219 | 0.45294 | 0.0048708
384.8 | 130.098 | 0.0072281 | 0.27926 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.40347 | 0.00063108 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
385 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.40347 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
385.2 | 130.098 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
385.4 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.019589 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
385.6 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
385.8 | 130.194 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
386 | 130.194 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 1.1695 | 0.0044883 | 0.25303 | 0.0046217 | 0.35695 | 0.0032709
386.2 | 130.2899 | 0.0088273 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.261 | 0.0048708
386.4 | 130.194 | 0.0088273 | 0.4712 | 0.0031381 | 0.18962 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.015026 | 0.59375 | 0.017284 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
386.6 | 130.3859 | 0.050413 | 0.18331 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.016626 | 0.40181 | 0.010886 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
386.8 | 130.098 | 0.021623 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.011827 | 0.40181 | 0.010886 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
387 | 130.194 | 0.018424 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.016626 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
387.2 | 130.098 | 0.013626 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0094199 | 0.35695 | 0.0032709
387.4 | 130.194 | 0.012026 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
387.6 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.45294 | 0.0048708
387.8 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.66945 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
388 | 130.2899 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
388.2 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
388.4 | 130.3859 | 0.0072281 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0028892 | 0.25303 | 0.0046217 | 0.35695 | 0.0048708
388.6 | 130.3859 | 0.0088273 | 0.27926 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0016718
388.8 | 130.2899 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
389 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0051309 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
389.2 | 130.3859 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.25303 | 0.0094199 | 0.35695 | 0.0032709
389.4 | 130.2899 | 0.0072281 | 0.4712 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
389.6 | 130.2899 | 0.0088273 | 0.27926 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.011827 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
389.8 | 130.2899 | 0.0072281 | 0.18331 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.16505 | 0.0032709
390 | 130.4819 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
390.2 | 130.3859 | 0.0088273 | 0.27926 | 0.004738 | 0.28557 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
390.4 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
390.6 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
390.8 | 130.3859 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
391 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
391.2 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.20987 | 0.010886 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
391.4 | 130.4819 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.5549 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
391.6 | 130.3859 | 0.010427 | 0.27926 | -0.0016601 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.49776 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
391.8 | 130.3859 | 0.010427 | 0.4712 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
392 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
392.2 | 130.3859 | 0.010427 | 0.27926 | 0.004738 | 0.28557 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
392.4 | 130.3859 | 0.0088273 | 0.087319 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.40347 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
392.6 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
392.8 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
393 | 130.3859 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0016718
393.2 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
393.4 | 130.3859 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.0067301 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.64488 | 0.0048708
393.6 | 130.3859 | 0.0088273 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.16505 | 0.0048708
393.8 | 130.3859 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
394 | 130.3859 | 0.010427 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
394.2 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
394.4 | 130.194 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0083293 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | -0.0017763 | 0.35695 | 0.0048708
394.6 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.45294 | 0.0032709
394.8 | 130.3859 | 0.010427 | -0.10462 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
395 | 130.194 | 0.0072281 | 0.66314 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | -0.076363 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | 0.0032709
395.2 | 130.2899 | 0.0088273 | 0.37521 | 0.0079364 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
395.4 | 130.002 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.011019 | 0.35695 | 0.0048708
395.6 | 130.2899 | 0.0088273 | 0.27926 | 0.0015389 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0016718
395.8 | 130.3859 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
396 | 130.2899 | 0.0088273 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.017929 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
396.2 | 130.194 | 0.010427 | 0.18331 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.74084 | 0.00647
396.4 | 130.2899 | 0.012026 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | -0.0028664 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0014227 | 0.35695 | 0.0032709
396.6 | 130.2899 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.25303 | 0.0062209 | 0.45294 | 0.0048708
396.8 | 130.2899 | 0.010427 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
397 | 130.194 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.5549 | 0.0083293 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | -0.00017715 | 0.35695 | 0.0048708
397.2 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.00647
397.4 | 130.194 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
397.6 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
397.8 | 130.194 | 0.010427 | 0.18331 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.20987 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
398 | 130.194 | 0.0088273 | 0.27926 | 0.004738 | 0.66945 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.68971 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
398.2 | 130.2899 | 0.0088273 | 0.18331 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
398.4 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
398.6 | 130.194 | 0.0088273 | 0.27926 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.00063108 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
398.8 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
399 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
399.2 | 130.194 | 0.012026 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | 0.0051309 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.069058 | 0.0048708
399.4 | 130.002 | 0.0088273 | 0.66314 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
399.6 | 130.002 | 0.0088273 | 0.27926 | 0.0063372 | 0.28557 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.68971 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
399.8 | 130.002 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
400 | 130.194 | 0.0088273 | 0.27926 | -6.0896e-05 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
400.2 | 130.194 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
400.4 | 130.098 | 0.0088273 | 0.37521 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 7.1911e-05
400.6 | 130.002 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | -0.020925 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
400.8 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
401 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.011268
401.2 | 130.098 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0096794 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
401.4 | 130.098 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.40347 | 0.00063108 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.00647
401.6 | 130.098 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.65085 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
401.8 | 130.098 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0012893 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
402 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.013427 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | -0.0015273
402.2 | 130.194 | 0.010427 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
402.4 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
402.6 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
402.8 | 129.9061 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | -0.00017715 | 0.35695 | 0.0048708
403 | 130.194 | 0.010427 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
403.2 | 130.194 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | -0.0060654 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
403.4 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0016718
403.6 | 130.098 | 0.0088273 | 0.18331 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0014227 | 0.54889 | 0.0080692
403.8 | 130.194 | 0.010427 | 0.27926 | -0.0032593 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
404 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
404.2 | 129.8101 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.0051309 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
404.4 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.45891 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
404.6 | 130.194 | 0.012026 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
404.8 | 130.2899 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0012893 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
405 | 130.2899 | 0.0088273 | 0.27926 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
405.2 | 130.2899 | 0.010427 | 0.27926 | 0.0015389 | 0.28557 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.49776 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
405.4 | 130.194 | 0.0088273 | 0.37521 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.017929 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
405.6 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.59375 | 0.0060882 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
405.8 | 130.194 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.64488 | 0.0048708
406 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.0080803 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
406.2 | 130.194 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.65085 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
406.4 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
406.6 | 130.2899 | 0.010427 | 0.087319 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.40347 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
406.8 | 130.2899 | 0.0088273 | 0.27926 | 0.004738 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
407 | 130.3859 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
407.2 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.20987 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
407.4 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | -0.0015162 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
407.6 | 130.2899 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.74084 | 0.0048708
407.8 | 130.2899 | 0.0088273 | -0.10462 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0054293 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
408 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0054293 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
408.2 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
408.4 | 130.194 | 0.010427 | -0.0086323 | 0.0031381 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0038295 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
408.6 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
408.8 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.65085 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0028892 | 0.82882 | 0.0046217 | 0.35695 | 0.0032709
409 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
409.2 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.28557 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0016718
409.4 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.15708 | 0.0046217 | 0.35695 | 0.0048708
409.6 | 130.4819 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0076874 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
409.8 | 130.2899 | 0.010427 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
410 | 130.3859 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
410.2 | 130.2899 | 0.010427 | 0.27926 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.59375 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
410.4 | 130.2899 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
410.6 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
410.8 | 130.3859 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.20987 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
411 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
411.2 | 130.2899 | 0.010427 | 0.18331 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
411.4 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0067301 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
411.6 | 130.2899 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
411.8 | 130.2899 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
412 | 130.6738 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
412.2 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.075065 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.73287 | 0.0046217 | 0.45294 | 0.0048708
412.4 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
412.6 | 130.3859 | 0.010427 | 0.27926 | 0.0015389 | 0.5735 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.78566 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
412.8 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
413 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.34898 | 0.0030219 | 0.45294 | 0.0048708
413.2 | 130.2899 | 0.010427 | 0.27926 | 0.0063372 | 0.28557 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0054293 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
413.4 | 130.194 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | -0.076363 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
413.6 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
413.8 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0016718
414 | 130.098 | 0.010427 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
414.2 | 130.2899 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.59375 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
414.4 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.16505 | 0.0048708
414.6 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
414.8 | 130.3859 | 0.010427 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
415 | 130.2899 | 0.010427 | 0.56715 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
415.2 | 130.2899 | 0.012026 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.16505 | 0.0048708
415.4 | 130.002 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.011019 | 0.35695 | 0.0048708
415.6 | 130.3859 | 0.010427 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
415.8 | 130.2899 | 0.010427 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.74084 | 0.0048708
416 | 130.2899 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
416.2 | 130.2899 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.68971 | 0.0044883 | 0.34898 | 0.0046217 | 0.45294 | 0.0032709
416.4 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.63692 | 0.0030219 | 0.35695 | 0.0048708
416.6 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
416.8 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.49776 | 0.0076874 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
417 | 130.3859 | 0.0088273 | 0.37521 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0016718
417.2 | 130.3859 | 0.012026 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
417.4 | 130.194 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | -0.020925 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | -0.00017715 | 0.35695 | 0.0048708
417.6 | 130.2899 | 0.0088273 | 0.27926 | 0.004738 | 0.7654 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.11392 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
417.8 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.0048708
418 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
418.2 | 130.4819 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
418.4 | 130.3859 | 0.010427 | 0.27926 | 0.004738 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
418.6 | 130.194 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
418.8 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0092866 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
419 | 130.3859 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.20987 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
419.2 | 130.3859 | 0.010427 | 0.18331 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
419.4 | 130.3859 | 0.010427 | 0.27926 | 0.0063372 | 0.38156 | 0.003282 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
419.6 | 130.2899 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.49776 | 0.0076874 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
419.8 | 130.3859 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
420 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
420.2 | 130.2899 | 0.010427 | 0.27926 | 0.004738 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0046217 | 0.45294 | 0.0032709
420.4 | 130.4819 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.54889 | 0.00647
420.6 | 130.194 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
420.8 | 130.3859 | 0.010427 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
421 | 130.2899 | 0.015225 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.49942 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
421.2 | 130.3859 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
421.4 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | -0.0017763 | 0.45294 | 0.0048708
421.6 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.019589 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
421.8 | 130.2899 | 0.0088273 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | -0.026893 | 0.0048708
422 | 130.2899 | 0.010427 | 0.27926 | 0.004738 | 0.28557 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.49776 | 0.0028892 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
422.2 | 130.2899 | 0.0088273 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0038295 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | -0.0031265
422.4 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
422.6 | 130.194 | 0.012026 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.40347 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
422.8 | 130.2899 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
423 | 130.2899 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
423.2 | 130.3859 | 0.0088273 | 0.27926 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.40347 | 0.0022303 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
423.4 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
423.6 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.18962 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
423.8 | 130.3859 | 0.012026 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
424 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
424.2 | 130.194 | 0.0088273 | 0.27926 | 0.0015389 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
424.4 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
424.6 | 130.194 | 0.0088273 | 0.18331 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
424.8 | 130.2899 | 0.012026 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.261 | 0.0032709
425 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.069058 | 0.0048708
425.2 | 130.194 | 0.0088273 | 0.37521 | 0.0031381 | 0.28557 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
425.4 | 130.2899 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | -0.026893 | 0.0032709
425.6 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
425.8 | 130.194 | 0.010427 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.40347 | 0.0070285 | 0.30582 | 0.0060882 | 0.34898 | 0.0046217 | 0.54889 | 7.1911e-05
426 | 130.2899 | 0.012026 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.011827 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0080692
426.2 | 130.2899 | 0.0088273 | 0.4712 | 0.004738 | 0.28557 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
426.4 | 130.4819 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
426.6 | 130.002 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
426.8 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.18962 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
427 | 130.2899 | 0.010427 | 0.37521 | 0.0031381 | 0.7654 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.017929 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
427.2 | 130.2899 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
427.4 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.45294 | 0.0048708
427.6 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
427.8 | 130.2899 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | -0.0015273
428 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.093666 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
428.2 | 130.2899 | 0.010427 | -0.0086323 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
428.4 | 130.194 | 0.010427 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
428.6 | 130.194 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
428.8 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.0051309 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
429 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.7468 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.25303 | 0.0046217 | 0.35695 | 0.0048708
429.2 | 130.2899 | 0.010427 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
429.4 | 130.2899 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
429.6 | 130.3859 | 0.012026 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0044662 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
429.8 | 130.2899 | 0.0088273 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
430 | 130.3859 | 0.010427 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
430.2 | 130.194 | 0.010427 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
430.4 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.59375 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
430.6 | 130.194 | 0.010427 | 0.37521 | 0.0015389 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
430.8 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.40347 | 0.0022303 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
431 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
431.2 | 130.2899 | 0.0088273 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
431.4 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
431.6 | 130.3859 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.17102 | 0.0051309 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0014227 | 0.35695 | 0.0048708
431.8 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | 0.0062209 | 0.261 | 0.0048708
432 | 130.2899 | 0.0088273 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | 0.0032709
432.2 | 130.4819 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
432.4 | 130.2899 | 0.0072281 | 0.37521 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.011827 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
432.6 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
432.8 | 130.2899 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
433 | 130.2899 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
433.2 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
433.4 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
433.6 | 130.194 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.26697 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | 0.0046217 | 0.261 | 0.0048708
433.8 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | -0.0028664 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
434 | 130.2899 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
434.2 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.25303 | 0.0046217 | 0.261 | 0.0048708
434.4 | 130.098 | 0.0072281 | 0.37521 | 0.0031381 | 0.28557 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
434.6 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
434.8 | 130.194 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0016718
435 | 130.098 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.20987 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
435.2 | 130.194 | 0.013626 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 0.0048708
435.4 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
435.6 | 130.194 | 0.018424 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.011827 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
435.8 | 129.8101 | 0.015225 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.30748 | 0.013427 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
436 | 130.194 | 0.040817 | 0.27926 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.013427 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
436.2 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.003531 | 0.21153 | 0.013427 | 0.49776 | 0.015685 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
436.4 | 130.098 | 0.010427 | 0.27926 | -6.0896e-05 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.015026 | 0.40181 | 0.010886 | 0.44497 | 0.0046217 | -0.026893 | 0.0048708
436.6 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | -1.6524 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
436.8 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0054293 | 0.017929 | 0.0044883 | 0.54092 | 0.0030219 | 0.261 | 0.0032709
437 | 130.098 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0022303 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
437.2 | 130.098 | 0.0088273 | 0.27926 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
437.4 | 130.098 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
437.6 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.28557 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0076874 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
437.8 | 129.8101 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
438 | 130.098 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.261 | 0.009669
438.2 | 130.002 | 0.0088273 | 0.37521 | 0.0079364 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
438.4 | 130.002 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.0016822 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
438.6 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
438.8 | 130.3859 | 0.0072281 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
439 | 130.098 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.5549 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
439.2 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.25303 | 0.0046217 | 0.261 | 0.0048708
439.4 | 130.098 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
439.6 | 130.098 | 0.0072281 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
439.8 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
440 | 130.002 | 0.0072281 | 0.27926 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | -0.078023 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
440.2 | 130.002 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
440.4 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.069058 | 0.0048708
440.6 | 130.098 | 0.0072281 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.34898 | 0.0046217 | 0.45294 | 0.0048708
440.8 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | -0.0044662 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | 0.0032709
441 | 130.002 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0030219 | 0.35695 | 0.0048708
441.2 | 130.098 | 0.0072281 | 0.27926 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
441.4 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
441.6 | 129.7141 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.011019 | 0.35695 | 0.0048708
441.8 | 130.002 | 0.0072281 | 0.27926 | 0.0031381 | 0.66945 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
442 | 130.098 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0032709
442.2 | 130.002 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
442.4 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.20987 | -0.0019091 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
442.6 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.25303 | 0.0046217 | 0.35695 | 0.0032709
442.8 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
443 | 130.002 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.54889 | 0.0048708
443.2 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.20987 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
443.4 | 129.9061 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.15708 | 0.0030219 | 0.35695 | 0.0048708
443.6 | 130.098 | 0.0072281 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.45891 | 0.0067301 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.64488 | 0.0048708
443.8 | 130.098 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
444 | 129.8101 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
444.2 | 130.002 | 0.0040291 | 0.4712 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
444.4 | 129.9061 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
444.6 | 129.9061 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0076874 | 0.25303 | 0.0046217 | 0.35695 | 0.0048708
444.8 | 129.9061 | 0.0056289 | 0.27926 | 0.0031381 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0016718
445 | 129.9061 | 0.0056289 | 0.27926 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0092866 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
445.2 | 129.9061 | 0.0056289 | 0.27926 | 0.004738 | 0.7654 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | -0.078023 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
445.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
445.6 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.0048708
445.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.92481 | 0.0046217 | 0.35695 | 0.0048708
446 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0092866 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
446.2 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
446.4 | 130.002 | 0.0056289 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
446.6 | 129.9061 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
446.8 | 129.9061 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.16505 | 0.0032709
447 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
447.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
447.4 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
447.6 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
447.8 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
448 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | -0.076363 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
448.2 | 129.9061 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
448.4 | 130.002 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
448.6 | 129.9061 | 0.0024299 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
448.8 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.069058 | 0.0048708
449 | 129.8101 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
449.2 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
449.4 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
449.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.73287 | 0.0046217 | 0.35695 | 0.0048708
449.8 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0067301 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
450 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
450.2 | 129.9061 | 0.0040291 | 0.37521 | 0.0015389 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0012893 | 0.54092 | 0.0046217 | 0.45294 | 0.0032709
450.4 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.40347 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.16505 | 0.0080692
450.6 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.68971 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
450.8 | 129.9061 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
451 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
451.2 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.017929 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
451.4 | 129.9061 | 0.0040291 | 0.66314 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0038295 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0080692
451.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.010886 | 0.54092 | 0.0046217 | 0.45294 | 0.0032709
451.8 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | -0.0012672 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
452 | 129.9061 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.0016822 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | -0.0019091 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
452.2 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.7654 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0076874 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
452.4 | 129.8101 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
452.6 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
452.8 | 129.9061 | 0.0056289 | 0.087319 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
453 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
453.2 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.012868
453.4 | 129.9061 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
453.6 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
453.8 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.11392 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
454 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0080692
454.2 | 129.8101 | 0.0072281 | 0.37521 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.261 | 0.011268
454.4 | 129.7141 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.49776 | 0.010886 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
454.6 | 129.8101 | 0.015225 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.015026 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 0.0048708
454.8 | 129.8101 | 0.0056289 | 0.37521 | 0.0031381 | 0.28557 | -0.0015162 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0076874 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
455 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.015026 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
455.2 | 130.002 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.0096794 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.78566 | 0.010886 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
455.4 | 129.9061 | 0.0040291 | 0.18331 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.019589 | 0.0086283 | 0.20987 | 0.0060882 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
455.6 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
455.8 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0028664 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
456 | 129.9061 | 0.0024299 | 0.27926 | 0.0031381 | 0.66945 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
456.2 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
456.4 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
456.6 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.66945 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
456.8 | 129.8101 | 0.0024299 | 0.37521 | 0.0031381 | 0.38156 | 0.0080803 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
457 | 129.9061 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
457.2 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
457.4 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.17102 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.261 | 0.0048708
457.6 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
457.8 | 129.9061 | 0.0024299 | 0.27926 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.68971 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
458 | 130.002 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
458.2 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
458.4 | 130.002 | 0.0024299 | 0.4712 | -0.0032593 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.59375 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
458.6 | 129.9061 | 0.0024299 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | -0.12288 | 0.0032709
458.8 | 129.8101 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
459 | 129.7141 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
459.2 | 129.7141 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.075065 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
459.4 | 129.9061 | 0.0024299 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
459.6 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.63692 | 0.0030219 | 0.35695 | 0.0048708
459.8 | 129.9061 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
460 | 130.002 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.0016822 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.012486 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
460.2 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0078201 | 0.069058 | 0.0048708
460.4 | 129.9061 | 0.00083003 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
460.6 | 129.8101 | 0.0040291 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
460.8 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0096794 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | -0.0035089 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
461 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
461.2 | 129.9061 | 0.0056289 | 0.27926 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
461.4 | 129.9061 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | -0.17401 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
461.6 | 130.002 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.06109 | 0.0046217 | 0.35695 | 0.0048708
461.8 | 130.2899 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | -0.0028664 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0094199 | 0.45294 | 0.0048708
462 | 130.002 | 0.0024299 | -0.0086323 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0038295 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
462.2 | 129.9061 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.261 | 0.0048708
462.4 | 130.002 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | -0.0015162 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.25303 | 0.0046217 | 0.35695 | 0.0048708
462.6 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.17102 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | -0.00017715 | 0.35695 | 0.0048708
462.8 | 130.002 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | -0.00017715 | 0.54889 | 0.0032709
463 | 129.9061 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.015026 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
463.2 | 129.9061 | 0.0040291 | 0.27926 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.20987 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
463.4 | 130.002 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | -0.0060654 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
463.6 | 130.002 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.012619 | 0.35695 | 0.0048708
463.8 | 129.9061 | -0.00076916 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.26697 | -0.0044662 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
464 | 130.098 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
464.2 | 129.8101 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.0080803 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
464.4 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
464.6 | 130.002 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
464.8 | 129.9061 | 0.0040291 | 0.4712 | -0.0016601 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
465 | 129.9061 | 0.00083003 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.54889 | 0.0048708
465.2 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
465.4 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.45294 | 0.0032709
465.6 | 129.7141 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
465.8 | 129.7141 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.15708 | 0.0046217 | 0.35695 | 0.0048708
466 | 129.9061 | 0.00083003 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
466.2 | 129.9061 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.59537 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
466.4 | 129.9061 | 0.0040291 | 0.66314 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.013427 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
466.6 | 129.9061 | 0.0040291 | 0.27926 | 0.0063372 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
466.8 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | -0.00030988 | 0.34898 | 0.0046217 | 0.45294 | 0.0048708
467 | 129.9061 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.49942 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0080692
467.2 | 129.9061 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.59375 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
467.4 | 129.9061 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
467.6 | 129.9061 | 0.0024299 | 0.27926 | 0.004738 | 0.66945 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
467.8 | 129.9061 | 0.0024299 | 0.37521 | 0.0031381 | 0.66945 | -0.003116 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
468 | 129.8101 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.26697 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
468.2 | 129.9061 | 0.0024299 | 0.4712 | 0.004738 | 0.28557 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
468.4 | 129.8101 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
468.6 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.78566 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
468.8 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
469 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0080692
469.2 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
469.4 | 130.002 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.5549 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | -0.00017715 | 0.35695 | 0.0048708
469.6 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.16505 | 0.0032709
469.8 | 129.9061 | 0.0024299 | 0.27926 | 0.004738 | 0.5735 | 0.0016822 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | -0.0019091 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
470 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.59375 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
470.2 | 130.002 | 0.0040291 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
470.4 | 129.9061 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
470.6 | 129.8101 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | -0.00017715 | 0.35695 | 0.0032709
470.8 | 129.9061 | 0.0040291 | 0.37521 | 0.0015389 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.11554 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
471 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0078201 | 0.069058 | 0.0048708
471.2 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
471.4 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.25303 | 0.0062209 | 0.35695 | 0.0048708
471.6 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0067301 | 0.21153 | 0.0070285 | 0.40181 | 0.0060882 | 0.34898 | 0.0046217 | 0.45294 | 0.0048708
471.8 | 130.002 | 0.0024299 | 0.27926 | -6.0896e-05 | 0.86139 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.49776 | 0.0028892 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
472 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
472.2 | 129.8101 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
472.4 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
472.6 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0016718
472.8 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
473 | 129.8101 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0016718
473.2 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | -0.026893 | 0.0048708
473.4 | 129.8101 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | 0.0067301 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
473.6 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | -0.034861 | 0.0046217 | 0.35695 | 0.0048708
473.8 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0016822 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.010886 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
474 | 130.002 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
474.2 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
474.4 | 129.8101 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
474.6 | 129.8101 | 0.0024299 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
474.8 | 129.9061 | 0.0024299 | 0.27926 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
475 | 129.9061 | 0.0040291 | -0.0086323 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.00033201 | 0.40347 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
475.2 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.73287 | 0.0046217 | 0.35695 | 0.0048708
475.4 | 129.8101 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
475.6 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.92481 | 0.0062209 | 0.35695 | 0.0048708
475.8 | 130.002 | 0.0024299 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0078201 | 0.35695 | 0.0032709
476 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.18962 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
476.2 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.36296 | 0.00033201 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
476.4 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
476.6 | 130.002 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.013427 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
476.8 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0054293 | 0.88165 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
477 | 129.8101 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.88165 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
477.2 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
477.4 | 129.8101 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0080692
477.6 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
477.8 | 129.8101 | 0.0040291 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
478 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0014227 | 0.35695 | 0.0048708
478.2 | 129.8101 | 0.0040291 | 0.37521 | 0.0015389 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.013427 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
478.4 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
478.6 | 129.8101 | 0.0040291 | 0.37521 | 0.0095362 | 0.66945 | 0.0048812 | 0.36296 | 0.003531 | 0.21153 | 0.013427 | 0.40181 | 0.0092866 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
478.8 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
479 | 129.7141 | 0.016825 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0014227 | 0.45294 | 0.00647
479.2 | 129.7141 | 0.012026 | 0.37521 | 0.004738 | 0.18962 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.20987 | 0.0092866 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
479.4 | 129.7141 | 0.0072281 | 0.56715 | -0.0032593 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.013427 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
479.6 | 129.8101 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.34898 | 0.0078201 | 0.35695 | 0.0048708
479.8 | 129.8101 | 0.0072281 | 0.56715 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
480 | 129.8101 | 0.0072281 | 0.4712 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0054293 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.261 | 0.00647
480.2 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
480.4 | 129.8101 | -0.00076916 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.74084 | 0.0048708
480.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0080692
480.8 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
481 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.16505 | 0.0048708
481.2 | 129.7141 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
481.4 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
481.6 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
481.8 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0016718
482 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0032709
482.2 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.00063108 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
482.4 | 129.8101 | 0.0040291 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
482.6 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
482.8 | 129.8101 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
483 | 129.9061 | 0.0040291 | 0.087319 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
483.2 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
483.4 | 129.8101 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | -0.026893 | 0.0048708
483.6 | 129.8101 | 0.0040291 | 0.37521 | 0.0031381 | 0.5735 | 0.0016822 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
483.8 | 129.7141 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | -0.0060654 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
484 | 129.9061 | 0.0040291 | 0.27926 | 0.0031381 | 0.7654 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
484.2 | 129.8101 | 0.0040291 | 0.087319 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.00033201 | -0.076363 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0016718
484.4 | 129.8101 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.019589 | 0.015026 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | -0.0015273
484.6 | 129.8101 | 0.0040291 | 0.27926 | 0.004738 | 0.5735 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
484.8 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0038295 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
485 | 129.9061 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.0064811 | 0.7468 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
485.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | -0.0012672 | 0.59537 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
485.4 | 130.002 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.261 | 0.0032709
485.6 | 129.9061 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.017929 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
485.8 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0054293 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
486 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
486.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
486.4 | 129.9061 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.16505 | 0.011268
486.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0067301 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
486.8 | 129.9061 | -0.00076916 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.019589 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
487 | 129.9061 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
487.2 | 129.9061 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | -0.12288 | 0.0048708
487.4 | 129.9061 | 0.0056289 | 0.37521 | 0.0015389 | -0.002325 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0012893 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
487.6 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | -0.0028664 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
487.8 | 130.002 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | -0.0033755 | 0.35695 | 0.0048708
488 | 130.002 | 0.0056289 | 0.27926 | 0.0015389 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.20987 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
488.2 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
488.4 | 129.9061 | 0.0072281 | 0.27926 | -6.0896e-05 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0080692
488.6 | 129.9061 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.009669
488.8 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0067301 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
489 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.82882 | 0.0062209 | 0.35695 | 0.0048708
489.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.28557 | 0.0064811 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
489.4 | 129.9061 | 0.00083003 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.16505 | 0.0048708
489.6 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | -0.0060654 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
489.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.35695 | 0.0032709
490 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
490.2 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
490.4 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
490.6 | 129.7141 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.65085 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0094199 | 0.35695 | 0.0048708
490.8 | 129.8101 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.16505 | 0.012868
491 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
491.2 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.86139 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
491.4 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.92481 | 0.0046217 | 0.35695 | 0.0048708
491.6 | 130.002 | 0.013626 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.069058 | 0.0048708
491.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.15708 | 0.0046217 | 0.35695 | 0.0048708
492 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.63692 | 0.0062209 | 0.35695 | 0.0048708
492.2 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
492.4 | 130.002 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
492.6 | 130.002 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
492.8 | 129.9061 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.06109 | 0.0046217 | 0.35695 | 0.0032709
493 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.7654 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | -0.00030988 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
493.2 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | -0.003116 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0032709
493.4 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
493.6 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | -0.003116 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0030219 | 0.35695 | 0.0032709
493.8 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.00647
494 | 130.098 | 0.0072281 | 0.4712 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
494.2 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.54092 | 0.0030219 | 0.45294 | 0.0016718
494.4 | 130.002 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.06109 | 0.0046217 | 0.261 | 0.0048708
494.6 | 130.098 | 0.0056289 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
494.8 | 130.3859 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
495 | 130.002 | 0.0072281 | 0.4712 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
495.2 | 130.098 | 0.0072281 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
495.4 | 130.194 | 0.00083003 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.16505 | 0.0048708
495.6 | 130.002 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0012893 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
495.8 | 130.002 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0092866 | 0.54092 | 0.0046217 | 0.45294 | 0.0032709
496 | 130.098 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
496.2 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0012893 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
496.4 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.82882 | 0.0046217 | 0.35695 | 0.0048708
496.6 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
496.8 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0012893 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
497 | 130.002 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
497.2 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.20987 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
497.4 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.65085 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
497.6 | 130.098 | 0.013626 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
497.8 | 130.098 | 0.0072281 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
498 | 130.098 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0096794 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
498.2 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | -0.0012672 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
498.4 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
498.6 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 0.0048708
498.8 | 130.098 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.45294 | 0.0048708
499 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
499.2 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | -0.026893 | 0.0032709
499.4 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0016822 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
499.6 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0076874 | 0.34898 | 0.0046217 | 0.45294 | 0.0048708
499.8 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.06109 | 0.0046217 | 0.35695 | 0.0048708
500 | 130.098 | 0.0088273 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.019589 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0080692
500.2 | 130.194 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.261 | 0.0032709
500.4 | 130.194 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
500.6 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
500.8 | 130.098 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0012893 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
501 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.59537 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
501.2 | 130.098 | 0.0088273 | 0.27926 | 0.004738 | 0.38156 | 0.0064811 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.73287 | 0.0046217 | 0.35695 | 0.00647
501.4 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.54889 | 0.0048708
501.6 | 130.098 | 0.010427 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
501.8 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.26697 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
502 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.7654 | 8.3003e-05 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.49776 | 0.010886 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
502.2 | 130.2899 | 0.0088273 | 0.27926 | 0.004738 | 0.7654 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.012486 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
502.4 | 130.3859 | 0.0088273 | 0.4712 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | -0.0028664 | 0.21153 | 0.013427 | 0.40181 | 0.018884 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
502.6 | 130.194 | 0.015225 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.018225 | 0.49776 | 0.015685 | 0.34898 | 0.0046217 | 0.261 | 0.0048708
502.8 | 129.9061 | 0.029621 | 0.37521 | 0.0015389 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.021424 | 0.49776 | 0.015685 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
503 | 130.098 | 0.048814 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | -0.0044662 | 0.30748 | 0.015026 | 0.40181 | 0.010886 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
503.2 | 130.194 | 0.044015 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0067301 | 0.40347 | 0.016626 | 0.49776 | 0.010886 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
503.4 | 130.194 | 0.034419 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.013427 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.35695 | 0.0080692
503.6 | 130.098 | 0.024822 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.20987 | 0.010886 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
503.8 | 130.002 | 0.020024 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.013427 | 0.40181 | 0.010886 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
504 | 130.002 | 0.016825 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.013427 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
504.2 | 130.194 | 0.018424 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.013427 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
504.4 | 130.2899 | 0.018424 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.30582 | 0.0092866 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
504.6 | 130.194 | 0.020024 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.49776 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
504.8 | 130.194 | 0.015225 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
505 | 130.002 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
505.2 | 130.098 | 0.012026 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
505.4 | 130.194 | 0.013626 | 0.27926 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.013427 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
505.6 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.11554 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
505.8 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.49942 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
506 | 130.194 | 0.010427 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | -0.076363 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
506.2 | 130.2899 | 0.010427 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | -0.0012672 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | -0.0033755 | 0.35695 | 0.0048708
506.4 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
506.6 | 130.098 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
506.8 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
507 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
507.2 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
507.4 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 8.3003e-05 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
507.6 | 130.098 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
507.8 | 130.2899 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.20987 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
508 | 130.194 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.011827 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
508.2 | 130.194 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
508.4 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
508.6 | 130.194 | 0.0088273 | 0.27926 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
508.8 | 130.194 | 0.010427 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
509 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
509.2 | 130.2899 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
509.4 | 130.2899 | 0.0088273 | 0.37521 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0054293 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
509.6 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.16505 | 0.0048708
509.8 | 130.194 | 0.0088273 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
510 | 130.194 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0054293 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | -0.0015273
510.2 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
510.4 | 130.194 | 0.0088273 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0016718
510.6 | 130.3859 | 0.0072281 | 0.18331 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
510.8 | 130.194 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
511 | 130.194 | 0.0088273 | 0.37521 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
511.2 | 130.2899 | 0.0088273 | 0.087319 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0038295 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0080692
511.4 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.28557 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
511.6 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
511.8 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.28557 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
512 | 130.194 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0054293 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
512.2 | 130.194 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
512.4 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
512.6 | 130.3859 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
512.8 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.49776 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
513 | 130.3859 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.00033201 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
513.2 | 130.194 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0094199 | 0.35695 | 0.00647
513.4 | 130.4819 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.82882 | 0.0046217 | 0.45294 | 0.0048708
513.6 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
513.8 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0080803 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
514 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.16505 | 0.0048708
514.2 | 130.2899 | 0.0088273 | 0.27926 | 0.0031381 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
514.4 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
514.6 | 130.3859 | 0.010427 | 0.37521 | -6.0896e-05 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
514.8 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.68971 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
515 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
515.2 | 130.2899 | 0.010427 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0038295 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
515.4 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0076874 | 0.06109 | 0.0062209 | 0.45294 | 0.0048708
515.6 | 130.3859 | 0.010427 | 0.4712 | -0.0016601 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
515.8 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
516 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
516.2 | 130.3859 | 0.010427 | 0.37521 | 0.0015389 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.010228 | 0.017929 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
516.4 | 130.2899 | 0.015225 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
516.6 | 130.2899 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.64488 | 0.0048708
516.8 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 0.0048708
517 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
517.2 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
517.4 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.261 | 0.0048708
517.6 | 130.2899 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.49942 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.64488 | 0.00647
517.8 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.28557 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.017929 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
518 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.49776 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
518.2 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | -0.0012672 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
518.4 | 130.2899 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
518.6 | 130.2899 | 0.010427 | 0.27926 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
518.8 | 130.5779 | 0.010427 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.5549 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
519 | 130.4819 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.003282 | 0.65085 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0014227 | 0.35695 | 0.0048708
519.2 | 129.9061 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
519.4 | 130.194 | 0.012026 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
519.6 | 130.098 | 0.013626 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.261 | 0.0048708
519.8 | 130.098 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
520 | 129.4263 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
520.2 | 130.194 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | -0.0028664 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
520.4 | 130.2899 | 0.010427 | 0.37521 | 0.0015389 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0012893 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
520.6 | 130.2899 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.261 | 0.0048708
520.8 | 130.098 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
521 | 130.194 | 0.012026 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.54889 | 0.0032709
521.2 | 130.098 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.5549 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.261 | 0.0048708
521.4 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.49942 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.54889 | 0.0032709
521.6 | 130.3859 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.59537 | 0.0086283 | 0.30582 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
521.8 | 130.2899 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
522 | 130.2899 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0083293 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0078201 | 0.261 | 0.0048708
522.2 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0067301 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
522.4 | 130.002 | 0.010427 | 0.27926 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
522.6 | 130.194 | 0.034419 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.261 | 0.0048708
522.8 | 130.4819 | 0.013626 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.003531 | 0.30748 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
523 | 130.194 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.015026 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
523.2 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.20987 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
523.4 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
523.6 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
523.8 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
524 | 130.002 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0014227 | 0.45294 | 0.0048708
524.2 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.010886 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
524.4 | 129.9061 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0078201 | 0.45294 | 0.0048708
524.6 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
524.8 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.73287 | 0.0046217 | 0.35695 | 0.0048708
525 | 130.194 | 0.0088273 | 0.37521 | -6.0896e-05 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
525.2 | 130.098 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
525.4 | 130.002 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.11554 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
525.6 | 130.002 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
525.8 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.92481 | 0.0046217 | 0.35695 | 0.0048708
526 | 130.002 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0096794 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.25303 | 0.0046217 | 0.35695 | 0.0048708
526.2 | 130.002 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
526.4 | 130.002 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
526.6 | 130.194 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
526.8 | 130.002 | 0.0088273 | 0.37521 | -0.0016601 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
527 | 130.002 | 0.0088273 | 0.27926 | 0.0015389 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.015026 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 0.00647
527.2 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.28557 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
527.4 | 130.002 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.11392 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
527.6 | 129.9061 | 0.0072281 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
527.8 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0078201 | 0.45294 | 0.0048708
528 | 129.9061 | 0.0072281 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
528.2 | 129.8101 | 0.00083003 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 0.0048708
528.4 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
528.6 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0012893 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
528.8 | 129.9061 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
529 | 129.9061 | 0.0040291 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
529.2 | 130.002 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.009669
529.4 | 129.9061 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
529.6 | 129.9061 | 0.0056289 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
529.8 | 130.098 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0014227 | 0.35695 | 0.0048708
530 | 129.8101 | 0.00083003 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
530.2 | 129.9061 | 0.0056289 | 0.37521 | 0.0031381 | 0.86139 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.017929 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
530.4 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.16505 | 0.0048708
530.6 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0016822 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
530.8 | 129.8101 | 0.0072281 | 0.27926 | -0.017655 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.013427 | 0.30582 | 0.0092866 | 0.54092 | 0.0046217 | 0.45294 | 0.0032709
531 | 129.7141 | 0.0056289 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
531.2 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
531.4 | 129.8101 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0096794 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
531.6 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.18962 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
531.8 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0067301 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.0048708
532 | 129.9061 | 0.0072281 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
532.2 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
532.4 | 129.7141 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
532.6 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
532.8 | 130.194 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0080803 | 0.075065 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
533 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.34898 | 0.0078201 | 0.35695 | 0.0048708
533.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | -0.0035089 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
533.4 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
533.6 | 129.8101 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
533.8 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | -0.003116 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
534 | 129.9061 | 0.0056289 | 0.18331 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.64488 | 0.0048708
534.2 | 130.002 | 0.00083003 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | -0.0044662 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
534.4 | 129.8101 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
534.6 | 129.9061 | 0.0040291 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
534.8 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
535 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.35695 | 0.00647
535.2 | 129.8101 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0054293 | 0.40181 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.009669
535.4 | 129.8101 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
535.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.18962 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
535.8 | 129.9061 | 0.0040291 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
536 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
536.2 | 129.9061 | 0.0056289 | -0.0086323 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
536.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
536.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
536.8 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
537 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0016718
537.2 | 130.002 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
537.4 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
537.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.35695 | 0.0048708
537.8 | 130.002 | 0.0024299 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.35695 | 0.00647
538 | 130.098 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.013427 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
538.2 | 130.098 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
538.4 | 130.2899 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
538.6 | 130.098 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.20987 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
538.8 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.261 | 0.00647
539 | 130.194 | 0.0040291 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
539.2 | 130.194 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
539.4 | 130.002 | 0.0024299 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
539.6 | 130.098 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.64488 | 0.00647
539.8 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.00647
540 | 130.194 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.261 | 0.00647
540.2 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.0048708
540.4 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.54889 | 0.0048708
540.6 | 130.194 | 0.0072281 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.0048708
540.8 | 130.194 | 0.0024299 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 7.1911e-05
541 | 130.194 | 0.0040291 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.64488 | 0.00647
541.2 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
541.4 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.25303 | 0.0046217 | 0.35695 | 0.0048708
541.6 | 130.194 | 0.0040291 | 0.27926 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
541.8 | 130.194 | 0.00083003 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0078201 | 0.35695 | 0.0048708
542 | 130.194 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
542.2 | 130.194 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
542.4 | 130.194 | 0.0024299 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
542.6 | 130.2899 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
542.8 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.7468 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
543 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
543.2 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.65085 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.0048708
543.4 | 130.194 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.92481 | 0.0046217 | 0.45294 | 0.00647
543.6 | 130.194 | 0.0024299 | 0.087319 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
543.8 | 130.194 | 0.0040291 | 0.4712 | 0.004738 | 1.917 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.024623 | 0.49776 | 0.010886 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
544 | 130.194 | 0.0040291 | 0.27926 | -0.019254 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.015026 | 0.68971 | 0.010886 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
544.2 | 129.7141 | 0.0040291 | 0.66314 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.017284 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
544.4 | 130.002 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.019824 | 0.49776 | 0.012486 | 0.34898 | 0.0014227 | 0.45294 | 0.00647
544.6 | 130.2899 | 0.03282 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.015026 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
544.8 | 130.2899 | 0.03282 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.011827 | 0.49776 | 0.0092866 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
545 | 130.194 | 0.018424 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.013427 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
545.2 | 130.2899 | 0.018424 | 0.37521 | 0.0063372 | 0.28557 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
545.4 | 130.3859 | 0.016825 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
545.6 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
545.8 | 130.2899 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.11554 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.16505 | 0.0032709
546 | 130.2899 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.0048708
546.2 | 130.2899 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0030219 | 0.45294 | 0.0048708
546.4 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
546.6 | 130.2899 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
546.8 | 130.2899 | 0.0040291 | 0.66314 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | -0.076363 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.0048708
547 | 130.4819 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0078201 | 0.35695 | 0.0048708
547.2 | 130.2899 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
547.4 | 130.3859 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0054293 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.54889 | -0.0015273
547.6 | 130.2899 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
547.8 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.28557 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
548 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.45294 | 0.00647
548.2 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.49776 | -0.00030988 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
548.4 | 130.3859 | 0.0040291 | 0.27926 | 0.004738 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.63692 | 0.0046217 | 0.45294 | 0.0048708
548.6 | 130.2899 | 0.0040291 | 0.18331 | 0.004738 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
548.8 | 130.3859 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
549 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
549.2 | 130.3859 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
549.4 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0080803 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
549.6 | 130.3859 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0016718
549.8 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0096794 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.45294 | 0.0048708
550 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0080803 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
550.2 | 130.4819 | -0.00076916 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
550.4 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.28557 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
550.6 | 130.3859 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0032709
550.8 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.017929 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
551 | 130.3859 | 0.00083003 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
551.2 | 130.4819 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
551.4 | 130.3859 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0046217 | 0.45294 | 0.0048708
551.6 | 130.3859 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
551.8 | 130.4819 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
552 | 130.3859 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.64488 | 0.0032709
552.2 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
552.4 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
552.6 | 130.3859 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
552.8 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
553 | 130.3859 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | -0.076363 | 0.0070285 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
553.2 | 130.3859 | 0.0040291 | 0.27926 | 0.004738 | 0.28557 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
553.4 | 130.3859 | 0.0040291 | 0.4712 | 0.0095362 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0038295 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
553.6 | 130.2899 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
553.8 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
554 | 130.3859 | 0.0040291 | 0.37521 | 0.0063372 | 0.28557 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
554.2 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | -0.0019091 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
554.4 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
554.6 | 130.3859 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
554.8 | 130.3859 | 0.0040291 | 0.37521 | 0.0015389 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.261 | -0.0015273
555 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
555.2 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.0048708
555.4 | 130.3859 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0038295 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
555.6 | 130.3859 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
555.8 | 130.2899 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.92481 | 0.0062209 | 0.35695 | 0.0048708
556 | 130.6738 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.075065 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
556.2 | 130.4819 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.25303 | 0.0046217 | 0.35695 | 0.0032709
556.4 | 130.4819 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
556.6 | 130.4819 | 0.0040291 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.26697 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.73287 | 0.0046217 | 0.45294 | 0.0048708
556.8 | 130.3859 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
557 | 130.4819 | 0.0040291 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
557.2 | 130.4819 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
557.4 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | -0.0012672 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.069058 | 0.0048708
557.6 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | -0.00030988 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
557.8 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
558 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0016718
558.2 | 130.3859 | 0.0040291 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
558.4 | 130.3859 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0016718
558.6 | 130.3859 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
558.8 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.28557 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
559 | 130.3859 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.011019 | 0.35695 | 0.0032709
559.2 | 130.3859 | 0.0040291 | 0.27926 | 0.0063372 | 0.18962 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
559.4 | 130.3859 | 0.0040291 | 0.37521 | 0.0095362 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.11392 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
559.6 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
559.8 | 130.3859 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.64488 | 0.0032709
560 | 130.4819 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0014227 | 0.35695 | 0.0048708
560.2 | 130.3859 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
560.4 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0032709
560.6 | 130.3859 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
560.8 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
561 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.68971 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
561.2 | 130.3859 | 0.0040291 | 0.4712 | -0.0016601 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
561.4 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.73287 | 0.0046217 | 0.35695 | 0.0048708
561.6 | 130.3859 | 0.0024299 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.35695 | 0.00647
561.8 | 130.3859 | 0.0024299 | 0.27926 | 0.0063372 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
562 | 130.3859 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.261 | 0.0048708
562.2 | 130.3859 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
562.4 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0054293 | 0.68971 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
562.6 | 130.3859 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
562.8 | 130.4819 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.5549 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0014227 | 0.45294 | 0.0048708
563 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
563.2 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0012893 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
563.4 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.59537 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 7.1911e-05
563.6 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
563.8 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.011019 | 0.35695 | 0.0048708
564 | 130.3859 | 0.0040291 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.49942 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 7.1911e-05
564.2 | 130.2899 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
564.4 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
564.6 | 130.3859 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | -0.0017763 | 0.35695 | 0.0048708
564.8 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
565 | 130.2899 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0054293 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.261 | 0.00647
565.2 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
565.4 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.63692 | 0.0046217 | 0.45294 | 0.0048708
565.6 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.00033201 | -0.076363 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
565.8 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.06109 | 0.0062209 | 0.35695 | 0.0048708
566 | 130.4819 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.7468 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0014227 | 0.35695 | 0.0048708
566.2 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
566.4 | 130.3859 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.65085 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
566.6 | 130.4819 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
566.8 | 130.4819 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
567 | 130.3859 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
567.2 | 130.3859 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
567.4 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
567.6 | 130.2899 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
567.8 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0080803 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
568 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.0048708
568.2 | 130.2899 | 0.0040291 | 0.37521 | 0.0015389 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
568.4 | 130.2899 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.0048708
568.6 | 130.2899 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
568.8 | 130.2899 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 0.00647
569 | 130.2899 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
569.2 | 130.2899 | 0.016825 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.45294 | 0.0048708
569.4 | 130.2899 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
569.6 | 130.2899 | 0.028021 | 0.27926 | 0.004738 | 0.47751 | 0.0016822 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0092866 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
569.8 | 130.194 | 0.018424 | 0.37521 | 0.0031381 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.018225 | 0.59375 | 0.010886 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
570 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.018884 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
570.2 | 130.194 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.015026 | 0.40181 | 0.0092866 | 0.54092 | 0.0046217 | 0.35695 | -0.0015273
570.4 | 130.194 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0051309 | 0.21153 | 0.0086283 | 0.49776 | 0.014085 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
570.6 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
570.8 | 130.194 | 0.0040291 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | -1.9462 | 0.0032709
571 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
571.2 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
571.4 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.7468 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
571.6 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
571.8 | 130.194 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.0048708
572 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0014227 | 0.45294 | 0.00647
572.2 | 130.194 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
572.4 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
572.6 | 130.098 | 0.0040291 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
572.8 | 130.194 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.0080803 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
573 | 130.194 | 0.0040291 | 0.37521 | 0.0031381 | 0.66945 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
573.2 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | -0.076363 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0080692
573.4 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
573.6 | 130.2899 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
573.8 | 130.002 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | -0.0012672 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.011019 | 0.45294 | 0.0048708
574 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.0048708
574.2 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
574.4 | 130.098 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
574.6 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0096794 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.25303 | 0.0046217 | 0.45294 | 0.0048708
574.8 | 130.098 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
575 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0051309 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.35695 | 0.0048708
575.2 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.82882 | 0.0046217 | 0.35695 | 0.0048708
575.4 | 130.098 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
575.6 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.74084 | 0.0048708
575.8 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0092866 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
576 | 130.002 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
576.2 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
576.4 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.00647
576.6 | 130.098 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
576.8 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.7468 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0092866 | 0.15708 | 0.0062209 | 0.45294 | 0.00647
577 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
577.2 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.0048708
577.4 | 130.002 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.20987 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
577.6 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | -0.0033755 | 0.35695 | 0.0048708
577.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
578 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0028892 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
578.2 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.49942 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.54889 | 0.0048708
578.4 | 129.9061 | 0.0056289 | 0.37521 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
578.6 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
578.8 | 130.002 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0022303 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
579 | 129.7141 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | -0.00017715 | 0.45294 | 0.0048708
579.2 | 130.002 | 0.012026 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.35695 | 0.0048708
579.4 | 130.002 | 0.013626 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
579.6 | 130.098 | 0.0024299 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.17102 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.82882 | 0.0062209 | 0.35695 | 0.0048708
579.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.78566 | 0.012486 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
580 | 129.9061 | 0.0056289 | 0.37521 | -6.0896e-05 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
580.2 | 130.002 | 0.0056289 | 0.66314 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
580.4 | 130.002 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.00647
580.6 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
580.8 | 130.002 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
581 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
581.2 | 129.7141 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.34898 | 0.0062209 | 0.45294 | 0.0048708
581.4 | 130.002 | 0.0072281 | 0.37521 | 0.0031381 | 0.86139 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
581.6 | 130.098 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.11554 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.83679 | 0.0048708
581.8 | 130.002 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.65085 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
582 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
582.2 | 129.8101 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0080803 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
582.4 | 129.8101 | 0.0088273 | 0.37521 | 0.004738 | 0.5735 | 0.011279 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.73287 | 0.0046217 | 0.35695 | 0.0048708
582.6 | 129.7141 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.65085 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
582.8 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
583 | 129.9061 | 0.0072281 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
583.2 | 130.002 | 0.0088273 | 0.37521 | 0.0095362 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
583.4 | 130.098 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
583.6 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.16505 | 0.0048708
583.8 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
584 | 130.194 | 0.010427 | 0.37521 | 0.0063372 | 0.28557 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0028892 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
584.2 | 130.194 | 0.010427 | 0.56715 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
584.4 | 130.098 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
584.6 | 130.194 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
584.8 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.73287 | 0.0046217 | 0.45294 | 0.0048708
585 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.25303 | 0.0062209 | 0.35695 | 0.0048708
585.2 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.68971 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
585.4 | 130.194 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.012868
585.6 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.25303 | 0.0062209 | 0.45294 | 0.0048708
585.8 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
586 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0028892 | -0.034861 | 0.0046217 | 0.35695 | 0.0048708
586.2 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.45294 | 0.0048708
586.4 | 130.2899 | 0.0088273 | 0.66314 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
586.6 | 130.2899 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
586.8 | 130.2899 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
587 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
587.2 | 130.2899 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.21153 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
587.4 | 130.2899 | 0.015225 | 0.37521 | 0.0015389 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
587.6 | 130.194 | 0.015225 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.11554 | 0.010228 | 0.30582 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
587.8 | 130.2899 | 0.03282 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
588 | 130.3859 | 0.010427 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
588.2 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0076874 | 0.34898 | 0.0046217 | 0.35695 | 0.00647
588.4 | 130.3859 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | -0.13085 | 0.0046217 | 0.35695 | 0.0032709
588.6 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
588.8 | 130.3859 | 0.012026 | 0.37521 | 0.0031381 | 0.47751 | -0.0015162 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
589 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
589.2 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | -0.034861 | 0.0046217 | 0.35695 | 0.00647
589.4 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
589.6 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
589.8 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0096794 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
590 | 130.3859 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.65085 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.06109 | 0.0046217 | 0.35695 | 0.0048708
590.2 | 130.194 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
590.4 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
590.6 | 129.8101 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.00647
590.8 | 130.2899 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
591 | 130.194 | 0.010427 | 0.18331 | 0.0079364 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.49942 | 0.0022303 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
591.2 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.35695 | 0.0048708
591.4 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
591.6 | 130.3859 | 0.013626 | -0.10462 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
591.8 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
592 | 130.4819 | 0.010427 | 0.37521 | 0.004738 | 0.28557 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.20987 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
592.2 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
592.4 | 130.2899 | 0.015225 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.64488 | 0.00647
592.6 | 130.4819 | 0.010427 | 0.18331 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0016718
592.8 | 130.3859 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
593 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0096794 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
593.2 | 130.4819 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
593.4 | 130.4819 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
593.6 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
593.8 | 130.3859 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
594 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
594.2 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
594.4 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.59375 | 0.0012893 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
594.6 | 130.3859 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
594.8 | 130.3859 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
595 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
595.2 | 130.3859 | 0.010427 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0022303 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
595.4 | 130.3859 | 0.010427 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
595.6 | 130.3859 | 0.0088273 | 0.37521 | 0.0079364 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
595.8 | 130.2899 | 0.0088273 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.0048708
596 | 130.3859 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
596.2 | 130.3859 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.64488 | 0.0048708
596.4 | 130.2899 | 0.010427 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0080692
596.6 | 130.3859 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0078201 | 0.45294 | 0.0048708
596.8 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
597 | 130.3859 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
597.2 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.28557 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.010886 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
597.4 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | -0.0019091 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
597.6 | 130.3859 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
597.8 | 130.194 | 0.013626 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
598 | 130.2899 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.74084 | 0.00647
598.2 | 130.5779 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | -0.0012672 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0094199 | 0.35695 | 0.0048708
598.4 | 130.2899 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
598.6 | 130.3859 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 0.0016718
598.8 | 130.2899 | 0.013626 | 0.27926 | 0.004738 | 0.47751 | 0.0080803 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
599 | 130.2899 | 0.013626 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
599.2 | 130.2899 | 0.018424 | 0.37521 | 0.004738 | 0.5735 | 8.3003e-05 | 0.45891 | 0.0019319 | 0.40347 | 0.013427 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
599.4 | 130.002 | 0.020024 | 0.37521 | 0.0063372 | 0.28557 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
599.6 | 130.194 | 0.047214 | 0.18331 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.019824 | 0.40181 | 0.014085 | 0.54092 | 0.0046217 | 0.45294 | 0.0032709
599.8 | 130.194 | 0.010427 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.013427 | 0.40181 | 0.0092866 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
600 | 130.194 | 0.010427 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.59537 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
600.2 | 130.194 | 0.0088273 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
600.4 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
600.6 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.26697 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
600.8 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | -0.0012672 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.16505 | 0.0048708
601 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
601.2 | 130.098 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
601.4 | 130.098 | 0.0088273 | 0.27926 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
601.6 | 130.194 | 0.0088273 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
601.8 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
602 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
602.2 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.59375 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
602.4 | 130.194 | 0.0072281 | -0.0086323 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
602.6 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.011019 | 0.45294 | 0.0048708
602.8 | 130.194 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
603 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0054293 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
603.2 | 130.098 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
603.4 | 130.2899 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.82882 | 0.0046217 | 0.35695 | 0.0048708
603.6 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
603.8 | 130.002 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.20987 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
604 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0096794 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
604.2 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
604.4 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.59537 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.45294 | 0.0016718
604.6 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
604.8 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
605 | 130.2899 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0014227 | 0.45294 | 0.0032709
605.2 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | -0.00017715 | 0.35695 | 0.0048708
605.4 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
605.6 | 130.002 | 0.0072281 | 0.4712 | 0.004738 | 0.28557 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0016718
605.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
606 | 130.002 | 0.0088273 | -0.0086323 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0032709
606.2 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
606.4 | 129.9061 | 0.0056289 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
606.6 | 130.002 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
606.8 | 130.002 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
607 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
607.2 | 130.002 | 0.0056289 | 0.37521 | -6.0896e-05 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
607.4 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | -0.0017763 | 0.35695 | 0.0048708
607.6 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.06109 | 0.0046217 | 0.35695 | 0.0048708
607.8 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | -0.0060654 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.64488 | 0.0048708
608 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.65085 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
608.2 | 130.002 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
608.4 | 130.2899 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0028664 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0094199 | 0.35695 | 0.0048708
608.6 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.06109 | 0.0046217 | 0.35695 | 0.00647
608.8 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.16505 | 0.00647
609 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.010886 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
609.2 | 130.002 | 0.0040291 | 0.27926 | 0.0063372 | 0.38156 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.0038295 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
609.4 | 130.002 | 0.0056289 | 0.4712 | -6.0896e-05 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
609.6 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.21153 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.0048708
609.8 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.06109 | 0.0062209 | 0.45294 | 0.0048708
610 | 130.002 | 0.0040291 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0062209 | 0.16505 | 0.0048708
610.2 | 130.002 | 0.0040291 | 0.37521 | 0.0031381 | 0.66945 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
610.4 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
610.6 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.017929 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
610.8 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
611 | 130.098 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
611.2 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
611.4 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
611.6 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 0.00647
611.8 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0076874 | 0.44497 | 0.0062209 | 0.261 | 0.0048708
612 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
612.2 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.69137 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0016718
612.4 | 130.002 | 0.0072281 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.016626 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
612.6 | 130.002 | 0.0072281 | 0.37521 | 0.0031381 | 0.093666 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
612.8 | 129.9061 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
613 | 129.8101 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.0092866 | 0.34898 | 0.0030219 | 0.35695 | 0.00647
613.2 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.015026 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
613.4 | 130.002 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.11554 | 0.015026 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
613.6 | 130.002 | 0.0040291 | 0.4712 | -0.0016601 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 1.6494 | 0.0044883 | 0.63692 | 0.0062209 | 0.35695 | 0.0048708
613.8 | 129.9061 | 0.0040291 | 0.37521 | 0.0079364 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0080692
614 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
614.2 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
614.4 | 130.002 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | -0.0044662 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.16505 | 0.0048708
614.6 | 130.002 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
614.8 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.011827 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
615 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.075065 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.35695 | 0.00647
615.2 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.069058 | 0.00647
615.4 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0067301 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
615.6 | 130.002 | 0.0040291 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
615.8 | 130.002 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
616 | 130.002 | 0.00083003 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
616.2 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0070285 | 0.49776 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
616.4 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
616.6 | 130.098 | 0.0056289 | -0.0086323 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
616.8 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0012893 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
617 | 130.194 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | -0.034861 | 0.0062209 | 0.45294 | 0.00647
617.2 | 130.002 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.35695 | 0.0048708
617.4 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | -0.020925 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
617.6 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0022303 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
617.8 | 130.002 | 0.0040291 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
618 | 130.002 | 0.0040291 | 0.56715 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.013427 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
618.2 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
618.4 | 130.098 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
618.6 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
618.8 | 130.098 | 0.0040291 | 0.27926 | -0.0016601 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
619 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0044883 | 0.25303 | 0.0046217 | 0.35695 | 0.0048708
619.2 | 130.098 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.49942 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0080692
619.4 | 130.098 | 0.0040291 | 0.37521 | 0.0015389 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.40347 | 0.015026 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0032709
619.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
619.8 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0028892 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
620 | 130.002 | 0.0040291 | 0.37521 | 0.011135 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.11392 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
620.2 | 130.002 | 0.0040291 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
620.4 | 129.9061 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
620.6 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0080803 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
620.8 | 130.002 | 0.00083003 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | -0.0028664 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.64488 | 0.0048708
621 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
621.2 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
621.4 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
621.6 | 130.098 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
621.8 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.5549 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0094199 | 0.35695 | 0.0048708
622 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
622.2 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
622.4 | 130.194 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
622.6 | 130.098 | 0.0040291 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 7.1911e-05
622.8 | 130.002 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
623 | 130.098 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
623.2 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
623.4 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.26697 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
623.6 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
623.8 | 130.002 | 0.0040291 | 0.37521 | 0.0031381 | 0.66945 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
624 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.093666 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
624.2 | 130.098 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
624.4 | 130.002 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.0048708
624.6 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.016626 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
624.8 | 130.002 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
625 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.0048708
625.2 | 130.002 | 0.0040291 | 0.66314 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
625.4 | 130.098 | 0.0040291 | 0.37521 | 0.0095362 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.017929 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
625.6 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.015026 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0080692
625.8 | 130.098 | 0.00083003 | 0.7591 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 7.1911e-05
626 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0051309 | 0.21153 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
626.2 | 130.098 | 0.0040291 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.013427 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
626.4 | 130.098 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
626.6 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | -0.076363 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
626.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
627 | 130.002 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
627.2 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
627.4 | 130.098 | 0.0040291 | 0.4712 | 0.011135 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.11392 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
627.6 | 130.002 | 0.0040291 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
627.8 | 130.002 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0067301 | -0.076363 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
628 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.075065 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
628.2 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0076874 | 0.25303 | 0.0046217 | 0.35695 | 0.00647
628.4 | 130.2899 | 0.0040291 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
628.6 | 130.194 | 0.0040291 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.69137 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
628.8 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
629 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.0048708
629.2 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.7468 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
629.4 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
629.6 | 130.098 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | -0.026893 | 0.0048708
629.8 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.261 | 0.00647
630 | 130.194 | 0.0040291 | 0.27926 | 0.011135 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.11392 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
630.2 | 130.098 | 0.0040291 | 0.56715 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
630.4 | 130.098 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
630.6 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0083293 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.16505 | 0.0048708
630.8 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.06109 | 0.0062209 | 0.35695 | 0.00647
631 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
631.2 | 130.2899 | 0.0040291 | 0.27926 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.35695 | 0.00647
631.4 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
631.6 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0062209 | 0.45294 | 0.0048708
631.8 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
632 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0076874 | 0.73287 | 0.0062209 | 0.35695 | 0.00647
632.2 | 130.098 | 0.0040291 | 0.27926 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
632.4 | 130.098 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
632.6 | 130.098 | 0.00083003 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
632.8 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
633 | 130.098 | 0.0040291 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.00647
633.2 | 130.002 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
633.4 | 130.098 | -0.0023683 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | -0.026893 | 0.00647
633.6 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
633.8 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0030219 | -0.026893 | 0.00647
634 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.65085 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
634.2 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.84279 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0078201 | 0.35695 | 0.0048708
634.4 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0016718
634.6 | 130.4819 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
634.8 | 130.194 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.69137 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
635 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
635.2 | 130.194 | -0.0023683 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.00647
635.4 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.25303 | 0.0062209 | 0.35695 | 0.0048708
635.6 | 130.194 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.49942 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
635.8 | 130.098 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
636 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
636.2 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
636.4 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.93278 | 0.0048708
636.6 | 130.2899 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.65085 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
636.8 | 130.194 | 0.0040291 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.45294 | 0.00647
637 | 130.194 | 0.0024299 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.26697 | 0.0099291 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
637.2 | 130.194 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
637.4 | 130.194 | 0.0040291 | 0.27926 | 0.004738 | 0.66945 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
637.6 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | -0.078023 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
637.8 | 130.194 | 0.0040291 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.49942 | 0.0038295 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
638 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
638.2 | 130.098 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.11392 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
638.4 | 130.002 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
638.6 | 130.194 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.0048708
638.8 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
639 | 130.194 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0032709
639.2 | 130.194 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
639.4 | 130.194 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
639.6 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.54889 | 0.0048708
639.8 | 130.2899 | 0.0088273 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
640 | 130.194 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0067301 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | -0.0017763 | 0.45294 | 0.0048708
640.2 | 130.098 | 0.015225 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.26697 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
640.4 | 130.2899 | 0.021623 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.012486 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
640.6 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.30582 | 0.0092866 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
640.8 | 130.194 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
641 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.013427 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
641.2 | 130.2899 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.16505 | 0.0048708
641.4 | 130.2899 | 0.0040291 | 0.56715 | 0.0015389 | 0.47751 | 0.014478 | 0.5549 | 0.003531 | 0.30748 | 0.013427 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
641.6 | 130.2899 | 0.0040291 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.5549 | 0.0019319 | 0.40347 | 0.0086283 | 0.59375 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
641.8 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 2.7482 | 0.0046217 | 0.45294 | 0.0048708
642 | 130.2899 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
642.2 | 130.2899 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0012893 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
642.4 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | -0.0015162 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.35695 | 0.0048708
642.6 | 130.2899 | 0.0040291 | 0.37521 | 0.0063372 | 0.093666 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
642.8 | 130.2899 | 0.0040291 | 0.18331 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.49942 | 0.0022303 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
643 | 130.2899 | 0.00083003 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.261 | 0.00647
643.2 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.25303 | 0.0046217 | 0.35695 | 0.0048708
643.4 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.20987 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.009669
643.6 | 130.194 | 0.0040291 | 0.27926 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0070285 | 0.11392 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
643.8 | 130.2899 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.69137 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0080692
644 | 130.2899 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
644.2 | 130.3859 | 0.0024299 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
644.4 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.49942 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
644.6 | 130.6738 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | -0.020925 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
644.8 | 131.0577 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.49776 | 0.010886 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
645 | 130.7698 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.59375 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
645.2 | 130.5779 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | -0.0015162 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.25303 | 0.0046217 | 0.35695 | 0.0032709
645.4 | 130.5779 | 0.0024299 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.17102 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0014227 | 0.35695 | 0.0048708
645.6 | 130.4819 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
645.8 | 130.5779 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.7468 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0094199 | 0.35695 | 0.0048708
646 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.28557 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.20987 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0032709
646.2 | 130.3859 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.012619 | 0.45294 | 0.0048708
646.4 | 130.3859 | 0.0040291 | 0.66314 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0080692
646.6 | 130.3859 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
646.8 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
647 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
647.2 | 130.4819 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
647.4 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.59375 | -0.0019091 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
647.6 | 130.3859 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
647.8 | 130.4819 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0094199 | 0.35695 | 0.0048708
648 | 130.5779 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
648.2 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0080692
648.4 | 130.3859 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.069058 | 0.0048708
648.6 | 130.3859 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0014227 | 0.35695 | 0.0048708
648.8 | 130.2899 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
649 | 130.2899 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
649.2 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
649.4 | 130.3859 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
649.6 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
649.8 | 130.3859 | 0.00083003 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
650 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
650.2 | 130.2899 | 0.0040291 | 0.27926 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0030219 | 0.74084 | 0.0048708
650.4 | 130.2899 | 0.0072281 | 0.087319 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
650.6 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
650.8 | 130.2899 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
651 | 130.2899 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
651.2 | 130.194 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
651.4 | 130.2899 | 0.0056289 | 0.4712 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
651.6 | 130.2899 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
651.8 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
652 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
652.2 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
652.4 | 130.2899 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
652.6 | 130.2899 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
652.8 | 130.4819 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.35695 | 0.00647
653 | 130.2899 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.78566 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
653.2 | 130.2899 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
653.4 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
653.6 | 130.2899 | 0.020024 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
653.8 | 130.194 | 0.016825 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
654 | 130.2899 | 0.042416 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.65085 | 0.003531 | 0.30748 | 0.011827 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
654.2 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.016626 | 0.49776 | 0.017284 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
654.4 | 130.2899 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.0092866 | 0.44497 | 0.0014227 | 0.45294 | 0.0048708
654.6 | 130.194 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.016626 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
654.8 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.11554 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
655 | 130.194 | 0.0024299 | 0.66314 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
655.2 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
655.4 | 130.194 | 0.0040291 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
655.6 | 130.194 | 0.0040291 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
655.8 | 130.098 | 0.0040291 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
656 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0094199 | 0.45294 | 0.0048708
656.2 | 130.098 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
656.4 | 130.098 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
656.6 | 130.098 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
656.8 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
657 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 8.3003e-05 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
657.2 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.68971 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
657.4 | 130.098 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.35695 | 0.00647
657.6 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.82882 | 0.0062209 | 0.45294 | 0.00647
657.8 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
658 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.45294 | 0.00647
658.2 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
658.4 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.5549 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
658.6 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
658.8 | 130.002 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0038295 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
659 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.011279 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
659.2 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
659.4 | 130.098 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0016718
659.6 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
659.8 | 130.098 | 0.0040291 | 0.27926 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
660 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
660.2 | 129.9061 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.017929 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
660.4 | 130.002 | 0.0040291 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
660.6 | 130.002 | 0.0040291 | 0.37521 | 0.0015389 | 0.5735 | 0.0080803 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
660.8 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
661 | 130.002 | 0.0040291 | 0.37521 | 0.0063372 | 0.7654 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
661.2 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
661.4 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
661.6 | 130.002 | 0.0040291 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
661.8 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0080803 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.35695 | 0.00647
662 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
662.2 | 130.002 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
662.4 | 130.002 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.49942 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
662.6 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
662.8 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
663 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
663.2 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.20987 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
663.4 | 130.002 | 0.0040291 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.11392 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
663.6 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
663.8 | 130.002 | 0.0056289 | 0.37521 | 0.0095362 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
664 | 129.9061 | 0.0056289 | 0.56715 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.69137 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0032709
664.2 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.63692 | 0.0062209 | 0.35695 | 0.0048708
664.4 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
664.6 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.7654 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.010886 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
664.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.012619 | 0.45294 | 0.0048708
665 | 130.002 | 0.0056289 | 0.27926 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
665.2 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0028892 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
665.4 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | -0.0019091 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
665.6 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0080692
665.8 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
666 | 129.9061 | 0.0072281 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.59375 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
666.2 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.35695 | 0.0048708
666.4 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | -0.0015162 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.0048708
666.6 | 129.9061 | 0.0088273 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0032709
666.8 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
667 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | -0.0044662 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
667.2 | 129.8101 | 0.013626 | 0.37521 | 0.004738 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
667.4 | 129.9061 | 0.016825 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | -0.0012672 | 0.59537 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
667.6 | 129.7141 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.014085 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
667.8 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.28557 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
668 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.011279 | 0.45891 | 0.0019319 | 0.30748 | 0.015026 | 0.40181 | 0.010886 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
668.2 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.019589 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
668.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
668.6 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.28557 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
668.8 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.17102 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
669 | 129.9061 | 0.0072281 | 0.27926 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
669.2 | 129.9061 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.11554 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.261 | 0.0048708
669.4 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0014227 | 0.64488 | 0.0048708
669.6 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0022303 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
669.8 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0028892 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
670 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
670.2 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.84279 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
670.4 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | -0.078023 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
670.6 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.075065 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
670.8 | 129.9061 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
671 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.92481 | 0.0062209 | 0.45294 | 0.0048708
671.2 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.36296 | 0.00033201 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
671.4 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.69137 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0078201 | -0.026893 | 0.0048708
671.6 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.21153 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
671.8 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0054293 | 0.20987 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
672 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.59375 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
672.2 | 130.002 | 0.0088273 | 0.37521 | 0.0063372 | 0.18962 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
672.4 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
672.6 | 129.6182 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
672.8 | 130.002 | 0.0088273 | 0.27926 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.59375 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
673 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
673.2 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
673.4 | 129.9061 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.019589 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.64488 | 0.0032709
673.6 | 130.002 | 0.013626 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0067301 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.0048708
673.8 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0016822 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
674 | 130.002 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 8.3003e-05 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
674.2 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0030219 | 0.54889 | 0.0048708
674.4 | 129.9061 | 0.010427 | 0.27926 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
674.6 | 130.002 | 0.0088273 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
674.8 | 130.002 | 0.010427 | 0.37521 | 0.0063372 | 0.28557 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.017929 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
675 | 129.9061 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0094199 | 0.35695 | 0.0048708
675.2 | 130.002 | 0.0088273 | 0.37521 | 0.0031381 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
675.4 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.84279 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.06109 | 0.0046217 | 0.45294 | 0.0048708
675.6 | 130.002 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
675.8 | 130.002 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 7.1911e-05
676 | 130.098 | 0.010427 | 0.4712 | 0.0063372 | 0.38156 | 0.003282 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
676.2 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
676.4 | 130.002 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
676.6 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
676.8 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.59375 | -0.0019091 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
677 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.73287 | 0.0062209 | 0.35695 | 0.00647
677.2 | 130.098 | 0.0088273 | 0.37521 | 0.011135 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.68971 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
677.4 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
677.6 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.010886 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
677.8 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.34898 | 0.0046217 | 0.45294 | 0.0048708
678 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
678.2 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
678.4 | 130.098 | 0.0088273 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.45294 | 0.009669
678.6 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
678.8 | 130.098 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
679 | 130.098 | 0.013626 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
679.2 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.20987 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.0048708
679.4 | 130.2899 | 0.012026 | 0.27926 | 0.004738 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
679.6 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
679.8 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
680 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.20987 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
680.2 | 130.3859 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
680.4 | 130.2899 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0094199 | 0.35695 | 0.00647
680.6 | 130.098 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
680.8 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.65085 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
681 | 130.194 | 0.016825 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
681.2 | 130.098 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.019589 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0016718
681.4 | 130.098 | 0.016825 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.011827 | 0.30582 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
681.6 | 130.098 | 0.029621 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0046217 | 0.35695 | 0.00647
681.8 | 130.194 | 0.0088273 | 0.37521 | 0.0031381 | 0.28557 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.017929 | 0.012486 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
682 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
682.2 | 130.2899 | 0.013626 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.00033201 | 0.69137 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
682.4 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.011279 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.9776 | 0.0044883 | 0.25303 | 0.0062209 | 0.45294 | 0.0048708
682.6 | 130.4819 | 0.012026 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0067301 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
682.8 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
683 | 130.2899 | 0.012026 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | -0.0044662 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.16505 | 0.0048708
683.2 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.00647
683.4 | 130.194 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.54889 | 0.0032709
683.6 | 130.2899 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | -0.00017715 | 0.45294 | 0.00647
683.8 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
684 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
684.2 | 130.6738 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | -0.020925 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
684.4 | 130.2899 | 0.010427 | 0.7591 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
684.6 | 130.194 | 0.010427 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.68971 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
684.8 | 130.2899 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.11392 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
685 | 130.2899 | 0.012026 | 0.37521 | 0.004738 | 0.28557 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
685.2 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
685.4 | 130.2899 | 0.012026 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
685.6 | 130.194 | 0.010427 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0014227 | 0.54889 | 0.0048708
685.8 | 130.3859 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
686 | 130.194 | 0.010427 | 0.27926 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
686.2 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
686.4 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.0048708
686.6 | 129.5222 | 0.0088273 | 0.56715 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
686.8 | 129.9061 | 0.015225 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
687 | 130.002 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.65085 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
687.2 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.0048708
687.4 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
687.6 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.17102 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
687.8 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.0048708
688 | 130.098 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
688.2 | 130.2899 | 0.010427 | 0.56715 | 0.011135 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.21153 | 0.0038295 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
688.4 | 130.2899 | 0.013626 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0083293 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.16505 | 0.00647
688.6 | 130.2899 | 0.013626 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
688.8 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
689 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.075065 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.45294 | 0.00647
689.2 | 130.2899 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.00033201 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
689.4 | 130.2899 | 0.012026 | 0.27926 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
689.6 | 130.2899 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.075065 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
689.8 | 130.2899 | 0.013626 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.00647
690 | 130.2899 | 0.012026 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
690.2 | 130.2899 | 0.013626 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.0048708
690.4 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
690.6 | 130.194 | 0.012026 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
690.8 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0016718
691 | 130.2899 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
691.2 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
691.4 | 130.2899 | 0.012026 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.0080692
691.6 | 130.002 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
691.8 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
692 | 130.5779 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
692.2 | 130.2899 | 0.010427 | 0.37521 | 0.0031381 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.017929 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
692.4 | 130.194 | 0.012026 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
692.6 | 130.2899 | 0.012026 | 0.37521 | 0.0031381 | 0.28557 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0012893 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
692.8 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
693 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
693.2 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
693.4 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
693.6 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0067301 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0094199 | 0.35695 | 0.00647
693.8 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.28557 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
694 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
694.2 | 130.194 | 0.0088273 | 0.27926 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
694.4 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0046217 | 0.45294 | 0.00647
694.6 | 130.194 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
694.8 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
695 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
695.2 | 130.2899 | 0.0088273 | 0.56715 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
695.4 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
695.6 | 130.194 | 0.010427 | 0.27926 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
695.8 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
696 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
696.2 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
696.4 | 130.194 | 0.0088273 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
696.6 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
696.8 | 130.098 | 0.0088273 | 0.37521 | 0.0063372 | 0.28557 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
697 | 130.194 | 0.013626 | 0.4712 | 0.0015389 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
697.2 | 130.194 | 0.018424 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
697.4 | 130.194 | 0.018424 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.013427 | 0.40181 | 0.0076874 | 0.06109 | 0.0062209 | 0.35695 | 0.0048708
697.6 | 130.194 | 0.036018 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.018225 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | -0.0015273
697.8 | 130.194 | 0.052013 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.018225 | 0.40181 | 0.014085 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
698 | 129.7141 | 0.010427 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.011827 | 0.40181 | 0.010886 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
698.2 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.30582 | 0.0092866 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
698.4 | 129.8101 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.012619 | 0.35695 | 0.0032709
698.6 | 129.9061 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
698.8 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
699 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
699.2 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
699.4 | 129.9061 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0078201 | 0.35695 | 0.0032709
699.6 | 129.8101 | 0.0088273 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
699.8 | 129.8101 | 0.0088273 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.20987 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
700 | 129.8101 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
700.2 | 129.8101 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0096794 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.35695 | 0.0048708
700.4 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
700.6 | 129.8101 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
700.8 | 129.8101 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
701 | 130.002 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.63692 | 0.0046217 | 0.45294 | 0.0048708
701.2 | 130.098 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
701.4 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
701.6 | 130.002 | 0.0088273 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
701.8 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
702 | 130.002 | 0.0088273 | 0.27926 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.11554 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0016718
702.2 | 130.002 | 0.0088273 | 0.37521 | 0.0063372 | 0.28557 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0012893 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
702.4 | 130.194 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
702.6 | 130.098 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
702.8 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
703 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0080692
703.2 | 130.098 | 0.0072281 | 0.27926 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.11392 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
703.4 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0096794 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
703.6 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.69137 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
703.8 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
704 | 130.002 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
704.2 | 130.002 | 0.0072281 | 0.37521 | 0.0031381 | 0.66945 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
704.4 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0080692
704.6 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.86139 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | -0.00030988 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
704.8 | 130.002 | 0.0072281 | 0.27926 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
705 | 129.9061 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
705.2 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
705.4 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.28557 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.017929 | 0.0044883 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
705.6 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0067301 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
705.8 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
706 | 129.9061 | 0.0072281 | 0.66314 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0078201 | 0.45294 | 0.0048708
706.2 | 130.002 | 0.0056289 | -0.0086323 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
706.4 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
706.6 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
706.8 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.66945 | 0.0016822 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
707 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | -0.0033755 | 0.45294 | 0.0048708
707.2 | 129.9061 | 0.0072281 | 0.27926 | 0.004738 | 0.7654 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
707.4 | 129.9061 | 0.0024299 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
707.6 | 129.8101 | 0.0072281 | 0.27926 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.0048708
707.8 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
708 | 129.9061 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0030219 | -0.026893 | 0.0048708
708.2 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.65085 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0078201 | 0.35695 | 0.0048708
708.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.65085 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
708.6 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0012893 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
708.8 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
709 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.261 | 0.0048708
709.2 | 129.8101 | 0.0056289 | 0.27926 | 0.0079364 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
709.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.36296 | 0.00033201 | 0.11554 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
709.6 | 129.8101 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.261 | 0.0048708
709.8 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.25303 | 0.0062209 | 0.35695 | 0.00647
710 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
710.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
710.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.35695 | 0.00647
710.6 | 129.8101 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
710.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
711 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.54889 | 0.00647
711.2 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
711.4 | 129.9061 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.069058 | 0.0048708
711.6 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.0048708
711.8 | 129.7141 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.26697 | 0.003531 | 0.30748 | 0.011827 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
712 | 129.8101 | 0.018424 | 0.27926 | 0.004738 | 0.66945 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
712.2 | 129.9061 | -0.0023683 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.36296 | 0.0019319 | 0.40347 | 0.013427 | 0.40181 | 0.0076874 | 0.63692 | 0.0046217 | 0.45294 | 0.0048708
712.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0016822 | 0.93874 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0092866 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
712.6 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.019589 | 0.0086283 | 0.78566 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
712.8 | 129.9061 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.49942 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
713 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0080692
713.2 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0014227 | 0.45294 | 0.00647
713.4 | 129.8101 | 0.0056289 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.49942 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
713.6 | 129.8101 | 0.0024299 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
713.8 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
714 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.17102 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
714.2 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0028892 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
714.4 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | -0.0015273
714.6 | 129.9061 | 0.0040291 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.011268
714.8 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | -0.0019091 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
715 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
715.2 | 129.9061 | 0.0056289 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 7.1911e-05
715.4 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
715.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.00063108 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
715.8 | 129.9061 | 0.0040291 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.019589 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
716 | 129.8101 | 0.0040291 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
716.2 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
716.4 | 129.7141 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0092866 | 0.63692 | 0.0046217 | 0.45294 | 0.0048708
716.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
716.8 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0083293 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
717 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
717.2 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | -0.0044662 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
717.4 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.65085 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
717.6 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.66945 | -0.0015162 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
717.8 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.010886 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
718 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0032709
718.2 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
718.4 | 130.194 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.011019 | 0.45294 | 0.00647
718.6 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0054293 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
718.8 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | -0.0031265
719 | 129.9061 | 0.0040291 | 0.4712 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
719.2 | 129.9061 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
719.4 | 130.002 | 0.0056289 | 0.4712 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
719.6 | 129.9061 | 0.0056289 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
719.8 | 129.9061 | 0.0056289 | 0.27926 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | 0.0048708
720 | 130.002 | 0.0024299 | -0.0086323 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
720.2 | 129.9061 | 0.0040291 | 0.37521 | 0.0015389 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
720.4 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
720.6 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 8.3003e-05 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.15708 | 0.0062209 | 0.45294 | 0.0048708
720.8 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
721 | 130.002 | 0.0040291 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.0048708
721.2 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0070285 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
721.4 | 130.002 | 0.0024299 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0099291 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.74084 | 0.0048708
721.6 | 130.002 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0080803 | 0.26697 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.82882 | 0.0062209 | 0.35695 | 0.0048708
721.8 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.11392 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
722 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
722.2 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
722.4 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.78566 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
722.6 | 130.098 | 0.0056289 | 0.4712 | 0.011135 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.59375 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
722.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.0099291 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.63692 | -0.0017763 | 0.45294 | 0.00647
723 | 130.098 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.261 | 0.0048708
723.2 | 130.002 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.26697 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.92481 | 0.0062209 | 0.45294 | 0.0048708
723.4 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.34898 | 0.0062209 | 0.45294 | 0.0048708
723.6 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.7468 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
723.8 | 130.098 | 0.016825 | 0.4712 | 0.004738 | 0.7654 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.017929 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
724 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0019319 | 0.30748 | 0.013427 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
724.2 | 130.098 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.44497 | 0.0030219 | 0.45294 | 0.00647
724.4 | 130.098 | 0.00083003 | 0.27926 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0099291 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.16505 | 0.00647
724.6 | 130.194 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.0080692
724.8 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.35695 | 0.0048708
725 | 130.098 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | -0.0012672 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
725.2 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.093666 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
725.4 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
725.6 | 130.194 | 0.00083003 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
725.8 | 130.098 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0078201 | 0.35695 | 0.0048708
726 | 130.4819 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.011019 | 0.45294 | 0.0048708
726.2 | 130.8658 | 0.0024299 | 0.66314 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
726.4 | 130.3859 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
726.6 | 130.3859 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.35695 | 0.0048708
726.8 | 130.2899 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.013427 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
727 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0067301 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
727.2 | 130.194 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.009669
727.4 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
727.6 | 130.2899 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
727.8 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
728 | 130.2899 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.65085 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
728.2 | 130.194 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.0022303 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
728.4 | 130.2899 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
728.6 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
728.8 | 130.194 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
729 | 130.194 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
729.2 | 130.2899 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.17102 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
729.4 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
729.6 | 130.098 | 0.0056289 | 0.37521 | 0.0079364 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0092866 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
729.8 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
730 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.26697 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
730.2 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
730.4 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
730.6 | 130.002 | 0.0040291 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
730.8 | 130.098 | 0.0056289 | 0.37521 | 0.0079364 | 0.28557 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
731 | 130.194 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
731.2 | 130.002 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
731.4 | 130.098 | 0.010427 | 0.37521 | 0.0063372 | 0.28557 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
731.6 | 130.2899 | 0.016825 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | -0.00017715 | 0.35695 | 0.00647
731.8 | 130.194 | 0.037618 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.21153 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
732 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.69137 | 0.011827 | 0.40181 | 0.018884 | 0.54092 | 0.0062209 | 0.64488 | 0.0048708
732.2 | 130.098 | 0.0040291 | 0.4712 | 0.004738 | 0.5735 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.019824 | 0.49776 | 0.012486 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
732.4 | 130.002 | 0.0056289 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
732.6 | 130.098 | 0.0040291 | 0.27926 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
732.8 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
733 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0032709
733.2 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
733.4 | 130.002 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
733.6 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.11554 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
733.8 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
734 | 130.002 | 0.0056289 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
734.2 | 129.9061 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.83679 | 0.00647
734.4 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | -0.0028664 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
734.6 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.11554 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
734.8 | 129.9061 | 0.0056289 | 0.18331 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 0.0048708
735 | 130.002 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
735.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.7468 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0094199 | 0.45294 | 0.00647
735.4 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
735.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
735.8 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
736 | 129.9061 | 0.0056289 | 0.56715 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
736.2 | 129.9061 | -0.00076916 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
736.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
736.6 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
736.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
737 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0012893 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
737.2 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
737.4 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | -0.0015273
737.6 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.010886 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
737.8 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.86139 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
738 | 129.7141 | 0.0072281 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0046217 | 0.16505 | 0.009669
738.2 | 129.7141 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
738.4 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
738.6 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.65085 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
738.8 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | -0.17235 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.009669
739 | 129.8101 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | -0.00030988 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
739.2 | 129.7141 | 0.012026 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.261 | 0.0048708
739.4 | 129.8101 | 0.018424 | 0.4712 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
739.6 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
739.8 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | -0.21287 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.017284 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
740 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | -0.00017715 | 0.261 | 0.00647
740.2 | 129.9061 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.20987 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
740.4 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
740.6 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.65085 | -0.0012672 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.0048708
740.8 | 129.8101 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.59537 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
741 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
741.2 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0054293 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
741.4 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0028892 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
741.6 | 129.9061 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
741.8 | 129.8101 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.11554 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
742 | 129.9061 | 0.0072281 | 0.7591 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
742.2 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
742.4 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0012893 | 0.63692 | 0.0062209 | 0.35695 | 0.0048708
742.6 | 129.9061 | 0.0088273 | 0.7591 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.11554 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
742.8 | 129.9061 | 0.010427 | 0.4712 | 0.0095362 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
743 | 130.002 | 0.010427 | 0.087319 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | -0.0031265
743.2 | 130.002 | 0.010427 | 0.27926 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.013427 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
743.4 | 130.002 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.84279 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.35695 | 0.0048708
743.6 | 129.8101 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
743.8 | 130.002 | 0.010427 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0070285 | 0.30582 | 0.0044883 | 0.44497 | 0.0062209 | 0.54889 | 0.0080692
744 | 130.2899 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
744.2 | 129.6182 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
744.4 | 130.002 | 0.0088273 | 0.37521 | 0.0015389 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0022303 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
744.6 | 130.002 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
744.8 | 130.002 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
745 | 130.002 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.40347 | 0.011827 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0080692
745.2 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
745.4 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
745.6 | 130.098 | 0.010427 | 0.4712 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
745.8 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
746 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0094199 | 0.069058 | 0.00647
746.2 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
746.4 | 130.002 | 0.015225 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
746.6 | 130.002 | 0.018424 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
746.8 | 130.194 | 0.0088273 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
747 | 130.194 | 0.012026 | 0.37521 | 0.0063372 | 0.7654 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | -0.00030988 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
747.2 | 130.194 | 0.012026 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
747.4 | 130.194 | 0.012026 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.40347 | 0.0070285 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
747.6 | 130.098 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
747.8 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
748 | 130.2899 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
748.2 | 130.194 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
748.4 | 129.9061 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.26697 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
748.6 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
748.8 | 130.2899 | 0.010427 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
749 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0067301 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.16505 | 0.00647
749.2 | 130.2899 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 8.3003e-05 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.35695 | 0.0048708
749.4 | 130.2899 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.0048708
749.6 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
749.8 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.34898 | -0.0017763 | 0.35695 | 0.00647
750 | 130.2899 | 0.012026 | 0.37521 | 0.004738 | 0.66945 | 8.3003e-05 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
750.2 | 130.2899 | 0.012026 | 0.27926 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
750.4 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
750.6 | 130.2899 | 0.012026 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
750.8 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
751 | 130.098 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
751.2 | 130.002 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.075065 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0014227 | 0.45294 | 0.00647
751.4 | 130.002 | 0.010427 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
751.6 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.49776 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
751.8 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
752 | 130.194 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.21153 | 0.013427 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
752.2 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.38156 | 8.3003e-05 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
752.4 | 130.194 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
752.6 | 130.194 | 0.0072281 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
752.8 | 130.098 | 0.012026 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0016718
753 | 130.098 | 0.020024 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
753.2 | 130.194 | 0.037618 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.40347 | 0.015026 | 0.49776 | 0.010886 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
753.4 | 130.002 | 0.012026 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.013427 | 0.49776 | 0.018884 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
753.6 | 130.002 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.82882 | 0.0062209 | 0.35695 | 0.0048708
753.8 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0032709
754 | 130.002 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
754.2 | 130.098 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.20987 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
754.4 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | -0.00017715 | 0.45294 | 0.0048708
754.6 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
754.8 | 130.098 | 0.013626 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
755 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
755.2 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
755.4 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
755.6 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
755.8 | 130.098 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.075065 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
756 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.012619 | 0.45294 | 0.0048708
756.2 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
756.4 | 129.9061 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 7.1911e-05
756.6 | 129.9061 | 0.0072281 | 0.27926 | 0.0095362 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0022303 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
756.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.7468 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0014227 | 0.35695 | 0.0048708
757 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0016822 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.25303 | 0.0046217 | 0.45294 | 0.0048708
757.2 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
757.4 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
757.6 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.65085 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
757.8 | 129.8101 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
758 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.11554 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
758.2 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.25303 | 0.0062209 | 0.45294 | 0.0048708
758.4 | 129.8101 | 0.0072281 | 0.37521 | 0.0095362 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
758.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.26697 | 0.0099291 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
758.8 | 129.8101 | 0.0056289 | 0.56715 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.019589 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
759 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0016822 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.45294 | 0.0048708
759.2 | 129.7141 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
759.4 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.66945 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0070285 | 0.59375 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
759.6 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
759.8 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.59375 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
760 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | -0.0017763 | 0.45294 | 0.0048708
760.2 | 129.8101 | 0.0056289 | 0.37521 | -0.0016601 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
760.4 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
760.6 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
760.8 | 129.8101 | 0.0056289 | 0.18331 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.019589 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0080692
761 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
761.2 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.0048708
761.4 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.20987 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
761.6 | 129.8101 | 0.010427 | 0.4712 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | -0.0031265
761.8 | 129.7141 | 0.016825 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
762 | 130.002 | 0.0056289 | 0.37521 | 0.033528 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.30748 | 0.010228 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
762.2 | 129.9061 | 0.0040291 | 0.4712 | -0.0016601 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
762.4 | 129.8101 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.64488 | 0.0048708
762.6 | 129.8101 | -0.00076916 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0046217 | 0.54889 | 0.009669
762.8 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.0048708
763 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
763.2 | 129.9061 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
763.4 | 129.8101 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0083293 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
763.6 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
763.8 | 129.9061 | 0.0024299 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.65085 | -0.0028664 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.261 | 0.00647
764 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
764.2 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | -0.078023 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
764.4 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
764.6 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
764.8 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0028892 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
765 | 129.7141 | -0.00076916 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
765.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.65085 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
765.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
765.6 | 129.9061 | 0.0040291 | 0.27926 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0032709
765.8 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
766 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | -0.026893 | 0.00647
766.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.82882 | 0.0062209 | 0.45294 | 0.00647
766.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | -0.076363 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0016718
766.6 | 129.9061 | 0.0056289 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | -0.0015273
766.8 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.65085 | -0.0044662 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
767 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.010886 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
767.2 | 129.9061 | 0.0056289 | 0.56715 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 7.1911e-05
767.4 | 130.098 | -0.00076916 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
767.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
767.8 | 129.9061 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
768 | 130.002 | 0.0056289 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0080692
768.2 | 129.9061 | 0.0040291 | 0.56715 | 0.004738 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.019589 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
768.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0054293 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
768.6 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.74084 | -0.0015273
768.8 | 129.9061 | 0.00083003 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
769 | 130.002 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0054293 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.0080692
769.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
769.4 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.59537 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.261 | 0.00647
769.6 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
769.8 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
770 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
770.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0080692
770.4 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.74084 | 0.0048708
770.6 | 130.098 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
770.8 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | -0.0019091 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
771 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.014085 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
771.2 | 130.002 | 0.0040291 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
771.4 | 129.9061 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.20987 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
771.6 | 130.002 | 0.0040291 | 0.27926 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.78732 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.16505 | 0.0048708
771.8 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
772 | 129.9061 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0099291 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
772.2 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
772.4 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.28557 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
772.6 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.38156 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
772.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
773 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.68971 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
773.2 | 129.9061 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
773.4 | 130.002 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | -0.00017715 | 0.35695 | 0.00647
773.6 | 130.002 | 0.0040291 | 0.37521 | 0.0095362 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
773.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
774 | 129.7141 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
774.2 | 130.002 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
774.4 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.012619 | 0.45294 | 0.00647
774.6 | 130.002 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
774.8 | 130.002 | -0.00076916 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | -0.026893 | 0.0048708
775 | 129.8101 | -0.0023683 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
775.2 | 129.9061 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
775.4 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.7654 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
775.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
775.8 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.49776 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
776 | 130.002 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.5549 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
776.2 | 129.9061 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0046217 | 0.45294 | 0.00647
776.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0012893 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
776.6 | 130.194 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0094199 | 0.35695 | 0.00647
776.8 | 129.9061 | 0.0040291 | 0.37521 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
777 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
777.2 | 129.9061 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.0048708
777.4 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
777.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
777.8 | 129.9061 | 0.0040291 | 0.4712 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0054293 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
778 | 130.002 | 0.0040291 | 0.18331 | 0.0063372 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
778.2 | 129.9061 | 0.0040291 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
778.4 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.011019 | 0.35695 | 0.00647
778.6 | 129.9061 | 0.0056289 | 0.56715 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0054293 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
778.8 | 130.002 | 0.0040291 | 0.4712 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
779 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.20987 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
779.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
779.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
779.6 | 129.9061 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.019589 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.83679 | 0.00647
779.8 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | -0.00030988 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
780 | 129.9061 | 0.0056289 | 0.37521 | 0.0031381 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.261 | 0.0048708
780.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
780.4 | 129.9061 | 0.0024299 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.5549 | 0.00033201 | 0.21153 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.64488 | 0.0048708
780.6 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
780.8 | 129.9061 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0016822 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
781 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
781.2 | 130.2899 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.0048708
781.4 | 129.9061 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
781.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0080803 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.34898 | 0.0062209 | 0.45294 | 0.0048708
781.8 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
782 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
782.2 | 129.7141 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
782.4 | 129.9061 | 0.0040291 | 0.66314 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.00647
782.6 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
782.8 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.78566 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
783 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.65085 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
783.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
783.4 | 129.9061 | 0.0040291 | 0.4712 | 0.004738 | 0.7654 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0012893 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
783.6 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | -0.020925 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
783.8 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
784 | 129.9061 | 0.0040291 | 0.56715 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
784.2 | 129.7141 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
784.4 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
784.6 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.26697 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
784.8 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
785 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
785.2 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
785.4 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.17102 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
785.6 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
785.8 | 129.9061 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.49942 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
786 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
786.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
786.4 | 129.9061 | 0.0056289 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.59375 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
786.6 | 129.9061 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.11554 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
786.8 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
787 | 130.002 | 0.0056289 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
787.2 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
787.4 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.16505 | 0.011268
787.6 | 130.002 | 0.0040291 | 0.37521 | 0.0015389 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
787.8 | 130.002 | 0.0056289 | 0.4712 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
788 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
788.2 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
788.4 | 130.002 | 0.0088273 | 0.66314 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.011268
788.6 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
788.8 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
789 | 130.002 | 0.024822 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.26697 | 0.003531 | 0.30748 | 0.011827 | 0.30582 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.0048708
789.2 | 129.9061 | 0.0056289 | 0.56715 | 0.012735 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.015026 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
789.4 | 129.4263 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.0054293 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
789.6 | 130.002 | 0.0040291 | -0.0086323 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.015026 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
789.8 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | -0.2683 | 0.0054293 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
790 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.019589 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.83679 | 0.00647
790.2 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.73287 | 0.0046217 | 0.35695 | 0.00647
790.4 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
790.6 | 130.098 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.35695 | 0.0048708
790.8 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
791 | 130.098 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
791.2 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.59375 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
791.4 | 130.098 | 0.0056289 | 0.27926 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
791.6 | 130.098 | 0.0024299 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0099291 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.34898 | 0.0062209 | 0.54889 | 0.00647
791.8 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0030219 | 0.16505 | 0.00647
792 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.28557 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.68971 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
792.2 | 130.3859 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.7468 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0094199 | 0.45294 | 0.0048708
792.4 | 130.2899 | 0.0040291 | 0.37521 | 0.0031381 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
792.6 | 130.5779 | 0.0056289 | 0.37521 | 0.0079364 | 0.093666 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
792.8 | 130.7698 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0028892 | 0.34898 | 0.0046217 | 0.45294 | 0.00647
793 | 130.2899 | 0.0056289 | 0.27926 | 0.011135 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0022303 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
793.2 | 130.2899 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
793.4 | 130.2899 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.0048708
793.6 | 130.2899 | 0.0040291 | 0.27926 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.35695 | 0.0048708
793.8 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
794 | 130.194 | 0.0040291 | 0.4712 | 0.004738 | 0.38156 | 0.0064811 | 0.65085 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
794.2 | 130.098 | 0.0056289 | 0.4712 | 0.004738 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
794.4 | 130.098 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.11392 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
794.6 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0080692
794.8 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.66945 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.35695 | 0.0048708
795 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
795.2 | 130.194 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.00647
795.4 | 130.098 | 0.0040291 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
795.6 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.20987 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
795.8 | 130.2899 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
796 | 130.194 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.34898 | 0.012619 | 0.45294 | 0.0048708
796.2 | 130.098 | 0.0024299 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
796.4 | 130.194 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
796.6 | 130.194 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.075065 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.54889 | 0.00647
796.8 | 129.9061 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
797 | 130.194 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.019589 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0080692
797.2 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.5549 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.82882 | 0.0062209 | 0.35695 | 0.00647
797.4 | 130.098 | 0.0040291 | 0.37521 | 0.0079364 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
797.6 | 130.194 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
797.8 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
798 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
798.2 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
798.4 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
798.6 | 130.098 | 0.0040291 | 0.37521 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
798.8 | 130.098 | 0.0040291 | 0.27926 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.11392 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
799 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
799.2 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
799.4 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.21153 | 0.0070285 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
799.6 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
799.8 | 130.098 | 0.0056289 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
800 | 130.194 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
800.2 | 130.194 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
800.4 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
800.6 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0028892 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
800.8 | 130.3859 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.0048708
801 | 130.098 | 0.0056289 | 0.18331 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
801.2 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0016718
801.4 | 130.002 | 0.0072281 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.0048708
801.6 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
801.8 | 130.098 | 0.010427 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
802 | 130.098 | 0.015225 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
802.2 | 130.098 | 0.020024 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
802.4 | 130.002 | 0.016825 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.68971 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
802.6 | 129.9061 | 0.029621 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.012486 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
802.8 | 130.3859 | 0.036018 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.010886 | 0.54092 | 0.0094199 | 0.45294 | 0.0048708
803 | 129.9061 | 0.0040291 | 0.27926 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.016626 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
803.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.023023 | 0.11392 | 0.014085 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
803.4 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.7654 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.018884 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
803.6 | 130.002 | 0.0040291 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
803.8 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.018225 | 0.59375 | 0.010886 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
804 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.17102 | 0.003531 | 0.30748 | 0.010228 | 0.59375 | 0.015685 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
804.2 | 130.002 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0016822 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
804.4 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
804.6 | 129.9061 | 0.0056289 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.20987 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
804.8 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.010886 | 0.34898 | 0.0062209 | 0.54889 | 0.00647
805 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.009669
805.2 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
805.4 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.54889 | 0.00647
805.6 | 130.002 | 0.0056289 | 0.27926 | -6.0896e-05 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
805.8 | 130.002 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.075065 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
806 | 130.002 | 0.0056289 | 0.4712 | 0.0031381 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0038295 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
806.2 | 130.002 | 0.0056289 | 0.27926 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.20987 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
806.4 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0094199 | 0.45294 | 0.00647
806.6 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.66945 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
806.8 | 130.002 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.26697 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
807 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
807.2 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0054293 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
807.4 | 130.002 | 0.0040291 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
807.6 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.0016718
807.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0038295 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
808 | 129.9061 | 0.0024299 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
808.2 | 129.9061 | 0.0056289 | 0.27926 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
808.4 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
808.6 | 130.002 | 0.0056289 | 0.37521 | 0.0095362 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
808.8 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
809 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.69137 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
809.2 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0016822 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.25303 | 0.0062209 | 0.54889 | 0.00647
809.4 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.075065 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
809.6 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
809.8 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
810 | 129.7141 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
810.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.7468 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
810.4 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
810.6 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
810.8 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.17102 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
811 | 130.098 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
811.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.075065 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
811.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.011279 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.59375 | -0.00030988 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
811.6 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
811.8 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
812 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.009669
812.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
812.4 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
812.6 | 129.9061 | 0.0056289 | 0.4712 | 0.011135 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
812.8 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.011279 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
813 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
813.2 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0083293 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
813.4 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0030219 | 0.45294 | 0.0048708
813.6 | 129.8101 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
813.8 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.26697 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
814 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
814.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
814.4 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.0099291 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
814.6 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0070285 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 7.1911e-05
814.8 | 129.7141 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
815 | 129.7141 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
815.2 | 129.8101 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
815.4 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.93278 | 0.00647
815.6 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
815.8 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
816 | 129.4263 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
816.2 | 129.8101 | 0.0040291 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
816.4 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.012868
816.6 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | -0.0015273
816.8 | 129.8101 | 0.0056289 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0032709
817 | 129.8101 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.014218 | 0.54889 | 0.00647
817.2 | 129.8101 | 0.0056289 | 0.66314 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
817.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
817.6 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
817.8 | 129.7141 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.003282 | 0.7468 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.15708 | 0.0062209 | 0.45294 | 0.00647
818 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
818.2 | 129.7141 | 0.0056289 | 0.4712 | 0.004738 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
818.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
818.6 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
818.8 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.86139 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0012893 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
819 | 129.8101 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.35695 | 0.0048708
819.2 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.0016718
819.4 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.20987 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
819.6 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
819.8 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
820 | 129.8101 | 0.0056289 | 0.66314 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.009669
820.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
820.4 | 129.8101 | 0.0072281 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
820.6 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.26697 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.92481 | 0.0062209 | 0.45294 | 0.0048708
820.8 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | -0.078023 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
821 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.06109 | 0.0062209 | 0.45294 | 0.0048708
821.2 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.017929 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
821.4 | 129.8101 | 0.0088273 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
821.6 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | -0.00030988 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
821.8 | 129.7141 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0054293 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
822 | 129.7141 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
822.2 | 129.3303 | 0.0072281 | 0.37521 | 0.0063372 | 0.18962 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
822.4 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.30582 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
822.6 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
822.8 | 129.8101 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | -0.0015162 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
823 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
823.2 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | -0.0015162 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.25303 | 0.0062209 | 0.45294 | 0.0048708
823.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0095362 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
823.6 | 129.6182 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0028892 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
823.8 | 129.8101 | 0.0072281 | 0.56715 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.78732 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 7.1911e-05
824 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
824.2 | 129.7141 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0046217 | 0.45294 | 0.0048708
824.4 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
824.6 | 129.8101 | 0.0072281 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
824.8 | 129.7141 | 0.0088273 | 0.56715 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
825 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.25303 | 0.0062209 | 0.45294 | 0.0048708
825.2 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | -0.020925 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
825.4 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.012486 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
825.6 | 129.8101 | 0.010427 | 0.37521 | 0.004738 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
825.8 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.17102 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.92481 | 0.0062209 | 0.45294 | 0.0048708
826 | 129.8101 | 0.0088273 | 0.37521 | -0.0016601 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
826.2 | 129.8101 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.012486 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
826.4 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
826.6 | 129.9061 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0096794 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
826.8 | 129.8101 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0078201 | 0.261 | 0.0048708
827 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.17102 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.34898 | 0.0046217 | 0.54889 | 0.0048708
827.2 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0016822 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
827.4 | 129.7141 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
827.6 | 129.7141 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
827.8 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0028892 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
828 | 129.9061 | 0.010427 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
828.2 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
828.4 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
828.6 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
828.8 | 130.002 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0014227 | 0.54889 | 0.00647
829 | 129.9061 | 0.0088273 | 0.4712 | 0.0079364 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
829.2 | 130.002 | 0.0088273 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | -0.026893 | 0.00647
829.4 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
829.6 | 129.9061 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.20987 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
829.8 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.7654 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0012893 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
830 | 129.9061 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | -0.020925 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
830.2 | 130.002 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
830.4 | 130.002 | 0.0088273 | 0.37521 | 0.0079364 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
830.6 | 130.002 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
830.8 | 130.098 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0099291 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
831 | 130.002 | 0.012026 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0054293 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
831.2 | 130.002 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
831.4 | 130.002 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
831.6 | 130.098 | 0.0040291 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | -0.026893 | 0.0048708
831.8 | 129.9061 | 0.0088273 | 0.4712 | 0.0015389 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
832 | 130.098 | 0.016825 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | -0.026893 | 0.00647
832.2 | 130.098 | 0.015225 | 0.37521 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
832.4 | 130.002 | 0.03282 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0092866 | 0.34898 | 0.0078201 | 0.35695 | 0.0048708
832.6 | 129.8101 | 0.016825 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.26697 | 0.003531 | 0.40347 | 0.015026 | 0.40181 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
832.8 | 130.098 | 0.012026 | 0.37521 | 0.011135 | 0.5735 | 0.003282 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0080692
833 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.73287 | 0.0062209 | 0.35695 | 0.00647
833.2 | 130.098 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.26697 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
833.4 | 130.098 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
833.6 | 130.098 | 0.012026 | 0.56715 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
833.8 | 130.098 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0054293 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.009669
834 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.017929 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
834.2 | 130.098 | 0.010427 | 0.56715 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
834.4 | 130.098 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
834.6 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | -0.034861 | 0.0062209 | 0.45294 | 0.00647
834.8 | 130.194 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
835 | 130.2899 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0028892 | 0.06109 | 0.0062209 | 0.45294 | 0.0048708
835.2 | 129.8101 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.003282 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0028892 | 0.92481 | 0.0062209 | 0.45294 | 0.00647
835.4 | 129.5222 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.26697 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.011019 | 0.45294 | 0.00647
835.6 | 130.098 | 0.012026 | 0.4712 | 0.0031381 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
835.8 | 130.098 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
836 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.28557 | 0.012878 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
836.2 | 130.098 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.009669
836.4 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0054293 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
836.6 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.84279 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.15708 | 0.0062209 | 0.45294 | 0.00647
836.8 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
837 | 130.194 | 0.013626 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.54889 | 0.00647
837.2 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
837.4 | 130.194 | 0.012026 | 0.4712 | 0.0031381 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
837.6 | 130.194 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
837.8 | 130.194 | 0.013626 | 0.66314 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
838 | 130.2899 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.7468 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
838.2 | 130.194 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.0080692
838.4 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
838.6 | 130.098 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
838.8 | 130.3859 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.011019 | 0.54889 | 0.00647
839 | 130.194 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0016822 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
839.2 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
839.4 | 130.194 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
839.6 | 129.8101 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
839.8 | 130.194 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
840 | 130.098 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.20987 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
840.2 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
840.4 | 130.098 | 0.0088273 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
840.6 | 130.098 | 0.0088273 | 0.27926 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
840.8 | 130.194 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
841 | 130.098 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
841.2 | 130.194 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.82882 | 0.0062209 | 0.45294 | 0.00647
841.4 | 130.2899 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.0048708
841.6 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.06109 | 0.0062209 | 0.35695 | 0.00647
841.8 | 130.002 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
842 | 130.002 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
842.2 | 130.002 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
842.4 | 130.002 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
842.6 | 130.098 | 0.020024 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
842.8 | 130.098 | 0.018424 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.013427 | 0.40181 | 0.0092866 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
843 | 130.002 | 0.037618 | 0.4712 | 0.004738 | 0.38156 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.013427 | 0.40181 | 0.010886 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
843.2 | 130.194 | 0.048814 | 0.27926 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.016626 | 0.88165 | 0.012486 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
843.4 | 130.002 | 0.012026 | 0.37521 | 0.0063372 | 0.38156 | 0.0096794 | 0.36296 | 0.0019319 | 0.30748 | 0.013427 | 0.40181 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
843.6 | 130.002 | 0.010427 | 0.37521 | 0.0079364 | 0.5735 | 0.0048812 | 0.45891 | 0.041918 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
843.8 | 130.002 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0046217 | 0.45294 | 0.0048708
844 | 130.002 | 0.010427 | 0.37521 | 0.004738 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0080692
844.2 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.0048708
844.4 | 130.002 | 0.010427 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
844.6 | 130.002 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
844.8 | 130.002 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
845 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
845.2 | 130.002 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
845.4 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
845.6 | 130.002 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
845.8 | 130.002 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
846 | 130.194 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
846.2 | 130.002 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
846.4 | 129.9061 | 0.0088273 | 0.37521 | 0.0031381 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
846.6 | 130.194 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.00033201 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
846.8 | 129.9061 | 0.0088273 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
847 | 129.8101 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
847.2 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.65085 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
847.4 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
847.6 | 129.9061 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.16505 | 0.0048708
847.8 | 129.9061 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.21153 | 0.0038295 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
848 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.54889 | 0.00647
848.2 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
848.4 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.075065 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.35695 | 0.00647
848.6 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
848.8 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
849 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
849.2 | 129.9061 | 0.0072281 | 0.37521 | 0.004738 | 0.093666 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
849.4 | 129.9061 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
849.6 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
849.8 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.65085 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
850 | 129.9061 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | -0.0012672 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
850.2 | 129.9061 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0012893 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
850.4 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.06109 | 0.0062209 | 0.35695 | 0.0048708
850.6 | 129.9061 | 0.0072281 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 7.1911e-05
850.8 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.017929 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
851 | 129.8101 | 0.0072281 | 0.087319 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | -0.0015273
851.2 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.86139 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
851.4 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
851.6 | 129.8101 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | -0.026893 | 0.0048708
851.8 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.014218 | 0.45294 | 0.00647
852 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
852.2 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
852.4 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
852.6 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
852.8 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
853 | 129.8101 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
853.2 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0051309 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
853.4 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | -0.0015162 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
853.6 | 129.6182 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.84279 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
853.8 | 130.194 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.35695 | 0.0048708
854 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
854.2 | 129.7141 | 0.0072281 | 0.37521 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
854.4 | 129.8101 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
854.6 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.0048708
854.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.78566 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
855 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
855.2 | 129.8101 | 0.0072281 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
855.4 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.010228 | 0.78566 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
855.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
855.8 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0076874 | 0.34898 | 0.0046217 | 0.45294 | 0.00647
856 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.68971 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
856.2 | 129.9061 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.11554 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
856.4 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
856.6 | 129.8101 | 0.0072281 | 0.37521 | 0.0015389 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
856.8 | 129.8101 | 0.0072281 | 0.56715 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
857 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.84279 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
857.2 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
857.4 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | -0.0028664 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.64488 | 0.0048708
857.6 | 129.8101 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.11392 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
857.8 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
858 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
858.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
858.4 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.59537 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0080692
858.6 | 129.9061 | 0.0072281 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.11554 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0016718
858.8 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
859 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
859.2 | 129.8101 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0083293 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
859.4 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
859.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
859.8 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
860 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
860.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.83679 | 0.00647
860.4 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
860.6 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
860.8 | 129.7141 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.59537 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
861 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
861.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.26697 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
861.4 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.18962 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
861.6 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.78732 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0080692
861.8 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.18962 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
862 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0096794 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
862.2 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.66945 | 8.3003e-05 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
862.4 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.35695 | 0.00647
862.6 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.00647
862.8 | 129.8101 | 0.0056289 | 0.27926 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
863 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.73287 | 0.0046217 | 0.45294 | 0.0048708
863.2 | 129.8101 | 0.0072281 | 0.56715 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0016718
863.4 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.17102 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
863.6 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | -0.0017763 | 0.45294 | 0.00647
863.8 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
864 | 129.7141 | 0.0072281 | 0.27926 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
864.2 | 129.8101 | 0.0072281 | 0.37521 | 0.0079364 | 0.093666 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
864.4 | 129.8101 | 0.0072281 | 0.087319 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | -0.0015273
864.6 | 129.8101 | 0.0072281 | 0.4712 | 0.011135 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
864.8 | 129.8101 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
865 | 129.8101 | 0.0072281 | 0.4712 | -6.0896e-05 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
865.2 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
865.4 | 130.002 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.65085 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
865.6 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.66945 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
865.8 | 129.6182 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
866 | 129.6182 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.68971 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
866.2 | 129.6182 | 0.020024 | 0.37521 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
866.4 | 129.7141 | 0.03282 | 0.27926 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.016626 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
866.6 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.17102 | 0.0019319 | 0.30748 | 0.011827 | 0.40181 | 0.010886 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
866.8 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.015026 | 0.40181 | 0.010886 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
867 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 2.2823 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.15708 | 0.0062209 | 0.45294 | 0.00647
867.2 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.027821 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
867.4 | 129.8101 | -0.00076916 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.68971 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
867.6 | 129.8101 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0096794 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
867.8 | 129.8101 | 0.0056289 | 0.37521 | 0.0015389 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
868 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.25303 | 0.012619 | 0.45294 | 0.00647
868.2 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.74084 | 0.00647
868.4 | 129.8101 | 0.0072281 | 0.37521 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
868.6 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.0048708
868.8 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.59375 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
869 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.7468 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.06109 | 0.0062209 | 0.45294 | 0.0048708
869.2 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
869.4 | 129.7141 | 0.0040291 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
869.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.28557 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
869.8 | 129.7141 | 0.0056289 | 0.66314 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.64488 | 0.00647
870 | 129.8101 | 0.0056289 | 0.66314 | -6.0896e-05 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
870.2 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
870.4 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.20987 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
870.6 | 129.5222 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
870.8 | 129.8101 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
871 | 129.7141 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.65085 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
871.2 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0080803 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
871.4 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
871.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0016822 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
871.8 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.00647
872 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.017929 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
872.2 | 129.8101 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
872.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0032709
872.6 | 129.8101 | 0.0040291 | 0.37521 | -0.0016601 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
872.8 | 129.8101 | 0.0056289 | 0.4712 | 0.0015389 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
873 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
873.2 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.0048708
873.4 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.82882 | 0.0062209 | 0.45294 | 0.0048708
873.6 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
873.8 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
874 | 129.8101 | 0.0056289 | 0.4712 | 0.011135 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.11392 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
874.2 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0028892 | 0.06109 | 0.0062209 | 0.54889 | 0.00647
874.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
874.6 | 129.7141 | 0.0024299 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0019319 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.16505 | 0.00647
874.8 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
875 | 129.8101 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
875.2 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.014085 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
875.4 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
875.6 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
875.8 | 130.002 | 0.0040291 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.075065 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
876 | 129.9061 | 0.0024299 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
876.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.093666 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
876.4 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
876.6 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.26697 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
876.8 | 129.9061 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
877 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
877.2 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
877.4 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 8.3003e-05 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.35695 | 0.00647
877.6 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.68971 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
877.8 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.20987 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
878 | 129.9061 | 0.0040291 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
878.2 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
878.4 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.78732 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
878.6 | 129.9061 | 0.0056289 | 0.56715 | 0.004738 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
878.8 | 130.002 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
879 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.012868
879.2 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
879.4 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
879.6 | 130.002 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0099291 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.00647
879.8 | 130.098 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.019589 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.0048708
880 | 130.098 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.68971 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
880.2 | 130.098 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0080803 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
880.4 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
880.6 | 130.002 | 0.013626 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | -0.0015273
880.8 | 130.194 | 0.023223 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.40181 | 0.0060882 | 0.06109 | 0.0062209 | 0.35695 | 0.00647
881 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.010886 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
881.2 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0019319 | 0.40347 | 0.013427 | 0.40181 | 0.0092866 | 0.34898 | 0.0062209 | 0.35695 | 0.00647
881.4 | 130.098 | 0.0040291 | 0.27926 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0067301 | 2.0349 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0080692
881.6 | 130.002 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.0048708
881.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
882 | 130.098 | 0.0040291 | 0.56715 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
882.2 | 130.098 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.59537 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
882.4 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.0016718
882.6 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
882.8 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
883 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
883.2 | 130.3859 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.82882 | 0.0062209 | 0.35695 | 0.00647
883.4 | 130.5779 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
883.6 | 130.3859 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
883.8 | 130.2899 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
884 | 130.194 | 0.0056289 | 0.4712 | 0.0015389 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
884.2 | 130.194 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
884.4 | 130.098 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0083293 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.0048708
884.6 | 130.194 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.26697 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
884.8 | 130.194 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
885 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | -0.076363 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
885.2 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.66945 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0070285 | 0.59375 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
885.4 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
885.6 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0096794 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
885.8 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
886 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
886.2 | 130.098 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.73287 | 0.0062209 | 0.45294 | 0.0048708
886.4 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0032709
886.6 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.26697 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
886.8 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
887 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
887.2 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
887.4 | 130.098 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
887.6 | 130.098 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | -0.0028664 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
887.8 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
888 | 130.002 | 0.013626 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.009669
888.2 | 130.098 | 0.018424 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
888.4 | 130.098 | 0.042416 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.17102 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
888.6 | 129.8101 | 0.0056289 | 0.37521 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.015685 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
888.8 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.59375 | 0.014085 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
889 | 130.002 | 0.0056289 | 0.56715 | 0.0015389 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
889.2 | 129.9061 | 0.0056289 | 0.27926 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.11554 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
889.4 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
889.6 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.59537 | 0.0054293 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
889.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
890 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.21153 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.261 | 0.0048708
890.2 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
890.4 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
890.6 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
890.8 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
891 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
891.2 | 129.8101 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
891.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.78566 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
891.6 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
891.8 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
892 | 129.9061 | 0.0056289 | 0.27926 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
892.2 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
892.4 | 129.8101 | 0.0056289 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
892.6 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
892.8 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
893 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | -0.076363 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
893.2 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
893.4 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.66945 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
893.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
893.8 | 129.7141 | 0.0056289 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
894 | 129.7141 | 0.00083003 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.11554 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
894.2 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
894.4 | 129.7141 | 0.0072281 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
894.6 | 129.6182 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.93278 | 0.00647
894.8 | 129.7141 | 0.015225 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
895 | 129.1384 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.84279 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0014227 | 0.45294 | 0.0048708
895.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.014085 | 0.54092 | 0.0062209 | 0.45294 | 7.1911e-05
895.4 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
895.6 | 129.7141 | 0.0072281 | 0.37521 | 0.011135 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.68971 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
895.8 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
896 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
896.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.7468 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
896.4 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0032709
896.6 | 129.8101 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0080803 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0092866 | 0.15708 | 0.0062209 | 0.45294 | 0.00647
896.8 | 129.8101 | 0.0088273 | 0.37521 | 0.004738 | 0.18962 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0012893 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
897 | 129.8101 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
897.2 | 129.8101 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
897.4 | 129.9061 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
897.6 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
897.8 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
898 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
898.2 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
898.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
898.6 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
898.8 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
899 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
899.2 | 129.9061 | 0.012026 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.59537 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.0048708
899.4 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
899.6 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
899.8 | 130.002 | 0.010427 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.78566 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
900 | 129.9061 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | -0.0012672 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
900.2 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.84279 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0014227 | 0.45294 | 0.00647
900.4 | 130.002 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
900.6 | 130.002 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
900.8 | 130.002 | 0.0088273 | 0.37521 | 0.004738 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
901 | 130.002 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
901.2 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.013427 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
901.4 | 129.9061 | 0.034419 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.015026 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.261 | 0.00647
901.6 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.38156 | 0.022476 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
901.8 | 130.2899 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
902 | 130.098 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
902.2 | 130.098 | 0.012026 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
902.4 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 7.1911e-05
902.6 | 130.002 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.00033201 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
902.8 | 130.098 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
903 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.68971 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
903.2 | 130.098 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
903.4 | 130.098 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
903.6 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
903.8 | 129.3303 | 0.012026 | 0.4712 | 0.011135 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.68971 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
904 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | -0.076363 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
904.2 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.73287 | 0.0030219 | 0.45294 | 0.00647
904.4 | 130.002 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.0048708
904.6 | 130.098 | 0.013626 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
904.8 | 130.098 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
905 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.00647
905.2 | 130.098 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
905.4 | 130.194 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
905.6 | 130.2899 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.65085 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
905.8 | 130.4819 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
906 | 130.194 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.7468 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.73287 | 0.0062209 | 0.35695 | 0.00647
906.2 | 130.194 | 0.010427 | 0.56715 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0054293 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
906.4 | 130.098 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
906.6 | 130.3859 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
906.8 | 130.194 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.012619 | 0.45294 | 0.0048708
907 | 130.098 | 0.012026 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
907.2 | 130.098 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
907.4 | 130.194 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0028892 | 0.15708 | 0.0062209 | 0.45294 | 0.00647
907.6 | 130.194 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
907.8 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
908 | 130.002 | 0.012026 | 0.4712 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
908.2 | 130.098 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
908.4 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
908.6 | 130.002 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
908.8 | 130.002 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0032709
909 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
909.2 | 129.9061 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
909.4 | 130.098 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.35695 | 0.00647
909.6 | 130.098 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
909.8 | 130.002 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.012486 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
910 | 130.002 | 0.012026 | 0.4712 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.016626 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
910.2 | 130.194 | 0.020024 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
910.4 | 129.9061 | 0.026422 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.68971 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
910.6 | 130.002 | 0.044015 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.016626 | 0.49776 | 0.010886 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
910.8 | 129.9061 | 0.020024 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.018225 | 0.68971 | 0.017284 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
911 | 130.002 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.40181 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
911.2 | 130.002 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.00033201 | 0.40347 | 0.0086283 | 1.3615 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
911.4 | 130.002 | 0.010427 | 0.37521 | 0.0063372 | 0.18962 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.015817 | 0.45294 | 0.00647
911.6 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.00033201 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
911.8 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
912 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.017929 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
912.2 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
912.4 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.11392 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
912.6 | 129.8101 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
912.8 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
913 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
913.2 | 129.8101 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0070285 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
913.4 | 129.9061 | 0.010427 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
913.6 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
913.8 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
914 | 129.8101 | 0.0088273 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
914.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.0048708
914.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
914.6 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.0048708
914.8 | 129.8101 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0016822 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
915 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
915.2 | 130.002 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
915.4 | 129.9061 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
915.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.013427 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
915.8 | 129.8101 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.84279 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.06109 | 0.0062209 | 0.45294 | 0.00647
916 | 129.7141 | 0.0088273 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0014227 | 0.45294 | 0.00647
916.2 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.65085 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
916.4 | 129.8101 | 0.0056289 | 0.087319 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
916.6 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
916.8 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0016822 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0046217 | 0.45294 | 0.0048708
917 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
917.2 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.66945 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
917.4 | 129.6182 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.00033201 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0014227 | 0.45294 | 0.0048708
917.6 | 129.7141 | 0.0072281 | 0.27926 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
917.8 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
918 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | -0.0012672 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.011019 | 0.45294 | 0.00647
918.2 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.30582 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
918.4 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
918.6 | 129.7141 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.015026 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
918.8 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0030219 | 0.45294 | 0.00647
919 | 129.7141 | 0.0056289 | 0.27926 | 0.011135 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
919.2 | 129.7141 | 0.0072281 | 0.37521 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
919.4 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | -0.0015273
919.6 | 129.7141 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0070285 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0048708
919.8 | 129.7141 | 0.0056289 | 0.4712 | 0.004738 | 0.18962 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.78566 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
920 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.63692 | 0.0046217 | 0.45294 | 0.0048708
920.2 | 129.7141 | 0.0056289 | 0.37521 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
920.4 | 129.7141 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
920.6 | 129.7141 | 0.0088273 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
920.8 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.82882 | 0.0078201 | 0.45294 | 0.00647
921 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0092866 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
921.2 | 129.6182 | 0.015225 | 0.37521 | 0.004738 | 0.28557 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.78566 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
921.4 | 129.4263 | 0.0024299 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
921.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.011279 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
921.8 | 129.7141 | 0.0056289 | 0.18331 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.0080692
922 | 129.7141 | 0.0040291 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.73287 | 0.0046217 | 0.45294 | 0.00647
922.2 | 129.7141 | 0.0072281 | 0.66314 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0048708
922.4 | 129.4263 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0030219 | 0.35695 | 0.00647
922.6 | 129.7141 | 0.0056289 | 0.37521 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
922.8 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0096794 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
923 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
923.2 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
923.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.59375 | 0.0012893 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
923.6 | 129.8101 | 0.00083003 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
923.8 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
924 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
924.2 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.66945 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
924.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
924.6 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.003282 | 0.26697 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0092866 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
924.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
925 | 129.8101 | 0.0056289 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
925.2 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
925.4 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.26697 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
925.6 | 129.8101 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
925.8 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
926 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | -0.0017763 | 0.45294 | 0.00647
926.2 | 129.9061 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
926.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
926.6 | 129.8101 | 0.0072281 | 0.087319 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
926.8 | 129.9061 | 0.0056289 | 0.4712 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.0080692
927 | 129.9061 | 0.0056289 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.0080692
927.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
927.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | -0.0028664 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.16505 | 0.0048708
927.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
927.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | -0.078023 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
928 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.30582 | 0.010886 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
928.2 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.40181 | 0.0044883 | 0.44497 | 0.0094199 | 0.45294 | 0.00647
928.4 | 130.2899 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
928.6 | 130.098 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0080803 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0092866 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
928.8 | 130.002 | 0.010427 | 0.37521 | 0.004738 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
929 | 130.002 | 0.012026 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.019589 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
929.2 | 130.002 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.21153 | 0.011827 | 0.49776 | 0.0092866 | 0.44497 | 0.0094199 | 0.83679 | 0.00647
929.4 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0092866 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
929.6 | 130.098 | 0.0056289 | 0.27926 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0083293 | 0.40347 | 0.010228 | 0.30582 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
929.8 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | -0.0047263
930 | 130.002 | 0.0056289 | 0.37521 | 0.0031381 | 0.18962 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
930.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.84279 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0014227 | 0.45294 | 0.00647
930.4 | 130.002 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
930.6 | 130.098 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
930.8 | 130.2899 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.011019 | 0.45294 | 0.00647
931 | 130.194 | 0.0056289 | 0.37521 | 0.0031381 | 0.093666 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
931.2 | 130.3859 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
931.4 | 130.2899 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
931.6 | 130.194 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
931.8 | 130.194 | 0.0056289 | 0.7591 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
932 | 130.098 | 0.0056289 | 0.4712 | 0.004738 | 0.7654 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.017929 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
932.2 | 130.098 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
932.4 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
932.6 | 130.194 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.34898 | 0.0046217 | 0.35695 | 0.00647
932.8 | 130.098 | 0.0024299 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
933 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | -0.00017715 | 0.45294 | 0.00647
933.2 | 130.098 | 0.0056289 | 0.4712 | 0.0031381 | 0.38156 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
933.4 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
933.6 | 130.098 | 0.0056289 | 0.27926 | 0.0095362 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
933.8 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
934 | 130.098 | 0.0040291 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
934.2 | 130.098 | 0.0056289 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
934.4 | 130.098 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
934.6 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
934.8 | 130.098 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
935 | 129.7141 | 0.0056289 | 0.4712 | 0.0015389 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
935.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
935.4 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
935.6 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
935.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
936 | 130.002 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
936.2 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
936.4 | 129.9061 | 0.020024 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.009669
936.6 | 129.9061 | 0.03282 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | -0.0028664 | 0.30748 | 0.011827 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.261 | 0.00647
936.8 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.019824 | 0.49776 | 0.014085 | 0.73287 | 0.0030219 | 0.45294 | 0.00647
937 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.015026 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
937.2 | 129.9061 | 0.0056289 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 2.1309 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.012868
937.4 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
937.6 | 130.002 | 0.00083003 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.64488 | 0.00647
937.8 | 129.8101 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.59537 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
938 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0070285 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
938.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
938.4 | 129.9061 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.012619 | 0.54889 | 0.00647
938.6 | 129.7141 | 0.0024299 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | -0.0012672 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
938.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
939 | 129.8101 | 0.0056289 | 0.27926 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
939.2 | 129.7141 | 0.0040291 | 0.27926 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 7.1911e-05
939.4 | 129.7141 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
939.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
939.8 | 129.7141 | 0.0040291 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
940 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.7468 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
940.2 | 129.8101 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | 0.011019 | 0.45294 | 0.00647
940.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.49942 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
940.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
940.8 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
941 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
941.2 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
941.4 | 129.7141 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | -0.0028664 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
941.6 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0067301 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
941.8 | 129.8101 | 0.0056289 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.011268
942 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
942.2 | 129.7141 | 0.0056289 | 0.56715 | 0.0095362 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
942.4 | 129.7141 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.82882 | 0.0062209 | 0.45294 | 0.00647
942.6 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.7468 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
942.8 | 129.7141 | 0.0056289 | 0.37521 | 0.0079364 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
943 | 129.6182 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
943.2 | 129.7141 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
943.4 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
943.6 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
943.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
944 | 129.7141 | 0.0072281 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
944.2 | 129.6182 | 0.0072281 | 0.7591 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
944.4 | 129.6182 | 0.0072281 | 0.37521 | 0.004738 | 0.28557 | 0.012878 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
944.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
944.8 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
945 | 129.6182 | 0.0072281 | 0.37521 | 0.004738 | 0.7654 | 8.3003e-05 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
945.2 | 129.6182 | 0.0072281 | 0.37521 | 0.0031381 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.012868
945.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0012893 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
945.6 | 129.5222 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.0048708
945.8 | 129.6182 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
946 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
946.2 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
946.4 | 129.6182 | 0.0072281 | 0.27926 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0038295 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
946.6 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
946.8 | 129.6182 | 0.0072281 | 0.37521 | 0.004738 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
947 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.92481 | 0.0062209 | 0.45294 | 0.00647
947.2 | 129.9061 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0046217 | 0.54889 | 0.00647
947.4 | 129.6182 | 0.012026 | 0.37521 | 0.011135 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
947.6 | 129.6182 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0078201 | 0.261 | 0.00647
947.8 | 129.5222 | 0.018424 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.003531 | 0.30748 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
948 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
948.2 | 129.3303 | 0.0056289 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
948.4 | 129.6182 | 0.0072281 | 0.66314 | 0.0015389 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
948.6 | 129.6182 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.075065 | 0.0019319 | 0.40347 | 0.015026 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
948.8 | 129.6182 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
949 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
949.2 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
949.4 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
949.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.92481 | 0.0062209 | 0.45294 | 0.00647
949.8 | 129.7141 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
950 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
950.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
950.4 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.17102 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
950.6 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.11554 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
950.8 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.86139 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
951 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
951.2 | 129.7141 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0067301 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
951.4 | 129.7141 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | -0.0028664 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.74084 | 0.0048708
951.6 | 129.7141 | 0.0088273 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
951.8 | 129.7141 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
952 | 129.6182 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
952.2 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0083293 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
952.4 | 129.6182 | 0.0024299 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
952.6 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
952.8 | 129.6182 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
953 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.34898 | 0.0014227 | 0.45294 | 0.00647
953.2 | 129.7141 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
953.4 | 130.098 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
953.6 | 129.8101 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.65085 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0030219 | 0.54889 | 0.00647
953.8 | 129.7141 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
954 | 129.7141 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
954.2 | 129.7141 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.11392 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
954.4 | 129.7141 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
954.6 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
954.8 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
955 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
955.2 | 129.7141 | 0.010427 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
955.4 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.74084 | 0.00647
955.6 | 129.8101 | 0.010427 | 0.37521 | 0.0031381 | 0.093666 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
955.8 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
956 | 129.7141 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
956.2 | 129.9061 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
956.4 | 129.7141 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
956.6 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
956.8 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
957 | 129.7141 | 0.012026 | 0.37521 | 0.004738 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
957.2 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
957.4 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
957.6 | 129.8101 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
957.8 | 129.7141 | 0.012026 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.11554 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
958 | 129.7141 | 0.010427 | 0.4712 | 0.004738 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
958.2 | 129.8101 | 0.012026 | 0.7591 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
958.4 | 129.7141 | 0.012026 | 0.37521 | 0.004738 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
958.6 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
958.8 | 129.7141 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
959 | 129.7141 | 0.0088273 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
959.2 | 129.7141 | 0.010427 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 7.1911e-05
959.4 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.18962 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.68971 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
959.6 | 129.7141 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.26697 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.06109 | 0.0062209 | 0.45294 | 0.00647
959.8 | 129.8101 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.26697 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
960 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0099291 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
960.2 | 129.7141 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | -0.0015162 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
960.4 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.011528 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.45294 | 0.00647
960.6 | 129.9061 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
960.8 | 129.8101 | 0.012026 | 0.37521 | 0.0079364 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
961 | 129.7141 | 0.012026 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
961.2 | 129.6182 | 0.010427 | 0.27926 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
961.4 | 129.7141 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.014085 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
961.6 | 129.7141 | 0.010427 | 0.37521 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
961.8 | 129.8101 | 0.013626 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0032709
962 | 129.7141 | 0.012026 | 0.18331 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0016718
962.2 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.17102 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0030219 | 0.54889 | 0.00647
962.4 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
962.6 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
962.8 | 130.098 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
963 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
963.2 | 129.7141 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.26697 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
963.4 | 129.9061 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
963.6 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
963.8 | 129.8101 | 0.021623 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 1.0208 | 0.0062209 | 0.45294 | 0.00647
964 | 129.8101 | 0.03122 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
964.2 | 129.2343 | 0.012026 | 0.37521 | 0.011135 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.015026 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
964.4 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.30748 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
964.6 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.86139 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
964.8 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
965 | 129.9061 | 0.012026 | 0.56715 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
965.2 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0044883 | 0.54092 | 0.011019 | 0.54889 | 0.00647
965.4 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | -0.0019091 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
965.6 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.30582 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
965.8 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
966 | 129.8101 | 0.012026 | 0.4712 | 0.004738 | 0.66945 | -0.0015162 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
966.2 | 129.9061 | 0.013626 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.83679 | 0.00647
966.4 | 129.9061 | 0.013626 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
966.6 | 129.9061 | 0.013626 | 0.4712 | 0.011135 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
966.8 | 130.002 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
967 | 129.9061 | 0.012026 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.0038295 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
967.2 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
967.4 | 129.8101 | 0.012026 | 0.4712 | 0.011135 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0038295 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
967.6 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
967.8 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
968 | 129.8101 | 0.012026 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
968.2 | 129.7141 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | 0.0078201 | 0.45294 | 0.00647
968.4 | 129.5222 | 0.010427 | 0.37521 | 0.0031381 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
968.6 | 129.1384 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.45294 | 0.00647
968.8 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
969 | 129.7141 | 0.012026 | 0.27926 | 0.011135 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
969.2 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.54889 | 0.00647
969.4 | 129.7141 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.34898 | 0.0062209 | 0.54889 | 0.00647
969.6 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | -0.0015162 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
969.8 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
970 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
970.2 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
970.4 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.92481 | 0.0062209 | 0.54889 | 0.00647
970.6 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
970.8 | 130.002 | 0.013626 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
971 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.019589 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.0048708
971.2 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
971.4 | 130.002 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 8.3003e-05 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
971.6 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.30582 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
971.8 | 130.098 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
972 | 130.002 | 0.013626 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
972.2 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.0048708
972.4 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.54889 | 0.0048708
972.6 | 129.9061 | 0.013626 | 0.4712 | 0.0079364 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
972.8 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
973 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0038295 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
973.2 | 129.9061 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.64488 | 7.1911e-05
973.4 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
973.6 | 129.9061 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
973.8 | 130.002 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0030219 | 0.45294 | 0.00647
974 | 129.9061 | 0.013626 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
974.2 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
974.4 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
974.6 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | -0.00030988 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
974.8 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
975 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | -0.0012672 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
975.2 | 129.9061 | 0.012026 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
975.4 | 130.002 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
975.6 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0014227 | 0.45294 | 0.0048708
975.8 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
976 | 130.002 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
976.2 | 129.9061 | 0.013626 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
976.4 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.0032709
976.6 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | -0.0012672 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
976.8 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
977 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
977.2 | 129.9061 | 0.012026 | 0.27926 | -6.0896e-05 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
977.4 | 129.9061 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.011268
977.6 | 129.8101 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
977.8 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
978 | 129.8101 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
978.2 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.86139 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
978.4 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
978.6 | 129.9061 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
978.8 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
979 | 129.9061 | 0.010427 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
979.2 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
979.4 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
979.6 | 129.9061 | 0.010427 | 0.18331 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.0070285 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
979.8 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
980 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.17102 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
980.2 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.069058 | 0.00647
980.4 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.0048708
980.6 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
980.8 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
981 | 129.9061 | 0.010427 | 0.4712 | 0.004738 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
981.2 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
981.4 | 129.8101 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
981.6 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0046217 | 0.45294 | 0.00647
981.8 | 129.8101 | 0.010427 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
982 | 129.8101 | 0.012026 | 0.27926 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
982.2 | 129.8101 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 8.3003e-05 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
982.4 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
982.6 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
982.8 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0083293 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
983 | 129.5222 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
983.2 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
983.4 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
983.6 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
983.8 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
984 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
984.2 | 129.8101 | 0.015225 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.7468 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.15708 | 0.0062209 | 0.54889 | 0.00647
984.4 | 129.7141 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.013427 | 0.59375 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
984.6 | 129.8101 | 0.016825 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
984.8 | 129.9061 | 0.021623 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.0019319 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0030219 | 0.45294 | 0.00647
985 | 129.8101 | 0.020024 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
985.2 | 129.7141 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.018225 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
985.4 | 129.5222 | 0.023223 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
985.6 | 129.7141 | 0.026422 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.015026 | 0.49776 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.012868
985.8 | 129.8101 | 0.039217 | 0.4712 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.021424 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
986 | 129.8101 | 0.047214 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.023023 | 0.49776 | 0.015685 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
986.2 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.015026 | 0.49776 | 0.018884 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
986.4 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.30582 | 0.010886 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
986.6 | 129.8101 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.015026 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
986.8 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
987 | 129.8101 | 0.010427 | 0.087319 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.35695 | 0.0032709
987.2 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | -0.00030988 | 0.54092 | 0.0062209 | 0.261 | 0.00647
987.4 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
987.6 | 129.7141 | 0.010427 | 0.37521 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
987.8 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
988 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
988.2 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
988.4 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
988.6 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
988.8 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
989 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
989.2 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
989.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.26697 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
989.6 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
989.8 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
990 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
990.2 | 129.8101 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | -0.0028664 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
990.4 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
990.6 | 129.7141 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.69137 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.0080692
990.8 | 129.7141 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
991 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
991.2 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | -0.0012672 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
991.4 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
991.6 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | -0.0012672 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
991.8 | 129.7141 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.64488 | 0.00647
992 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
992.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
992.4 | 129.7141 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
992.6 | 129.7141 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
992.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
993 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.11554 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
993.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
993.4 | 129.7141 | 0.0088273 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
993.6 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0016822 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
993.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0079364 | 0.18962 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
994 | 129.7141 | 0.0088273 | 0.37521 | 0.004738 | 0.5735 | 0.012878 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
994.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
994.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
994.6 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
994.8 | 129.7141 | 0.0072281 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
995 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
995.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
995.4 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
995.6 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
995.8 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
996 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.012619 | 0.54889 | 0.00647
996.2 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
996.4 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.93278 | 0.00647
996.6 | 129.6182 | 0.0088273 | 0.27926 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
996.8 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
997 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
997.2 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
997.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0031381 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
997.6 | 129.7141 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.25303 | 0.014218 | 0.45294 | 0.00647
997.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
998 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
998.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
998.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | -0.0012672 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
998.6 | 129.6182 | 0.0056289 | 0.37521 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
998.8 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.34898 | 0.0062209 | 0.54889 | 0.00647
999 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
999.2 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.003282 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
999.4 | 129.6182 | 0.0056289 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
999.6 | 129.5222 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
999.8 | 129.6182 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1000 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | -0.0019091 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1000.2 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.011279 | 0.36296 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1000.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1000.6 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0062209 | 0.64488 | 0.00647
1000.8 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1001 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.59375 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1001.2 | 129.5222 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1001.4 | 129.5222 | 0.010427 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1001.6 | 129.4263 | 0.016825 | 0.4712 | 0.0063372 | 0.18962 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1001.8 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.018225 | 0.40181 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
1002 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.38156 | 8.3003e-05 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1002.2 | 129.6182 | 0.0088273 | 0.087319 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1002.4 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1002.6 | 129.6182 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | -0.0015273
1002.8 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.014467
1003 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1003.2 | 129.6182 | 0.0056289 | 0.4712 | 0.0095362 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0016718
1003.4 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1003.6 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1003.8 | 129.5222 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.016626 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1004 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
1004.2 | 129.6182 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
1004.4 | 129.6182 | 0.0056289 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.015026 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1004.6 | 129.6182 | 0.0056289 | 0.27926 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1004.8 | 129.2343 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | -0.0017763 | 0.45294 | 0.0048708
1005 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1005.2 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0030219 | 0.83679 | 0.0048708
1005.4 | 129.7141 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1005.6 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1005.8 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.011268
1006 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1006.2 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1006.4 | 129.6182 | 0.0056289 | 0.37521 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
1006.6 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1006.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
1007 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1007.2 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0028892 | 1.0208 | 0.0062209 | 0.45294 | 0.00647
1007.4 | 129.7141 | 0.0072281 | 0.27926 | 0.0031381 | 0.38156 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1007.6 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1007.8 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1008 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1008.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.35695 | 0.00647
1008.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0094199 | 0.45294 | 0.0048708
1008.6 | 129.7141 | 0.0056289 | 0.4712 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
1008.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1009 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1009.2 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1009.4 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.17102 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1009.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1009.8 | 129.7141 | 0.0056289 | 0.37521 | 0.0079364 | 0.38156 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.68971 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1010 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1010.2 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1010.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0016822 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1010.6 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.26697 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.92481 | 0.0062209 | 0.45294 | 0.00647
1010.8 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.010886 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1011 | 129.9061 | 0.024822 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
1011.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.013427 | 0.49776 | 0.0092866 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1011.4 | 129.8101 | 0.0056289 | -0.0086323 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1011.6 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.00033201 | 0.59537 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.261 | 0.0048708
1011.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0038295 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1012 | 129.9061 | 0.0056289 | 0.7591 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
1012.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1012.4 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1012.6 | 129.9061 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.11554 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.0048708
1012.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1013 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1013.2 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
1013.4 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0096794 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1013.6 | 130.2899 | -0.00076916 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1013.8 | 130.5779 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
1014 | 130.098 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1014.2 | 130.098 | 0.00083003 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.11554 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1014.4 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1014.6 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0046217 | 0.35695 | 0.00647
1014.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
1015 | 130.098 | 0.00083003 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1015.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1015.4 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.11392 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1015.6 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.093666 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1015.8 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1016 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.010886 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1016.2 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1016.4 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1016.6 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1016.8 | 129.9061 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1017 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1017.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 8.3003e-05 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1017.4 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.59537 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1017.6 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1017.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.7468 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1018 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1018.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1018.4 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1018.6 | 129.9061 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.59537 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1018.8 | 129.8101 | 0.016825 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
1019 | 129.8101 | 0.024822 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.7468 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.010886 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1019.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.018225 | 0.49776 | 0.014085 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1019.4 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.66945 | 0.0048812 | 0.65085 | 0.0067301 | 0.49942 | 0.016626 | 0.49776 | 0.012486 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1019.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1019.8 | 129.8101 | 0.0056289 | 0.37521 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1020 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.18962 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1020.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.7654 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.009669
1020.4 | 129.8101 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.73287 | 0.0046217 | 0.45294 | 0.00647
1020.6 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1020.8 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.66945 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0028892 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1021 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1021.2 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.7654 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1021.4 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1021.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0016822 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1021.8 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1022 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1022.2 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.69137 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1022.4 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1022.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.017929 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1022.8 | 129.7141 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.0080692
1023 | 129.6182 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1023.2 | 129.6182 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
1023.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1023.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
1023.8 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.06109 | 0.0062209 | 0.45294 | 0.00647
1024 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.18962 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1024.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1024.4 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1024.6 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.92481 | 0.0062209 | 0.45294 | 0.00647
1024.8 | 129.4263 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.0080692
1025 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0028892 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1025.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1025.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | -0.0019091 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1025.6 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1025.8 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1026 | 129.5222 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1026.2 | 129.3303 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1026.4 | 129.5222 | 0.0072281 | 0.27926 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1026.6 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | -0.0012672 | 0.40347 | 0.010228 | 0.40181 | 0.014085 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1026.8 | 129.5222 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.35695 | 0.0080692
1027 | 129.5222 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.00647
1027.2 | 129.5222 | 0.0072281 | 0.4712 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1027.4 | 129.5222 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1027.6 | 129.6182 | 0.0088273 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1027.8 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1028 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1028.2 | 129.5222 | 0.0088273 | 0.37521 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1028.4 | 129.5222 | 0.0088273 | 0.37521 | 0.004738 | 0.093666 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1028.6 | 129.4263 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.78566 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1028.8 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
1029 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.7654 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1029.2 | 129.5222 | 0.0088273 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1029.4 | 129.5222 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.59375 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1029.6 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1029.8 | 129.6182 | 0.012026 | 0.37521 | 0.0079364 | 0.093666 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1030 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1030.2 | 129.6182 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.013427 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1030.4 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1030.6 | 129.6182 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
1030.8 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1031 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1031.2 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1031.4 | 129.6182 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
1031.6 | 129.7141 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.82882 | 0.0062209 | 0.45294 | 0.00647
1031.8 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.075065 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.0048708
1032 | 129.6182 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1032.2 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.59537 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1032.4 | 129.6182 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.83679 | 0.00647
1032.6 | 129.7141 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1032.8 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1033 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1033.2 | 129.7141 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1033.4 | 129.7141 | 0.010427 | 0.4712 | 0.004738 | 0.38156 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1033.6 | 129.8101 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1033.8 | 129.6182 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.82882 | 0.0078201 | 0.45294 | 0.00647
1034 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.010886 | 0.15708 | 0.0062209 | 0.45294 | 0.00647
1034.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | 7.1911e-05
1034.4 | 129.7141 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1034.6 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.003531 | 0.40347 | 0.013427 | 0.40181 | 0.010886 | 0.82882 | 0.0062209 | 0.45294 | 0.00647
1034.8 | 129.8101 | 0.039217 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1035 | 129.7141 | 0.012026 | -0.58446 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.69137 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0016718
1035.2 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | -0.6927 | 0.0019319 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1035.4 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.95734 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.59375 | -0.027501 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1035.6 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.011279 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
1035.8 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.54889 | 0.00647
1036 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1036.2 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.78566 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1036.4 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.84279 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0030219 | 0.45294 | 0.00647
1036.6 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.015026 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.35695 | 0.0080692
1036.8 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | -0.0015273
1037 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0014227 | 0.54889 | 0.00647
1037.2 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.78566 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1037.4 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1037.6 | 129.3303 | 0.012026 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1037.8 | 129.6182 | 0.013626 | 0.4712 | 0.011135 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1038 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
1038.2 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1038.4 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1038.6 | 129.8101 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1038.8 | 130.002 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0083293 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1039 | 129.9061 | 0.012026 | 0.4712 | 0.004738 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1039.2 | 129.9061 | 0.012026 | 0.27926 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1039.4 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.0080692
1039.6 | 130.098 | 0.016825 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1039.8 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1040 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.0054293 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1040.2 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1040.4 | 129.9061 | 0.016825 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.74084 | 0.00647
1040.6 | 129.9061 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.16505 | 0.00647
1040.8 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1041 | 130.098 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1041.2 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1041.4 | 130.098 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1041.6 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.012619 | 0.54889 | 0.00647
1041.8 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1042 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1042.2 | 129.8101 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.003282 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.010886 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1042.4 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 8.3003e-05 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1042.6 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.00033201 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.261 | 0.00647
1042.8 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1043 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1043.2 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1043.4 | 129.8101 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.69137 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1043.6 | 130.194 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.17102 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1043.8 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1044 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.0080692
1044.2 | 129.7141 | 0.010427 | 0.37521 | 0.004738 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1044.4 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1044.6 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1044.8 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1045 | 129.8101 | 0.021623 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1045.2 | 129.7141 | 0.036018 | 0.56715 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.015026 | 0.59375 | 0.010886 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1045.4 | 129.9061 | 0.023223 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.00033201 | 0.40347 | 0.021424 | 0.59375 | 0.015685 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1045.6 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1045.8 | 129.7141 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.20987 | 0.0060882 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
1046 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 2.5642 | 0.00647
1046.2 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1046.4 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.65085 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1046.6 | 129.7141 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1046.8 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.17102 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1047 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.7468 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
1047.2 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1047.4 | 129.7141 | 0.010427 | 0.66314 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1047.6 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1047.8 | 129.6182 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1048 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1048.2 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0044883 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1048.4 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1048.6 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
1048.8 | 129.6182 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | -0.0028664 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1049 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1049.2 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | -0.0012672 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.35695 | 0.0048708
1049.4 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.11554 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0016718
1049.6 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1049.8 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1050 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1050.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
1050.4 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1050.6 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.7654 | 8.3003e-05 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1050.8 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1051 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.093666 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0092866 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1051.2 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.59375 | 0.0044883 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1051.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.34898 | 0.0078201 | 0.45294 | 0.00647
1051.6 | 129.5222 | 0.0072281 | 0.56715 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1051.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1052 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1052.2 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1052.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1052.6 | 129.5222 | 0.0072281 | 0.7591 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1052.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
1053 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1053.2 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.83679 | 0.00647
1053.4 | 129.5222 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1053.6 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1053.8 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.019589 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1054 | 129.5222 | 0.0072281 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
1054.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1054.4 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | -0.00030988 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1054.6 | 129.5222 | 0.0056289 | 0.4712 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
1054.8 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | -0.00017715 | 0.45294 | 0.00647
1055 | 129.5222 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1055.2 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1055.4 | 129.5222 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1055.6 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.069058 | 0.00647
1055.8 | 129.5222 | 0.0072281 | 0.37521 | 0.011135 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1056 | 129.4263 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1056.2 | 129.5222 | 0.0056289 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.261 | 0.00647
1056.4 | 129.4263 | 0.0056289 | 0.4712 | 0.0031381 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.88165 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
1056.6 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1056.8 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.26697 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1057 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1057.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0028892 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1057.4 | 129.5222 | 0.0072281 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1057.6 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1057.8 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.78732 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
1058 | 129.5222 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.019589 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
1058.2 | 129.5222 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1058.4 | 129.5222 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1058.6 | 129.5222 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1058.8 | 129.0424 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.011827 | 0.40181 | 0.010886 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
1059 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.86139 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1059.2 | 129.4263 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.075065 | 0.003531 | 0.40347 | 0.013427 | 0.40181 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1059.4 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.014478 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0030219 | 0.35695 | 0.00647
1059.6 | 129.4263 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1059.8 | 129.4263 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1060 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | -0.0015162 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1060.2 | 129.4263 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1060.4 | 129.4263 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1060.6 | 129.5222 | 0.0056289 | 0.66314 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
1060.8 | 129.5222 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1061 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1061.2 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.261 | 0.00647
1061.4 | 129.5222 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1061.6 | 129.2343 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.45294 | 0.00647
1061.8 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1062 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0016822 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1062.2 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
1062.4 | 129.4263 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1062.6 | 129.5222 | 0.0072281 | -0.0086323 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
1062.8 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1063 | 129.5222 | 0.0056289 | 0.7591 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1063.2 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.014085 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1063.4 | 129.4263 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
1063.6 | 129.2343 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
1063.8 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1064 | 129.5222 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.49942 | 0.015026 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
1064.2 | 129.6182 | 0.0056289 | 0.4712 | -0.0016601 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1064.4 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1064.6 | 129.5222 | 0.0056289 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.35695 | 0.0048708
1064.8 | 129.5222 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1065 | 129.4263 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
1065.2 | 129.6182 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1065.4 | 129.6182 | 0.0072281 | 0.37521 | 0.0095362 | 0.093666 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1065.6 | 129.6182 | 0.0056289 | 0.4712 | 0.0079364 | 0.28557 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1065.8 | 129.3303 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
1066 | 129.7141 | 0.0056289 | 0.37521 | 0.012735 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1066.2 | 129.3303 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
1066.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 1.0208 | 0.0062209 | 0.45294 | 0.00647
1066.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0030219 | 0.54889 | 0.00647
1066.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0095362 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1067 | 129.7141 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1067.2 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.11554 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1067.4 | 129.7141 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1067.6 | 129.7141 | 0.016825 | 0.18331 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1067.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.013427 | 0.49776 | 0.0092866 | 0.44497 | 0.0062209 | 0.54889 | 0.0048708
1068 | 129.8101 | 0.0056289 | 0.4712 | 0.0079364 | 0.18962 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.013427 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1068.2 | 129.7141 | 0.0056289 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.78566 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
1068.4 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.093666 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1068.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1068.8 | 129.8101 | 0.0056289 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1069 | 129.9061 | 0.0056289 | 0.27926 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | -0.026893 | 0.00647
1069.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
1069.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.012619 | 0.54889 | 0.00647
1069.6 | 129.8101 | 0.0040291 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | -0.0015273
1069.8 | 130.098 | 0.0056289 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.0032709
1070 | 130.3859 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1070.2 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1070.4 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.83679 | 0.00647
1070.6 | 129.8101 | 0.0056289 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1070.8 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.59537 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1071 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1071.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1071.4 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1071.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1071.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1072 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0062209 | 0.54889 | 0.0048708
1072.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1072.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1072.6 | 129.8101 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1072.8 | 129.9061 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.11554 | 0.0086283 | 0.40181 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.009669
1073 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.011019 | 0.54889 | 0.00647
1073.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1073.4 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1073.6 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
1073.8 | 129.8101 | 0.018424 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
1074 | 129.8101 | 0.037618 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1074.2 | 129.7141 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.016626 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1074.4 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0012893 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1074.6 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.012619 | 0.54889 | 0.00647
1074.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1075 | 129.7141 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.74084 | 0.00647
1075.2 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1075.4 | 129.7141 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1075.6 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1075.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
1076 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1076.2 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1076.4 | 129.6182 | 0.0072281 | 0.27926 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1076.6 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1076.8 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.013427 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1077 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1077.2 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0016822 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1077.4 | 129.5222 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.59375 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1077.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.075065 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1077.8 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1078 | 129.4263 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0099291 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1078.2 | 129.5222 | 0.0072281 | 0.087319 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0032709
1078.4 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1078.6 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | -0.00030988 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1078.8 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1079 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0078201 | 0.45294 | 0.00647
1079.2 | 129.5222 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1079.4 | 129.5222 | 0.012026 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0054293 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1079.6 | 129.4263 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
1079.8 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.7654 | 0.003282 | 0.45891 | 0.0051309 | 0.30748 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0094199 | 0.64488 | 0.00647
1080 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1080.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1080.4 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.0048708
1080.6 | 129.5222 | 0.0088273 | 0.4712 | 0.004738 | 0.18962 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1080.8 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
1081 | 129.5222 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0032709
1081.2 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.20987 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1081.4 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.35695 | 0.00647
1081.6 | 129.5222 | 0.0088273 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1081.8 | 129.5222 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1082 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1082.2 | 129.6182 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1082.4 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
1082.6 | 129.6182 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1082.8 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1083 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1083.2 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.093666 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1083.4 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
1083.6 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1083.8 | 129.6182 | 0.010427 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0070285 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1084 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1084.2 | 129.6182 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1084.4 | 129.7141 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1084.6 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1084.8 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1085 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1085.2 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.015026 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
1085.4 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1085.6 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0094199 | 0.35695 | 0.00647
1085.8 | 129.7141 | 0.03282 | 0.37521 | 0.0063372 | 0.093666 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1086 | 129.7141 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1086.2 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | -0.80259 | 0.0062209 | 0.54889 | 0.0048708
1086.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1086.6 | 129.8101 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.0086283 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1086.8 | 129.7141 | 0.012026 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1087 | 129.8101 | 0.012026 | 0.4712 | 0.0031381 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1087.2 | 129.8101 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1087.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.009669
1087.6 | 129.3303 | 0.012026 | 0.37521 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.20987 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1087.8 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1088 | 129.7141 | 0.012026 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1088.2 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1088.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0094199 | 0.45294 | 0.00647
1088.6 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0083293 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.261 | 0.00647
1088.8 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
1089 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1089.2 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1089.4 | 129.8101 | 0.013626 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1089.6 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1089.8 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1090 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1090.2 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1090.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1090.6 | 130.002 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1090.8 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1091 | 129.7141 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1091.2 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1091.4 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1091.6 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1091.8 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 8.3003e-05 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1092 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1092.2 | 129.8101 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
1092.4 | 129.7141 | 0.0088273 | 0.56715 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
1092.6 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0028892 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1092.8 | 129.7141 | 0.016825 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0080692
1093 | 129.6182 | 0.028021 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.012486 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1093.2 | 129.7141 | 0.050413 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.59537 | 0.021424 | 0.49776 | 0.014085 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1093.4 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1093.6 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1093.8 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.16505 | 0.00647
1094 | 129.7141 | 0.012026 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1094.2 | 129.7141 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1094.4 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1094.6 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1094.8 | 129.6182 | 0.012026 | 0.56715 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.0048708
1095 | 129.6182 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 8.3003e-05 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1095.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1095.4 | 129.6182 | 0.010427 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1095.6 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1095.8 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1096 | 129.6182 | 0.010427 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1096.2 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0054293 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1096.4 | 129.6182 | 0.010427 | 0.37521 | 0.0063372 | 0.86139 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1096.6 | 129.5222 | 0.012026 | 0.7591 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1096.8 | 129.6182 | 0.010427 | 0.37521 | 0.0015389 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1097 | 129.6182 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
1097.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1097.4 | 129.6182 | 0.0088273 | 0.37521 | 0.0095362 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1097.6 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.28557 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1097.8 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0070285 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1098 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1098.2 | 129.6182 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.68971 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1098.4 | 129.5222 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.17102 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1098.6 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1098.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.261 | 0.00647
1099 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.68971 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1099.2 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.069058 | 0.00647
1099.4 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | -0.0012672 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.012619 | 0.45294 | 0.00647
1099.6 | 129.5222 | 0.0072281 | 0.087319 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0054293 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1099.8 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1100 | 129.5222 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0016718
1100.2 | 129.3303 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0030219 | 0.54889 | 0.00647
1100.4 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
1100.6 | 129.5222 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1100.8 | 129.5222 | 0.0072281 | 0.27926 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
1101 | 129.4263 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1101.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1101.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1101.6 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1101.8 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.069058 | 0.00647
1102 | 129.4263 | 0.0056289 | 0.18331 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 7.1911e-05
1102.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1102.4 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.0054293 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1102.6 | 129.5222 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1102.8 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.92481 | 0.0062209 | 0.45294 | 0.00647
1103 | 129.4263 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1103.2 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.17102 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1103.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.0048708
1103.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1103.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1104 | 129.4263 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1104.2 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1104.4 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1104.6 | 129.5222 | 0.0056289 | 0.37521 | -6.0896e-05 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0048708
1104.8 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1105 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1105.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.30748 | 0.0086283 | 0.017929 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1105.4 | 129.5222 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
1105.6 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.012619 | 0.45294 | 0.00647
1105.8 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.00033201 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1106 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.84279 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1106.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.011268
1106.4 | 129.4263 | 0.0088273 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.78732 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1106.6 | 129.4263 | 0.0088273 | 0.37521 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.78566 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1106.8 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.30582 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1107 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1107.2 | 129.4263 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.018225 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1107.4 | 129.3303 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1107.6 | 129.4263 | 0.010427 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1107.8 | 129.3303 | 0.013626 | 0.37521 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0092866 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1108 | 129.3303 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.16505 | 0.00647
1108.2 | 129.4263 | 0.018424 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1108.4 | 129.3303 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1108.6 | 129.2343 | 0.018424 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.73287 | 0.0078201 | 0.35695 | 0.00647
1108.8 | 129.3303 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1109 | 129.3303 | 0.0072281 | 0.4712 | 0.004738 | 0.66945 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1109.2 | 129.3303 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1109.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1109.6 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0092866 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
1109.8 | 129.5222 | 0.0056289 | 0.4712 | -0.012856 | 0.5735 | 0.012878 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1110 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.010886 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1110.2 | 129.4263 | 0.0056289 | 0.4712 | 0.0063372 | 0.28557 | 0.0080803 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.010886 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1110.4 | 129.5222 | 0.0040291 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1110.6 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1110.8 | 129.4263 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0038295 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.261 | 0.00647
1111 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1111.2 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.73287 | -0.0017763 | 0.45294 | 0.00647
1111.4 | 129.6182 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0028892 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1111.6 | 129.4263 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1111.8 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1112 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | -0.012973 | 0.45294 | 0.0048708
1112.2 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | -0.00017715 | 0.64488 | 0.00647
1112.4 | 129.4263 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 7.1911e-05
1112.6 | 129.4263 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1112.8 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.012878 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1113 | 129.5222 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.20987 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1113.2 | 129.4263 | 0.0056289 | 0.4712 | 0.0079364 | 0.18962 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1113.4 | 129.5222 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0083293 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1113.6 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1113.8 | 129.5222 | 0.0072281 | 0.66314 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1114 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1114.2 | 129.4263 | 0.0056289 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1114.4 | 129.5222 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1114.6 | 129.4263 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1114.8 | 129.5222 | 0.0040291 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
1115 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.38156 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1115.2 | 129.4263 | 0.0056289 | 0.7591 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1115.4 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | -0.0015273
1115.6 | 129.4263 | 0.0056289 | 0.37521 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1115.8 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | -0.0015273
1116 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.93874 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1116.2 | 129.5222 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.84279 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
1116.4 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1116.6 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
1116.8 | 129.5222 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1117 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1117.2 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.009669
1117.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1117.6 | 129.4263 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
1117.8 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1118 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1118.2 | 129.5222 | 0.0072281 | 0.37521 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.261 | 0.00647
1118.4 | 129.4263 | 0.0056289 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1118.6 | 129.5222 | 0.0056289 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1118.8 | 129.5222 | 0.0056289 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1119 | 129.5222 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1119.2 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.7468 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
1119.4 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1119.6 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0094199 | 0.45294 | 0.0048708
1119.8 | 129.5222 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1120 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0046217 | 0.54889 | 0.00647
1120.2 | 129.5222 | 0.0056289 | 0.37521 | 0.0095362 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1120.4 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1120.6 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1120.8 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1121 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1121.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0016718
1121.4 | 129.4263 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1121.6 | 129.5222 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1121.8 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.84279 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1122 | 129.5222 | 0.0056289 | -0.0086323 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
1122.2 | 129.5222 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.83679 | 0.00647
1122.4 | 129.6182 | 0.00083003 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1122.6 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1122.8 | 129.6182 | 0.0056289 | 0.27926 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.20987 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1123 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1123.2 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0094199 | 0.45294 | 0.00647
1123.4 | 129.6182 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0014227 | 0.45294 | 0.00647
1123.6 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.82882 | 0.0062209 | 0.45294 | 0.00647
1123.8 | 129.5222 | 0.0056289 | 0.27926 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
1124 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.74084 | 0.0080692
1124.2 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
1124.4 | 129.5222 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
1124.6 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1124.8 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.014218 | 0.45294 | 0.00647
1125 | 129.5222 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1125.2 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.075065 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1125.4 | 129.5222 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.35695 | 0.0080692
1125.6 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1125.8 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1126 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0030219 | 0.93278 | 0.00647
1126.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1126.4 | 129.5222 | 0.0056289 | -0.0086323 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 7.1911e-05
1126.6 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1126.8 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1127 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1127.2 | 129.5222 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1127.4 | 129.5222 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | -0.026893 | 0.00647
1127.6 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1127.8 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.59537 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1128 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1128.2 | 129.6182 | 0.0072281 | 0.4712 | 0.004738 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1128.4 | 129.6182 | 0.0056289 | 0.27926 | -0.0016601 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1128.6 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0094199 | 0.35695 | 0.00647
1128.8 | 129.7141 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.00033201 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1129 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.30582 | 0.0012893 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1129.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1129.4 | 129.6182 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1129.6 | 129.6182 | 0.0056289 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.069058 | 0.00647
1129.8 | 129.6182 | 0.0072281 | -0.0086323 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0032709
1130 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1130.2 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0083293 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1130.4 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0030219 | 0.93278 | 0.00647
1130.6 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1130.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1131 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1131.2 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1131.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.28557 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1131.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0079364 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1131.8 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1132 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0016822 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1132.2 | 130.098 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1132.4 | 129.8101 | 0.0056289 | 0.56715 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1132.6 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0028892 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1132.8 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1133 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1133.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1133.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1133.6 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.013427 | 0.20987 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1133.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1134 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.011279 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.45294 | 0.0048708
1134.2 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | -0.0012672 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1134.4 | 129.9061 | 0.018424 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1134.6 | 129.9061 | 0.0088273 | 0.37521 | 0.0063372 | 0.86139 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.011827 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1134.8 | 129.8101 | 0.0056289 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1135 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.015026 | 0.40181 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1135.2 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.014085 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1135.4 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1135.6 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1135.8 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1136 | 130.002 | 0.0024299 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1136.2 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1136.4 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1136.6 | 130.194 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1136.8 | 130.3859 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1137 | 130.6738 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1137.2 | 130.098 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.16505 | 0.0048708
1137.4 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.59537 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1137.6 | 130.194 | 0.00083003 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1137.8 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.78566 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1138 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.26697 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1138.2 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1138.4 | 130.098 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1138.6 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1138.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
1139 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0032709
1139.2 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0028892 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1139.4 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1139.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.011279 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1139.8 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | -0.0012672 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.16505 | 0.00647
1140 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.17102 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1140.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1140.4 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1140.6 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.009669
1140.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1141 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.38156 | 0.011279 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1141.2 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
1141.4 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.59375 | 0.0060882 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1141.6 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1141.8 | 130.002 | 0.016825 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.011268
1142 | 129.9061 | 0.024822 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.013427 | 0.68971 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1142.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.0051309 | 0.49942 | 0.019824 | 0.49776 | 0.015685 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1142.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.019824 | 0.59375 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1142.6 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.30582 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1142.8 | 129.8101 | 0.0072281 | 0.37521 | 0.0095362 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1143 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.74084 | 0.00647
1143.2 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1143.4 | 129.9061 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1143.6 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.34898 | 0.0062209 | 0.54889 | 0.0080692
1143.8 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1144 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1144.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1144.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.014218 | 0.54889 | 0.00647
1144.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.74084 | 0.00647
1144.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
1145 | 129.6182 | 0.0056289 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.15708 | 0.0062209 | 0.45294 | 0.00647
1145.2 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1145.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1145.6 | 129.7141 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1145.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.69137 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1146 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.88331 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.011268
1146.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0048708
1146.4 | 129.7141 | 0.0072281 | 0.66314 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1146.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0012893 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1146.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1147 | 129.6182 | 0.0056289 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1147.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.86139 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0028892 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1147.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1147.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1147.8 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1148 | 129.6182 | 0.0072281 | 0.37521 | 0.0015389 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1148.2 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
1148.4 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.74084 | 0.00647
1148.6 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1148.8 | 129.2343 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1149 | 129.6182 | 0.010427 | 0.66314 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
1149.2 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 8.3003e-05 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.45294 | 0.00647
1149.4 | 129.6182 | 0.015225 | 0.18331 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1149.6 | 129.4263 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1149.8 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.38156 | 0.003282 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1150 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1150.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.011268
1150.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.7654 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1150.6 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1150.8 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1151 | 129.6182 | 0.0088273 | 0.18331 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
1151.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.017929 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1151.4 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.21153 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1151.6 | 129.4263 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1151.8 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | -0.0015273
1152 | 129.6182 | 0.010427 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1152.2 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.069058 | 0.00647
1152.4 | 129.7141 | 0.010427 | 0.27926 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
1152.6 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1152.8 | 129.6182 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.35695 | 0.00647
1153 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.7654 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1153.2 | 129.7141 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1153.4 | 129.6182 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.26697 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0014227 | 0.45294 | 0.00647
1153.6 | 129.7141 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1153.8 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.28557 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1154 | 129.6182 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1154.2 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.016626 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1154.4 | 129.7141 | 0.012026 | 0.4712 | 0.011135 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1154.6 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.66945 | 0.012878 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1154.8 | 129.7141 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.003282 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1155 | 129.7141 | 0.010427 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1155.2 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1155.4 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1155.6 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1155.8 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1156 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1156.2 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1156.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1156.6 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1156.8 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
1157 | 129.8101 | 0.012026 | 0.37521 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1157.2 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.016626 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1157.4 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.013427 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0032709
1157.6 | 129.9061 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1157.8 | 129.9061 | 0.016825 | 0.37521 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1158 | 129.8101 | 0.023223 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.010886 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1158.2 | 129.7141 | 0.036018 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.015026 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1158.4 | 129.9061 | 0.018424 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.93278 | 0.00647
1158.6 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1158.8 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1159 | 130.002 | 0.013626 | 0.37521 | 0.0063372 | 0.7654 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1159.2 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1159.4 | 129.9061 | 0.012026 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
1159.6 | 129.9061 | 0.013626 | 0.37521 | 0.012735 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1159.8 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1160 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1160.2 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1160.4 | 130.098 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0044883 | 0.73287 | 0.0094199 | 0.54889 | 0.00647
1160.6 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.82882 | 0.0062209 | 0.54889 | 0.00647
1160.8 | 129.6182 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1161 | 129.3303 | 0.016825 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1161.2 | 129.9061 | 0.015225 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1161.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.30582 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1161.6 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0099291 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.261 | 0.0048708
1161.8 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.011268
1162 | 129.8101 | 0.020024 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1162.2 | 129.9061 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.83679 | 0.00647
1162.4 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.003282 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1162.6 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1162.8 | 130.002 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.003282 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1163 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1163.2 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1163.4 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0054293 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1163.6 | 130.098 | 0.013626 | 0.27926 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1163.8 | 130.002 | 0.013626 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.261 | 0.00647
1164 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1164.2 | 130.002 | 0.013626 | 0.4712 | 0.0095362 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0038295 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1164.4 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0030219 | 0.54889 | 0.00647
1164.6 | 130.002 | 0.012026 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.30582 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1164.8 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0028892 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1165 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1165.2 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1165.4 | 130.002 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.59375 | 0.0012893 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1165.6 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1165.8 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | -0.0012672 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1166 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1166.2 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1166.4 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
1166.6 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1166.8 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.7654 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1167 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1167.2 | 129.9061 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1167.4 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1167.6 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1167.8 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1168 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.26697 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
1168.2 | 129.8101 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.009669
1168.4 | 129.7141 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1168.6 | 129.7141 | 0.020024 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1168.8 | 129.6182 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1169 | 129.7141 | 0.029621 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.015026 | 0.49776 | 0.012486 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1169.2 | 129.8101 | 0.050413 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.019824 | 0.49776 | 0.014085 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1169.4 | 129.8101 | 0.040817 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.020483 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
1169.6 | 129.8101 | 0.013626 | 0.4712 | 0.0015389 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1169.8 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.11392 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1170 | 129.8101 | 0.010427 | 0.4712 | 0.004738 | 0.66945 | 0.0016822 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1170.2 | 129.5222 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.011019 | 0.54889 | 0.00647
1170.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1170.6 | 130.098 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1170.8 | 129.5222 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1171 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1171.2 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1171.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1171.6 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1171.8 | 129.7141 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1172 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.00647
1172.2 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1172.4 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0070285 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.0080692
1172.6 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1172.8 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1173 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1173.2 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1173.4 | 129.8101 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.0048708
1173.6 | 129.7141 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1173.8 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1174 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0044883 | 0.15708 | 0.0062209 | 0.45294 | 0.00647
1174.2 | 129.7141 | 0.010427 | 0.56715 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.0038295 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1174.4 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
1174.6 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1174.8 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1175 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1175.2 | 129.6182 | 0.010427 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1175.4 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.78566 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1175.6 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.92481 | 0.0062209 | 0.45294 | 0.00647
1175.8 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.30582 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1176 | 129.7141 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1176.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0019319 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1176.4 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.015026 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1176.6 | 129.7141 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1176.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1177 | 129.7141 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1177.2 | 129.7141 | 0.010427 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.011268
1177.4 | 129.6182 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 7.1911e-05
1177.6 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | -0.00017715 | 0.45294 | 0.00647
1177.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1178 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.7468 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1178.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0019319 | -0.076363 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1178.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0014227 | 0.45294 | 0.00647
1178.6 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1178.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1179 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.78566 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1179.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1179.4 | 129.7141 | 0.0088273 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0046217 | 0.64488 | 0.00647
1179.6 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1179.8 | 129.7141 | 0.0072281 | 0.087319 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0054293 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
1180 | 129.7141 | 0.010427 | 0.37521 | 0.011135 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1180.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1180.4 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.74084 | 0.0080692
1180.6 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.012619 | 0.54889 | 0.00647
1180.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1181 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1181.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1181.4 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1181.6 | 129.6182 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.011019 | 0.54889 | 0.0080692
1181.8 | 129.6182 | 0.0088273 | 0.4712 | 0.0031381 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.261 | 0.0048708
1182 | 129.6182 | 0.010427 | 0.18331 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
1182.2 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1182.4 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1182.6 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.78732 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0032709
1182.8 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0028892 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1183 | 129.6182 | 0.0088273 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
1183.2 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
1183.4 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | -0.0028664 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.261 | 0.00647
1183.6 | 129.6182 | 0.0088273 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1183.8 | 129.6182 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1184 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0083293 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1184.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | -0.0019091 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1184.4 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1184.6 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.20987 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1184.8 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1185 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0030219 | 0.83679 | 0.00647
1185.2 | 129.6182 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1185.4 | 129.6182 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1185.6 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1185.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1186 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.17102 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.92481 | 0.0062209 | 0.54889 | 0.00647
1186.2 | 129.9061 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.261 | 0.00647
1186.4 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.88165 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1186.6 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 8.3003e-05 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1186.8 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1187 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1187.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1187.4 | 129.6182 | 0.0024299 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.74084 | 0.00647
1187.6 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1187.8 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1188 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1188.2 | 129.7141 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1188.4 | 129.7141 | 0.010427 | 0.4712 | 0.0079364 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1188.6 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1188.8 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1189 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1189.2 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0014227 | 0.45294 | 0.00647
1189.4 | 129.7141 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1189.6 | 129.7141 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.36296 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0030219 | 0.35695 | 0.00647
1189.8 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1190 | 129.9061 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.83679 | 0.00647
1190.2 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1190.4 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1190.6 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0092866 | 0.54092 | 0.0046217 | 0.35695 | 0.00647
1190.8 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1191 | 129.9061 | 0.039217 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.016626 | 0.59375 | 0.010886 | 0.54092 | 0.0062209 | 0.83679 | 0.00647
1191.2 | 129.8101 | 0.021623 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1191.4 | 129.8101 | 0.012026 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1191.6 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0062209 | 0.54889 | 0.00647
1191.8 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1192 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.7654 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0028892 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1192.2 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1192.4 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.009669
1192.6 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1192.8 | 130.002 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1193 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.012486 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1193.2 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1193.4 | 129.9061 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1193.6 | 130.002 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.009669
1193.8 | 130.002 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.012868
1194 | 130.002 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1194.2 | 130.098 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1194.4 | 130.098 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.00647
1194.6 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.26697 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.92481 | 0.0062209 | 0.45294 | 0.00647
1194.8 | 129.9061 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1195 | 129.8101 | 0.015225 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1195.2 | 129.4263 | 0.012026 | 0.66314 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1195.4 | 129.9061 | 0.016825 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1195.6 | 130.002 | 0.013626 | 0.37521 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1195.8 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1196 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.30582 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1196.2 | 129.9061 | 0.015225 | 0.18331 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1196.4 | 130.098 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
1196.6 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1196.8 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1197 | 129.7141 | 0.028021 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.016626 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1197.2 | 129.8101 | 0.015225 | 0.37521 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.20987 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1197.4 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.38156 | 8.3003e-05 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1197.6 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.35695 | 0.0048708
1197.8 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1198 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | -0.0012672 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1198.2 | 129.8101 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.11392 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1198.4 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0062209 | 0.54889 | 0.00647
1198.6 | 129.8101 | 0.012026 | 0.4712 | 0.012735 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1198.8 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0048812 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1199 | 129.7141 | 0.012026 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.069058 | 0.00647
1199.2 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.78566 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1199.4 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.7654 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1199.6 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.011279 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | 0.0062209 | 0.54889 | 0.00647
1199.8 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.011827 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1200 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.015026 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.35695 | 0.0080692
1200.2 | 129.7141 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1200.4 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1200.6 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.34898 | 0.0062209 | 0.54889 | 0.00647
1200.8 | 129.7141 | 0.012026 | 0.56715 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1201 | 129.7141 | 0.010427 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1201.2 | 129.5222 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.93874 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1201.4 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.45294 | 0.00647
1201.6 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1201.8 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0016822 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1202 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1202.2 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1202.4 | 129.6182 | 0.010427 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1202.6 | 129.6182 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.014467
1202.8 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.011019 | 0.069058 | 0.00647
1203 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1203.2 | 129.6182 | 0.0088273 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.0070285 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1203.4 | 129.6182 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0070285 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
1203.6 | 129.6182 | 0.0088273 | 0.66314 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1203.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.68971 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1204 | 129.5222 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1204.2 | 129.6182 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1204.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | -0.0012672 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1204.6 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | -0.020721
1204.8 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0044883 | 0.34898 | 0.0078201 | 0.54889 | 0.00647
1205 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.68971 | 0.014085 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1205.2 | 129.6182 | 0.010427 | 0.37521 | 0.0079364 | 0.47751 | 0.0080803 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1205.4 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.78566 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1205.6 | 129.4263 | 0.015225 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1205.8 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.68971 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1206 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1206.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1206.4 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1206.6 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1206.8 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1207 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1207.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0030219 | 0.54889 | 0.00647
1207.4 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1207.6 | 130.002 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1207.8 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1208 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1208.2 | 129.6182 | 0.0088273 | -0.0086323 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1208.4 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1208.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1208.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1209 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1209.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.92481 | 0.0078201 | 0.54889 | 0.00647
1209.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.7468 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1209.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1209.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.075065 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
1210 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1210.2 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.0080692
1210.4 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1210.6 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1210.8 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.0080692
1211 | 129.7141 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1211.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1211.4 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1211.6 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1211.8 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0070285 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1212 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1212.2 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1212.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1212.6 | 129.8101 | 0.0072281 | 0.4712 | -6.0896e-05 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1212.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.78566 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1213 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.0080692
1213.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1213.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1213.6 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1213.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1214 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1214.2 | 129.9061 | 0.0056289 | 0.18331 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1214.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | -0.0012672 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1214.6 | 129.9061 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1214.8 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.018225 | 0.49776 | 0.014085 | 0.63692 | 0.0046217 | 0.74084 | 0.00647
1215 | 129.9061 | 0.037618 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.010886 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1215.2 | 129.8101 | 0.016825 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.11392 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1215.4 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1215.6 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1215.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1216 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1216.2 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1216.4 | 129.9061 | 0.0072281 | 0.56715 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1216.6 | 129.9061 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1216.8 | 129.9061 | 0.0088273 | 0.18331 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1217 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1217.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1217.4 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.78566 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
1217.6 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.0054293 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1217.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.82882 | 0.0062209 | 0.45294 | 0.00647
1218 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1218.2 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0099291 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1218.4 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
1218.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1218.8 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.20987 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1219 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1219.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.011279 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
1219.4 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.11392 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1219.6 | 130.002 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1219.8 | 130.002 | 0.0056289 | 0.56715 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1220 | 130.002 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1220.2 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1220.4 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.010886 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1220.6 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.16505 | 0.00647
1220.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.010886 | 0.25303 | 0.0062209 | 0.54889 | 0.00647
1221 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1221.2 | 130.002 | 0.0072281 | 0.66314 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.69137 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1221.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1221.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1221.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1222 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.68971 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1222.2 | 130.002 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1222.4 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.49776 | 0.0092866 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
1222.6 | 129.9061 | 0.00083003 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1222.8 | 130.002 | 0.0056289 | 0.37521 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.0038295 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1223 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.35695 | 0.0048708
1223.2 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1223.4 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1223.6 | 130.2899 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.78732 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1223.8 | 130.7698 | 0.0088273 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1224 | 130.4819 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1224.2 | 130.2899 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.92481 | 0.0078201 | 0.54889 | 0.00647
1224.4 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.7654 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1224.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.11392 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1224.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1225 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1225.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.011268
1225.4 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1225.6 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1225.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.011279 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1226 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.36296 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1226.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1226.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.74084 | 0.00647
1226.6 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 8.3003e-05 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1226.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1227 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
1227.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0030219 | 0.54889 | 0.00647
1227.4 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1227.6 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0080692
1227.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1228 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | -0.21883 | 0.0080692
1228.2 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1228.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1228.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.014085 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1228.8 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.017677 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.012486 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1229 | 129.8101 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.015026 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1229.2 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.18962 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1229.4 | 129.7141 | 0.0072281 | 0.56715 | 0.0079364 | 0.38156 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.009669
1229.6 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.010886 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1229.8 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1230 | 129.9061 | 0.024822 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1230.2 | 129.8101 | 0.018424 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1230.4 | 129.8101 | 0.018424 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.92481 | 0.0062209 | 0.45294 | 0.00647
1230.6 | 129.8101 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.78732 | 0.011827 | 0.40181 | 0.0092866 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1230.8 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1231 | 129.8101 | 0.012026 | 0.4712 | 0.0079364 | 0.7654 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1231.2 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.20987 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1231.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1231.6 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1231.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0046217 | 0.45294 | 0.00647
1232 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1232.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0046217 | 0.35695 | 0.00647
1232.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.54889 | 0.0080692
1232.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1232.8 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1233 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1233.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1233.4 | 129.8101 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1233.6 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1233.8 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.15708 | 0.0062209 | 0.45294 | 0.00647
1234 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0044883 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1234.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1234.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.017929 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1234.6 | 129.8101 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.21153 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1234.8 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.64488 | 0.00647
1235 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0028892 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1235.2 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1235.4 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1235.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.34898 | 0.0094199 | 0.45294 | 0.00647
1235.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.78566 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1236 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1236.2 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1236.4 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.84279 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1236.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.82882 | 0.0078201 | 0.45294 | 0.00647
1236.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.00033201 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1237 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0032709
1237.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1237.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1237.6 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
1237.8 | 129.7141 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1238 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 8.3003e-05 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1238.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.78566 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1238.4 | 129.7141 | 0.0056289 | 0.85505 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1238.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1238.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1239 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.82882 | 0.0078201 | 0.45294 | 0.00647
1239.2 | 129.7141 | 0.0056289 | 0.56715 | 0.004738 | 0.38156 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.68971 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1239.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | -0.0028664 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.74084 | 0.00647
1239.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1239.8 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1240 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1240.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.069058 | 0.00647
1240.4 | 129.6182 | 0.00083003 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1240.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
1240.8 | 129.7141 | 0.0088273 | 0.18331 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1241 | 129.7141 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1241.2 | 129.7141 | 0.00083003 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.59537 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.069058 | 0.00647
1241.4 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1241.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1241.8 | 129.8101 | 0.0056289 | 0.37521 | 0.004738 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1242 | 129.8101 | 0.0072281 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1242.2 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0030219 | 0.74084 | 0.00647
1242.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.73287 | 0.0062209 | 0.45294 | 0.0080692
1242.6 | 129.8101 | 0.0056289 | 0.56715 | 0.012735 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.20987 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1242.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1243 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1243.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1243.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1243.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1243.8 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1244 | 129.7141 | -0.00076916 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1244.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.019589 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1244.4 | 129.8101 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0019319 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.261 | 0.00647
1244.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1244.8 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1245 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.015817 | 0.45294 | 0.00647
1245.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1245.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1245.6 | 129.7141 | 0.0024299 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1245.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.84279 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.011019 | 0.45294 | 0.00647
1246 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1246.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.012619 | 0.45294 | 0.00647
1246.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1246.6 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1246.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1247 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1247.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1247.4 | 129.7141 | 0.0056289 | 0.56715 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1247.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.012486 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1247.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1248 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1248.2 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1248.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1248.6 | 129.7141 | 0.0072281 | 0.4712 | -6.0896e-05 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1248.8 | 129.8101 | 0.0056289 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1249 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1249.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1249.4 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
1249.6 | 129.7141 | 0.0040291 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | -0.0028664 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1249.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1250 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.011268
1250.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1250.4 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1250.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1250.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1251 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1251.2 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1251.4 | 129.7141 | 0.0056289 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.54889 | 0.0032709
1251.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1251.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1252 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1252.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0016822 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1252.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1252.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0094199 | 0.35695 | 0.00647
1252.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1253 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1253.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1253.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.7654 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1253.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.7468 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1253.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1254 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1254.2 | 129.8101 | 0.00083003 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.21153 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.261 | 0.0032709
1254.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0083293 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.64488 | 0.00647
1254.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | -0.0019091 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1254.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.012619 | 0.45294 | 0.00647
1255 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1255.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1255.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1255.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.20987 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1255.8 | 129.8101 | 0.0056289 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1256 | 129.7141 | 0.0040291 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.261 | 0.00647
1256.2 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.013427 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1256.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.075065 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1256.6 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1256.8 | 129.7141 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.011268
1257 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1257.2 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1257.4 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1257.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.86139 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0028892 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1257.8 | 129.8101 | 0.0088273 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1258 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.11392 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1258.2 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
1258.4 | 129.9061 | 0.018424 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.06109 | 0.0062209 | 0.54889 | 0.00647
1258.6 | 129.9061 | 0.016825 | 0.66314 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.21153 | 0.015026 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1258.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.015026 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1259 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.010886 | 0.34898 | 0.0094199 | 0.45294 | 0.00647
1259.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.68971 | 0.010886 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1259.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | -0.0076652 | 0.49942 | 0.011827 | 0.49776 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1259.6 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1259.8 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1260 | 129.9061 | 0.0056289 | 0.56715 | 0.0015389 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1260.2 | 129.8101 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1260.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1260.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1260.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.093666 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1261 | 129.9061 | 0.00083003 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.74084 | 0.00647
1261.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1261.4 | 129.9061 | 0.0056289 | 0.4712 | 0.004738 | 0.28557 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1261.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1261.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1262 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1262.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1262.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1262.6 | 130.098 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1262.8 | 130.194 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1263 | 130.5779 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.012486 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1263.2 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1263.4 | 130.098 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1263.6 | 130.002 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1263.8 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1264 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0054293 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.012868
1264.2 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1264.4 | 130.002 | 0.00083003 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1264.6 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.88165 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1264.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1265 | 130.002 | 0.0072281 | 0.37521 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0083293 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1265.2 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.86139 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1265.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1265.6 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1265.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1266 | 130.002 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.015026 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1266.2 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1266.4 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.0048708
1266.6 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1266.8 | 129.9061 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.20987 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1267 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.7468 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1267.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1267.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1267.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1267.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1268 | 129.9061 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1268.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1268.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0016822 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1268.6 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1268.8 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.011268
1269 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0016718
1269.2 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1269.4 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1269.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1269.8 | 129.9061 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1270 | 129.9061 | 0.0056289 | 0.37521 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1270.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.34898 | 0.0078201 | 0.45294 | 0.00647
1270.4 | 129.9061 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1270.6 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1270.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1271 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.78566 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1271.2 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1271.4 | 129.9061 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1271.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1271.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.003282 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1272 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1272.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1272.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1272.6 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.11554 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1272.8 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1273 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.11392 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1273.2 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.012619 | 0.54889 | 0.00647
1273.4 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1273.6 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.38156 | 0.011279 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1273.8 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1274 | 129.9061 | 0.016825 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1274.2 | 129.9061 | 0.021623 | 0.4712 | 0.0063372 | 0.66945 | 0.011279 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.64488 | 0.00647
1274.4 | 129.8101 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.40181 | 0.0044883 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1274.6 | 129.9061 | 0.029621 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.012486 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1274.8 | 129.8101 | 0.03122 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1275 | 129.9061 | 0.040817 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.015026 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1275.2 | 130.098 | 0.039217 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.015026 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1275.4 | 129.5222 | 0.018424 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.015026 | 0.49776 | 0.010886 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1275.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.016626 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1275.8 | 129.6182 | 0.0072281 | 0.56715 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.014085 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1276 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.013427 | 0.49776 | 0.015685 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1276.2 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.015026 | 0.49776 | 0.017284 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1276.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.016626 | 0.59375 | 0.012486 | 0.54092 | 0.0046217 | 0.45294 | 0.0080692
1276.6 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.018225 | 0.59375 | 0.012486 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1276.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.019824 | 0.68971 | 0.012486 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1277 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.011279 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.014085 | 0.73287 | 0.0078201 | 0.45294 | 0.0080692
1277.2 | 129.8101 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.017284 | 0.63692 | 0.0078201 | 0.16505 | 0.00647
1277.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1277.6 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1277.8 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.0054293 | 0.40181 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1278 | 129.8101 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0046217 | 0.54889 | 0.0080692
1278.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0030219 | 0.54889 | 0.0080692
1278.4 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1278.6 | 129.8101 | 0.0056289 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1278.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.74084 | 0.00647
1279 | 129.9061 | 0.0056289 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1279.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1279.4 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1279.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1279.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1280 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0016822 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1280.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1280.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.014085 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1280.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0079364 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0012893 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1280.8 | 129.8101 | 0.0072281 | 0.7591 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1281 | 129.7141 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1281.2 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1281.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1281.6 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0019319 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1281.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1282 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1282.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1282.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1282.6 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.011279 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1282.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1283 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.016626 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1283.2 | 129.8101 | 0.0072281 | 0.37521 | -6.0896e-05 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1283.4 | 129.7141 | 0.0072281 | 0.7591 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1283.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1283.8 | 129.7141 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.0048708
1284 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0016822 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1284.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0016822 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1284.4 | 129.7141 | 0.0056289 | 0.27926 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1284.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0030219 | 0.54889 | 0.00647
1284.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1285 | 129.7141 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.34898 | 0.0078201 | 0.54889 | 0.00647
1285.2 | 129.7141 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1285.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | -0.0012672 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.0080692
1285.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.7654 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1285.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.59375 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1286 | 129.7141 | 0.0072281 | 0.27926 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1286.2 | 129.7141 | 0.0072281 | 0.66314 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1286.4 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1286.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1286.8 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
1287 | 129.7141 | 0.0072281 | 0.56715 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.009669
1287.2 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.66945 | 0.0080803 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1287.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.7468 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1287.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.7468 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1287.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.38156 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1288 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.86139 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1288.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
1288.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.86139 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1288.6 | 129.7141 | 0.0056289 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1288.8 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1289 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1289.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1289.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1289.6 | 129.7141 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0099291 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1289.8 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.0080692
1290 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1290.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.011279 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1290.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1290.6 | 129.7141 | 0.0072281 | 0.56715 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1290.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0070285 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1291 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.015026 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1291.2 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1291.4 | 129.7141 | 0.0056289 | 0.18331 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1291.6 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.012486 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1291.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1292 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
1292.2 | 129.7141 | 0.0072281 | 0.37521 | 0.012735 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1292.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1292.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1292.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0095362 | 0.28557 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1293 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1293.2 | 129.7141 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1293.4 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.92481 | 0.0078201 | 0.54889 | 0.0080692
1293.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1293.8 | 129.6182 | 0.0072281 | 0.4712 | 0.004738 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1294 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1294.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.010886 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1294.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.86139 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1294.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1294.8 | 129.6182 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.26697 | 0.011528 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.011019 | 0.45294 | 0.00647
1295 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1295.2 | 129.6182 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1295.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1295.6 | 129.7141 | 0.0072281 | 0.37521 | 0.0095362 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1295.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.69137 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1296 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1296.2 | 129.7141 | 0.0072281 | 0.56715 | 0.0095362 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1296.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.261 | 0.00647
1296.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1296.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.86139 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1297 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1297.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1297.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.7654 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1297.6 | 129.8101 | 0.00083003 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1297.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1298 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1298.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.011019 | 0.45294 | 0.00647
1298.4 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1298.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1298.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.012619 | 0.54889 | 0.00647
1299 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.012619 | 0.54889 | 0.00647
1299.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0095362 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1299.4 | 129.6182 | 0.00083003 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.83679 | 0.00647
1299.6 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0083293 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1299.8 | 129.6182 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0048708
1300 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1300.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.78732 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1300.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.003282 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1300.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.26697 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1300.8 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.26697 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1301 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1301.2 | 129.6182 | 0.0072281 | 0.66314 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1301.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.014085 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1301.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.0032709
1301.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1302 | 129.6182 | 0.0056289 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1302.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | -0.00030988 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1302.4 | 129.6182 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.7468 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1302.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.075065 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0030219 | 0.54889 | 0.0080692
1302.8 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.009669
1303 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1303.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.0048708
1303.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1303.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.7654 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1303.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1304 | 129.6182 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.069058 | 0.00647
1304.2 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1304.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1304.6 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.93278 | 0.0080692
1304.8 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1305 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1305.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1305.4 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1305.6 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1305.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.7654 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1306 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.011268
1306.2 | 129.6182 | 0.0072281 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1306.4 | 129.7141 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.261 | 0.00647
1306.6 | 129.2343 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1306.8 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1307 | 129.7141 | 0.0072281 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1307.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.18962 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1307.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1307.6 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.012878 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.45294 | 0.0080692
1307.8 | 129.7141 | 0.0072281 | 0.56715 | 0.012735 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1308 | 129.7141 | 0.0072281 | 0.56715 | 0.012735 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1308.2 | 129.7141 | 0.0072281 | 0.4712 | -6.0896e-05 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1308.4 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0083293 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.0080692
1308.6 | 129.6182 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1308.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.00647
1309 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | -0.00030988 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1309.2 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0046217 | 0.64488 | 0.0080692
1309.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1309.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.35695 | 0.0080692
1309.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1310 | 129.6182 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0070285 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1310.2 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1310.4 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1310.6 | 129.6182 | 0.0056289 | -0.0086323 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1310.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.014467
1311 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1311.2 | 129.7141 | 0.0072281 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.78732 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1311.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1311.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1311.8 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1312 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1312.2 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1312.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0028892 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1312.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1312.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.010886 | 0.44497 | 0.0062209 | 0.54889 | 0.0080692
1313 | 129.6182 | 0.0072281 | 0.4712 | 0.004738 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 7.1911e-05
1313.2 | 129.6182 | 0.0088273 | 0.18331 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0054293 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.012868
1313.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.7654 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.009669
1313.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1313.8 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1314 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1314.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0099291 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1314.4 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.69137 | 0.0038295 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1314.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1314.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1315 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1315.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1315.4 | 129.6182 | 0.00083003 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.069058 | 0.00647
1315.6 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1315.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.0080692
1316 | 129.6182 | 0.0024299 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.16505 | 0.00647
1316.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0015389 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1316.4 | 129.5222 | 0.0072281 | 0.087319 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1316.6 | 129.6182 | 0.0072281 | 0.7591 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1316.8 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.26697 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.82882 | 0.0078201 | 0.45294 | 0.00647
1317 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1317.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1317.4 | 129.4263 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
1317.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0083293 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1317.8 | 129.6182 | 0.0088273 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1318 | 129.5222 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.00647
1318.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.012878 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
1318.4 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1318.6 | 129.6182 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1318.8 | 129.5222 | 0.0088273 | 0.37521 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0032709
1319 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1319.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1319.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1319.6 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1319.8 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1320 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1320.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1320.4 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1320.6 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.014478 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1320.8 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1321 | 129.6182 | 0.010427 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1321.2 | 129.5222 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1321.4 | 129.5222 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1321.6 | 129.5222 | 0.012026 | 0.56715 | 0.011135 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1321.8 | 129.5222 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1322 | 129.3303 | 0.013626 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.82882 | 0.0078201 | 0.54889 | 0.00647
1322.2 | 129.5222 | 0.018424 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1322.4 | 129.4263 | 0.013626 | 0.56715 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.35695 | 0.011268
1322.6 | 129.3303 | 0.0072281 | 0.85505 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1322.8 | 129.5222 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1323 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.28557 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.00647
1323.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0083293 | 0.40347 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1323.4 | 129.5222 | 0.012026 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.009669
1323.6 | 129.6182 | 0.0072281 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1323.8 | 129.5222 | 0.0088273 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.0080692
1324 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1324.2 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | -0.078023 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1324.4 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1324.6 | 129.5222 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1324.8 | 129.5222 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1325 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1325.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.011019 | 0.45294 | 0.0080692
1325.4 | 129.6182 | 0.0088273 | 0.37521 | 0.0031381 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.012868
1325.6 | 129.6182 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1325.8 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0070285 | 0.59375 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1326 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0030219 | 0.45294 | 0.00647
1326.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.93874 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1326.4 | 129.6182 | 0.0088273 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.16505 | 0.00647
1326.6 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.011019 | 0.45294 | 0.00647
1326.8 | 129.4263 | 0.0088273 | 0.4712 | 0.011135 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1327 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0046217 | 0.54889 | 0.0080692
1327.2 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.82882 | 0.0078201 | 0.45294 | 0.00647
1327.4 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1327.6 | 129.4263 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1327.8 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1328 | 129.4263 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1328.2 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1328.4 | 129.5222 | 0.0088273 | 0.7591 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1328.6 | 129.6182 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.36296 | 0.0067301 | 0.59537 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1328.8 | 129.6182 | 0.013626 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1329 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1329.2 | 129.6182 | 0.012026 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0012893 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1329.4 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1329.6 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1329.8 | 129.6182 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1330 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1330.2 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.069058 | 0.0080692
1330.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1330.6 | 129.6182 | 0.013626 | 0.4712 | 0.0063372 | 0.95734 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1330.8 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.78566 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1331 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1331.2 | 129.7141 | 0.012026 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1331.4 | 129.4263 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.93874 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
1331.6 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1331.8 | 129.7141 | 0.010427 | 0.37521 | 0.0095362 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1332 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1332.2 | 129.7141 | 0.010427 | 0.66314 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1332.4 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1332.6 | 129.7141 | 0.012026 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1332.8 | 129.8101 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.21153 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.16505 | 0.00647
1333 | 129.7141 | 0.013626 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.30582 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1333.2 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0062209 | 0.54889 | 0.0080692
1333.4 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1333.6 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.003531 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1333.8 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.30582 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1334 | 129.7141 | 0.012026 | 0.4712 | 0.004738 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1334.2 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1334.4 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0044883 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1334.6 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1334.8 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1335 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.18962 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1335.2 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1335.4 | 129.8101 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1335.6 | 129.9061 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1335.8 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.011528 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.64488 | 0.00647
1336 | 129.9061 | 0.028021 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1336.2 | 129.7141 | 0.036018 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.59375 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1336.4 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1336.6 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
1336.8 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1337 | 129.9061 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.011268
1337.2 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1337.4 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1337.6 | 129.9061 | 0.012026 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1337.8 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1338 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1338.2 | 129.9061 | 0.013626 | 0.4712 | 0.011135 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1338.4 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.18962 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1338.6 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.261 | 0.0080692
1338.8 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1339 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1339.2 | 130.002 | 0.013626 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0028892 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1339.4 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1339.6 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.011528 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1339.8 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1340 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1340.2 | 129.9061 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1340.4 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1340.6 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.20987 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1340.8 | 129.3303 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1341 | 129.2343 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.012878 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1341.2 | 129.7141 | 0.015225 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.019589 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1341.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1341.6 | 129.8101 | 0.015225 | 0.66314 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.93278 | 0.0080692
1341.8 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.68971 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1342 | 129.9061 | 0.013626 | 0.4712 | 0.0079364 | 0.18962 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1342.2 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.015026 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1342.4 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1342.6 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
1342.8 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0070285 | 0.9776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1343 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1343.2 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.014218 | 0.54889 | 0.00647
1343.4 | 129.9061 | 0.013626 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1343.6 | 129.9061 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1343.8 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0014227 | 0.45294 | 0.00647
1344 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.26697 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.012619 | 0.45294 | 0.00647
1344.2 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1344.4 | 129.9061 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1344.6 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1344.8 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.0080692
1345 | 129.9061 | 0.015225 | 0.18331 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1345.2 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.26697 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1345.4 | 130.098 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1345.6 | 130.002 | 0.013626 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1345.8 | 129.8101 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1346 | 130.002 | 0.013626 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.7468 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.25303 | 0.0078201 | 0.45294 | 0.00647
1346.2 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1346.4 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1346.6 | 130.002 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1346.8 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1347 | 130.002 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0046217 | 0.45294 | 0.0080692
1347.2 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.26697 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1347.4 | 130.098 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1347.6 | 130.002 | 0.013626 | 0.66314 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.003531 | 0.69137 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1347.8 | 129.9061 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1348 | 129.9061 | 0.015225 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1348.2 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1348.4 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1348.6 | 130.002 | 0.013626 | 0.56715 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.78566 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1348.8 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1349 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1349.2 | 130.002 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0083293 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1349.4 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1349.6 | 130.002 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1349.8 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1350 | 130.002 | 0.013626 | 0.37521 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.11554 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1350.2 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.86139 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1350.4 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.011279 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1350.6 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1350.8 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.74084 | 0.00647
1351 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1351.2 | 129.8101 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1351.4 | 129.8101 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0030219 | 0.54889 | 0.00647
1351.6 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1351.8 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1352 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.25303 | 0.0062209 | 0.45294 | 0.0080692
1352.2 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1352.4 | 129.9061 | 0.012026 | 0.37521 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1352.6 | 129.9061 | 0.012026 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1352.8 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1353 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.0054293 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1353.2 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1353.4 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1353.6 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1353.8 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1354 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0094199 | 0.54889 | 0.00647
1354.2 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1354.4 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.82882 | 0.0062209 | 0.45294 | 0.00647
1354.6 | 130.002 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1354.8 | 129.8101 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1355 | 129.9061 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.261 | 0.00647
1355.2 | 129.8101 | 0.013626 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1355.4 | 129.8101 | 0.023223 | 0.4712 | 0.0063372 | 0.5735 | 0.0016822 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1355.6 | 129.6182 | 0.026422 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.012486 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1355.8 | 129.8101 | 0.052013 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.021424 | 0.49776 | 0.014085 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1356 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.011827 | 0.59375 | 0.018884 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1356.2 | 129.9061 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 1.2266 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0048708
1356.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1356.6 | 129.8101 | 0.015225 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1356.8 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.7468 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1357 | 129.7141 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.011268
1357.2 | 129.7141 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0099291 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
1357.4 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1357.6 | 129.6182 | 0.012026 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0030219 | 0.45294 | 0.0080692
1357.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1358 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1358.2 | 129.7141 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1358.4 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1358.6 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1358.8 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.82882 | 0.0078201 | 0.45294 | 0.00647
1359 | 129.7141 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.45294 | 0.00647
1359.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0044883 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1359.4 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.7654 | 0.0016822 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1359.6 | 129.7141 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1359.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.016626 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1360 | 129.7141 | 0.0088273 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.93278 | 0.00647
1360.2 | 129.7141 | 0.010427 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1360.4 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1360.6 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1360.8 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1361 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1361.2 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1361.4 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1361.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1361.8 | 129.3303 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
1362 | 129.6182 | 0.0088273 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1362.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1362.4 | 129.6182 | 0.0072281 | 0.56715 | 0.012735 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1362.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.26697 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.15708 | 0.0062209 | 0.45294 | 0.00647
1362.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1363 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1363.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.012878 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1363.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0015389 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1363.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.69137 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.069058 | 0.00647
1363.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1364 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1364.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1364.4 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1364.6 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
1364.8 | 129.6182 | 0.0088273 | 0.4712 | 0.0015389 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.30582 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1365 | 129.5222 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.93874 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1365.2 | 129.6182 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1365.4 | 129.6182 | 0.0072281 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.40347 | 0.015026 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.64488 | 0.011268
1365.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1365.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.011019 | 0.45294 | 0.00647
1366 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1366.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0046217 | 0.54889 | 0.0080692
1366.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.012868
1366.6 | 129.6182 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.00647
1366.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1367 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1367.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1367.4 | 129.7141 | 0.0072281 | 0.37521 | 0.012735 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1367.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1367.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | 0.0078201 | 0.45294 | 0.00647
1368 | 129.6182 | 0.0072281 | 0.4712 | 0.004738 | 0.38156 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1368.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.11554 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.0032709
1368.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1368.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1368.8 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.26697 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0046217 | 0.54889 | 0.00647
1369 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1369.2 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1369.4 | 129.7141 | 0.010427 | 0.087319 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1369.6 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.20987 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1369.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1370 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1370.2 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1370.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.18962 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1370.6 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.0080692
1370.8 | 129.7141 | 0.0056289 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1371 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0044883 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1371.2 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | -0.00030988 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1371.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1371.6 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.78732 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1371.8 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1372 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1372.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1372.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1372.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1372.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1373 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1373.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1373.4 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1373.6 | 129.7141 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1373.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1374 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1374.2 | 129.6182 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.30748 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1374.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.7468 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1374.6 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.069058 | 0.00647
1374.8 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.014085 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1375 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1375.2 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1375.4 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1375.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.95734 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1375.8 | 129.6182 | 0.0056289 | 0.4712 | 0.004738 | 0.95734 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.11392 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1376 | 129.7141 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1376.2 | 129.7141 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1376.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.014085 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1376.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1376.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1377 | 129.7141 | 0.0088273 | 0.18331 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.013427 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1377.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1377.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1377.6 | 129.7141 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0080692
1377.8 | 129.7141 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1378 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.86139 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1378.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0031381 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1378.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1378.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1378.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.11554 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1379 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
1379.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1379.4 | 129.7141 | 0.0088273 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1379.6 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.83679 | 0.00647
1379.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1380 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1380.2 | 129.8101 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.35695 | 0.00647
1380.4 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1380.6 | 129.8101 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1380.8 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1381 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1381.2 | 129.7141 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.64488 | 0.0080692
1381.4 | 129.8101 | 0.023223 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.010886 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1381.6 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.40181 | 0.012486 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1381.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1382 | 129.7141 | 0.0056289 | 0.56715 | 0.004738 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1382.2 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1382.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.003282 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1382.6 | 129.8101 | 0.0072281 | 0.56715 | 0.004738 | 0.47751 | 0.017677 | 0.45891 | 0.0051309 | 0.49942 | 0.013427 | 0.68971 | 0.010886 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1382.8 | 129.8101 | 0.0056289 | 0.66314 | 0.004738 | 0.66945 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.011827 | 0.49776 | 0.012486 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1383 | 129.8101 | 0.0072281 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1383.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1383.4 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1383.6 | 129.6182 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1383.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.012486 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1384 | 129.8101 | 0.0056289 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1384.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.011279 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1384.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
1384.6 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1384.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.92481 | 0.0078201 | 0.45294 | 0.00647
1385 | 129.8101 | 0.0072281 | 0.56715 | 0.0015389 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1385.2 | 129.8101 | 0.0088273 | 0.18331 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1385.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.069058 | 0.00647
1385.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.86139 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1385.8 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1386 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1386.2 | 129.8101 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0054293 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1386.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1386.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1386.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | -0.0015273
1387 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.73287 | 0.0062209 | 0.45294 | 0.00647
1387.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.47751 | 0.011279 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1387.4 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1387.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1387.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1388 | 130.098 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1388.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1388.4 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1388.6 | 130.002 | 0.0072281 | 0.66314 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1388.8 | 130.194 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1389 | 130.3859 | 0.0072281 | 0.18331 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0016718
1389.2 | 130.6738 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1389.4 | 130.5779 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1389.6 | 130.194 | 0.0056289 | 0.27926 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1389.8 | 130.2899 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.014218 | 0.54889 | 0.00647
1390 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.011268
1390.2 | 130.098 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1390.4 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.012619 | 0.54889 | 0.00647
1390.6 | 130.002 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1390.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1391 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1391.2 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.0086283 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1391.4 | 130.002 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1391.6 | 129.9061 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1391.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1392 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
1392.2 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1392.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1392.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1392.8 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1393 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
1393.2 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1393.4 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1393.6 | 130.002 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1393.8 | 130.002 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1394 | 130.002 | 0.0072281 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1394.2 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1394.4 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0060882 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1394.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.011019 | 0.45294 | 0.00647
1394.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1395 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1395.2 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1395.4 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1395.6 | 130.002 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.0048708
1395.8 | 130.002 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1396 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1396.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1396.4 | 130.098 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1396.6 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1396.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.00647
1397 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0062209 | 0.45294 | 0.00647
1397.2 | 130.002 | 0.0024299 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.16505 | 0.00647
1397.4 | 130.002 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1397.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1397.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1398 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.16505 | 0.00647
1398.2 | 129.7141 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1398.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1398.6 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.0080692
1398.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1399 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1399.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1399.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1399.6 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1399.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1400 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1400.2 | 129.9061 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1400.4 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1400.6 | 129.9061 | 0.0072281 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.25303 | 0.0062209 | 0.45294 | 0.00647
1400.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1401 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1401.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1401.4 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1401.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1401.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.011827 | 0.20987 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1402 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1402.2 | 129.7141 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0064811 | 0.65085 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
1402.4 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1402.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0014227 | 0.54889 | 0.00647
1402.8 | 129.9061 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.011019 | 0.54889 | 0.00647
1403 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1403.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 8.3003e-05 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.0080692
1403.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1403.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1403.8 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0054293 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1404 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1404.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1404.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1404.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1404.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.65085 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1405 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1405.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.00033201 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1405.4 | 129.8101 | 0.0072281 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1405.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0046217 | 0.54889 | 0.00647
1405.8 | 129.8101 | 0.0088273 | 0.18331 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0016718
1406 | 129.8101 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1406.2 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.68971 | 0.0028892 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1406.4 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1406.6 | 129.8101 | 0.012026 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1406.8 | 129.9061 | 0.013626 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1407 | 129.8101 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0044883 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1407.2 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.0080692
1407.4 | 129.8101 | 0.012026 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1407.6 | 129.8101 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1407.8 | 129.8101 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1408 | 129.8101 | 0.016825 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.92481 | 0.0078201 | 0.54889 | 0.00647
1408.2 | 129.7141 | 0.018424 | 0.4712 | 0.0063372 | 0.47751 | 0.0016822 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1408.4 | 129.8101 | 0.020024 | 0.7591 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1408.6 | 129.7141 | 0.026422 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.68971 | 0.010886 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1408.8 | 129.9061 | 0.040817 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.59375 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1409 | 129.9061 | 0.042416 | 0.56715 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.016626 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1409.2 | 129.8101 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1409.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.016626 | 0.40181 | 0.010886 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1409.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.016626 | 0.59375 | 0.012486 | 0.44497 | 0.014218 | 0.54889 | 0.0080692
1409.8 | 129.5222 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.015026 | 0.78566 | 0.012486 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1410 | 129.4263 | 0.0072281 | 0.37521 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.014085 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1410.2 | 129.8101 | 0.0056289 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.0092866 | 0.54092 | 0.0030219 | 0.45294 | 0.00647
1410.4 | 129.9061 | 0.0072281 | 0.66314 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1410.6 | 129.8101 | 0.0040291 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0099291 | 0.49942 | 0.015026 | 0.59375 | 0.010886 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1410.8 | 129.8101 | 0.0072281 | 0.56715 | 0.043124 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.016626 | 0.49776 | 0.018884 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1411 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.018225 | 0.49776 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1411.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.019824 | 0.59375 | 0.014085 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1411.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | -0.020461 | 0.49942 | 0.0086283 | 0.49776 | 0.010886 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1411.6 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.015685 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1411.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | -0.02656 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1412 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.034878 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1412.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 1.5006 | 0.0078201 | 0.54889 | 0.009669
1412.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.0080692
1412.6 | 129.8101 | 0.0024299 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 1.9804 | 0.0094199 | 0.64488 | 0.0080692
1412.8 | 129.8101 | 0.0024299 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.83679 | 0.0080692
1413 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1413.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1413.4 | 129.8101 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.03821 | 0.54889 | 0.0080692
1413.6 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.026881 | 0.73287 | 0.0062209 | 0.54889 | 0.009669
1413.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1414 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.013427 | -2.0934 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1414.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1414.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0044883 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1414.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1414.8 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1415 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1415.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1415.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.0054293 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1415.6 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0032709
1415.8 | 129.8101 | 0.0088273 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.35695 | 0.0048708
1416 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1416.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1416.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | -1.7543 | 0.0032709
1416.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1416.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1417 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | -0.0015273
1417.2 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1417.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0048708
1417.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.7468 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.16505 | 0.0080692
1417.8 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.35695 | 0.0080692
1418 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.0080692
1418.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0032709
1418.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.0048708
1418.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.74084 | 0.00647
1418.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1419 | 129.9061 | 0.0072281 | 0.4712 | 0.0015389 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1419.2 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.009669
1419.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0038295 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1419.6 | 129.8101 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1419.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1420 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | -0.017771 | 0.64488 | 0.0080692
1420.2 | 129.9061 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.0080692
1420.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0044883 | 0.92481 | 0.0078201 | 0.54889 | 0.0080692
1420.6 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1420.8 | 129.9061 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.30748 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0048708
1421 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0044883 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1421.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1421.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.014218 | 0.54889 | 0.0080692
1421.6 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0044883 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1421.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0030219 | 0.54889 | 0.0080692
1422 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1422.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1422.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.03686
1422.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.014218 | 0.54889 | 0.00647
1422.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1423 | 129.8101 | 0.0072281 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | -0.0063255
1423.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1423.4 | 129.8101 | 0.0072281 | 0.37521 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1423.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1423.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1424 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1424.2 | 129.9061 | 0.010427 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.0080692
1424.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1424.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1424.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | -0.017522
1425 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.011268
1425.2 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1425.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1425.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1425.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1426 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.26697 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1426.2 | 129.8101 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1426.4 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0054293 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1426.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.69137 | 0.0038295 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1426.8 | 129.8101 | 0.0072281 | 0.56715 | 0.011135 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1427 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1427.2 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1427.4 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1427.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1427.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1428 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0030219 | 0.54889 | 0.0080692
1428.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.17102 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1428.4 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1428.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.86139 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.010886 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1428.8 | 129.8101 | 0.0072281 | 0.37521 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.0080692
1429 | 129.8101 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1429.2 | 129.8101 | 0.0072281 | 0.18331 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0032709
1429.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.86139 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1429.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1429.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0015389 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1430 | 129.7141 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0080692
1430.2 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0070285 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1430.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1430.6 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1430.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1431 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1431.2 | 130.002 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0048812 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1431.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.30748 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1431.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.83679 | 0.00647
1431.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.34898 | 0.0078201 | 0.54889 | 0.00647
1432 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1432.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1432.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0095362 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.009669
1432.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.7654 | 0.0016822 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1432.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1433 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1433.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.64488 | 0.00647
1433.4 | 129.8101 | 0.0056289 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1433.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1433.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1434 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1434.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1434.4 | 129.7141 | 0.0072281 | 0.56715 | 0.0095362 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1434.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 1.0208 | 0.0062209 | 0.54889 | 0.00647
1434.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1435 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1435.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.0080692
1435.4 | 129.7141 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0094199 | 0.83679 | 0.0080692
1435.6 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.011019 | 0.45294 | 0.0080692
1435.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1436 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1436.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1436.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0012893 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1436.6 | 129.7141 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0080692
1436.8 | 129.7141 | 0.0072281 | 0.56715 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1437 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1437.2 | 129.7141 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1437.4 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1437.6 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.009669
1437.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.16505 | 0.00647
1438 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.15708 | 0.0078201 | 0.54889 | 0.00647
1438.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | -0.0028664 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0080692
1438.4 | 129.7141 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1438.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1438.8 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1439 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.014218 | 0.54889 | 0.00647
1439.2 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1439.4 | 129.6182 | 0.0072281 | 0.56715 | 0.011135 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1439.6 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1439.8 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0032709
1440 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1440.2 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.78732 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.0080692
1440.4 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.0080692
1440.6 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1440.8 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1441 | 129.3303 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1441.2 | 129.5222 | 0.0088273 | 0.4712 | 0.0079364 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1441.4 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1441.6 | 129.6182 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1441.8 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.075065 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1442 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1442.2 | 129.4263 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1442.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1442.6 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1442.8 | 129.6182 | 0.0088273 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0032709
1443 | 129.7141 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0080692
1443.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0079364 | 0.66945 | 8.3003e-05 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1443.4 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1443.6 | 129.5222 | 0.010427 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1443.8 | 129.6182 | 0.013626 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1444 | 129.6182 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1444.2 | 129.6182 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1444.4 | 129.5222 | 0.015225 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1444.6 | 129.3303 | 0.0088273 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1444.8 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.88165 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1445 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | -0.48216 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.013427 | 0.59375 | 0.012486 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1445.2 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.36296 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.010886 | 0.34898 | 0.0062209 | 0.45294 | 0.0080692
1445.4 | 129.7141 | 0.0088273 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1445.6 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.030213 | 0.54889 | 0.0080692
1445.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | -0.00030988 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1446 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1446.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.18962 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1446.4 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1446.6 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1446.8 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1447 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
1447.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1447.4 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1447.6 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1447.8 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1448 | 129.7141 | 0.0040291 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1448.2 | 129.7141 | 0.010427 | 0.37521 | -6.0896e-05 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.30582 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1448.4 | 129.6182 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1448.6 | 129.6182 | 0.010427 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1448.8 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1449 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.7654 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1449.2 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1449.4 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0096794 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1449.6 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1449.8 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1450 | 129.6182 | 0.010427 | -0.0086323 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.012868
1450.2 | 129.6182 | 0.012026 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0019319 | 0.11554 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1450.4 | 129.7141 | 0.013626 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1450.6 | 129.7141 | 0.013626 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1450.8 | 129.7141 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.012868
1451 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1451.2 | 129.7141 | 0.013626 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1451.4 | 129.7141 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.20987 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1451.6 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1451.8 | 129.6182 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.15708 | 0.0062209 | 0.54889 | 0.00647
1452 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1452.2 | 129.7141 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1452.4 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1452.6 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1452.8 | 129.8101 | 0.012026 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1453 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1453.2 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1453.4 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1453.6 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.011279 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1453.8 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1454 | 129.8101 | 0.010427 | 0.66314 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1454.2 | 129.8101 | 0.012026 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.59537 | 0.0086283 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1454.4 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.010886 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1454.6 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.36296 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1454.8 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1455 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0099291 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.261 | 0.00647
1455.2 | 129.8101 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1455.4 | 129.8101 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1455.6 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1455.8 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1456 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1456.2 | 129.9061 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.00033201 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1456.4 | 129.8101 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.40181 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1456.6 | 129.8101 | 0.036018 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.74084 | 0.0080692
1456.8 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.012486 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1457 | 129.8101 | 0.015225 | 0.4712 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1457.2 | 130.098 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | -0.36592 | 0.0060882 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1457.4 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 1.4126 | 0.00647
1457.6 | 130.002 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1457.8 | 129.9061 | 0.015225 | 0.7591 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1458 | 130.002 | 0.013626 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0048708
1458.2 | 129.9061 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1458.4 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1458.6 | 129.6182 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
1458.8 | 129.9061 | 0.015225 | 0.18331 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0032709
1459 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0028892 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1459.2 | 130.002 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1459.4 | 129.9061 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1459.6 | 129.8101 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1459.8 | 129.6182 | 0.012026 | 0.4712 | 0.0079364 | 0.28557 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1460 | 129.5222 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1460.2 | 129.8101 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0014227 | 0.45294 | 0.0080692
1460.4 | 129.8101 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0099291 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.0080692
1460.6 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1460.8 | 129.9061 | 0.012026 | 0.66314 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1461 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0016822 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.82882 | 0.0062209 | 0.54889 | 0.0080692
1461.2 | 130.002 | 0.015225 | 0.56715 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1461.4 | 130.002 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 1.0208 | 0.0078201 | 0.54889 | 0.00647
1461.6 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1461.8 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1462 | 130.098 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.11554 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1462.2 | 130.098 | 0.015225 | 0.37521 | 0.011135 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.0038295 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1462.4 | 130.098 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.011268
1462.6 | 129.9061 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1462.8 | 130.098 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0019319 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.35695 | 0.00647
1463 | 130.098 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0032709
1463.2 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1463.4 | 130.098 | 0.013626 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1463.6 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1463.8 | 130.002 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1464 | 130.002 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0012893 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1464.2 | 130.2899 | 0.013626 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0046217 | 0.54889 | 0.00647
1464.4 | 130.002 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1464.6 | 130.002 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1464.8 | 130.002 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.26697 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.0080692
1465 | 130.002 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1465.2 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1465.4 | 130.002 | 0.012026 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1465.6 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1465.8 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0083293 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1466 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.21153 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1466.2 | 129.9061 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.15708 | 0.0078201 | 0.54889 | 0.00647
1466.4 | 129.9061 | 0.010427 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1466.6 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0016822 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.45294 | 0.0080692
1466.8 | 129.9061 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1467 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1467.2 | 129.9061 | 0.023223 | 0.56715 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1467.4 | 129.9061 | 0.045615 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.015026 | 0.59375 | 0.010886 | 0.63692 | 0.0078201 | 0.45294 | 0.0032709
1467.6 | 129.8101 | 0.012026 | 0.7591 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.017284 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1467.8 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1468 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.011279 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.45294 | 0.00647
1468.2 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.00647
1468.4 | 129.9061 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1468.6 | 129.8101 | 0.012026 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1468.8 | 129.9061 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1469 | 129.8101 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.0054293 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1469.2 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.25303 | 0.0078201 | 0.54889 | 0.00647
1469.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1469.6 | 129.8101 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1469.8 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1470 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1470.2 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1470.4 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1470.6 | 129.8101 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1470.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.00647
1471 | 129.8101 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1471.2 | 129.7141 | 0.010427 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1471.4 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1471.6 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1471.8 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1472 | 129.7141 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1472.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0012893 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1472.4 | 129.6182 | 0.0088273 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.00647
1472.6 | 129.7141 | 0.012026 | 0.37521 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.009669
1472.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0031381 | 0.47751 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1473 | 129.7141 | 0.0088273 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1473.2 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.17102 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1473.4 | 129.7141 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.011268
1473.6 | 129.7141 | 0.0088273 | 0.56715 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1473.8 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1474 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1474.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1474.4 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1474.6 | 129.4263 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1474.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1475 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1475.2 | 129.6182 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 7.1911e-05
1475.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0044883 | 0.25303 | 0.0078201 | 0.54889 | 0.0080692
1475.6 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1475.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1476 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1476.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1476.4 | 129.4263 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.003531 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1476.6 | 129.6182 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1476.8 | 129.6182 | 0.018424 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.40181 | 0.010886 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1477 | 129.5222 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1477.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1477.4 | 129.5222 | 0.0056289 | 0.7591 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | -0.69867 | 0.0048708
1477.6 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1477.8 | 129.4263 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.16505 | 0.00647
1478 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1478.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0031381 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1478.4 | 129.6182 | 0.0072281 | 0.66314 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1478.6 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1478.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0016822 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.25303 | 0.0078201 | 0.54889 | 0.00647
1479 | 129.7141 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.011019 | 0.54889 | 0.0080692
1479.2 | 129.6182 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1479.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1479.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1479.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1480 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1480.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.0080692
1480.4 | 129.7141 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1480.6 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1480.8 | 129.7141 | 0.0072281 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1481 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1481.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1481.4 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1481.6 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.00647
1481.8 | 129.7141 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1482 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1482.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1482.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1482.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0012893 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1482.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1483 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.28557 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1483.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1483.4 | 129.8101 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.014218 | 0.54889 | 0.0080692
1483.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.017929 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1483.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.00647
1484 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0016822 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1484.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1484.4 | 129.9061 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1484.6 | 129.9061 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1484.8 | 129.8101 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1485 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.0080692
1485.2 | 129.9061 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1485.4 | 130.002 | 0.013626 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1485.6 | 130.002 | 0.024822 | 0.4712 | 0.0079364 | 0.5735 | 0.0096794 | 0.45891 | 0.0051309 | 0.40347 | 0.015026 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1485.8 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.40181 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1486 | 130.002 | 0.0072281 | 1.047 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.78566 | 0.010886 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1486.2 | 129.9061 | 0.0072281 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1486.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.0054293 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1486.6 | 130.194 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0083293 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0080692
1486.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1487 | 130.002 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1487.2 | 129.9061 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0014227 | 0.45294 | 0.00647
1487.4 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1487.6 | 130.194 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1487.8 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.30748 | 0.0038295 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1488 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1488.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0062209 | 0.54889 | 0.00647
1488.4 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0048812 | 0.17102 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1488.6 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1488.8 | 130.002 | 0.0056289 | 0.7591 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.11554 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1489 | 130.098 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1489.2 | 130.2899 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0044883 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1489.4 | 130.5779 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.0038295 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1489.6 | 130.4819 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.0054293 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1489.8 | 130.2899 | 0.0056289 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.30582 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1490 | 130.194 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1490.2 | 130.098 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0032709
1490.4 | 130.194 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1490.6 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1490.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1491 | 130.098 | 0.0072281 | 0.37521 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.003531 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1491.2 | 130.002 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0012893 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1491.4 | 130.002 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.069058 | 0.00647
1491.6 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1491.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1492 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1492.2 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1492.4 | 130.098 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1492.6 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0028892 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1492.8 | 130.002 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0083293 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1493 | 130.002 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1493.2 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1493.4 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.009669
1493.6 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1493.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1494 | 130.098 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.73287 | 0.0078201 | 0.45294 | 0.0080692
1494.2 | 130.098 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1494.4 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1494.6 | 130.002 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1494.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.009669
1495 | 130.002 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1495.2 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.64488 | 0.00647
1495.4 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1495.6 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1495.8 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1496 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1496.2 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.28557 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1496.4 | 130.002 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1496.6 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.26697 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1496.8 | 130.002 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1497 | 130.002 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1497.2 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1497.4 | 130.098 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1497.6 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0054293 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1497.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1498 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.009669
1498.2 | 130.002 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.0054293 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1498.4 | 130.002 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.012868
1498.6 | 130.002 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1498.8 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.30582 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1499 | 129.9061 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1499.2 | 130.002 | 0.0088273 | 0.4712 | 0.0063372 | 0.7654 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1499.4 | 130.098 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.25303 | 0.0078201 | 0.54889 | 0.00647
1499.6 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0054293 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1499.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1500 | 130.002 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1500.2 | 130.002 | 0.012026 | 0.56715 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1500.4 | 130.098 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1500.6 | 130.098 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1500.8 | 130.098 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1501 | 130.002 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1501.2 | 129.9061 | 0.016825 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1501.4 | 130.002 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1501.6 | 129.9061 | 0.021623 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
1501.8 | 129.6182 | 0.021623 | 0.37521 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1502 | 129.8101 | 0.024822 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.0080692
1502.2 | 129.8101 | 0.020024 | 0.4712 | 0.0063372 | 0.28557 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1502.4 | 129.8101 | 0.023223 | 0.56715 | 0.0063372 | 0.66945 | 0.003282 | 0.45891 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1502.6 | 129.7141 | 0.024822 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1502.8 | 129.8101 | 0.037618 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.013427 | 0.49776 | 0.010886 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1503 | 129.9061 | 0.037618 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1503.2 | 130.002 | 0.042416 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.010886 | 0.54092 | 0.0078201 | 0.35695 | 0.0032709
1503.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.88165 | 0.012486 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1503.6 | 129.7141 | 0.0088273 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.016626 | 0.59375 | 0.012486 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1503.8 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1504 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.010886 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1504.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.014085 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1504.4 | 129.4263 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.59375 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1504.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.018225 | 0.30582 | 0.010886 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1504.8 | 129.5222 | 0.0088273 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.010886 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1505 | 129.2343 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.016626 | 0.59375 | 0.010886 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1505.2 | 129.6182 | 0.0072281 | 0.56715 | 0.0095362 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.012486 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1505.4 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.010886 | 0.63692 | 0.011019 | 0.54889 | 0.00647
1505.6 | 131.0577 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.59537 | 0.015026 | 0.59375 | 0.012486 | 0.63692 | 0.0094199 | 0.45294 | 0.0048708
1505.8 | 129.3303 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.00033201 | 0.49942 | 0.016626 | 0.59375 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1506 | 129.9061 | 0.0040291 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.40181 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1506.2 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.0044883 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1506.4 | 129.7141 | 0.0040291 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.59375 | 0.010886 | 0.63692 | 0.0094199 | 0.83679 | 0.00647
1506.6 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.015026 | 0.49776 | 0.012486 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1506.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.010886 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1507 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1507.2 | 129.6182 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1507.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.018225 | 0.59375 | 0.012486 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1507.6 | 129.7141 | 0.0088273 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.012486 | 0.34898 | 0.0078201 | 0.54889 | 0.0080692
1507.8 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.016626 | 0.78566 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1508 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.49776 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1508.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.59375 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1508.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.010886 | 0.25303 | 0.0078201 | 0.54889 | 0.00647
1508.6 | 130.002 | 0.028021 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1508.8 | 129.9061 | 0.021623 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.016626 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1509 | 130.194 | 0.042416 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.015026 | 0.59375 | 0.010886 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1509.2 | 130.002 | 0.044015 | 0.4712 | 0.0063372 | 0.28557 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1509.4 | 129.9061 | 0.036018 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.49776 | 0.010886 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1509.6 | 129.9061 | 0.034419 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0019319 | 0.69137 | 0.013427 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.261 | 0.00647
1509.8 | 129.9061 | 0.026422 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1510 | 129.8101 | 0.024822 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1510.2 | 129.8101 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.013427 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1510.4 | 129.9061 | 0.021623 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.59537 | 0.013427 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1510.6 | 129.8101 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.40181 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1510.8 | 130.002 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.64488 | 0.009669
1511 | 130.002 | 0.020024 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1511.2 | 129.9061 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.40181 | 0.0092866 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1511.4 | 130.002 | 0.021623 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1511.6 | 130.002 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1511.8 | 129.9061 | 0.016825 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1512 | 129.9061 | 0.013626 | 0.56715 | 0.0079364 | 0.38156 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1512.2 | 129.9061 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.78566 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1512.4 | 129.9061 | 0.015225 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.73287 | 0.0094199 | 0.45294 | 0.0080692
1512.6 | 129.9061 | 0.012026 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1512.8 | 130.002 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1513 | 129.9061 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.0080692
1513.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.015026 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1513.4 | 129.8101 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.012868
1513.6 | 129.8101 | 0.0088273 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.78732 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1513.8 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1514 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1514.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1514.4 | 129.8101 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1514.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1514.8 | 129.8101 | 0.0056289 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1515 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.11554 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1515.2 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1515.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1515.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1515.8 | 129.8101 | 0.0072281 | 0.56715 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1516 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1516.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1516.4 | 129.9061 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1516.6 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1516.8 | 130.002 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1517 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.012619 | 0.54889 | 0.00647
1517.2 | 129.9061 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1517.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1517.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1517.8 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1518 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1518.2 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1518.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1518.6 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.0080692
1518.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0044883 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1519 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0054293 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1519.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1519.4 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1519.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1519.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0030219 | 0.45294 | 0.00647
1520 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1520.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1520.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1520.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1520.8 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1521 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1521.2 | 129.9061 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.11554 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1521.4 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1521.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0016822 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1521.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1522 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1522.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.00033201 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1522.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1522.6 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1522.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.20987 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1523 | 129.9061 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1523.2 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1523.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1523.6 | 129.9061 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1523.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1524 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1524.2 | 129.9061 | 0.0072281 | 0.4712 | 0.004738 | 0.86139 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.11392 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1524.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1524.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1524.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1525 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1525.2 | 129.8101 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1525.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.64488 | 0.0080692
1525.6 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1525.8 | 129.9061 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0048708
1526 | 129.8101 | 0.0088273 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1526.2 | 129.9061 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1526.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.010886 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1526.6 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1526.8 | 129.9061 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1527 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0016822 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1527.2 | 129.8101 | 0.0072281 | 0.27926 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1527.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1527.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0094199 | 0.54889 | 0.00647
1527.8 | 129.8101 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1528 | 129.8101 | 0.0072281 | 0.4712 | 0.011135 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1528.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.0016718
1528.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.88165 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1528.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.7654 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1528.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1529 | 129.9061 | 0.012026 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1529.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.88165 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1529.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1529.6 | 129.8101 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1529.8 | 129.8101 | 0.0056289 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1530 | 129.8101 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1530.2 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1530.4 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | 0.00647
1530.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1530.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.54889 | 0.00647
1531 | 129.8101 | 0.0072281 | 0.56715 | 0.0031381 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1531.2 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1531.4 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.0054293 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1531.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1531.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1532 | 129.8101 | 0.0072281 | 0.7591 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1532.2 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1532.4 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1532.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0030219 | 0.54889 | 0.00647
1532.8 | 129.8101 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1533 | 129.8101 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | -0.0012672 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1533.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1533.4 | 129.8101 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1533.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1533.8 | 130.098 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.014218 | 0.54889 | 0.00647
1534 | 129.9061 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1534.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1534.4 | 129.8101 | 0.0072281 | 0.66314 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1534.6 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1534.8 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1535 | 129.8101 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1535.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0016822 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1535.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0083293 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1535.6 | 129.8101 | 0.0056289 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1535.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1536 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1536.2 | 129.8101 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
1536.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1536.6 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1536.8 | 129.8101 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1537 | 129.8101 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1537.2 | 129.8101 | 0.013626 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1537.4 | 129.8101 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1537.6 | 129.7141 | 0.018424 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.78732 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1537.8 | 129.8101 | 0.021623 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1538 | 129.8101 | 0.039217 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.015026 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1538.2 | 129.5222 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.010886 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1538.4 | 129.1384 | 0.0072281 | 0.4712 | 0.0031381 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.015026 | 0.68971 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1538.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.016626 | 0.59375 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1538.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1539 | 129.7141 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.30748 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1539.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1539.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.0048708
1539.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1539.8 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.0080692
1540 | 129.7141 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1540.2 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1540.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1540.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1540.8 | 129.6182 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1541 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1541.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1541.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1541.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1541.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1542 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.83679 | 0.0080692
1542.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.86139 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1542.4 | 129.5222 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1542.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.86139 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1542.8 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.003282 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1543 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1543.2 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1543.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1543.6 | 129.5222 | 0.0056289 | 0.7591 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.012868
1543.8 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1544 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1544.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1544.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1544.6 | 129.5222 | 0.0088273 | 0.7591 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1544.8 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1545 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | -0.0012672 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1545.2 | 129.4263 | 0.0072281 | 0.4712 | -6.0896e-05 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1545.4 | 129.4263 | 0.0088273 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1545.6 | 129.4263 | 0.0072281 | 0.087319 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1545.8 | 129.3303 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1546 | 129.5222 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.016626 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1546.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1546.4 | 129.4263 | 0.0088273 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1546.6 | 129.5222 | 0.010427 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1546.8 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0094199 | 0.45294 | 0.0080692
1547 | 129.5222 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1547.2 | 129.5222 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.011528 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1547.4 | 129.4263 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1547.6 | 129.4263 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1547.8 | 129.4263 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1548 | 129.3303 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.25303 | 0.0078201 | 0.45294 | 0.00647
1548.2 | 129.4263 | 0.0088273 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1548.4 | 129.4263 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0016822 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1548.6 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.25303 | 0.0078201 | 0.45294 | 0.00647
1548.8 | 129.5222 | 0.0088273 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1549 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.014218 | 0.45294 | 0.00647
1549.2 | 129.4263 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1549.4 | 129.4263 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0048708
1549.6 | 129.5222 | 0.010427 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1549.8 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.17102 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1550 | 129.4263 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.012619 | 0.54889 | 0.00647
1550.2 | 129.4263 | 0.0088273 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1550.4 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1550.6 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0038295 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1550.8 | 129.4263 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1551 | 129.4263 | 0.010427 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0048708
1551.2 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | -0.00017715 | 0.54889 | 0.00647
1551.4 | 129.4263 | 0.012026 | 0.7591 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0070285 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.014467
1551.6 | 129.4263 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1551.8 | 129.3303 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.78566 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1552 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.15708 | 0.0078201 | 0.54889 | 0.00647
1552.2 | 129.5222 | 0.012026 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1552.4 | 129.4263 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1552.6 | 129.5222 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1552.8 | 129.5222 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0016822 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1553 | 129.5222 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.0080692
1553.2 | 129.5222 | 0.013626 | 0.4712 | 0.0063372 | 0.7654 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.68971 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1553.4 | 129.4263 | 0.012026 | 0.56715 | 0.0015389 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1553.6 | 129.4263 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1553.8 | 129.6182 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1554 | 129.4263 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1554.2 | 129.5222 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | -0.0012672 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1554.4 | 129.4263 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.26697 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1554.6 | 129.6182 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | 0.0080692
1554.8 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1555 | 129.5222 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1555.2 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1555.4 | 129.5222 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1555.6 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.075065 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1555.8 | 129.5222 | 0.010427 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1556 | 129.5222 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1556.2 | 129.5222 | 0.013626 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1556.4 | 129.5222 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.93278 | 0.00647
1556.6 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1556.8 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.7654 | 0.003282 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1557 | 129.6182 | 0.016825 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1557.2 | 129.7141 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.00647
1557.4 | 129.5222 | 0.034419 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.20987 | 0.0092866 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1557.6 | 129.6182 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.59375 | 0.012486 | 0.25303 | 0.0078201 | 0.54889 | 0.0080692
1557.8 | 129.7141 | 0.015225 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | -0.0028664 | 0.40347 | 0.010228 | 0.49776 | 0.010886 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1558 | 129.6182 | 0.013626 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0028892 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1558.2 | 129.7141 | 0.015225 | 0.56715 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.016066
1558.4 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1558.6 | 129.7141 | 0.013626 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1558.8 | 129.7141 | 0.013626 | 0.4712 | 0.0079364 | 0.18962 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1559 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1559.2 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1559.4 | 129.7141 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1559.6 | 129.7141 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1559.8 | 129.5222 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1560 | 129.7141 | 0.015225 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1560.2 | 129.7141 | 0.013626 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.009669
1560.4 | 129.6182 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1560.6 | 129.3303 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1560.8 | 129.1384 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.014085 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1561 | 129.6182 | 0.013626 | 0.56715 | 0.0015389 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1561.2 | 129.6182 | 0.015225 | 0.4712 | 0.0063372 | 0.47751 | 0.012878 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0044883 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1561.4 | 129.6182 | 0.013626 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1561.6 | 129.6182 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1561.8 | 129.8101 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1562 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1562.2 | 129.7141 | 0.013626 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1562.4 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1562.6 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1562.8 | 129.8101 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1563 | 129.7141 | 0.013626 | 0.56715 | 0.0015389 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1563.2 | 129.7141 | 0.013626 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1563.4 | 129.5222 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1563.6 | 129.7141 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1563.8 | 129.6182 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1564 | 129.7141 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1564.2 | 129.7141 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1564.4 | 129.7141 | 0.015225 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1564.6 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.47751 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1564.8 | 129.7141 | 0.013626 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1565 | 129.7141 | 0.012026 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1565.2 | 129.7141 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0016718
1565.4 | 129.7141 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.0080692
1565.6 | 129.7141 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1565.8 | 129.7141 | 0.012026 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1566 | 129.7141 | 0.012026 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.69137 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1566.2 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1566.4 | 129.6182 | 0.012026 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1566.6 | 129.7141 | 0.013626 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1566.8 | 129.7141 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1567 | 129.7141 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1567.2 | 129.5222 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.016626 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1567.4 | 129.6182 | 0.015225 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1567.6 | 129.6182 | 0.021623 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1567.8 | 129.4263 | 0.020024 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1568 | 129.5222 | 0.048814 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.016626 | 0.49776 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1568.2 | 129.6182 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.015685 | 0.34898 | 0.0078201 | 0.54889 | 0.0080692
1568.4 | 129.4263 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.009669
1568.6 | 129.6182 | 0.013626 | 0.4712 | 0.0063372 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.11392 | -0.017904 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1568.8 | 129.6182 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.00033201 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1569 | 129.5222 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.0080692
1569.2 | 129.6182 | 0.012026 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1569.4 | 129.5222 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1569.6 | 129.2343 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1569.8 | 129.4263 | 0.013626 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1570 | 129.5222 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1570.2 | 129.5222 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.00033201 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1570.4 | 129.5222 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1570.6 | 129.5222 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0016718
1570.8 | 129.4263 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1571 | 129.4263 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1571.2 | 129.4263 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1571.4 | 129.5222 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1571.6 | 129.4263 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.7468 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1571.8 | 129.4263 | 0.010427 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.012619 | 0.45294 | 0.0080692
1572 | 129.5222 | 0.012026 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1572.2 | 129.4263 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0019319 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.0080692
1572.4 | 129.4263 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.64488 | 0.0080692
1572.6 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | -0.0012672 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1572.8 | 129.4263 | 0.010427 | 0.56715 | 0.0079364 | 0.86139 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1573 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1573.2 | 129.3303 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1573.4 | 129.4263 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1573.6 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.012868
1573.8 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1574 | 129.4263 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1574.2 | 129.3303 | 0.010427 | 0.4712 | 0.004738 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.016626 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1574.4 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0028892 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1574.6 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1574.8 | 129.3303 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
1575 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1575.2 | 129.3303 | 0.0040291 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1575.4 | 129.3303 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1575.6 | 129.3303 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1575.8 | 129.3303 | 0.0088273 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1576 | 129.4263 | 0.0024299 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1576.2 | 129.4263 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1576.4 | 129.3303 | 0.0072281 | 0.66314 | 0.0015389 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1576.6 | 129.3303 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.00033201 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1576.8 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.21153 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1577 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.011268
1577.2 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1577.4 | 129.3303 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1577.6 | 129.3303 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1577.8 | 129.2343 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1578 | 129.2343 | 0.023223 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0083293 | 0.59537 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1578.2 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1578.4 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.92481 | 0.0094199 | 0.45294 | 0.00647
1578.6 | 129.0424 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0030219 | 0.261 | 0.0080692
1578.8 | 129.3303 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.0086283 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1579 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1579.2 | 129.3303 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1579.4 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.00647
1579.6 | 129.3303 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1579.8 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1580 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1580.2 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1580.4 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.015817 | 0.54889 | 0.0080692
1580.6 | 129.3303 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1580.8 | 129.4263 | 0.0072281 | 0.56715 | 0.011135 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1581 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1581.2 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1581.4 | 129.4263 | 0.013626 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1581.6 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1581.8 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1582 | 129.4263 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1582.2 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1582.4 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1582.6 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1582.8 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1583 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1583.2 | 129.4263 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1583.4 | 129.4263 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.011528 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0080692
1583.6 | 129.2343 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1583.8 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1584 | 129.1384 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0046217 | 0.54889 | 0.0080692
1584.2 | 129.3303 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0046217 | 0.54889 | 0.00647
1584.4 | 129.4263 | 0.0072281 | 0.18331 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.012868
1584.6 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1584.8 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1585 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.92481 | 0.0078201 | 0.54889 | 0.00647
1585.2 | 129.4263 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.11392 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1585.4 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1585.6 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1585.8 | 129.5222 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0019319 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1586 | 129.5222 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.011528 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1586.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1586.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
1586.6 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1586.8 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1587 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1587.2 | 129.6182 | 0.010427 | 0.37521 | 0.0031381 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1587.4 | 129.6182 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0016822 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1587.6 | 129.6182 | 0.015225 | 0.4712 | 0.0095362 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1587.8 | 129.7141 | 0.026422 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1588 | 129.5222 | 0.0072281 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.009669
1588.2 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.010886 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1588.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1588.6 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.018225 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.16505 | 0.0080692
1588.8 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.0080692
1589 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.0032709
1589.2 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1589.4 | 129.5222 | 0.0024299 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1589.6 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1589.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1590 | 129.7141 | 0.00083003 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1590.2 | 129.7141 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1590.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.003282 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1590.6 | 129.5222 | 0.00083003 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1590.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1591 | 129.7141 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1591.2 | 129.7141 | 0.0024299 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.74084 | 0.00647
1591.4 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1591.6 | 130.194 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.30582 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1591.8 | 130.2899 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.009669
1592 | 129.9061 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1592.2 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1592.4 | 129.8101 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1592.6 | 129.7141 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1592.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1593 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1593.2 | 129.9061 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1593.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.012486 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1593.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1593.8 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1594 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1594.2 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.38156 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1594.4 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1594.6 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1594.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1595 | 129.7141 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1595.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.0080692
1595.4 | 129.7141 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1595.6 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1595.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1596 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1596.2 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1596.4 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1596.6 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.7468 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1596.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1597 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1597.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.36296 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1597.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1597.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1597.8 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1598 | 129.7141 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1598.2 | 129.7141 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1598.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0032709
1598.6 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1598.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1599 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1599.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.0080692
1599.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1599.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1599.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1600 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1600.2 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1600.4 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1600.6 | 129.6182 | 0.0088273 | 0.18331 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1600.8 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.64488 | 0.0080692
1601 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.010886 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1601.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.011268
1601.4 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1601.6 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1601.8 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.012486 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1602 | 129.7141 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.7468 | 0.0019319 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1602.2 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1602.4 | 129.8101 | 0.013626 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1602.6 | 129.6182 | 0.018424 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.013427 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1602.8 | 129.5222 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1603 | 129.6182 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.012868
1603.2 | 129.5222 | 0.023223 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.36296 | 0.0067301 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1603.4 | 129.5222 | 0.026422 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1603.6 | 129.6182 | 0.037618 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0019319 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1603.8 | 129.6182 | 0.036018 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.59375 | 0.0092866 | 0.73287 | 0.0046217 | 0.54889 | 0.00647
1604 | 129.5222 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.261 | 0.00647
1604.2 | 129.2343 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1604.4 | 129.5222 | 0.0072281 | 0.37521 | 0.0063372 | 0.28557 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.018225 | 0.59375 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1604.6 | 129.4263 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.024075 | 0.5549 | 0.0051309 | 0.40347 | 0.015026 | 0.49776 | 0.012486 | 0.73287 | 0.0062209 | 0.54889 | 0.0080692
1604.8 | 129.4263 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0096794 | 0.65085 | 0.0067301 | 0.40347 | 0.0086283 | 0.59375 | 0.0092866 | 0.73287 | 0.0078201 | 0.64488 | 0.0080692
1605 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0054293 | 0.49776 | 0.0092866 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1605.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.45294 | 0.0080692
1605.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1605.6 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1605.8 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.7654 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1606 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1606.2 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1606.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.38156 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1606.6 | 129.5222 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0099291 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1606.8 | 129.4263 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1607 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1607.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1607.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1607.6 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1607.8 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1608 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.20987 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1608.2 | 129.5222 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1608.4 | 129.4263 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1608.6 | 129.4263 | 0.0072281 | 0.66314 | 0.0015389 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1608.8 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.009669
1609 | 129.5222 | 0.0072281 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1609.2 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.82882 | 0.0078201 | 0.64488 | 0.0080692
1609.4 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1609.6 | 129.4263 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.00033201 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1609.8 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.0080692
1610 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1610.2 | 129.4263 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1610.4 | 129.4263 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1610.6 | 129.4263 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.83679 | 0.0080692
1610.8 | 129.2343 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1611 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1611.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1611.4 | 129.4263 | 0.0072281 | 0.4712 | 0.011135 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1611.6 | 129.4263 | 0.0072281 | 0.7591 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1611.8 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.0080692
1612 | 129.4263 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.0080692
1612.2 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1612.4 | 129.3303 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1612.6 | 129.4263 | 0.0088273 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1612.8 | 129.3303 | 0.0072281 | 0.4712 | 0.0015389 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1613 | 129.4263 | 0.0072281 | 0.087319 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.011268
1613.2 | 129.4263 | 0.0072281 | 0.4712 | 0.0079364 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1613.4 | 129.2343 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1613.6 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1613.8 | 129.3303 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.0080692
1614 | 129.3303 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1614.2 | 129.4263 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.0080692
1614.4 | 129.4263 | 0.0072281 | 0.7591 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1614.6 | 129.4263 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0028892 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1614.8 | 129.4263 | 0.0088273 | 0.4712 | 0.0015389 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1615 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1615.2 | 129.3303 | 0.0024299 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1615.4 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0016822 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1615.6 | 129.4263 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1615.8 | 129.4263 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.016626 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.009669
1616 | 129.4263 | 0.0072281 | 0.56715 | 0.0031381 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1616.2 | 129.4263 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1616.4 | 129.5222 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.74084 | 0.0080692
1616.6 | 129.4263 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1616.8 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0030219 | 0.64488 | 0.00647
1617 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1617.2 | 129.4263 | 0.0088273 | 0.37521 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1617.4 | 128.0827 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0016718
1617.6 | 127.8908 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1617.8 | 128.5625 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1618 | 129.2343 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1618.2 | 129.3303 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1618.4 | 129.2343 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1618.6 | 129.2343 | 0.0088273 | 0.27926 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1618.8 | 129.3303 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1619 | 129.2343 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1619.2 | 129.2343 | 0.0088273 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.010886 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1619.4 | 129.2343 | 0.0072281 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.009669
1619.6 | 129.2343 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1619.8 | 129.2343 | 0.0088273 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1620 | 129.2343 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1620.2 | 129.3303 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1620.4 | 129.3303 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1620.6 | 129.3303 | 0.0072281 | 0.4712 | 0.0015389 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1620.8 | 129.2343 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1621 | 129.2343 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1621.2 | 129.2343 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.74084 | 0.0080692
1621.4 | 129.2343 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1621.6 | 129.2343 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1621.8 | 129.2343 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1622 | 129.2343 | 0.013626 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1622.2 | 129.1384 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1622.4 | 129.1384 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1622.6 | 129.2343 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1622.8 | 129.2343 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0012893 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1623 | 129.2343 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.0080692
1623.2 | 129.2343 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1623.4 | 129.2343 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1623.6 | 129.2343 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.00647
1623.8 | 129.2343 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.11392 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1624 | 129.2343 | 0.0088273 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1624.2 | 129.1384 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0016718
1624.4 | 129.2343 | 0.0088273 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1624.6 | 129.1384 | 0.0088273 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1624.8 | 129.2343 | 0.0072281 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1625 | 129.1384 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1625.2 | 129.1384 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.7468 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1625.4 | 129.2343 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1625.6 | 129.2343 | 0.010427 | 0.4712 | 0.004738 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.009669
1625.8 | 129.2343 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1626 | 129.2343 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1626.2 | 129.2343 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1626.4 | 129.1384 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.20987 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1626.6 | 129.2343 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1626.8 | 129.2343 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.011528 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1627 | 129.2343 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.83679 | 0.0080692
1627.2 | 129.2343 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.009669
1627.4 | 129.3303 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1627.6 | 129.3303 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1627.8 | 129.1384 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.36296 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0094199 | 0.64488 | 0.00647
1628 | 129.2343 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1628.2 | 129.1384 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1628.4 | 129.1384 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1628.6 | 129.0424 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1628.8 | 129.2343 | 0.010427 | 0.4712 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.0070285 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1629 | 129.0424 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1629.2 | 129.1384 | 0.010427 | 0.7591 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1629.4 | 129.2343 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.78566 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1629.6 | 129.2343 | 0.010427 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1629.8 | 129.1384 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1630 | 129.2343 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1630.2 | 129.2343 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1630.4 | 129.2343 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 8.3003e-05 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1630.6 | 129.0424 | 0.015225 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1630.8 | 129.2343 | 0.010427 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1631 | 129.3303 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1631.2 | 129.1384 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1631.4 | 129.1384 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1631.6 | 129.1384 | 0.012026 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1631.8 | 129.1384 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1632 | 129.1384 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1632.2 | 129.1384 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1632.4 | 129.0424 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.84279 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1632.6 | 129.1384 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1632.8 | 129.1384 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
1633 | 128.9464 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1633.2 | 129.1384 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.54889 | 0.00647
1633.4 | 129.1384 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0096794 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.64488 | 0.0032709
1633.6 | 129.1384 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0099291 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1633.8 | 129.2343 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | -0.00096876 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1634 | 129.1384 | 0.012026 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1634.2 | 129.1384 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.92481 | 0.0078201 | 0.54889 | 0.0080692
1634.4 | 129.2343 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1634.6 | 129.1384 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1634.8 | 129.1384 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.11392 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1635 | 129.1384 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1635.2 | 129.0424 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1635.4 | 129.3303 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1635.6 | 129.4263 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1635.8 | 129.1384 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1636 | 129.3303 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1636.2 | 129.1384 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1636.4 | 129.1384 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1636.6 | 129.2343 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.64488 | 0.0048708
1636.8 | 129.2343 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1637 | 129.2343 | 0.013626 | 0.56715 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1637.2 | 129.0424 | 0.012026 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1637.4 | 129.2343 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1637.6 | 129.1384 | 0.012026 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1637.8 | 129.3303 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
1638 | 129.1384 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.83679 | 0.0080692
1638.2 | 129.1384 | 0.015225 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1638.4 | 129.2343 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1638.6 | 129.2343 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1638.8 | 129.1384 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1639 | 128.9464 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1639.2 | 129.2343 | 0.013626 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1639.4 | 129.1384 | 0.013626 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0080692
1639.6 | 129.2343 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1639.8 | 129.2343 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1640 | 129.1384 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1640.2 | 129.1384 | 0.015225 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1640.4 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1640.6 | 129.1384 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1640.8 | 129.2343 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1641 | 129.3303 | 0.015225 | 0.4712 | 0.0079364 | 0.47751 | 0.0048812 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1641.2 | 129.2343 | 0.015225 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1641.4 | 129.2343 | 0.015225 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1641.6 | 129.3303 | 0.015225 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1641.8 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.00647
1642 | 129.2343 | 0.015225 | 0.4712 | 0.0063372 | 0.47751 | 0.0016822 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1642.2 | 129.2343 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.69137 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1642.4 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1642.6 | 129.3303 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1642.8 | 129.2343 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1643 | 129.2343 | 0.016825 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1643.2 | 129.2343 | 0.015225 | 0.66314 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1643.4 | 129.3303 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.014467
1643.6 | 129.3303 | 0.013626 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1643.8 | 129.2343 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.92481 | 0.0078201 | 0.54889 | 0.0080692
1644 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.25303 | 0.0078201 | 0.54889 | 0.0080692
1644.2 | 129.3303 | 0.015225 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1644.4 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1644.6 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1644.8 | 129.3303 | 0.015225 | 0.37521 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.009669
1645 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1645.2 | 129.4263 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1645.4 | 129.3303 | 0.016825 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.0038295 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1645.6 | 129.3303 | 0.016825 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.11392 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1645.8 | 129.3303 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1646 | 129.3303 | 0.016825 | 0.18331 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1646.2 | 129.3303 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1646.4 | 129.3303 | 0.013626 | 0.7591 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1646.6 | 129.3303 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0019319 | 0.11554 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1646.8 | 129.2343 | 0.021623 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | -0.0012672 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1647 | 129.3303 | 0.037618 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1647.2 | 129.4263 | 0.016825 | -0.10462 | 0.0063372 | 0.5735 | 0.003282 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1647.4 | 129.4263 | 0.016825 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.78566 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1647.6 | 129.4263 | 0.015225 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | -0.79462 | 0.0080692
1647.8 | 129.5222 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1648 | 129.4263 | 0.016825 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1648.2 | 129.4263 | 0.016825 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1648.4 | 129.5222 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1648.6 | 129.5222 | 0.016825 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1648.8 | 129.4263 | 0.016825 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1649 | 129.4263 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.64488 | 0.0080692
1649.2 | 129.5222 | 0.015225 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1649.4 | 129.4263 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.20987 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1649.6 | 129.3303 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1649.8 | 128.8504 | 0.016825 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1650 | 129.3303 | 0.016825 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1650.2 | 129.2343 | 0.015225 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1650.4 | 129.3303 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | -0.0012672 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1650.6 | 129.5222 | 0.016825 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1650.8 | 129.5222 | 0.016825 | 0.37521 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1651 | 129.7141 | 0.016825 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1651.2 | 129.4263 | 0.016825 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1651.4 | 129.4263 | 0.016825 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1651.6 | 129.5222 | 0.016825 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.00647
1651.8 | 129.5222 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1652 | 129.5222 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.30582 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1652.2 | 129.5222 | 0.018424 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1652.4 | 129.5222 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1652.6 | 129.5222 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1652.8 | 129.5222 | 0.016825 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1653 | 129.5222 | 0.016825 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.00033201 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1653.2 | 129.4263 | 0.016825 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1653.4 | 129.5222 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.54889 | 0.00647
1653.6 | 129.4263 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1653.8 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1654 | 129.5222 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1654.2 | 129.5222 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1654.4 | 129.4263 | 0.013626 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.0080692
1654.6 | 129.4263 | 0.013626 | 0.56715 | 0.0079364 | 0.66945 | 0.0048812 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1654.8 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1655 | 129.4263 | 0.016825 | 0.4712 | 0.0079364 | 0.38156 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1655.2 | 129.4263 | 0.013626 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0094199 | 0.54889 | 0.0080692
1655.4 | 129.4263 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1655.6 | 129.3303 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1655.8 | 129.4263 | 0.023223 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.20987 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1656 | 129.3303 | 0.03122 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.015026 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1656.2 | 129.4263 | 0.042416 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.021424 | 0.59375 | 0.012486 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1656.4 | 129.2343 | 0.020024 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.65085 | 0.003531 | 0.40347 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1656.6 | 129.4263 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.012486 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1656.8 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.0048708
1657 | 129.3303 | 0.016825 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1657.2 | 129.3303 | 0.015225 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.261 | 0.00647
1657.4 | 129.3303 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1657.6 | 129.3303 | 0.016825 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.0016718
1657.8 | 129.3303 | 0.016825 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0032709
1658 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.47751 | 0.011279 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1658.2 | 129.3303 | 0.015225 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1658.4 | 129.3303 | 0.013626 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1658.6 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1658.8 | 129.3303 | 0.015225 | 0.4712 | 0.0079364 | 0.18962 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1659 | 129.3303 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1659.2 | 129.3303 | 0.015225 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0032709
1659.4 | 129.3303 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1659.6 | 129.2343 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1659.8 | 129.3303 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1660 | 129.3303 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1660.2 | 129.2343 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1660.4 | 129.2343 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1660.6 | 129.2343 | 0.012026 | 0.18331 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.0032709
1660.8 | 129.2343 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1661 | 129.2343 | 0.012026 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1661.2 | 129.2343 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.35695 | 0.009669
1661.4 | 129.2343 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1661.6 | 129.1384 | 0.012026 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1661.8 | 129.2343 | 0.013626 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1662 | 129.1384 | 0.013626 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1662.2 | 129.2343 | 0.012026 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.78566 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1662.4 | 129.2343 | 0.012026 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1662.6 | 129.0424 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1662.8 | 129.2343 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.011528 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1663 | 129.2343 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.16505 | 0.00647
1663.2 | 129.2343 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1663.4 | 129.2343 | 0.010427 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | -0.0012672 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1663.6 | 129.1384 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | -0.0012672 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1663.8 | 129.2343 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1664 | 129.2343 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.0080692
1664.2 | 129.1384 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1664.4 | 129.1384 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.0016718
1664.6 | 129.1384 | 0.015225 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1664.8 | 129.0424 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1665 | 129.1384 | 0.010427 | 0.7591 | 0.0095362 | 0.5735 | 0.0080803 | 0.65085 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.0080692
1665.2 | 129.2343 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0099291 | 0.019589 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1665.4 | 129.1384 | 0.010427 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1665.6 | 129.1384 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1665.8 | 129.2343 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1666 | 129.1384 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1666.2 | 129.1384 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1666.4 | 129.2343 | 0.0088273 | 0.56715 | 0.0063372 | 0.86139 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.30582 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1666.6 | 129.0424 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1666.8 | 129.2343 | 0.012026 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0080692
1667 | 129.4263 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.00647
1667.2 | 129.2343 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.0080692
1667.4 | 129.1384 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1667.6 | 129.3303 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.0080692
1667.8 | 129.2343 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0083293 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1668 | 129.2343 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1668.2 | 129.2343 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1668.4 | 129.2343 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.012486 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1668.6 | 129.2343 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.012868
1668.8 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1669 | 129.3303 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1669.2 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.7654 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1669.4 | 129.3303 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0038295 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1669.6 | 129.3303 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1669.8 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1670 | 129.3303 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
1670.2 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1670.4 | 129.3303 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1670.6 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.003282 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1670.8 | 129.3303 | 0.010427 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.0080692
1671 | 129.3303 | 0.0088273 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1671.2 | 129.4263 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1671.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1671.6 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.0054293 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1671.8 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1672 | 129.4263 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1672.2 | 129.4263 | 0.0072281 | 0.4712 | -6.0896e-05 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1672.4 | 129.4263 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1672.6 | 129.4263 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1672.8 | 129.3303 | 0.013626 | 0.37521 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1673 | 129.5222 | 0.020024 | 0.56715 | 0.0031381 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1673.2 | 129.5222 | 0.026422 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1673.4 | 129.4263 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1673.6 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.40181 | 0.010886 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1673.8 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1674 | 129.8101 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.83679 | 0.0080692
1674.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1674.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1674.6 | 129.4263 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0060882 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1674.8 | 129.5222 | 0.0072281 | 0.66314 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1675 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1675.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.78566 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1675.4 | 129.5222 | 0.0072281 | 0.4712 | 0.012735 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1675.6 | 129.6182 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.15708 | 0.0078201 | 0.54889 | 0.0080692
1675.8 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.009669
1676 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1676.2 | 129.8101 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1676.4 | 130.3859 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1676.6 | 129.7141 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1676.8 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1677 | 129.7141 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1677.2 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1677.4 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1677.6 | 129.6182 | 0.0056289 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | -0.0012672 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1677.8 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1678 | 129.8101 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1678.2 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.18962 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1678.4 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1678.6 | 129.6182 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1678.8 | 129.5222 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.011019 | 0.54889 | 0.00647
1679 | 129.5222 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1679.2 | 129.5222 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1679.4 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1679.6 | 129.5222 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.78566 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1679.8 | 129.6182 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1680 | 129.6182 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1680.2 | 129.6182 | 0.0072281 | 0.56715 | 0.0079364 | 0.86139 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1680.4 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.83679 | 0.00647
1680.6 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1680.8 | 129.5222 | 0.0088273 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1681 | 129.6182 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1681.2 | 129.5222 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1681.4 | 129.4263 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1681.6 | 129.5222 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.0080692
1681.8 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1682 | 129.5222 | 0.0072281 | 0.18331 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1682.2 | 129.5222 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1682.4 | 129.5222 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1682.6 | 129.5222 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.015026 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1682.8 | 129.4263 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1683 | 129.4263 | 0.016825 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0030219 | 0.54889 | 0.00647
1683.2 | 129.5222 | 0.040817 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.015026 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1683.4 | 129.0424 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.018225 | 0.59375 | 0.012486 | 0.54092 | 0.0094199 | 0.54889 | 0.011268
1683.6 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.016626 | 0.59375 | 0.015685 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1683.8 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0086283 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1684 | 129.4263 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.25303 | 0.0078201 | 0.54889 | 0.011268
1684.2 | 129.4263 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.64488 | 0.0080692
1684.4 | 129.5222 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1684.6 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1684.8 | 129.3303 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.7468 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.009669
1685 | 129.3303 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1685.2 | 129.3303 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.84279 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.010886 | 0.25303 | 0.0094199 | 0.54889 | 0.0080692
1685.4 | 129.4263 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1685.6 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.0080692
1685.8 | 129.4263 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.78732 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.0080692
1686 | 129.3303 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1686.2 | 129.4263 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.34898 | 0.0094199 | 0.64488 | 0.0080692
1686.4 | 129.3303 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1686.6 | 129.4263 | 0.010427 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.78732 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1686.8 | 129.4263 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1687 | 129.4263 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1687.2 | 129.4263 | 0.010427 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1687.4 | 129.5222 | 0.010427 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0062209 | 0.54889 | 0.0080692
1687.6 | 129.3303 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1687.8 | 129.3303 | 0.010427 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.78566 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1688 | 129.5222 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.012619 | 0.54889 | 0.0080692
1688.2 | 129.3303 | 0.0088273 | 0.27926 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1688.4 | 129.3303 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.010886 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1688.6 | 129.3303 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.00033201 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1688.8 | 129.2343 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1689 | 129.3303 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0083293 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.0080692
1689.2 | 129.3303 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1689.4 | 129.3303 | 0.012026 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1689.6 | 129.0424 | 0.010427 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0014227 | 0.54889 | 0.0080692
1689.8 | 129.3303 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.64488 | 0.00647
1690 | 129.3303 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.0080692
1690.2 | 129.3303 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1690.4 | 129.3303 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.69137 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1690.6 | 129.3303 | 0.010427 | 0.4712 | 0.0079364 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1690.8 | 129.3303 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1691 | 129.2343 | 0.012026 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1691.2 | 129.3303 | 0.016825 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.0080692
1691.4 | 129.3303 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1691.6 | 129.2343 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.93278 | 0.0080692
1691.8 | 129.2343 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1692 | 129.0424 | 0.013626 | 0.66314 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.009669
1692.2 | 129.2343 | 0.013626 | 0.4712 | 0.0031381 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1692.4 | 129.2343 | 0.012026 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0048708
1692.6 | 129.2343 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1692.8 | 129.2343 | 0.012026 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1693 | 129.2343 | 0.012026 | 0.56715 | 0.011135 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1693.2 | 129.0424 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1693.4 | 129.0424 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.012619 | 0.54889 | 0.0080692
1693.6 | 129.1384 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.016626 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1693.8 | 129.2343 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.11554 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.009669
1694 | 129.2343 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.54889 | 0.0080692
1694.2 | 129.4263 | 0.021623 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1694.4 | 129.0424 | 0.015225 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1694.6 | 128.8504 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1694.8 | 129.1384 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1695 | 129.1384 | 0.013626 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1695.2 | 129.1384 | 0.015225 | 0.4712 | 0.011135 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1695.4 | 129.2343 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1695.6 | 129.1384 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1695.8 | 129.1384 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.0080692
1696 | 129.2343 | 0.015225 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.68971 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1696.2 | 129.2343 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1696.4 | 129.2343 | 0.015225 | 0.4712 | 0.0079364 | 0.38156 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1696.6 | 129.2343 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1696.8 | 129.2343 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.83679 | 0.0080692
1697 | 129.2343 | 0.015225 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1697.2 | 129.2343 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1697.4 | 129.2343 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1697.6 | 129.2343 | 0.013626 | 0.37521 | 0.011135 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.0038295 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1697.8 | 129.1384 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1698 | 129.2343 | 0.015225 | 0.4712 | 0.0063372 | 0.28557 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1698.2 | 129.5222 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1698.4 | 129.2343 | 0.013626 | 0.66314 | 0.0015389 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1698.6 | 129.2343 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.011528 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.35695 | 0.00647
1698.8 | 129.3303 | 0.016825 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1699 | 129.2343 | 0.016825 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1699.2 | 129.2343 | 0.016825 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.20987 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1699.4 | 129.3303 | 0.016825 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1699.6 | 129.3303 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.010886 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1699.8 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1700 | 129.3303 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1700.2 | 129.2343 | 0.016825 | 0.56715 | 0.0079364 | 0.5735 | 0.0016822 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1700.4 | 129.3303 | 0.016825 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1700.6 | 129.3303 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1700.8 | 129.2343 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.82882 | 0.0078201 | 0.54889 | 0.00647
1701 | 129.2343 | 0.016825 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1701.2 | 129.1384 | 0.016825 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.84279 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1701.4 | 129.3303 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.54889 | 0.0080692
1701.6 | 129.4263 | 0.018424 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1701.8 | 129.3303 | 0.018424 | 0.4712 | 0.0063372 | 0.18962 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1702 | 129.3303 | 0.018424 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1702.2 | 129.2343 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.011279 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.73287 | 0.0062209 | 0.54889 | 0.0080692
1702.4 | 129.3303 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1702.6 | 129.3303 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.00647
1702.8 | 129.2343 | 0.016825 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1703 | 129.3303 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1703.2 | 129.2343 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0083293 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1703.4 | 129.5222 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.00647
1703.6 | 129.3303 | 0.016825 | 0.4712 | 0.0063372 | 0.86139 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1703.8 | 129.4263 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1704 | 129.3303 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 7.1911e-05
1704.2 | 129.4263 | 0.016825 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1704.4 | 129.4263 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1704.6 | 129.4263 | 0.016825 | 0.7591 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1704.8 | 129.4263 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.17102 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1705 | 129.4263 | 0.023223 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1705.2 | 129.4263 | 0.015225 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.78566 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1705.4 | 129.4263 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0016822 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1705.6 | 129.3303 | 0.016825 | 0.56715 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1705.8 | 129.4263 | 0.016825 | 0.37521 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.21153 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1706 | 129.4263 | 0.03282 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.013427 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.45294 | 0.0080692
1706.2 | 129.5222 | 0.018424 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1706.4 | 129.5222 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1706.6 | 129.5222 | 0.018424 | 0.4712 | 0.0063372 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.11392 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1706.8 | 129.5222 | 0.020024 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1707 | 129.6182 | 0.018424 | 0.56715 | 0.0063372 | 0.47751 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1707.2 | 129.5222 | 0.020024 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1707.4 | 129.5222 | 0.018424 | 0.4712 | 0.0079364 | 0.66945 | 0.011279 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1707.6 | 129.5222 | 0.020024 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.0080692
1707.8 | 129.5222 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.82882 | 0.0078201 | 0.54889 | 0.0080692
1708 | 129.6182 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.64488 | 0.00647
1708.2 | 129.6182 | 0.020024 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1708.4 | 129.4263 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1708.6 | 129.6182 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1708.8 | 129.3303 | 0.021623 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.16505 | 0.00647
1709 | 129.2343 | 0.020024 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1709.2 | 129.4263 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1709.4 | 129.4263 | 0.021623 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.7468 | 0.003531 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.44497 | 0.0094199 | 0.54889 | 0.0080692
1709.6 | 129.7141 | 0.020024 | 0.4712 | 0.0063372 | 0.7654 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1709.8 | 129.7141 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1710 | 129.7141 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1710.2 | 129.6182 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.7468 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.15708 | 0.0078201 | 0.45294 | 0.0080692
1710.4 | 129.7141 | 0.020024 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1710.6 | 129.7141 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1710.8 | 129.7141 | 0.020024 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1711 | 129.7141 | 0.020024 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1711.2 | 129.7141 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.011279 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1711.4 | 129.6182 | 0.021623 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1711.6 | 129.7141 | 0.020024 | 0.56715 | 0.0079364 | 0.47751 | 0.011279 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1711.8 | 129.7141 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1712 | 129.7141 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1712.2 | 129.7141 | 0.018424 | 0.4712 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1712.4 | 129.7141 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1712.6 | 129.7141 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1712.8 | 129.6182 | 0.018424 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1713 | 129.6182 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1713.2 | 129.7141 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1713.4 | 129.6182 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1713.6 | 129.4263 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1713.8 | 129.5222 | 0.028021 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1714 | 129.5222 | 0.042416 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1714.2 | 129.5222 | 0.018424 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1714.4 | 129.5222 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1714.6 | 129.5222 | 0.021623 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.003531 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1714.8 | 129.5222 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0032709
1715 | 129.4263 | 0.018424 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.84279 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1715.2 | 129.5222 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1715.4 | 129.5222 | 0.018424 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.011268
1715.6 | 129.5222 | 0.020024 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1715.8 | 129.4263 | 0.018424 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1716 | 129.5222 | 0.016825 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1716.2 | 129.5222 | 0.016825 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1716.4 | 129.4263 | 0.018424 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1716.6 | 129.4263 | 0.016825 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.0054293 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1716.8 | 129.4263 | 0.015225 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1717 | 129.0424 | 0.018424 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1717.2 | 129.3303 | 0.015225 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1717.4 | 129.4263 | 0.016825 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1717.6 | 129.4263 | 0.016825 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1717.8 | 129.4263 | 0.016825 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.015026 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1718 | 129.3303 | 0.015225 | 0.56715 | 0.0095362 | 0.28557 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1718.2 | 129.4263 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | -0.0012672 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1718.4 | 129.4263 | 0.015225 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.84279 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1718.6 | 129.3303 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1718.8 | 129.3303 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.21153 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1719 | 129.2343 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1719.2 | 129.3303 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1719.4 | 129.4263 | 0.013626 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1719.6 | 129.3303 | 0.013626 | 0.4712 | 0.0063372 | 0.18962 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1719.8 | 129.3303 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1720 | 129.3303 | 0.013626 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1720.2 | 129.3303 | 0.013626 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1720.4 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0099291 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1720.6 | 129.3303 | 0.012026 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.78732 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1720.8 | 129.2343 | 0.015225 | 0.4712 | 0.0079364 | 0.47751 | 0.0016822 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1721 | 129.3303 | 0.013626 | 0.7591 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1721.2 | 129.3303 | 0.013626 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.21153 | 0.010228 | 0.68971 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1721.4 | 129.3303 | 0.015225 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.033661
1721.6 | 129.4263 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1721.8 | 129.4263 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1722 | 129.3303 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1722.2 | 129.3303 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.003282 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1722.4 | 129.4263 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.014085 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1722.6 | 129.3303 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1722.8 | 129.3303 | 0.012026 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1723 | 129.2343 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.011019 | 0.54889 | 0.00647
1723.2 | 129.4263 | 0.012026 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.00647
1723.4 | 128.9464 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1723.6 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1723.8 | 129.3303 | 0.010427 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1724 | 129.3303 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.83679 | 0.0080692
1724.2 | 129.4263 | 0.010427 | 0.66314 | 0.004738 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1724.4 | 129.3303 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.069058 | 0.0080692
1724.6 | 129.4263 | 0.0088273 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.011268
1724.8 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1725 | 129.5222 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1725.2 | 129.4263 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1725.4 | 129.5222 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1725.6 | 129.5222 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1725.8 | 129.5222 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1726 | 129.3303 | 0.012026 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1726.2 | 129.5222 | 0.010427 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1726.4 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1726.6 | 129.6182 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.011019 | 0.45294 | 0.00647
1726.8 | 129.5222 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1727 | 129.5222 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1727.2 | 129.6182 | 0.018424 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1727.4 | 129.6182 | 0.021623 | 0.56715 | 0.0063372 | 0.86139 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1727.6 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.7468 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1727.8 | 129.6182 | 0.0088273 | 0.37521 | 0.0079364 | 0.47751 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.88165 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1728 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1728.2 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1728.4 | 129.6182 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1728.6 | 129.6182 | 0.0088273 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1728.8 | 129.6182 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1729 | 129.6182 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1729.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.40347 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1729.4 | 129.6182 | 0.0088273 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1729.6 | 129.2343 | 0.0088273 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0046217 | 0.45294 | 0.0080692
1729.8 | 129.7141 | 0.0056289 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1730 | 129.7141 | 0.010427 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1730.2 | 130.194 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.25303 | 0.0062209 | 0.54889 | 0.00647
1730.4 | 129.9061 | 0.010427 | 0.4712 | 0.0063372 | 0.47751 | 0.0016822 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1730.6 | 129.8101 | 0.010427 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0070285 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1730.8 | 129.8101 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.00033201 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1731 | 129.7141 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1731.2 | 129.7141 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1731.4 | 129.5222 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.35695 | 0.0080692
1731.6 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1731.8 | 129.7141 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1732 | 129.7141 | 0.0088273 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0048708
1732.2 | 129.7141 | 0.0088273 | 0.56715 | 0.0079364 | 0.28557 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1732.4 | 129.7141 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1732.6 | 129.7141 | 0.0088273 | 0.56715 | 0.0063372 | 0.86139 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1732.8 | 129.6182 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1733 | 129.6182 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1733.2 | 129.7141 | 0.0088273 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1733.4 | 129.7141 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1733.6 | 129.7141 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1733.8 | 129.7141 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0019319 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1734 | 129.7141 | 0.010427 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1734.2 | 129.7141 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1734.4 | 129.7141 | 0.012026 | 0.7591 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1734.6 | 129.7141 | 0.010427 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1734.8 | 129.7141 | 0.012026 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1735 | 129.6182 | 0.010427 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1735.2 | 129.7141 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1735.4 | 129.7141 | 0.012026 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1735.6 | 129.7141 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1735.8 | 129.7141 | 0.016825 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.25303 | 0.0078201 | 0.54889 | 0.0080692
1736 | 129.7141 | 0.021623 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1736.2 | 129.6182 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1736.4 | 129.7141 | 0.039217 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.78566 | 0.010886 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1736.6 | 129.4263 | 0.010427 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.015026 | 0.59375 | 0.010886 | 0.73287 | 0.0078201 | 0.64488 | 0.0080692
1736.8 | 129.6182 | 0.010427 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.019824 | 0.59375 | 0.012486 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1737 | 129.6182 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.59537 | 0.011827 | 0.68971 | 0.010886 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1737.2 | 129.6182 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1737.4 | 129.6182 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1737.6 | 129.3303 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1737.8 | 129.6182 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.64488 | 0.00647
1738 | 129.6182 | 0.012026 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1738.2 | 129.5222 | 0.010427 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1738.4 | 129.5222 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1738.6 | 129.6182 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1738.8 | 129.5222 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1739 | 129.4263 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1739.2 | 129.5222 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1739.4 | 129.5222 | 0.012026 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1739.6 | 129.5222 | 0.012026 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1739.8 | 129.7141 | 0.012026 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.011019 | 0.64488 | 0.0080692
1740 | 129.2343 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1740.2 | 129.5222 | 0.013626 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1740.4 | 129.5222 | 0.012026 | 0.56715 | 0.0079364 | 0.66945 | 0.0048812 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1740.6 | 129.4263 | 0.013626 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1740.8 | 129.4263 | 0.013626 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1741 | 129.4263 | 0.013626 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1741.2 | 129.4263 | 0.015225 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.92481 | 0.0078201 | 0.54889 | 0.0080692
1741.4 | 129.4263 | 0.015225 | 0.4712 | 0.0079364 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1741.6 | 129.4263 | 0.015225 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.014218 | 0.54889 | 0.0080692
1741.8 | 129.3303 | 0.012026 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1742 | 129.3303 | 0.013626 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1742.2 | 129.3303 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1742.4 | 129.3303 | 0.015225 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0094199 | 0.54889 | 0.0080692
1742.6 | 129.2343 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1742.8 | 129.2343 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.92481 | 0.0094199 | 0.54889 | 0.00647
1743 | 129.3303 | 0.016825 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1743.2 | 129.3303 | 0.016825 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1743.4 | 129.4263 | 0.015225 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1743.6 | 129.3303 | 0.016825 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.0080692
1743.8 | 129.3303 | 0.015225 | 0.37521 | 0.0079364 | 0.66945 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1744 | 129.3303 | 0.018424 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1744.2 | 129.3303 | 0.016825 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1744.4 | 129.3303 | 0.020024 | 0.4712 | 0.0063372 | 0.28557 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1744.6 | 129.3303 | 0.023223 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1744.8 | 129.0424 | 0.013626 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1745 | 129.2343 | 0.016825 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.78566 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1745.2 | 129.3303 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.88165 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1745.4 | 129.3303 | 0.013626 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1745.6 | 129.3303 | 0.018424 | 0.56715 | 0.0063372 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1745.8 | 129.3303 | 0.015225 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1746 | 129.3303 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1746.2 | 129.3303 | 0.018424 | 0.4712 | 0.0063372 | 0.7654 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1746.4 | 129.4263 | 0.016825 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1746.6 | 129.2343 | 0.018424 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1746.8 | 129.3303 | 0.016825 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1747 | 129.3303 | 0.016825 | 0.18331 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1747.2 | 129.4263 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1747.4 | 129.4263 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1747.6 | 129.3303 | 0.020024 | 0.56715 | 0.0063372 | 0.66945 | 0.011279 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1747.8 | 129.4263 | 0.020024 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1748 | 129.4263 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1748.2 | 129.3303 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0019319 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1748.4 | 129.3303 | 0.020024 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0046217 | 0.74084 | 0.0080692
1748.6 | 129.3303 | 0.020024 | 0.37521 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.011019 | 0.64488 | 0.009669
1748.8 | 129.4263 | 0.018424 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1749 | 129.7141 | 0.021623 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1749.2 | 129.4263 | 0.020024 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1749.4 | 129.3303 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0014227 | 0.54889 | 0.00647
1749.6 | 129.5222 | 0.021623 | 0.56715 | 0.0063372 | 0.47751 | 0.0048812 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1749.8 | 129.5222 | 0.021623 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.78732 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1750 | 129.3303 | 0.021623 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.84279 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1750.2 | 129.6182 | 0.021623 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.17102 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.011019 | 0.45294 | 0.0080692
1750.4 | 129.5222 | 0.021623 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1750.6 | 129.5222 | 0.020024 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1750.8 | 129.5222 | 0.021623 | 0.37521 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1751 | 129.5222 | 0.018424 | 0.7591 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.21153 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1751.2 | 129.5222 | 0.026422 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1751.4 | 129.6182 | 0.021623 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1751.6 | 129.5222 | 0.021623 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1751.8 | 129.5222 | 0.021623 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1752 | 129.5222 | 0.021623 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1752.2 | 129.6182 | 0.021623 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.00033201 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1752.4 | 129.5222 | 0.020024 | 0.18331 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1752.6 | 129.6182 | 0.021623 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1752.8 | 129.7141 | 0.021623 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1753 | 129.6182 | 0.021623 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1753.2 | 129.7141 | 0.015225 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1753.4 | 129.6182 | 0.020024 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0054293 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1753.6 | 129.6182 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1753.8 | 129.6182 | 0.013626 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1754 | 129.5222 | 0.020024 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1754.2 | 129.6182 | 0.024822 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1754.4 | 129.6182 | 0.044015 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1754.6 | 129.0424 | 0.029621 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.010886 | 0.73287 | 0.0078201 | 0.64488 | 0.00647
1754.8 | 129.7141 | 0.023223 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1755 | 129.7141 | 0.023223 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.73287 | 0.0062209 | 0.54889 | 0.0080692
1755.2 | 129.7141 | 0.023223 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.012486 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1755.4 | 129.7141 | 0.023223 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1755.6 | 129.7141 | 0.024822 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.0038295 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1755.8 | 129.7141 | 0.021623 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0099291 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1756 | 129.6182 | 0.023223 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1756.2 | 129.6182 | 0.023223 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.84279 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.25303 | 0.0078201 | 0.54889 | 0.00647
1756.4 | 129.7141 | 0.023223 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1756.6 | 129.9061 | 0.023223 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1756.8 | 129.7141 | 0.023223 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1757 | 129.7141 | 0.023223 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1757.2 | 129.8101 | 0.024822 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.014218 | 0.54889 | 0.00647
1757.4 | 129.8101 | 0.024822 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1757.6 | 129.7141 | 0.023223 | 0.4712 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.11392 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1757.8 | 129.7141 | 0.023223 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.69137 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1758 | 129.7141 | 0.023223 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1758.2 | 129.6182 | 0.023223 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.84279 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1758.4 | 129.2343 | 0.023223 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1758.6 | 129.2343 | 0.024822 | 0.4712 | 0.0079364 | 0.38156 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1758.8 | 129.6182 | 0.026422 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1759 | 129.6182 | 0.023223 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1759.2 | 129.7141 | 0.023223 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1759.4 | 129.8101 | 0.024822 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.012619 | 0.54889 | 0.0080692
1759.6 | 129.7141 | 0.023223 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1759.8 | 129.7141 | 0.024822 | 0.4712 | 0.0095362 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1760 | 129.8101 | 0.024822 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.7468 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1760.2 | 129.7141 | 0.024822 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1760.4 | 129.7141 | 0.024822 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1760.6 | 129.7141 | 0.024822 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.0070285 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1760.8 | 129.7141 | 0.023223 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.0086283 | 0.30582 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1761 | 129.7141 | 0.023223 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1761.2 | 129.7141 | 0.023223 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1761.4 | 129.7141 | 0.024822 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1761.6 | 129.7141 | 0.024822 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.7468 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1761.8 | 129.7141 | 0.024822 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1762 | 129.7141 | 0.024822 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0083293 | 0.21153 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.74084 | 0.0080692
1762.2 | 129.7141 | 0.024822 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1762.4 | 129.7141 | 0.024822 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1762.6 | 129.7141 | 0.024822 | 0.7591 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1762.8 | 129.7141 | 0.023223 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1763 | 129.8101 | 0.021623 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1763.2 | 129.6182 | 0.024822 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1763.4 | 129.7141 | 0.023223 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1763.6 | 129.7141 | 0.021623 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1763.8 | 129.7141 | 0.023223 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1764 | 129.6182 | 0.021623 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1764.2 | 129.5222 | 0.021623 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.74084 | 0.0080692
1764.4 | 129.5222 | 0.024822 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1764.6 | 129.5222 | 0.026422 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1764.8 | 129.5222 | 0.020024 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.0070285 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1765 | 129.4263 | 0.016825 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1765.2 | 129.5222 | 0.023223 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.00647
1765.4 | 129.4263 | 0.021623 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1765.6 | 129.2343 | 0.023223 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1765.8 | 129.4263 | 0.052013 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.016626 | 0.59375 | 0.0092866 | 0.63692 | 0.011019 | 0.35695 | 0.0080692
1766 | 129.2343 | 0.023223 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.010886 | 0.54092 | 0.011019 | 0.54889 | 0.00647
1766.2 | 129.3303 | 0.023223 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 1.2266 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1766.4 | 129.3303 | 0.024822 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1766.6 | 129.2343 | 0.023223 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | -0.027368 | 0.45294 | 0.00647
1766.8 | 129.4263 | 0.023223 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1767 | 129.3303 | 0.023223 | 0.56715 | 0.0095362 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1767.2 | 129.2343 | 0.023223 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1767.4 | 129.2343 | 0.024822 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1767.6 | 129.2343 | 0.023223 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1767.8 | 129.2343 | 0.021623 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1768 | 129.2343 | 0.024822 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.26697 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1768.2 | 129.1384 | 0.021623 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.69137 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1768.4 | 129.1384 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1768.6 | 129.1384 | 0.023223 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1768.8 | 129.1384 | 0.023223 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1769 | 129.0424 | 0.021623 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1769.2 | 129.0424 | 0.023223 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1769.4 | 129.0424 | 0.023223 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.20987 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1769.6 | 129.1384 | 0.016825 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1769.8 | 129.0424 | 0.020024 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1770 | 129.1384 | 0.021623 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1770.2 | 129.0424 | 0.021623 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1770.4 | 129.0424 | 0.021623 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1770.6 | 129.0424 | 0.021623 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1770.8 | 128.9464 | 0.021623 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1771 | 128.9464 | 0.020024 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1771.2 | 129.0424 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1771.4 | 128.8504 | 0.020024 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1771.6 | 128.9464 | 0.021623 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1771.8 | 128.9464 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1772 | 129.0424 | 0.015225 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1772.2 | 128.9464 | 0.021623 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1772.4 | 128.8504 | 0.021623 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1772.6 | 128.9464 | 0.020024 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.36296 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1772.8 | 128.8504 | 0.021623 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.00647
1773 | 128.9464 | 0.020024 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1773.2 | 128.8504 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1773.4 | 128.8504 | 0.020024 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1773.6 | 128.9464 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1773.8 | 128.9464 | 0.020024 | 0.4712 | 0.0079364 | 0.66945 | 0.0096794 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1774 | 128.8504 | 0.020024 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1774.2 | 128.9464 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1774.4 | 128.8504 | 0.020024 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1774.6 | 128.8504 | 0.018424 | 0.4712 | 0.0063372 | 0.28557 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1774.8 | 128.8504 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.82882 | 0.0078201 | 0.54889 | 0.0080692
1775 | 128.8504 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1775.2 | 128.8504 | 0.016825 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.82882 | 0.0078201 | 0.54889 | 0.0080692
1775.4 | 128.8504 | 0.013626 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1775.6 | 128.8504 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1775.8 | 128.8504 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1776 | 128.8504 | 0.016825 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1776.2 | 128.8504 | 0.015225 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1776.4 | 128.7545 | 0.020024 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1776.6 | 128.7545 | 0.015225 | 0.56715 | 0.0079364 | 0.7654 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1776.8 | 128.7545 | 0.018424 | 0.56715 | 0.0079364 | 0.38156 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1777 | 128.7545 | 0.021623 | 0.4712 | 0.0079364 | 0.5735 | 0.011279 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1777.2 | 128.6585 | 0.03282 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1777.4 | 128.8504 | 0.020024 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.36296 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1777.6 | 128.8504 | 0.018424 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1777.8 | 128.8504 | 0.018424 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1778 | 128.8504 | 0.020024 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1778.2 | 128.7545 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.261 | 0.00647
1778.4 | 128.8504 | 0.018424 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1778.6 | 128.8504 | 0.018424 | 0.4712 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1778.8 | 128.7545 | 0.020024 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1779 | 128.7545 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1779.2 | 128.6585 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1779.4 | 128.8504 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1779.6 | 128.7545 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1779.8 | 128.7545 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.00033201 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1780 | 128.7545 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.0080692
1780.2 | 128.7545 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1780.4 | 128.8504 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1780.6 | 128.7545 | 0.020024 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1780.8 | 128.7545 | 0.020024 | 0.7591 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1781 | 128.7545 | 0.020024 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1781.2 | 128.7545 | 0.020024 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1781.4 | 128.6585 | 0.018424 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1781.6 | 128.7545 | 0.018424 | 0.4712 | 0.0063372 | 0.38156 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1781.8 | 128.7545 | 0.018424 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1782 | 128.7545 | 0.020024 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1782.2 | 128.7545 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.69137 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1782.4 | 128.7545 | 0.020024 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1782.6 | 128.8504 | 0.018424 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.20987 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1782.8 | 128.7545 | 0.018424 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1783 | 128.7545 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1783.2 | 128.7545 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1783.4 | 128.7545 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1783.6 | 128.7545 | 0.018424 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1783.8 | 128.6585 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0083293 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1784 | 128.7545 | 0.016825 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1784.2 | 128.7545 | 0.018424 | 0.66314 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1784.4 | 128.7545 | 0.016825 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1784.6 | 128.6585 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.25303 | 0.0078201 | 0.54889 | 0.00647
1784.8 | 128.6585 | 0.018424 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.011019 | 0.54889 | 0.00647
1785 | 128.5625 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1785.2 | 128.7545 | 0.020024 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1785.4 | 128.8504 | 0.018424 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1785.6 | 128.7545 | 0.018424 | 0.56715 | 0.011135 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1785.8 | 128.5625 | 0.018424 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1786 | 128.7545 | 0.016825 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.00647
1786.2 | 128.6585 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.7468 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1786.4 | 128.7545 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1786.6 | 128.7545 | 0.016825 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.00033201 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1786.8 | 128.7545 | 0.016825 | 0.7591 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.21153 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1787 | 128.7545 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1787.2 | 128.7545 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1787.4 | 128.7545 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1787.6 | 128.8504 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1787.8 | 128.7545 | 0.018424 | 0.56715 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1788 | 128.7545 | 0.016825 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1788.2 | 128.6585 | 0.020024 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1788.4 | 128.7545 | 0.018424 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1788.6 | 128.7545 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1788.8 | 128.7545 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1789 | 128.7545 | 0.018424 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1789.2 | 128.6585 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1789.4 | 128.7545 | 0.018424 | 0.56715 | 0.0015389 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1789.6 | 128.6585 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1789.8 | 128.7545 | 0.016825 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.00647
1790 | 128.6585 | 0.018424 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1790.2 | 128.6585 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.00647
1790.4 | 128.6585 | 0.018424 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.36296 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1790.6 | 128.6585 | 0.018424 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1790.8 | 128.6585 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1791 | 128.6585 | 0.018424 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1791.2 | 128.6585 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1791.4 | 128.6585 | 0.016825 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1791.6 | 128.6585 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1791.8 | 128.6585 | 0.018424 | 0.56715 | 0.0095362 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1792 | 128.5625 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1792.2 | 128.6585 | 0.016825 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1792.4 | 128.6585 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1792.6 | 128.6585 | 0.016825 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1792.8 | 128.5625 | 0.020024 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1793 | 128.5625 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1793.2 | 128.6585 | 0.018424 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1793.4 | 128.6585 | 0.016825 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1793.6 | 128.6585 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1793.8 | 128.5625 | 0.020024 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1794 | 128.5625 | 0.018424 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1794.2 | 128.5625 | 0.018424 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1794.4 | 128.5625 | 0.018424 | 0.4712 | 0.0063372 | 0.66945 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1794.6 | 128.5625 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1794.8 | 128.6585 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0060882 | 0.82882 | 0.0078201 | 0.54889 | 0.0080692
1795 | 128.5625 | 0.020024 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1795.2 | 128.6585 | 0.018424 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1795.4 | 128.6585 | 0.018424 | 0.4712 | 0.0079364 | 0.38156 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1795.6 | 128.5625 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1795.8 | 128.5625 | 0.020024 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1796 | 128.5625 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0016822 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1796.2 | 128.5625 | 0.018424 | 0.4712 | 0.0063372 | 0.7654 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1796.4 | 128.3706 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1796.6 | 128.1787 | 0.018424 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.00647
1796.8 | 128.2746 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.0070285 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.261 | 0.00647
1797 | 128.3706 | 0.018424 | 0.56715 | 0.0063372 | 0.7654 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1797.2 | 128.3706 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.34898 | 0.0078201 | 0.54889 | 0.0080692
1797.4 | 128.3706 | 0.020024 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1797.6 | 128.1787 | 0.018424 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1797.8 | 128.1787 | 0.020024 | 0.56715 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0054293 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1798 | 128.1787 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1798.2 | 128.3706 | 0.020024 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.54889 | 0.00647
1798.4 | 128.4666 | 0.020024 | 0.4712 | 0.0031381 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1798.6 | 128.4666 | 0.021623 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1798.8 | 128.4666 | 0.020024 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1799 | 128.5625 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1799.2 | 128.4666 | 0.020024 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1799.4 | 128.5625 | 0.020024 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.0080692
1799.6 | 128.5625 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1799.8 | 128.4666 | 0.020024 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1800 | 128.4666 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0083293 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1800.2 | 128.1787 | 0.020024 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1800.4 | 128.4666 | 0.020024 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1800.6 | 128.3706 | 0.020024 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1800.8 | 128.4666 | 0.020024 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.26697 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1801 | 128.6585 | 0.020024 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1801.2 | 128.4666 | 0.018424 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0030219 | 0.54889 | 0.00647
1801.4 | 128.5625 | 0.020024 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1801.6 | 128.5625 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.261 | 0.0080692
1801.8 | 128.3706 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1802 | 128.4666 | 0.020024 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1802.2 | 128.4666 | 0.020024 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.011019 | 0.54889 | 0.0080692
1802.4 | 128.4666 | 0.021623 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1802.6 | 128.4666 | 0.021623 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.0080692
1802.8 | 128.3706 | 0.020024 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.011019 | 0.64488 | 0.0080692
1803 | 128.3706 | 0.020024 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1803.2 | 128.3706 | 0.021623 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.009669
1803.4 | 128.3706 | 0.021623 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1803.6 | 128.3706 | 0.021623 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1803.8 | 128.3706 | 0.021623 | 0.4712 | 0.0063372 | 0.66945 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1804 | 128.3706 | 0.020024 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1804.2 | 128.3706 | 0.021623 | 0.56715 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.20987 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1804.4 | 128.3706 | 0.021623 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1804.6 | 128.3706 | 0.021623 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
1804.8 | 128.3706 | 0.021623 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.003531 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.16505 | 0.0080692
1805 | 128.3706 | 0.021623 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1805.2 | 128.3706 | 0.021623 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1805.4 | 128.3706 | 0.021623 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1805.6 | 128.3706 | 0.021623 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.0080692
1805.8 | 128.3706 | 0.021623 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.69137 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1806 | 128.3706 | 0.021623 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0046217 | 0.64488 | 0.00647
1806.2 | 128.3706 | 0.021623 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.20987 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1806.4 | 128.3706 | 0.021623 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1806.6 | 128.2746 | 0.021623 | 0.56715 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1806.8 | 127.8908 | 0.021623 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.34898 | 0.0078201 | 0.35695 | 0.00647
1807 | 127.9867 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1807.2 | 128.0827 | 0.024822 | 0.66314 | 0.011135 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.0054293 | 0.49776 | 0.0060882 | 0.73287 | 0.0062209 | 0.35695 | 0.00647
1807.4 | 127.9867 | 0.023223 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1807.6 | 127.7948 | 0.023223 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1807.8 | 127.6029 | 0.023223 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1808 | 127.6988 | 0.023223 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1808.2 | 127.5069 | 0.026422 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0080692
1808.4 | 127.6988 | 0.021623 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1808.6 | 127.5069 | 0.023223 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1808.8 | 127.6029 | 0.023223 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.7468 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.54889 | 0.0080692
1809 | 127.6029 | 0.023223 | 0.4712 | 0.0063372 | 0.7654 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1809.2 | 127.7948 | 0.023223 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1809.4 | 127.6029 | 0.021623 | 0.56715 | 0.0015389 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1809.6 | 127.6988 | 0.016825 | 0.7591 | -6.0896e-05 | 0.7654 | 0.0048812 | 0.45891 | 0.0067301 | 0.30748 | 0.015026 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1809.8 | 127.6029 | 0.023223 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.011019 | 0.45294 | 0.011268
1810 | 127.7948 | 0.024822 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.78732 | 0.015026 | 0.49776 | 0.0012893 | 0.63692 | 0.0078201 | 0.35695 | 0.0032709
1810.2 | 127.7948 | 0.028021 | 0.4712 | 0.0063372 | 0.5735 | 0.011279 | 0.45891 | 0.0083293 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.44497 | 0.0046217 | 0.45294 | 0.0080692
1810.4 | 128.0827 | 0.026422 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.7468 | 0.0019319 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1810.6 | 128.0827 | 0.024822 | 0.4712 | 0.004738 | 0.86139 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.010886 | 0.73287 | 0.0062209 | 0.74084 | 0.0080692
1810.8 | 128.3706 | 0.024822 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1811 | 128.3706 | 0.024822 | 0.56715 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1811.2 | 128.3706 | 0.024822 | 0.66314 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1811.4 | 128.3706 | 0.024822 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1811.6 | 128.5625 | 0.023223 | 0.4712 | 0.004738 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1811.8 | 128.5625 | 0.024822 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1812 | 128.6585 | 0.023223 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.00647
1812.2 | 128.5625 | 0.024822 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1812.4 | 128.5625 | 0.024822 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.011019 | 0.54889 | 0.00647
1812.6 | 128.5625 | 0.024822 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.16505 | 0.0080692
1812.8 | 128.5625 | 0.023223 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.21153 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1813 | 128.5625 | 0.023223 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1813.2 | 128.6585 | 0.023223 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1813.4 | 128.5625 | 0.024822 | 0.4712 | 0.004738 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1813.6 | 128.5625 | 0.024822 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1813.8 | 128.5625 | 0.026422 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1814 | 128.5625 | 0.028021 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1814.2 | 128.5625 | 0.029621 | 0.56715 | 0.0063372 | 0.66945 | 0.0096794 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1814.4 | 128.5625 | 0.028021 | 0.4712 | 0.0079364 | 0.7654 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.30582 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1814.6 | 128.4666 | 0.03282 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1814.8 | 128.4666 | 0.03122 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1815 | 128.4666 | 0.028021 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0083293 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0046217 | 0.54889 | 0.00647
1815.2 | 128.6585 | 0.037618 | 0.4712 | 0.0063372 | 0.5735 | 0.0096794 | 0.17102 | 0.0067301 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1815.4 | 128.4666 | 0.03282 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.00033201 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1815.6 | 128.3706 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0048812 | 0.45891 | 0.0051309 | 0.49942 | 0.015026 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1815.8 | 128.5625 | 0.026422 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.016626 | 0.59375 | 0.010886 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1816 | 128.4666 | 0.023223 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.012486 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1816.2 | 128.4666 | 0.026422 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1816.4 | 128.4666 | 0.023223 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.00033201 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1816.6 | 128.4666 | 0.024822 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1816.8 | 128.4666 | 0.024822 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 2.3643 | 0.0078201 | 0.54889 | 0.0080692
1817 | 128.3706 | 0.024822 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1817.2 | 128.4666 | 0.026422 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1817.4 | 128.4666 | 0.024822 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1817.6 | 128.3706 | 0.024822 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1817.8 | 128.1787 | 0.026422 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1818 | 128.2746 | 0.028021 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1818.2 | 128.2746 | 0.024822 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1818.4 | 128.2746 | 0.026422 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.011268
1818.6 | 128.2746 | 0.024822 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1818.8 | 128.2746 | 0.026422 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1819 | 128.0827 | 0.026422 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1819.2 | 128.1787 | 0.026422 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1819.4 | 128.1787 | 0.026422 | 0.56715 | 0.011135 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1819.6 | 128.0827 | 0.026422 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1819.8 | 128.2746 | 0.026422 | 0.56715 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1820 | 128.2746 | 0.028021 | 0.56715 | 0.0063372 | 0.38156 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1820.2 | 128.4666 | 0.026422 | 0.56715 | 0.0079364 | 0.66945 | 0.011279 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1820.4 | 128.7545 | 0.028021 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1820.6 | 128.7545 | 0.020024 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1820.8 | 128.2746 | 0.023223 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1821 | 128.2746 | 0.028021 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1821.2 | 128.2746 | 0.028021 | 0.4712 | 0.0079364 | 0.28557 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.68971 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1821.4 | 128.1787 | 0.026422 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0032709
1821.6 | 128.1787 | 0.026422 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1821.8 | 128.1787 | 0.026422 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1822 | 128.0827 | 0.026422 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1822.2 | 127.9867 | 0.028021 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1822.4 | 127.9867 | 0.028021 | 0.56715 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1822.6 | 127.8908 | 0.026422 | 0.56715 | 0.0063372 | 0.28557 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1822.8 | 127.7948 | 0.024822 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1823 | 127.7948 | 0.026422 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1823.2 | 127.7948 | 0.026422 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.011019 | 0.54889 | 0.0080692
1823.4 | 127.6029 | 0.028021 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1823.6 | 127.6029 | 0.026422 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1823.8 | 127.5069 | 0.028021 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1824 | 127.4109 | 0.028021 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0032709
1824.2 | 127.4109 | 0.028021 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.009669
1824.4 | 127.315 | 0.028021 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1824.6 | 127.123 | 0.028021 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.26697 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1824.8 | 126.9311 | 0.028021 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0032709
1825 | 127.0271 | 0.029621 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1825.2 | 127.0271 | 0.028021 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1825.4 | 126.9311 | 0.028021 | 0.56715 | 0.0063372 | 0.66945 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1825.6 | 126.9311 | 0.029621 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1825.8 | 126.9311 | 0.029621 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1826 | 126.9311 | 0.03282 | 0.56715 | 0.004738 | 0.7654 | 0.0064811 | 0.65085 | 0.003531 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.44497 | 0.011019 | 0.45294 | 0.009669
1826.2 | 127.315 | 0.028021 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0019319 | 0.59537 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1826.4 | 126.9311 | 0.03122 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0092866 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1826.6 | 127.0271 | 0.029621 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.00033201 | 0.40347 | 0.011827 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1826.8 | 127.0271 | 0.03122 | 0.56715 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.54092 | 0.0062209 | 0.54889 | 0.009669
1827 | 126.8351 | 0.034419 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1827.2 | 126.8351 | 0.039217 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1827.4 | 126.5472 | 0.03122 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1827.6 | 126.4513 | 0.034419 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1827.8 | 126.4513 | 0.047214 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1828 | 126.1634 | 0.018424 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1828.2 | 126.3553 | 0.024822 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.021424 | 0.40181 | 0.012486 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1828.4 | 126.2593 | 0.028021 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.59537 | 0.011827 | 0.59375 | 0.0092866 | 0.73287 | 0.0094199 | 0.54889 | 0.00647
1828.6 | 126.2593 | 0.03282 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.009669
1828.8 | 126.1634 | 0.03122 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.30582 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1829 | 126.1634 | 0.03122 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.36296 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1829.2 | 126.2593 | 0.03122 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1829.4 | 126.0674 | 0.03282 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1829.6 | 125.9714 | 0.03122 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1829.8 | 126.0674 | 0.03282 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1830 | 125.9714 | 0.03282 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1830.2 | 125.8755 | 0.03282 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1830.4 | 125.9714 | 0.03282 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1830.6 | 125.8755 | 0.03282 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1830.8 | 125.7795 | 0.034419 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1831 | 125.8755 | 0.034419 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1831.2 | 125.8755 | 0.034419 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1831.4 | 125.8755 | 0.036018 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1831.6 | 125.7795 | 0.034419 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1831.8 | 125.7795 | 0.036018 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1832 | 125.7795 | 0.036018 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.009669
1832.2 | 125.6835 | 0.037618 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1832.4 | 125.6835 | 0.036018 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1832.6 | 125.6835 | 0.036018 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1832.8 | 125.6835 | 0.037618 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1833 | 125.6835 | 0.037618 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1833.2 | 125.4916 | 0.037618 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1833.4 | 125.5876 | 0.037618 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0099291 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.00647
1833.6 | 125.5876 | 0.036018 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.0080692
1833.8 | 125.5876 | 0.037618 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1834 | 125.5876 | 0.036018 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0019319 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1834.2 | 125.5876 | 0.039217 | 0.4712 | 0.0079364 | 0.66945 | 0.0048812 | 0.45891 | 0.0099291 | 0.49942 | 0.010228 | 0.59375 | 0.015685 | 0.63692 | 0.0078201 | 0.45294 | 0.012868
1834.4 | 125.8755 | 0.037618 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1834.6 | 126.0674 | 0.037618 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.0070285 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1834.8 | 126.0674 | 0.039217 | 0.4712 | 0.0063372 | 0.66945 | 0.0096794 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1835 | 126.0674 | 0.039217 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.0080692
1835.2 | 126.1634 | 0.040817 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1835.4 | 126.0674 | 0.037618 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.011019 | 0.54889 | 0.0080692
1835.6 | 126.2593 | 0.040817 | 0.56715 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1835.8 | 126.5472 | 0.040817 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.68971 | 0.0092866 | 0.63692 | 0.0094199 | 0.35695 | 0.0080692
1836 | 126.6432 | 0.039217 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.00647
1836.2 | 126.6432 | 0.040817 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1836.4 | 126.4513 | 0.039217 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1836.6 | 126.6432 | 0.039217 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1836.8 | 127.315 | 0.042416 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1837 | 127.123 | 0.042416 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.45294 | 0.009669
1837.2 | 127.219 | 0.048814 | 0.66314 | 0.0095362 | 0.47751 | 0.0080803 | 0.45891 | 0.011528 | 0.59537 | 0.011827 | 0.68971 | 0.0028892 | 0.63692 | 0.011019 | 0.64488 | 0.00647
1837.4 | 127.6029 | 0.040817 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1837.6 | 127.5069 | 0.042416 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1837.8 | 127.4109 | 0.042416 | 0.37521 | 0.0095362 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.74084 | 0.00647
1838 | 127.6029 | 0.042416 | 0.27926 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | -0.002568 | 1.2655 | 0.0060882 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1838.2 | 127.6029 | 0.042416 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.68971 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1838.4 | 127.9867 | 0.042416 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1838.6 | 127.8908 | 0.044015 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1838.8 | 127.8908 | 0.042416 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.21153 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1839 | 127.7948 | 0.042416 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1839.2 | 127.6988 | 0.042416 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1839.4 | 127.7948 | 0.045615 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1839.6 | 127.315 | 0.058411 | 0.56715 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1839.8 | 126.0674 | 0.25194 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1840 | 125.6835 | 0.29993 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.010228 | 0.78566 | 0.0092866 | 0.63692 | 0.0078201 | 0.74084 | 0.00647
1840.2 | 125.2996 | 0.33032 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.011827 | 1.1695 | 0.012486 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1840.4 | 125.1077 | 0.36231 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 1.3615 | 0.018884 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1840.6 | 124.7239 | 0.3895 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 1.5534 | 0.023682 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1840.8 | 124.34 | 0.41349 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.015026 | 1.7453 | 0.02848 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1841 | 124.0521 | 0.44068 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 1.7453 | 0.03008 | 0.63692 | 0.0094199 | 0.45294 | 0.0080692
1841.2 | 123.9561 | 0.46147 | 0.66314 | 0.0095362 | 0.38156 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.016626 | 1.8413 | 0.03008 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1841.4 | 123.3803 | 0.48387 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 1.7453 | 0.033279 | 0.63692 | 0.011019 | 0.45294 | 0.011268
1841.6 | 123.2844 | 0.50466 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 1.8413 | 0.031679 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1841.8 | 123.3803 | 0.52705 | 0.56715 | 0.011135 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.013427 | 1.8413 | 0.03008 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1842 | 123.1884 | 0.54305 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 1.7453 | 0.031679 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1842.2 | 123.2844 | 0.55264 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.0086283 | 1.7453 | 0.03008 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1842.4 | 122.7085 | 0.56864 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 2.0333 | 0.031679 | 0.63692 | 0.0094199 | 0.74084 | 0.00647
1842.6 | 123.0924 | 0.58303 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.0022303 | 1.7453 | 0.031679 | 0.82882 | 0.0094199 | 0.64488 | 7.1911e-05
1842.8 | 122.8045 | 0.60222 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 1.8413 | 0.031679 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1843 | 122.7085 | 0.61342 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 1.8413 | 0.031679 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1843.2 | 122.5166 | 0.61982 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 1.8413 | 0.03008 | 0.54092 | 0.0094199 | 0.64488 | 0.00647
1843.4 | 122.4206 | 0.62782 | 0.37521 | 0.0063372 | 0.86139 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 1.7453 | 0.031679 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1843.6 | 122.3247 | 0.63901 | 0.37521 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.78732 | 0.010228 | 1.8413 | 0.033279 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1843.8 | 122.1327 | 0.64861 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 1.8413 | 0.031679 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1844 | 122.0368 | 0.65981 | 0.56715 | 0.004738 | 0.38156 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 1.8413 | 0.031679 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1844.2 | 121.8448 | 0.6678 | 0.56715 | 0.0063372 | 0.7654 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 1.9373 | 0.034878 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1844.4 | 121.7489 | 0.6774 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 1.8413 | 0.033279 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1844.6 | 121.5569 | 0.687 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 2.0333 | 0.031679 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1844.8 | 121.5569 | 0.69179 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.0086283 | 1.9373 | 0.038077 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1845 | 121.1731 | 0.70619 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 1.8413 | 0.033279 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1845.2 | 120.8852 | 0.71259 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 1.9373 | 0.033279 | 0.44497 | 0.0062209 | 0.74084 | 0.0080692
1845.4 | 120.5013 | 0.71899 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 2.0333 | 0.031679 | 0.73287 | 0.0094199 | 0.64488 | 0.00647
1845.6 | 120.4053 | 0.72378 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 1.9373 | 0.033279 | 0.34898 | 0.0078201 | 0.54889 | 0.009669
1845.8 | 120.3094 | 0.73978 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.011827 | 1.9373 | 0.033279 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1846 | 120.3094 | 0.75737 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.78732 | 0.010228 | 1.8413 | 0.03008 | 0.54092 | 0.0094199 | 0.64488 | 0.00647
1846.2 | 120.0215 | 0.76857 | 0.66314 | 0.004738 | 0.5735 | 0.0048812 | 0.65085 | 0.0067301 | 0.59537 | 0.010228 | 2.2252 | 0.034878 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1846.4 | 120.1174 | 0.79416 | 0.4712 | 0.0031381 | 0.5735 | 0.0064811 | 0.45891 | 0.0083293 | 0.30748 | 0.010228 | 1.9373 | 0.034878 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1846.6 | 120.3094 | 0.82135 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 2.0333 | 0.034878 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1846.8 | 119.7336 | 0.85014 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 1.9373 | 0.038077 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1847 | 119.1577 | 0.87893 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 2.1292 | 0.034878 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1847.2 | 118.9658 | 0.90932 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0099291 | 0.49942 | 0.010228 | 2.0333 | 0.036477 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1847.4 | 118.6779 | 0.92851 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 2.1292 | 0.033279 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1847.6 | 121.8448 | 0.99729 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 2.1292 | 0.039676 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1847.8 | 121.7489 | 1.0517 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 2.3212 | 0.039676 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1848 | 121.461 | 1.0885 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 2.5131 | 0.038077 | 0.54092 | 0.0078201 | 0.45294 | 0.009669
1848.2 | 121.0771 | 1.1572 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 2.4171 | 0.039676 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1848.4 | 120.5013 | 1.2212 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 2.3212 | 0.039676 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1848.6 | 119.9255 | 1.2964 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 2.3212 | 0.041276 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1848.8 | 119.2537 | 1.3876 | 0.66314 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 2.4171 | 0.041276 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1849 | 118.7739 | 1.4499 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 2.3212 | 0.039676 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1849.2 | 117.9102 | 1.5443 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 2.3212 | 0.039676 | 0.63692 | 0.0046217 | 0.54889 | 0.00647
1849.4 | 117.2384 | 1.6563 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 2.3212 | 0.039676 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1849.6 | 115.9908 | 1.8194 | 0.66314 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 2.3212 | 0.039676 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1849.8 | 115.8949 | 1.8306 | 0.66314 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.011827 | 2.3212 | 0.038077 | 0.73287 | 0.011019 | 0.64488 | 0.0080692
1850 | 125.2037 | 0.61822 | 0.7591 | 0.0079364 | 0.47751 | 0.0080803 | 0.7468 | 0.0099291 | 0.49942 | 0.013427 | 1.8413 | 0.03008 | 1.0208 | 0.0046217 | 0.45294 | 0.017666
1850.2 | 126.0674 | 0.41509 | 0.56715 | 0.011135 | 0.18962 | 0.003282 | 0.26697 | 0.0067301 | 0.40347 | 0.0054293 | 1.5534 | 0.015685 | 0.82882 | 0.0078201 | 0.64488 | 0.00647
1850.4 | 122.5166 | 0.94131 | 0.56715 | 0.0063372 | 0.7654 | 0.0064811 | 0.36296 | 0.0051309 | 0.30748 | 0.011827 | 1.1695 | 0.025281 | 0.82882 | 0.011019 | 0.64488 | 0.009669
1850.6 | 120.8852 | 1.154 | 0.66314 | 0.0063372 | 0.5735 | 0.0048812 | 0.65085 | 0.0067301 | 0.49942 | 0.013427 | 1.5534 | 0.025281 | 0.44497 | 0.0078201 | 0.64488 | 0.009669
1850.8 | 120.7892 | 1.186 | 0.56715 | 0.0079364 | 0.28557 | 0.0064811 | 0.5549 | 0.0019319 | 0.59537 | 0.0086283 | 1.8413 | 0.026881 | 0.73287 | 0.0078201 | 0.64488 | 0.0080692
1851 | 122.2287 | 0.99889 | 0.27926 | 0.0063372 | 0.47751 | 0.003282 | 0.26697 | 0.0099291 | 0.30748 | 0.0070285 | 1.9373 | 0.015685 | 0.63692 | 0.017417 | 1.2207 | 0.00647
1851.2 | 122.4206 | 0.9781 | 0.4712 | 0.012735 | 0.7654 | 0.003282 | 0.5549 | 0.0067301 | 0.49942 | 0.0070285 | 1.5534 | 0.025281 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1851.4 | 121.9408 | 1.0357 | 0.66314 | 0.0063372 | 0.47751 | 0.0096794 | 0.45891 | 0.0083293 | 0.69137 | 0.0070285 | 1.6494 | 0.023682 | 0.73287 | 0.011019 | 0.261 | 0.00647
1851.6 | 122.4206 | 0.9653 | 0.56715 | -6.0896e-05 | 0.47751 | 0.0048812 | 0.36296 | 0.0067301 | 0.78732 | 0.011827 | 1.8413 | 0.02848 | 0.25303 | 0.0078201 | 0.54889 | 0.009669
1851.8 | 122.4206 | 1.0117 | 0.7591 | 0.0095362 | 0.38156 | 0.011279 | 0.26697 | -0.0076652 | 0.30748 | 0.0070285 | 1.5534 | 0.02848 | 0.82882 | 0.0094199 | 0.35695 | 0.0080692
1852 | 124.34 | 0.679 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.17102 | 0.003531 | 0.59537 | 0.013427 | 1.4574 | 0.023682 | 0.44497 | 0.0046217 | 0.64488 | 0.011268
1852.2 | 125.1077 | 0.59743 | 0.37521 | 0.004738 | 0.86139 | 8.3003e-05 | 0.17102 | 0.0051309 | 0.69137 | 0.018225 | 1.5534 | 0.022083 | 0.73287 | 0.011019 | 0.35695 | 0.0032709
1852.4 | 124.0521 | 0.75577 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 1.4574 | 0.022083 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1852.6 | 125.2996 | 0.58143 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 1.4574 | 0.025281 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1852.8 | 125.0117 | 0.61822 | 0.66314 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.69137 | 0.011827 | 1.5534 | 0.026881 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1853 | 124.244 | 0.70939 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 1.7453 | 0.03008 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1853.2 | 123.7642 | 0.79096 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 1.8413 | 0.034878 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1853.4 | 123.2844 | 0.85014 | 0.66314 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 1.9373 | 0.034878 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1853.6 | 123.1884 | 0.84534 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 1.9373 | 0.034878 | 0.63692 | 0.0094199 | 0.64488 | 0.0048708
1853.8 | 121.365 | 1.0821 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 2.0333 | 0.036477 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1854 | 121.365 | 1.1172 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 2.2252 | 0.038077 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1854.2 | 122.2287 | 0.94771 | 0.7591 | 0.0095362 | 0.66945 | 0.011279 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 2.0333 | 0.034878 | 0.63692 | 0.0094199 | 0.45294 | 0.0080692
1854.4 | 123.3803 | 0.84054 | 0.66314 | 0.0063372 | 0.47751 | 0.0096794 | 0.65085 | 0.0067301 | 0.69137 | 0.0086283 | 2.0333 | 0.03008 | 0.44497 | 0.0078201 | 0.74084 | 0.0048708
1854.6 | 123.9561 | 0.77017 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 1.7453 | 0.03008 | 0.54092 | 0.0078201 | 0.54889 | 0.0016718
1854.8 | 123.5722 | 0.85014 | 0.7591 | 0.0095362 | 0.47751 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 1.7453 | 0.03008 | 0.73287 | 0.0078201 | 0.64488 | 0.00647
1855 | 122.9965 | 0.92851 | 0.56715 | 0.0063372 | 0.7654 | 0.0096794 | 0.36296 | 0.013128 | 0.69137 | 0.011827 | 1.8413 | 0.031679 | 0.63692 | 0.0094199 | 0.74084 | 0.00647
1855.2 | 122.7085 | 0.93331 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 1.7453 | 0.031679 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1855.4 | 121.8448 | 1.0533 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 1.9373 | 0.033279 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1855.6 | 121.6529 | 1.0597 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 1.9373 | 0.033279 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1855.8 | 120.7892 | 1.202 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 2.0333 | 0.034878 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1856 | 119.6376 | 1.346 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 2.1292 | 0.036477 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1856.2 | 119.9255 | 1.2996 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 2.1292 | 0.036477 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1856.4 | 118.8698 | 1.4211 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0083293 | 0.59537 | 0.011827 | 2.2252 | 0.038077 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1856.6 | 119.0618 | 1.4179 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 2.2252 | 0.042875 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1856.8 | 118.9658 | 1.4419 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 2.2252 | 0.039676 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1857 | 118.9658 | 1.4291 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 2.3212 | 0.038077 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1857.2 | 119.0618 | 1.4131 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 2.2252 | 0.038077 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1857.4 | 119.4457 | 1.3572 | 0.66314 | 0.0079364 | 0.66945 | 0.0064811 | 0.65085 | 0.0067301 | 0.59537 | 0.010228 | 2.2252 | 0.036477 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1857.6 | 119.3497 | 1.378 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 2.2252 | 0.034878 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1857.8 | 119.6376 | 1.33 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 2.2252 | 0.036477 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1858 | 119.6376 | 1.3476 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.69137 | 0.011827 | 2.0333 | 0.036477 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1858.2 | 119.1577 | 1.3828 | 0.66314 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 2.1292 | 0.034878 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1858.4 | 119.2537 | 1.3956 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 4.53 | 0.011827 | 2.1292 | 0.036477 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1858.6 | 119.8295 | 1.2884 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 5.0099 | 0.016626 | 2.2252 | 0.036477 | 0.54092 | 0.0062209 | 0.35695 | 0.0080692
1858.8 | 121.5569 | 1.0677 | 0.66314 | 0.0079364 | 1.0533 | 0.0080803 | 0.45891 | 0.0083293 | 1.747 | 0.011827 | 2.0333 | 0.03008 | 0.82882 | 0.0078201 | 0.64488 | 0.00647
1859 | 120.7892 | 1.178 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 1.0752 | 0.015026 | 1.9373 | 0.031679 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1859.2 | 120.4053 | 1.2644 | 0.56715 | 0.011135 | 0.47751 | 0.0080803 | 0.36296 | 0.003531 | 0.97926 | 0.015026 | 1.9373 | 0.031679 | 1.0208 | 0.0094199 | 0.54889 | 0.0080692
1859.4 | 120.8852 | 1.1748 | 0.4712 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.003531 | 0.78732 | 0.015026 | 1.8413 | 0.03008 | 0.54092 | 0.012619 | 0.54889 | 0.0080692
1859.6 | 120.1174 | 1.2644 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0019319 | 0.88331 | 0.016626 | 1.8413 | 0.038077 | 0.54092 | 0.011019 | 0.74084 | 0.0048708
1859.8 | 118.1021 | 1.5235 | 0.56715 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0051309 | 1.1712 | 0.015026 | 2.0333 | 0.036477 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1860 | 119.5416 | 1.3476 | 0.4712 | 0.0095362 | 0.5735 | 0.0048812 | 0.5549 | 0.0083293 | 0.97926 | 0.015026 | 2.0333 | 0.034878 | 0.63692 | 0.0062209 | 0.64488 | 0.009669
1860.2 | 120.1174 | 1.2772 | 0.66314 | 0.0095362 | 0.7654 | 0.0080803 | 0.5549 | 0.0051309 | 0.88331 | 0.015026 | 2.2252 | 0.038077 | 0.44497 | 0.0078201 | 0.45294 | 0.0080692
1860.4 | 120.6932 | 1.1988 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.78732 | 0.011827 | 1.9373 | 0.034878 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1860.6 | 121.8448 | 1.0437 | 0.4712 | 0.0079364 | 0.47751 | 0.0048812 | 0.5549 | 0.0051309 | 0.78732 | 0.010228 | 1.9373 | 0.033279 | 0.63692 | 0.0062209 | 0.64488 | 0.00647
1860.8 | 120.6932 | 1.218 | 0.66314 | 0.0095362 | 0.47751 | 0.0080803 | 0.45891 | 0.0019319 | 0.49942 | 0.013427 | 1.9373 | 0.034878 | 0.73287 | 0.0078201 | 0.54889 | 0.011268
1861 | 121.461 | 1.1029 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 1.9373 | 0.02848 | 0.73287 | 0.0094199 | 0.45294 | 0.011268
1861.2 | 120.8852 | 1.1988 | 0.66314 | 0.011135 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.78732 | 0.011827 | 2.0333 | 0.034878 | 0.63692 | 0.0078201 | 0.74084 | 0.0080692
1861.4 | 121.1731 | 1.1204 | 0.66314 | 0.0095362 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.78732 | 0.013427 | 2.1292 | 0.031679 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1861.6 | 121.269 | 1.1125 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.015026 | 1.9373 | 0.033279 | 0.63692 | 0.011019 | 0.64488 | 0.00647
1861.8 | 124.0521 | 0.74138 | 0.27926 | 0.0063372 | 0.66945 | 0.003282 | 0.26697 | 0.003531 | 0.78732 | 0.0038295 | 2.2252 | 0.02848 | 0.44497 | 0.0030219 | 0.64488 | 0.00647
1862 | 124.148 | 0.73338 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.78732 | 0.011827 | 1.8413 | 0.031679 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1862.2 | 123.1884 | 0.86613 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.003531 | 0.78732 | 0.011827 | 1.9373 | 0.034878 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1862.4 | 120.3094 | 1.2468 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.88331 | 0.015026 | 2.609 | 0.044475 | 0.73287 | 0.0078201 | 0.64488 | 0.0080692
1862.6 | 118.6779 | 1.4675 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.97926 | 0.011827 | 3.0889 | 0.052472 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1862.8 | 120.3094 | 1.2468 | 0.56715 | 0.0079364 | 0.47751 | 0.0096794 | 0.5549 | 0.0067301 | 1.0752 | 0.015026 | 2.609 | 0.044475 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1863 | 119.7336 | 1.3092 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0019319 | 0.78732 | 0.010228 | 1.9373 | 0.031679 | 0.63692 | 0.0078201 | 0.64488 | 0.011268
1863.2 | 118.486 | 1.4947 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.78732 | 0.011827 | 1.7453 | 0.03008 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1863.4 | 117.1424 | 1.6787 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.78732 | 0.011827 | 1.7453 | 0.03008 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1863.6 | 114.3594 | 2.0417 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.69137 | 0.011827 | 1.7453 | 0.03008 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1863.8 | 111.7683 | 2.3808 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.69137 | 0.015026 | 1.9373 | 0.033279 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1864 | 109.0812 | 2.7471 | 0.66314 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 2.1292 | 0.036477 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1864.2 | 109.2731 | 2.7247 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.69137 | 0.011827 | 2.0333 | 0.034878 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1864.4 | 107.7377 | 2.9182 | 0.66314 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.0067301 | 0.78732 | 0.011827 | 2.1292 | 0.038077 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1864.6 | 107.9296 | 2.9022 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 2.3212 | 0.036477 | 0.63692 | 0.0062209 | 0.54889 | 0.009669
1864.8 | 108.5054 | 2.8047 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.69137 | 0.011827 | 1.9373 | 0.033279 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1865 | 109.1772 | 2.7215 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 1.9373 | 0.034878 | 0.54092 | 0.0078201 | 0.64488 | 0.009669
1865.2 | 112.7279 | 2.2689 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0083293 | 0.59537 | 0.013427 | 1.9373 | 0.033279 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1865.4 | 115.415 | 1.8946 | 0.66314 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 2.2252 | 0.038077 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1865.6 | 115.1271 | 1.9906 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.69137 | 0.011827 | 2.1292 | 0.033279 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1865.8 | 115.7029 | 1.7938 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.78732 | 0.010228 | 2.0333 | 0.031679 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1866 | 104.2828 | 3.3789 | 0.7591 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.0067301 | 0.69137 | 0.011827 | 2.609 | 0.038077 | 0.63692 | 0.0046217 | 0.261 | 0.0080692
1866.2 | 102.0756 | 3.6572 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.69137 | 0.011827 | 2.8969 | 0.049273 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1866.4 | 101.8836 | 3.6636 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.69137 | 0.011827 | 3.0889 | 0.042875 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1866.6 | 102.8433 | 3.5484 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.69137 | 0.011827 | 2.609 | 0.042875 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1866.8 | 102.8433 | 3.5628 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 2.801 | 0.046074 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1867 | 102.4595 | 3.5692 | 0.66314 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 2.9929 | 0.047674 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1867.2 | 101.4038 | 3.6892 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 3.1849 | 0.050873 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1867.4 | 96.9893 | 4.3098 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.69137 | 0.011827 | 3.8566 | 0.062069 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1867.6 | 95.6458 | 4.4857 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.65085 | 0.0083293 | 0.59537 | 0.013427 | 4.9123 | 0.076464 | 0.54092 | 0.0094199 | 0.64488 | 0.00647
1867.8 | 101.9796 | 3.6268 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.69137 | 0.010228 | 7.4074 | 0.11965 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1868 | 105.8183 | 3.1901 | 0.7591 | 0.0095362 | 0.66945 | 0.0064811 | 0.84279 | 0.0067301 | 0.88331 | 0.010228 | 7.5034 | 0.12125 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1868.2 | 99.1966 | 4.0155 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.69137 | 0.010228 | 8.7509 | 0.13244 | 0.73287 | 0.0078201 | 0.54889 | 0.009669
1868.4 | 93.7264 | 4.7208 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 14.7969 | 0.22681 | 0.73287 | 0.0078201 | 0.64488 | 0.0080692
1868.6 | 92.8627 | 4.8376 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.69137 | 0.011827 | 17.1001 | 0.2684 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1868.8 | 93.4385 | 4.7448 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0083293 | 0.69137 | 0.010228 | 18.8275 | 0.29399 | 0.73287 | 0.0078201 | 0.45294 | 0.009669
1869 | 94.6861 | 4.5961 | 0.7591 | 0.0079364 | 0.66945 | 0.003282 | 0.65085 | 0.0051309 | 0.69137 | 0.011827 | 13.0695 | 0.21082 | 0.73287 | 0.0078201 | 0.74084 | 0.0080692
1869.2 | 95.9337 | 4.4169 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 9.1348 | 0.14844 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1869.4 | 97.1812 | 4.2394 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.7468 | 0.0051309 | 0.69137 | 0.010228 | 16.0445 | 0.2556 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1869.6 | 97.853 | 4.1914 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.59537 | 0.011827 | 18.7315 | 0.30838 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1869.8 | 100.3482 | 3.8507 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 9.7106 | 0.15964 | 0.63692 | 0.0014227 | 0.54889 | 0.0080692
1870 | 101.4998 | 3.7116 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 7.6953 | 0.13244 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1870.2 | 101.7877 | 3.662 | 0.7591 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.69137 | 0.010228 | 6.7357 | 0.11645 | 0.63692 | 0.0078201 | 0.74084 | 0.0080692
1870.4 | 100.732 | 3.7995 | 0.66314 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.59537 | 0.011827 | 6.9276 | 0.11645 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1870.6 | 105.4344 | 3.1693 | 0.66314 | 0.012735 | 0.66945 | 0.0080803 | 0.7468 | 0.0051309 | 0.69137 | 0.0070285 | 7.2155 | 0.11965 | 0.73287 | 0.0030219 | 0.64488 | 0.00647
1870.8 | 108.3134 | 2.8079 | 0.95104 | 0.0095362 | 0.7654 | 0.003282 | 0.45891 | 0.0067301 | 0.49942 | 0.0086283 | 6.0639 | 0.11005 | 0.63692 | 0.0062209 | 0.83679 | 0.0016718
1871 | 111.2884 | 2.4224 | 0.66314 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.0067301 | 0.88331 | 0.013427 | 5.4881 | 0.095657 | 0.92481 | 0.0062209 | 0.64488 | 0.0080692
1871.2 | 112.2481 | 2.2673 | 0.4712 | 0.0079364 | 0.66945 | -0.0015162 | 1.1307 | 0.003531 | 0.88331 | 0.011827 | 4.7203 | 0.084461 | 0.63692 | 0.0030219 | 0.069058 | 0.012868
1871.4 | 112.3441 | 2.2433 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.003531 | 0.88331 | 0.010228 | 4.5284 | 0.082862 | 0.54092 | 0.0078201 | 0.64488 | 0.0048708
1871.6 | 108.6014 | 2.7919 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.65085 | 0.0067301 | 0.88331 | 0.0038295 | 6.2558 | 0.098856 | 0.63692 | 0.012619 | 0.54889 | 0.0080692
1871.8 | 107.0659 | 2.9886 | 0.85505 | 0.0095362 | 0.7654 | 0.0064811 | 0.65085 | 0.003531 | 0.59537 | 0.0086283 | 6.9276 | 0.11645 | 0.73287 | 0.0094199 | 0.54889 | 0.00647
1872 | 107.4498 | 2.9086 | 0.37521 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0083293 | 0.59537 | 0.011827 | 6.0639 | 0.10845 | 0.73287 | 0.011019 | 0.64488 | 0.0016718
1872.2 | 110.7127 | 2.5008 | 0.27926 | 0.0079364 | 0.47751 | 0.0064811 | 0.45891 | 0.011528 | 0.019589 | 0.010228 | 5.4881 | 0.092459 | 0.44497 | 0.012619 | 0.54889 | 0.0048708
1872.4 | 107.8336 | 2.9054 | 0.56715 | 0.0063372 | 0.66945 | 0.011279 | 0.45891 | 0.0067301 | 0.59537 | 0.013427 | 6.5437 | 0.11165 | 0.73287 | 0.0062209 | 0.45294 | 0.0048708
1872.6 | 107.0659 | 3.0014 | 0.85505 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.015026 | 6.3518 | 0.11005 | 0.73287 | 0.0046217 | 0.74084 | 0.011268
1872.8 | 105.1465 | 3.2589 | 0.56715 | 0.0095362 | 0.7654 | 0.0048812 | 0.7468 | 0.003531 | 0.88331 | 0.0086283 | 7.0235 | 0.11325 | 0.54092 | 0.0094199 | 0.45294 | 0.012868
1873 | 106.586 | 3.0462 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.7468 | 0.0019319 | 1.0752 | 0.011827 | 6.3518 | 0.11005 | 0.63692 | 0.0046217 | 0.45294 | 0.00647
1873.2 | 106.2981 | 3.0846 | 0.66314 | 0.0079364 | 0.66945 | 0.0048812 | 0.7468 | 0.0067301 | 0.30748 | 0.010228 | 6.4477 | 0.11325 | 0.34898 | 0.014218 | 0.64488 | 0.009669
1873.4 | 104.5707 | 3.2557 | 0.7591 | 0.004738 | 0.47751 | 0.0080803 | 0.7468 | 0.00033201 | 0.88331 | 0.013427 | 7.2155 | 0.12765 | 0.82882 | 0.0078201 | 0.64488 | 0.0048708
1873.6 | 100.0603 | 3.8843 | 0.37521 | 0.0095362 | 0.38156 | 0.0064811 | 0.45891 | 0.0051309 | 0.30748 | 0.018225 | 8.0792 | 0.13085 | 0.63692 | 0.012619 | 1.0287 | 0.0080692
1873.8 | 102.1715 | 3.5916 | 0.66314 | 0.0095362 | 0.66945 | 0.0096794 | -0.21287 | 0.0067301 | 0.40347 | 0.016626 | 8.655 | 0.12765 | 0.06109 | 0.0078201 | 0.261 | 0.009669
1874 | 107.5457 | 2.9038 | 0.66314 | 0.0063372 | 0.38156 | 0.0080803 | 0.84279 | 0.011528 | 0.49942 | 0.0070285 | 8.9429 | 0.15484 | 0.63692 | 0.011019 | 0.45294 | 0.009669
1874.2 | 108.6973 | 2.7247 | 0.66314 | 0.015934 | 0.95734 | 0.003282 | 0.65085 | 0.011528 | 0.49942 | 0.010228 | 5.68 | 0.10685 | 0.25303 | 0.0030219 | 1.0287 | -0.0015273
1874.4 | 101.3079 | 3.7212 | 0.7591 | 0.0063372 | 0.66945 | 0.0048812 | 0.17102 | 0.0083293 | 0.88331 | 0.015026 | 7.3114 | 0.11805 | 0.73287 | 0.0078201 | 0.74084 | 0.0080692
1874.6 | 102.0756 | 3.6348 | 1.047 | 0.004738 | 0.38156 | 0.0048812 | 0.45891 | 0.0051309 | 0.30748 | 0.013427 | 7.1195 | 0.10685 | 0.92481 | 0.0046217 | 0.261 | 0.014467
1874.8 | 102.4595 | 3.5804 | 0.56715 | 0.0095362 | 1.0533 | 0.0080803 | 0.7468 | 0.0083293 | -0.17235 | 0.015026 | 6.1598 | 0.10365 | 0.73287 | 0.0046217 | 0.64488 | 0.019265
1875 | 105.3385 | 3.1757 | 0.37521 | 0.0063372 | 0.66945 | 0.0096794 | 0.45891 | 0.0067301 | 0.49942 | 0.013427 | 5.584 | 0.092459 | 0.73287 | 0.017417 | 0.45294 | 0.0080692
1875.2 | 106.1062 | 3.0942 | 1.4309 | 0.0015389 | 0.7654 | 0.0064811 | 1.0347 | 0.0051309 | 0.59537 | 0.016626 | 6.1598 | 0.10206 | 0.34898 | 0.0062209 | 1.3166 | 0.017666
1875.4 | 105.2425 | 3.1773 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.45891 | 0.0083293 | 0.69137 | 0.010228 | 6.2558 | 0.10046 | 1.0208 | 0.0078201 | 0.261 | 0.0080692
1875.6 | 102.4595 | 3.5324 | 0.7591 | 0.0031381 | 0.66945 | 0.003282 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 6.8316 | 0.12285 | 0.06109 | 0.012619 | 0.45294 | 0.009669
1875.8 | 100.3482 | 3.8155 | 0.4712 | 0.0079364 | 0.7654 | 0.0064811 | 0.36296 | 0.003531 | 0.88331 | 0.016626 | 7.4074 | 0.11805 | 0.44497 | 0.0062209 | 0.35695 | 0.012868
1876 | 101.8836 | 3.5724 | 0.4712 | -0.0064583 | 0.47751 | 0.0064811 | 0.65085 | 0.0067301 | 0.59537 | 0.010228 | 6.7357 | 0.11645 | 0.73287 | 0.0062209 | 0.74084 | 0.014467
1876.2 | 106.2022 | 3.0206 | 0.66314 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.0019319 | 0.59537 | 0.0070285 | 5.68 | 0.097257 | 0.82882 | 0.015817 | 0.45294 | 0.00647
1876.4 | 105.5304 | 3.1518 | 0.66314 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.78732 | 0.013427 | 4.5284 | 0.082862 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1876.6 | 104.4748 | 3.2925 | 0.56715 | 0.0095362 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.69137 | 0.010228 | 4.5284 | 0.084461 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1876.8 | 104.3788 | 3.3549 | 0.37521 | 0.011135 | 0.66945 | 0.0064811 | 0.075065 | 0.013128 | 0.88331 | 0.018225 | 4.4324 | 0.078063 | 0.73287 | 0.011019 | 0.64488 | 0.012868
1877 | 100.6361 | 3.8075 | 0.7591 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 5.0082 | 0.086061 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1877.2 | 97.0853 | 4.2538 | 0.56715 | 0.004738 | 0.66945 | 0.011279 | 0.45891 | 0.0019319 | 0.59537 | 0.011827 | 5.584 | 0.095657 | 0.44497 | 0.0078201 | 0.45294 | 0.0080692
1877.4 | 96.8934 | 4.2394 | 0.56715 | 0.0063372 | 0.38156 | 0.0064811 | 0.45891 | 0.0051309 | 0.59537 | 0.010228 | 5.68 | 0.098856 | 0.63692 | 0.0062209 | 0.54889 | 0.009669
1877.6 | 98.5248 | 4.0474 | 0.66314 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.0051309 | 0.69137 | 0.010228 | 5.3921 | 0.08926 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1877.8 | 103.5151 | 3.4173 | 0.66314 | 0.011135 | 0.7654 | 0.0048812 | 0.5549 | 0.0051309 | 0.78732 | 0.010228 | 4.5284 | 0.08766 | 0.44497 | 0.0094199 | 0.64488 | 0.009669
1878 | 100.828 | 3.7851 | 0.66314 | 0.0063372 | 0.66945 | 0.0096794 | 0.5549 | 0.003531 | 0.49942 | 0.013427 | 4.9123 | 0.08766 | 0.73287 | 0.011019 | 0.54889 | 0.009669
1878.2 | 103.4191 | 3.4477 | 0.56715 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 5.1042 | 0.092459 | 0.92481 | 0.0062209 | 0.54889 | 0.0032709
1878.4 | 104.6667 | 3.2909 | 0.37521 | 0.011135 | 0.66945 | 0.0096794 | 0.65085 | 0.0067301 | 0.59537 | 0.0070285 | 4.5284 | 0.068466 | 0.73287 | 0.011019 | 0.74084 | 0.0080692
1878.6 | 103.803 | 3.3741 | 0.56715 | 0.011135 | 0.28557 | 0.0064811 | 0.36296 | 0.0099291 | 0.97926 | 0.0038295 | 4.9123 | 0.084461 | 0.73287 | 0.0014227 | 0.16505 | 0.0080692
1878.8 | 99.9643 | 3.8603 | 0.56715 | 0.004738 | 0.66945 | 0.012878 | 0.36296 | 0.003531 | 0.49942 | 0.010228 | 6.2558 | 0.10685 | 0.92481 | 0.0062209 | 0.45294 | 0.011268
1879 | 99.5804 | 3.8939 | 0.66314 | -0.0016601 | 0.66945 | 0.0048812 | 0.45891 | 0.0083293 | 0.49942 | 0.0070285 | 6.4477 | 0.11325 | 1.2127 | 0.0046217 | 0.83679 | 0.0048708
1879.2 | 98.3329 | 4.105 | 0.7591 | 0.004738 | 0.5735 | 0.003282 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 6.2558 | 0.10525 | 0.54092 | 0.011019 | 0.83679 | 0.011268
1879.4 | 98.045 | 4.0874 | 0.66314 | 0.0095362 | 0.66945 | 0.0096794 | 0.65085 | 0.003531 | 0.88331 | 0.010228 | 5.68 | 0.086061 | 0.73287 | -0.00017715 | 0.64488 | 0.012868
1879.6 | 89.4079 | 5.1831 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.7468 | 0.0051309 | 0.59537 | 0.011827 | 6.8316 | 0.11805 | 0.63692 | 0.0078201 | 0.64488 | 0.011268
1879.8 | 83.9378 | 5.3206 | 0.7591 | 0.004738 | 0.5735 | 0.0080803 | 0.36296 | 0.0083293 | 0.88331 | 0.015026 | 7.5034 | 0.12285 | 0.34898 | 0.012619 | 0.261 | 0.00647
1880 | 80.5789 | 5.3206 | 0.7591 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0099291 | 0.59537 | 0.015026 | 7.6953 | 0.12925 | 0.54092 | 0.0078201 | 0.74084 | 0.0048708
1880.2 | 26.4534 | 2.0449 | 0.66314 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.59537 | 0.010228 | 4.2405 | 0.073265 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1880.4 | 4.189 | 0.16397 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 1.6494 | 0.025281 | 0.54092 | 0.0094199 | 0.54889 | 0.009669
1880.6 | 1.7898 | 0.042416 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.9776 | 0.017284 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1880.8 | 1.214 | 0.024822 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.010228 | 0.88165 | 0.014085 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1881 | 1.1181 | 0.018424 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.78566 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1881.2 | 0.92614 | 0.016825 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.78566 | 0.012486 | 0.63692 | 0.0062209 | 0.64488 | 0.0080692
1881.4 | 0.92614 | 0.015225 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 0.68971 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1881.6 | 0.83014 | 0.013626 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.68971 | 0.0092866 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1881.8 | 0.83014 | 0.012026 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1882 | 0.83014 | 0.012026 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.68971 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1882.2 | 0.73419 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1882.4 | 0.73419 | 0.010427 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1882.6 | 0.73419 | 0.010427 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1882.8 | 0.83014 | 0.010427 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1883 | 0.73419 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.011019 | 0.64488 | 0.0080692
1883.2 | 0.73419 | 0.0088273 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1883.4 | 0.73419 | 0.010427 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.45294 | 0.0080692
1883.6 | 0.73419 | 0.010427 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.59537 | 0.010228 | 0.59375 | 0.0092866 | 0.73287 | 0.0094199 | 0.54889 | 0.00647
1883.8 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.68971 | 0.012486 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1884 | 0.73419 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1884.2 | 0.73419 | 0.0088273 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1884.4 | 0.73419 | 0.0088273 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1884.6 | 0.54225 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1884.8 | 0.73419 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1885 | 0.73419 | 0.0088273 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.78566 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1885.2 | 0.63824 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1885.4 | 0.73419 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.011019 | 0.64488 | 0.0080692
1885.6 | 0.73419 | 0.010427 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1885.8 | 0.63824 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1886 | 0.73419 | 0.0088273 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1886.2 | 0.63824 | 0.0088273 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1886.4 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1886.6 | 0.63824 | 0.0072281 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1886.8 | 0.73419 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.59375 | 0.010886 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1887 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1887.2 | 0.73419 | 0.0088273 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.64488 | 0.0080692
1887.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.78566 | 0.0092866 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1887.6 | 0.63824 | 0.0072281 | 0.7591 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.59537 | 0.013427 | 0.49776 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.009669
1887.8 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.47751 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1888 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1888.2 | 0.63824 | 0.0072281 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1888.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1888.6 | 0.73419 | 0.0088273 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1888.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1889 | 0.73419 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1889.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1889.4 | 0.73419 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1889.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1889.8 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.011268
1890 | 0.63824 | 0.0072281 | 0.7591 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1890.2 | 0.63824 | 0.0088273 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.015026 | 0.59375 | 0.0092866 | 0.73287 | 0.0078201 | 0.64488 | 0.0080692
1890.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1890.6 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.009669
1890.8 | 0.73419 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0062209 | 0.64488 | 0.0080692
1891 | 0.63824 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1891.2 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.0070285 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.009669
1891.4 | 0.63824 | 0.0072281 | 0.7591 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1891.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.73287 | 0.012619 | 0.64488 | 0.0080692
1891.8 | 0.63824 | 0.0088273 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0092866 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1892 | 0.63824 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.54889 | 0.0080692
1892.2 | 0.54225 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1892.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.7468 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1892.6 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.00647
1892.8 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.015026 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1893 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.64488 | 0.0080692
1893.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1893.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1893.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0048812 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1893.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1894 | 0.63824 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.69137 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1894.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.015026 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.009669
1894.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0092866 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1894.6 | 0.63824 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1894.8 | 0.4463 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.7468 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1895 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.011279 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1895.2 | 0.73419 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1895.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0080692
1895.6 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.0080692
1895.8 | 0.63824 | 0.0072281 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.7468 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.0080692
1896 | 0.54225 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.36296 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.44497 | 0.0094199 | 0.54889 | 0.0080692
1896.2 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1896.4 | 0.63824 | 0.0088273 | 0.4712 | 0.0079364 | 0.95734 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0062209 | 0.64488 | 0.0080692
1896.6 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.011268
1896.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0048812 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1897 | 0.73419 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1897.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1897.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1897.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1897.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1898 | 0.63824 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1898.2 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1898.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0096794 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1898.6 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.7654 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1898.8 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1899 | 0.4463 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.64488 | 0.0080692
1899.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1899.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.69137 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1899.6 | 0.63824 | 0.0072281 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.35695 | 0.00647
1899.8 | 0.54225 | 0.0072281 | 0.7591 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.64488 | 0.0080692
1900 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1900.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1900.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1900.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1900.8 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1901 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.00647
1901.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.68971 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1901.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.69137 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1901.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.00647
1901.8 | 0.54225 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1902 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1902.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1902.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1902.6 | 0.73419 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1902.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.40181 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1903 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1903.2 | 0.4463 | 0.0056289 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1903.4 | 0.54225 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.44497 | 0.011019 | 0.54889 | 0.0080692
1903.6 | 0.63824 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.35695 | 0.0080692
1903.8 | 0.4463 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1904 | 0.73419 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1904.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.54889 | 0.0080692
1904.4 | 0.73419 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1904.6 | 0.54225 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1904.8 | 0.54225 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1905 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.82882 | 0.0078201 | 0.54889 | 0.00647
1905.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.68971 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1905.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.0086283 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1905.6 | 0.54225 | 0.0072281 | 0.7591 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1905.8 | 0.63824 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1906 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1906.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1906.4 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.011019 | 0.45294 | 0.00647
1906.6 | 0.73419 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.34898 | 0.0078201 | 0.64488 | 0.0080692
1906.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1907 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0048812 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1907.2 | 0.63824 | 0.0040291 | 0.4712 | 0.0079364 | 0.093666 | 0.0080803 | 0.45891 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1907.4 | 0.63824 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.003531 | 0.11554 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.45294 | 0.00647
1907.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1907.8 | 0.54225 | 0.010427 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1908 | 0.54225 | 0.0056289 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.35695 | 0.0080692
1908.2 | 0.63824 | 0.0072281 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1908.4 | 0.63824 | 0.0056289 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1908.6 | 0.73419 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0046217 | 0.45294 | 0.0080692
1908.8 | 0.54225 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1909 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1909.2 | 0.73419 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.82882 | 0.0078201 | 0.45294 | 0.0080692
1909.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1909.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.010886 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1909.8 | 0.63824 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.0080692
1910 | 0.63824 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.74084 | 0.0080692
1910.2 | 0.54225 | 0.0072281 | 0.66314 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0094199 | 0.45294 | 0.009669
1910.4 | 0.63824 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1910.6 | 0.54225 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1910.8 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0048708
1911 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.0048708
1911.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1911.4 | 0.54225 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.64488 | 0.0080692
1911.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.009669
1911.8 | 0.73419 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.012619 | 0.64488 | 0.00647
1912 | 0.54225 | 0.0056289 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.69137 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.00647
1912.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1912.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.015026 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1912.6 | 0.63824 | 0.0088273 | 0.7591 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.009669
1912.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1913 | 0.54225 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.34898 | 0.0078201 | 0.54889 | 0.0080692
1913.2 | 0.54225 | 0.0056289 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.0080692
1913.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1913.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1913.8 | 0.4463 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1914 | 0.54225 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1914.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1914.4 | 0.4463 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1914.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.64488 | 0.0080692
1914.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1915 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1915.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1915.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.68971 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1915.6 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.009669
1915.8 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1916 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1916.2 | 0.54225 | 0.0072281 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1916.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.7654 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1916.6 | 0.54225 | 0.0056289 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1916.8 | 0.54225 | 0.0072281 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.35695 | 0.009669
1917 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.011268
1917.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1917.4 | 0.63824 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1917.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1917.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1918 | 0.63824 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1918.2 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.74084 | 0.0080692
1918.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1918.6 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1918.8 | 0.63824 | 0.0072281 | 0.4712 | 0.011135 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1919 | 0.54225 | 0.0072281 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1919.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.78566 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1919.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1919.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1919.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.012619 | 0.64488 | 0.0080692
1920 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.0080692
1920.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.59537 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.009669
1920.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.7468 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1920.6 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.74084 | 0.0080692
1920.8 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1921 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.0086283 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1921.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1921.4 | 0.54225 | 0.0072281 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1921.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1921.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.74084 | 0.0080692
1922 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1922.2 | 0.73419 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1922.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1922.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1922.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1923 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1923.2 | 0.54225 | 0.0056289 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1923.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1923.6 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1923.8 | 0.54225 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1924 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1924.2 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1924.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1924.6 | 0.54225 | 0.0072281 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1924.8 | 0.63824 | 0.0088273 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1925 | 0.4463 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.82882 | 0.0078201 | 0.64488 | 0.0080692
1925.2 | 0.54225 | 0.0056289 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.0080692
1925.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1925.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1925.8 | 0.4463 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1926 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1926.2 | 0.63824 | -0.0071672 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1926.4 | 0.54225 | 0.0072281 | 0.4712 | -0.016055 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1926.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1926.8 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 1.4591 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.0080692
1927 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0083293 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1927.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.015817 | 0.64488 | 0.00647
1927.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.016066
1927.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.69137 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1927.8 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1928 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1928.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1928.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1928.6 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1928.8 | 0.63824 | 0.0072281 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1929 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1929.2 | 0.4463 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1929.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1929.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1929.8 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.69137 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.0080692
1930 | 0.54225 | 0.0056289 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1930.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1930.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.7468 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1930.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1930.8 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1931 | 0.4463 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1931.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1931.4 | 0.63824 | 0.0088273 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1931.6 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1931.8 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1932 | 0.63824 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1932.2 | 0.63824 | 0.0056289 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1932.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1932.6 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1932.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1933 | 0.54225 | 0.0088273 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1933.2 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1933.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1933.6 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1933.8 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1934 | 0.54225 | 0.0040291 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1934.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.35695 | 0.00647
1934.4 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1934.6 | 0.54225 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1934.8 | 0.54225 | 0.0056289 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1935 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1935.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0083293 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.011019 | 0.35695 | 0.00647
1935.4 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1935.6 | 0.54225 | 0.010427 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1935.8 | 0.73419 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.7468 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1936 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1936.2 | 0.54225 | 0.010427 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1936.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1936.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1936.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1937 | 0.4463 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0099291 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.011019 | 0.45294 | 0.0080692
1937.2 | 0.54225 | 0.0088273 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1937.4 | 0.54225 | 0.0088273 | 0.66314 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1937.6 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.30582 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1937.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.44497 | 0.0094199 | 0.54889 | 0.00647
1938 | 0.4463 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1938.2 | 0.54225 | 0.0056289 | 0.56715 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1938.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.30582 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1938.6 | 0.54225 | 0.0088273 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1938.8 | 0.73419 | 0.0056289 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1939 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1939.2 | 0.63824 | 0.0056289 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1939.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1939.6 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1939.8 | 0.4463 | 0.0072281 | 0.66314 | 0.0063372 | 0.66945 | 0.0064811 | 0.7468 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1940 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0060882 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1940.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.011268
1940.4 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.35695 | 0.0080692
1940.6 | 0.73419 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0094199 | 0.45294 | 0.0080692
1940.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1941 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.003531 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.011019 | 0.54889 | 0.00647
1941.2 | 0.4463 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.7468 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0030219 | 0.45294 | 0.0080692
1941.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | -0.78865 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.00647
1941.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1941.8 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1942 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1942.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.011279 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1942.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1942.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1942.8 | 0.63824 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.30748 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1943 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.7468 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1943.2 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.7468 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1943.4 | 0.63824 | 0.0088273 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1943.6 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0083293 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1943.8 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.74084 | 0.00647
1944 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1944.2 | 0.54225 | 0.0072281 | 0.56715 | 0.004738 | 0.47751 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.78566 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1944.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1944.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.92481 | 0.0078201 | 0.54889 | 0.0080692
1944.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1945 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.78566 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1945.2 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.30582 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1945.4 | 0.73419 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.011019 | 0.54889 | 0.00647
1945.6 | 0.54225 | 0.0072281 | 0.56715 | 0.012735 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1945.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1946 | 0.54225 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.009669
1946.2 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1946.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1946.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1946.8 | 0.63824 | 0.0072281 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.35695 | 0.00647
1947 | 0.63824 | 0.0072281 | 0.66314 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1947.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.40181 | 0.0060882 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1947.4 | 0.63824 | 0.0056289 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.74084 | 0.00647
1947.6 | 0.63824 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1947.8 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1948 | 0.54225 | 0.0056289 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.35695 | 0.009669
1948.2 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.84279 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.82882 | 0.0094199 | 0.54889 | 0.0080692
1948.4 | 0.63824 | 0.0072281 | 0.66314 | 0.011135 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1948.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1948.8 | 0.63824 | 0.0072281 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.00647
1949 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1949.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1949.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.44497 | 0.0094199 | 0.54889 | 0.0080692
1949.6 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.74084 | 0.009669
1949.8 | 0.54225 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.35695 | 0.00647
1950 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.36296 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.011019 | 0.64488 | 0.0080692
1950.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.40181 | 0.0092866 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1950.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.011019 | 0.54889 | 0.00647
1950.6 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1950.8 | 0.54225 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.011019 | 0.54889 | 0.00647
1951 | 0.63824 | 0.0088273 | 0.66314 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0080692
1951.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1951.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0064811 | 0.36296 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.64488 | 0.0080692
1951.6 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.7468 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1951.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.011279 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1952 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.82882 | 0.0078201 | 0.64488 | 0.0080692
1952.2 | 0.4463 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1952.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.64488 | 0.0048708
1952.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0048708
1952.8 | 0.63824 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.013427 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.0080692
1953 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1953.2 | 0.54225 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.35695 | 0.00647
1953.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.59537 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1953.6 | 0.54225 | 0.0072281 | 0.66314 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1953.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.012619 | 0.54889 | 0.0080692
1954 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0099291 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1954.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1954.4 | 0.4463 | 0.0088273 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1954.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.68971 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1954.8 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.7468 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1955 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1955.2 | 0.4463 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.84279 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1955.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0095362 | 0.47751 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1955.6 | 0.63824 | 0.0072281 | 0.4712 | 0.011135 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1955.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.00647
1956 | 0.54225 | 0.0088273 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1956.2 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.40181 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1956.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1956.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1956.8 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1957 | 0.54225 | 0.010427 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0080692
1957.2 | 0.63824 | 0.0072281 | 0.37521 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.013427 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0048708
1957.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1957.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.00647
1957.8 | 0.4463 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.0080692
1958 | 0.63824 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.00647
1958.2 | 0.63824 | 0.010427 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0083293 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1958.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1958.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1958.8 | 0.54225 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1959 | 0.54225 | 0.0072281 | 0.4712 | 0.0095362 | 0.47751 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1959.2 | 0.63824 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1959.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1959.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0044883 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1959.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1960 | 0.54225 | 0.0056289 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0060882 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1960.2 | 0.54225 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1960.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.74084 | 0.0080692
1960.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1960.8 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.7468 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.45294 | 0.0080692
1961 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1961.2 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.7654 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1961.4 | 0.54225 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.54092 | 0.011019 | 0.54889 | 0.0080692
1961.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1961.8 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.74084 | 0.00647
1962 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.009669
1962.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1962.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1962.6 | 0.4463 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1962.8 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.74084 | 0.0080692
1963 | 0.54225 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0062209 | 0.45294 | 0.00647
1963.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.7654 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1963.4 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.011019 | 0.54889 | 0.0080692
1963.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.68971 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1963.8 | 0.73419 | 0.0056289 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.011019 | 0.54889 | 0.0080692
1964 | 0.54225 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1964.2 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0048812 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1964.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.009669
1964.6 | 0.54225 | 0.0072281 | 0.56715 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1964.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1965 | 0.54225 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1965.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1965.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.7468 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0094199 | 0.45294 | 0.00647
1965.6 | 0.4463 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.92481 | 0.0094199 | 0.54889 | 0.0080692
1965.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0095362 | 0.7654 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1966 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.011019 | 0.54889 | 0.00647
1966.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1966.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1966.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.010886 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1966.8 | 0.63824 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.69137 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1967 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1967.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.0094199 | 0.64488 | 0.0080692
1967.4 | 0.73419 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0062209 | 0.54889 | 0.0080692
1967.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.009669
1967.8 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.011019 | 0.54889 | 0.0080692
1968 | 0.63824 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0083293 | 0.59537 | 0.010228 | 0.49776 | 0.0092866 | 0.73287 | 0.0062209 | 0.54889 | 0.00647
1968.2 | 0.63824 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0083293 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1968.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1968.6 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.59375 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1968.8 | 0.63824 | 0.0072281 | 0.4712 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1969 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1969.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1969.4 | 0.54225 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.011019 | 0.64488 | 0.0080692
1969.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0048812 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.010886 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1969.8 | 0.63824 | 0.0072281 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1970 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1970.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1970.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.010886 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1970.6 | 0.63824 | 0.0056289 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1970.8 | 0.4463 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1971 | 0.63824 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.73287 | 0.0078201 | 0.64488 | 0.0080692
1971.2 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1971.4 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.45294 | 0.0080692
1971.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1971.8 | 0.54225 | 0.0072281 | 0.56715 | 0.011135 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1972 | 0.4463 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1972.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.009669
1972.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1972.6 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0048708
1972.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1973 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.74084 | 0.009669
1973.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1973.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1973.6 | 0.63824 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.00647
1973.8 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.009669
1974 | 0.4463 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.011019 | 0.64488 | 0.00647
1974.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1974.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1974.6 | 0.54225 | 0.0056289 | 0.56715 | 0.0079364 | 0.47751 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.010886 | 0.73287 | 0.0094199 | 0.64488 | 0.0080692
1974.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.40181 | 0.0060882 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1975 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.009669
1975.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.73287 | 0.0094199 | 0.54889 | 0.00647
1975.4 | 0.63824 | 0.0072281 | 0.56715 | 0.004738 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1975.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1975.8 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1976 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1976.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.36296 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1976.4 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.45891 | 0.0083293 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1976.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1976.8 | 0.54225 | 0.0072281 | 0.66314 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.00647
1977 | 0.54225 | 0.0072281 | 0.56715 | 0.011135 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.009669
1977.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.30582 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1977.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1977.6 | 0.54225 | 0.0072281 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.013427 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.0048708
1977.8 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.49776 | 0.0092866 | 0.73287 | 0.0078201 | 0.54889 | 0.0048708
1978 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.64488 | 0.0080692
1978.2 | 0.54225 | 0.0040291 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.011019 | 0.64488 | 0.00647
1978.4 | 0.54225 | 0.0072281 | 0.56715 | 0.004738 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1978.6 | 0.63824 | 0.0072281 | 0.66314 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.009669
1978.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.261 | 0.0080692
1979 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.73287 | 0.0062209 | 0.54889 | 0.0080692
1979.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.44497 | 0.0078201 | 0.45294 | 0.0080692
1979.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.010886 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1979.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.00647
1979.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.012486 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1980 | 0.63824 | 0.0072281 | 0.37521 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.30748 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.00647
1980.2 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.00647
1980.4 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.45294 | 0.0080692
1980.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1980.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1981 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.35695 | 0.0080692
1981.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1981.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1981.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.44497 | 0.0078201 | 0.54889 | 0.0080692
1981.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1982 | 0.63824 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1982.2 | 0.4463 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1982.4 | 0.63824 | 0.0088273 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.011268
1982.6 | 0.63824 | 0.0072281 | 0.4712 | 0.0095362 | 0.66945 | 0.0096794 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1982.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1983 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1983.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1983.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1983.6 | 0.54225 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.00647
1983.8 | 0.4463 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1984 | 0.54225 | 0.0088273 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1984.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
1984.4 | 0.63824 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.64488 | 0.0080692
1984.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1984.8 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1985 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.0092866 | 0.73287 | 0.0078201 | 0.54889 | 0.00647
1985.2 | 0.54225 | 0.0056289 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.45294 | 0.00647
1985.4 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1985.6 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1985.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1986 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1986.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
1986.4 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1986.6 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0083293 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1986.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.009669
1987 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.40347 | 0.011827 | 0.59375 | 0.010886 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1987.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1987.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1987.6 | 0.63824 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.011019 | 0.54889 | 0.00647
1987.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1988 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1988.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1988.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1988.6 | 0.54225 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.74084 | 0.00647
1988.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.68971 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1989 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0060882 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1989.2 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1989.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1989.6 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.73287 | 0.011019 | 0.64488 | 0.0080692
1989.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.010228 | 0.59375 | 0.0060882 | 0.54092 | 0.0094199 | 0.64488 | 0.0080692
1990 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.65085 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
1990.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.009669
1990.4 | 0.54225 | 0.0056289 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1990.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.45294 | 0.0080692
1990.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.011279 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1991 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.010886 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1991.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.015026 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1991.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0095362 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.011268
1991.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.011019 | 0.64488 | 0.0080692
1991.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.64488 | 0.00647
1992 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0096794 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1992.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0095362 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.69137 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1992.4 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1992.6 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.54092 | 0.0062209 | 0.54889 | 0.0080692
1992.8 | 0.63824 | 0.0072281 | 0.37521 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.69137 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1993 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1993.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
1993.4 | 0.63824 | 0.0056289 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1993.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1993.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
1994 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.64488 | 0.0080692
1994.2 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.47751 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1994.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1994.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1994.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0048812 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1995 | 0.54225 | 0.0072281 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.0086283 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1995.2 | 0.63824 | 0.0072281 | 0.7591 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1995.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0060882 | 0.54092 | 0.011019 | 0.54889 | 0.0080692
1995.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0048812 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1995.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.7654 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1996 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1996.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.40181 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1996.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.013427 | 0.59375 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.00647
1996.6 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.73287 | 0.0094199 | 0.64488 | 0.0080692
1996.8 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0046217 | 0.54889 | 0.0080692
1997 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0094199 | 0.54889 | 0.00647
1997.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0092866 | 0.63692 | 0.0078201 | 0.74084 | 0.009669
1997.4 | 0.4463 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
1997.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
1997.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.7468 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1998 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.45891 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.011019 | 0.64488 | 0.0080692
1998.2 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.66945 | 0.0080803 | 0.65085 | 0.0051309 | 0.49942 | 0.010228 | 0.49776 | 0.0092866 | 0.73287 | 0.0078201 | 0.64488 | 0.0080692
1998.4 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.65085 | 0.0051309 | 0.49942 | 0.011827 | 0.59375 | 0.012486 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
1998.6 | 0.54225 | 0.0088273 | 0.56715 | 0.0079364 | 0.66945 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
1998.8 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.68971 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
1999 | 0.54225 | 0.0072281 | 0.56715 | 0.0095362 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.73287 | 0.0078201 | 0.64488 | 0.0080692
1999.2 | 0.54225 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.009669
1999.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0064811 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.40181 | 0.0092866 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
1999.6 | 0.4463 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
1999.8 | 0.54225 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.0080692
2000 | 0.63824 | 0.0088273 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.003531 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.64488 | 0.0080692
2000.2 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0092866 | 0.54092 | 0.0078201 | 0.64488 | 0.0080692
2000.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0095362 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.45294 | 0.0080692
2000.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.003531 | 0.49942 | 0.011827 | 0.59375 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
2000.8 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.011268
2001 | 0.63824 | 0.0072281 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.45891 | 0.0051309 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.0080692
2001.2 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.66945 | 0.0080803 | 0.65085 | 0.0083293 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0094199 | 0.54889 | 0.0080692
2001.4 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.7654 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.013427 | 0.68971 | 0.0092866 | 0.73287 | 0.0094199 | 0.54889 | 0.009669
2001.6 | 0.54225 | 0.0072281 | 0.56715 | 0.004738 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.015026 | 0.59375 | 0.0092866 | 0.63692 | 0.0094199 | 0.54889 | 0.011268
2001.8 | 0.54225 | 0.0072281 | 0.4712 | 0.0095362 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.59375 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
2002 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.011827 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.64488 | 0.0080692
2002.2 | 0.54225 | 0.0056289 | 0.66314 | 0.0079364 | 0.66945 | 0.0080803 | 0.5549 | 0.0051309 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0078201 | 0.54889 | 0.0080692
2002.4 | 0.63824 | 0.0056289 | 0.4712 | 0.0063372 | 0.5735 | 0.0080803 | 0.5549 | 0.0083293 | 0.59537 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0062209 | 0.54889 | 0.0080692
2002.6 | 0.54225 | 0.0056289 | 0.56715 | 0.0095362 | 0.66945 | 0.0080803 | 0.65085 | 0.0067301 | 0.59537 | 0.0086283 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.54889 | 0.011268
2002.8 | 0.63824 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0096794 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0078201 | 0.54889 | 0.0080692
2003 | 0.63824 | 0.0088273 | 0.66314 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.59537 | 0.011827 | 0.59375 | 0.0076874 | 0.54092 | 0.0094199 | 0.35695 | 0.00647
2003.2 | 0.73419 | 0.0072281 | 0.56715 | 0.0079364 | 0.5735 | 0.0064811 | 0.7468 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0092866 | 0.54092 | 0.0094199 | 0.54889 | 0.0080692
2003.4 | 0.63824 | 0.0072281 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.010228 | 0.49776 | 0.0076874 | 0.63692 | 0.0094199 | 0.45294 | 0.0080692
2003.6 | 0.63824 | 0.0072281 | 0.56715 | 0.0063372 | 0.5735 | 0.0080803 | 0.65085 | 0.0067301 | 0.49942 | 0.010228 | 0.59375 | 0.0076874 | 0.73287 | 0.0078201 | 0.54889 | 0.0080692
2003.8 | 0.54225 | 0.0072281 | 0.56715 | 0.0079364 | 0.47751 | 0.0080803 | 0.5549 | 0.0067301 | 0.49942 | 0.011827 | 0.68971 | 0.0092866 | 0.63692 | 0.0078201 | 0.54889 | 0.00647
2004 | 0.63824 | 0.0056289 | 0.4712 | 0.0079364 | 0.5735 | 0.0080803 | 0.5549 | 0.0051309 | 0.40347 | 0.010228 | 0.49776 | 0.0076874 | 0.54092 | 0.0046217 | 0.54889 | 0.0080692
2004.2 | 0.54225 | 0.0056289 | 0.4712 | 0.0063372 | 0.66945 | 0.0080803 | 0.5549 | 0.0067301 | 0.40347 | 0.011827 | 0.49776 | 0.0076874 | 0.73287 | 0.0078201 | 0.45294 | 0.0080692
2004.4 | 1.406 | 0.016825 | 0.7591 | 0.015934 | 0.66945 | 0.017677 | 0.65085 | 0.014727 | 0.59537 | 0.021424 | 1.1695 | 0.017284 | 0.82882 | 0.017417 | 1.2207 | 0.016066
2004.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2264 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2004.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2005 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2005.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2005.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.2051 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2005.6 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2005.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2006 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2006.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2006.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2006.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2006.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2007 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2007.2 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2251
2007.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2007.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2007.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2008 | -73.4485 | -1.2291 | -73.3276 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2008.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2008.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2008.6 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2008.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2009 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.2499 | -1.2299
2009.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2009.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2009.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2009.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2010 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2010.2 | -73.2565 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2010.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2010.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.227 | -73.3459 | -1.2299
2010.8 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2011 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.2499 | -1.2299
2011.2 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2011.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2011.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.228 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2011.8 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2264 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2012 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.3213 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2012.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2012.4 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.301 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2012.6 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2012.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2013 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2013.2 | -73.4485 | -1.2291 | -73.3276 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2013.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2013.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2013.8 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2014 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2014.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2014.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2255 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2014.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.228 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2014.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.301 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2015 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.3213 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2015.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2015.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2015.6 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2015.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2016 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2016.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2016.4 | -73.3525 | -1.2291 | -73.3276 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2016.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2016.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2017 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2017.2 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2017.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2017.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2264 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2017.8 | -73.4485 | -1.2291 | -73.3276 | -1.2284 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2018 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2283
2018.2 | -73.4485 | -1.2291 | -73.2316 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2018.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2264 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2018.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2018.8 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2019 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.301 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2019.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2019.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2019.6 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.2579 | -1.2302 | -73.4418 | -1.2299
2019.8 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2020 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2020.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2020.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2239 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2020.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2020.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2021 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.2499 | -1.2283
2021.2 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2021.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.301 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2283
2021.6 | -73.4485 | -1.2291 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.228 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2021.8 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2264 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2286 | -73.4418 | -1.2299
2022 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2022.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2267
2022.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2022.6 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2022.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2023 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2023.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2023.4 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.3399 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2023.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2267
2023.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2024 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2024.2 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2024.4 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.3399 | -1.228 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2024.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2024.8 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2025 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.3399 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2025.2 | -73.4485 | -1.2291 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.1539 | -1.2299
2025.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2025.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2025.8 | -73.4485 | -1.2291 | -73.4236 | -1.2268 | -73.5132 | -1.2283 | -73.5318 | -1.228 | -73.6832 | -1.2246 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2026 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2026.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2026.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2026.6 | -73.4485 | -1.2291 | -73.4236 | -1.2268 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2026.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2027 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2027.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2027.4 | -73.4485 | -1.2291 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2027.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2027.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2028 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2028.2 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2028.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2028.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2028.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2029 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.2499 | -1.2299
2029.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2029.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.228 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2029.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.3459 | -1.2299
2029.8 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2030 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2030.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2030.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2030.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.4913 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2030.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2031 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2031.2 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2031.4 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2031.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2031.8 | -73.2565 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2032 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2032.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2032.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2032.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2032.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2033 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2033.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2033.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2033.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2033.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2034 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2255 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2034.2 | -73.4485 | -1.2276 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2034.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2034.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.228 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.3459 | -1.2299
2034.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2283
2035 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2035.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.228 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2035.4 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2264 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2035.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2035.8 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2036 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2036.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2036.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2036.6 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2264 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.227 | -73.4418 | -1.2299
2036.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.3213 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2037 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2037.2 | -73.4485 | -1.2291 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.4913 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2037.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2037.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2037.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2038 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2038.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2038.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2038.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2038.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2039 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2039.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2039.4 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2039.6 | -73.4485 | -1.2291 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.228 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2039.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2040 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2040.2 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2040.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2040.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.228 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2040.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2041 | -73.4485 | -1.2276 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.228 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2041.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.3399 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2041.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2041.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.2579 | -1.2286 | -73.4418 | -1.2299
2041.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2264 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2042 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2042.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2042.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2042.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2042.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2043 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2043.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.4913 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2267
2043.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.1619 | -1.2302 | -73.4418 | -1.2299
2043.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2043.8 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2044 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2044.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2044.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2044.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2044.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2045 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2045.2 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2271 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2045.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2045.6 | -73.4485 | -1.2291 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.228 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.2499 | -1.2299
2045.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2255 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2046 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2046.2 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2046.4 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2264 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2046.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2046.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2047 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.2499 | -1.2299
2047.2 | -73.4485 | -1.2291 | -73.3276 | -1.23 | -73.4173 | -1.2283 | -73.4359 | -1.228 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2047.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2047.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2255 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2047.8 | -73.3525 | -1.2291 | -73.2316 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2048 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2048.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2255 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2048.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.301 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2048.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2048.8 | -73.2565 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2049 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2049.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2049.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2049.6 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2286 | -73.4418 | -1.2299
2049.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2050 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2050.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2050.4 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2050.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2267
2050.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2051 | -73.4485 | -1.226 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2051.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2051.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2051.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2051.8 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.228 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.227 | -73.4418 | -1.2299
2052 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2052.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2052.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2251 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2255 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2052.6 | -73.3525 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2052.8 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2053 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.397 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2053.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2053.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2053.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2053.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.2579 | -1.2302 | -73.4418 | -1.2299
2054 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.2579 | -1.2302 | -73.4418 | -1.2299
2054.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2054.4 | -73.4485 | -1.2291 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2054.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2054.8 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2286 | -73.4418 | -1.2299
2055 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2055.2 | -73.4485 | -1.2291 | -73.2316 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2283
2055.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2283
2055.6 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2267
2055.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2056 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2056.2 | -73.3525 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2056.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2056.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2271 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2056.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2264 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2057 | -73.4485 | -1.2291 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2057.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2057.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.228 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2057.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2057.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2058 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2264 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2058.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2267 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2058.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2058.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2058.8 | -73.4485 | -1.2291 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.2499 | -1.2299
2059 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2059.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2059.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2059.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2059.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.3213 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2060 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2060.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.397 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2283
2060.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2060.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2251 | -73.5318 | -1.228 | -73.6832 | -1.2262 | -73.397 | -1.2255 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2060.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.3538 | -1.2302 | -73.4418 | -1.2299
2061 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.228 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2061.2 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2061.4 | -73.4485 | -1.2291 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2061.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2061.8 | -73.4485 | -1.2276 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2062 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2214 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2062.2 | -73.4485 | -1.2291 | -73.2316 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2062.4 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2062.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2264 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.3538 | -1.227 | -73.3459 | -1.2299
2062.8 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.4173 | -1.2283 | -73.5318 | -1.2296 | -73.5873 | -1.2246 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.3459 | -1.2299
2063 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.1539 | -1.2283
2063.2 | -73.4485 | -1.2291 | -73.4236 | -1.2284 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2063.4 | -73.4485 | -1.2291 | -73.3276 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.4913 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.2499 | -1.2283
2063.6 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.5318 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2287 | -73.4498 | -1.2302 | -73.4418 | -1.2299
2063.8 | -73.4485 | -1.2291 | -73.4236 | -1.23 | -73.5132 | -1.2283 | -73.4359 | -1.2296 | -73.6832 | -1.2262 | -73.493 | -1.2271 | -73.1619 | -1.2286 | -73.4418 | -1.2299

## Temperature Data
Fire Time | Time | Circuit 1 TC for 3c | Circuit 2 TC for 3c | Penlight Exposure Temperature | Time | North 25 C | Cable 1 | Cable 2
0 | -344 | 20.5585 | 20.5925 | 20.6689 | 0 | 20.6689 | 20.5585 | 20.5925
0.6292 | -343.3708 | 20.5645 | 20.5874 | 20.6584 | 0.6292 | 20.6584 | 20.5645 | 20.5874
1.2229 | -342.7771 | 20.5583 | 20.5885 | 20.6621 | 1.2229 | 20.6621 | 20.5583 | 20.5885
2.2229 | -341.7771 | 20.5528 | 20.5907 | 20.6669 | 2.2229 | 20.6669 | 20.5528 | 20.5907
3.2229 | -340.7771 | 20.5406 | 20.5955 | 20.6606 | 3.2229 | 20.6606 | 20.5406 | 20.5955
4.2229 | -339.7771 | 20.5547 | 20.5911 | 20.6656 | 4.2229 | 20.6656 | 20.5547 | 20.5911
5.2229 | -338.7771 | 20.5665 | 20.593 | 20.6629 | 5.2229 | 20.6629 | 20.5665 | 20.593
6.2229 | -337.7771 | 20.5577 | 20.5955 | 20.6583 | 6.2229 | 20.6583 | 20.5577 | 20.5955
7.2229 | -336.7771 | 20.5525 | 20.5936 | 20.6648 | 7.2229 | 20.6648 | 20.5525 | 20.5936
8.2229 | -335.7771 | 20.5577 | 20.5927 | 20.6662 | 8.2229 | 20.6662 | 20.5577 | 20.5927
9.2229 | -334.7771 | 20.5401 | 20.5901 | 20.6754 | 9.2229 | 20.6754 | 20.5401 | 20.5901
10.2229 | -333.7771 | 20.5573 | 20.598 | 20.6781 | 10.2229 | 20.6781 | 20.5573 | 20.598
11.2229 | -332.7771 | 20.5497 | 20.5925 | 20.6854 | 11.2229 | 20.6854 | 20.5497 | 20.5925
12.2229 | -331.7771 | 20.5464 | 20.59 | 20.6717 | 12.2229 | 20.6717 | 20.5464 | 20.59
13.2229 | -330.7771 | 20.5523 | 20.5876 | 20.6711 | 13.2229 | 20.6711 | 20.5523 | 20.5876
14.2229 | -329.7771 | 20.5532 | 20.582 | 20.6761 | 14.2229 | 20.6761 | 20.5532 | 20.582
15.2229 | -328.7771 | 20.5582 | 20.5961 | 20.6745 | 15.2229 | 20.6745 | 20.5582 | 20.5961
16.2229 | -327.7771 | 20.5525 | 20.5953 | 20.6771 | 16.2229 | 20.6771 | 20.5525 | 20.5953
17.2229 | -326.7771 | 20.5558 | 20.5932 | 20.6807 | 17.2229 | 20.6807 | 20.5558 | 20.5932
18.2229 | -325.7771 | 20.5492 | 20.5932 | 20.6706 | 18.2229 | 20.6706 | 20.5492 | 20.5932
19.2229 | -324.7771 | 20.5443 | 20.5912 | 20.6746 | 19.2229 | 20.6746 | 20.5443 | 20.5912
20.2229 | -323.7771 | 20.542 | 20.5938 | 20.6738 | 20.2229 | 20.6738 | 20.542 | 20.5938
21.2229 | -322.7771 | 20.5432 | 20.5914 | 20.6791 | 21.2229 | 20.6791 | 20.5432 | 20.5914
22.2229 | -321.7771 | 20.5429 | 20.5983 | 20.675 | 22.2229 | 20.675 | 20.5429 | 20.5983
23.2229 | -320.7771 | 20.5388 | 20.5961 | 20.6764 | 23.2229 | 20.6764 | 20.5388 | 20.5961
24.2229 | -319.7771 | 20.5522 | 20.5927 | 20.6754 | 24.2229 | 20.6754 | 20.5522 | 20.5927
25.2229 | -318.7771 | 20.5448 | 20.5933 | 20.668 | 25.2229 | 20.668 | 20.5448 | 20.5933
26.2229 | -317.7771 | 20.5374 | 20.5945 | 20.6738 | 26.2229 | 20.6738 | 20.5374 | 20.5945
27.2229 | -316.7771 | 20.5436 | 20.6021 | 20.669 | 27.2229 | 20.669 | 20.5436 | 20.6021
28.2229 | -315.7771 | 20.5326 | 20.5845 | 20.6671 | 28.2229 | 20.6671 | 20.5326 | 20.5845
29.2229 | -314.7771 | 20.5456 | 20.592 | 20.6739 | 29.2229 | 20.6739 | 20.5456 | 20.592
30.2229 | -313.7771 | 20.5423 | 20.5844 | 20.6642 | 30.2229 | 20.6642 | 20.5423 | 20.5844
31.2229 | -312.7771 | 20.5428 | 20.5887 | 20.676 | 31.2229 | 20.676 | 20.5428 | 20.5887
32.2229 | -311.7771 | 20.5457 | 20.5909 | 20.67 | 32.2229 | 20.67 | 20.5457 | 20.5909
33.2229 | -310.7771 | 20.535 | 20.5871 | 20.6675 | 33.2229 | 20.6675 | 20.535 | 20.5871
34.2229 | -309.7771 | 20.5339 | 20.5897 | 20.6708 | 34.2229 | 20.6708 | 20.5339 | 20.5897
35.2229 | -308.7771 | 20.5373 | 20.5887 | 20.6717 | 35.2229 | 20.6717 | 20.5373 | 20.5887
36.2229 | -307.7771 | 20.5309 | 20.5893 | 20.6702 | 36.2229 | 20.6702 | 20.5309 | 20.5893
37.2229 | -306.7771 | 20.5319 | 20.5939 | 20.669 | 37.2229 | 20.669 | 20.5319 | 20.5939
38.2229 | -305.7771 | 20.5407 | 20.588 | 20.6648 | 38.2229 | 20.6648 | 20.5407 | 20.588
39.2229 | -304.7771 | 20.5266 | 20.5913 | 20.6636 | 39.2229 | 20.6636 | 20.5266 | 20.5913
40.2229 | -303.7771 | 20.5302 | 20.5854 | 20.6681 | 40.2229 | 20.6681 | 20.5302 | 20.5854
41.2229 | -302.7771 | 20.5228 | 20.5898 | 20.6772 | 41.2229 | 20.6772 | 20.5228 | 20.5898
42.2229 | -301.7771 | 20.5338 | 20.589 | 20.6656 | 42.2229 | 20.6656 | 20.5338 | 20.589
43.2229 | -300.7771 | 20.5321 | 20.5928 | 20.6616 | 43.2229 | 20.6616 | 20.5321 | 20.5928
44.2229 | -299.7771 | 20.5289 | 20.5876 | 20.6686 | 44.2229 | 20.6686 | 20.5289 | 20.5876
45.2229 | -298.7771 | 20.53 | 20.5926 | 20.6719 | 45.2229 | 20.6719 | 20.53 | 20.5926
46.2229 | -297.7771 | 20.5204 | 20.5853 | 20.6663 | 46.2229 | 20.6663 | 20.5204 | 20.5853
47.2229 | -296.7771 | 20.535 | 20.5838 | 20.674 | 47.2229 | 20.674 | 20.535 | 20.5838
48.2229 | -295.7771 | 20.5288 | 20.5849 | 20.673 | 48.2229 | 20.673 | 20.5288 | 20.5849
49.2229 | -294.7771 | 20.5281 | 20.5901 | 20.6684 | 49.2229 | 20.6684 | 20.5281 | 20.5901
50.2229 | -293.7771 | 20.5192 | 20.5879 | 20.6683 | 50.2229 | 20.6683 | 20.5192 | 20.5879
51.2229 | -292.7771 | 20.5335 | 20.5903 | 20.6772 | 51.2229 | 20.6772 | 20.5335 | 20.5903
52.2229 | -291.7771 | 20.5234 | 20.5873 | 20.6702 | 52.2229 | 20.6702 | 20.5234 | 20.5873
53.2229 | -290.7771 | 20.524 | 20.5889 | 20.6669 | 53.2229 | 20.6669 | 20.524 | 20.5889
54.2229 | -289.7771 | 20.5191 | 20.592 | 20.6711 | 54.2229 | 20.6711 | 20.5191 | 20.592
55.2229 | -288.7771 | 20.52 | 20.5865 | 20.6766 | 55.2229 | 20.6766 | 20.52 | 20.5865
56.2229 | -287.7771 | 20.5096 | 20.5852 | 20.6735 | 56.2229 | 20.6735 | 20.5096 | 20.5852
57.2229 | -286.7771 | 20.5241 | 20.5802 | 20.6697 | 57.2229 | 20.6697 | 20.5241 | 20.5802
58.2229 | -285.7771 | 20.5201 | 20.5866 | 20.6741 | 58.2229 | 20.6741 | 20.5201 | 20.5866
59.2229 | -284.7771 | 20.4776 | 20.59 | 20.671 | 59.2229 | 20.671 | 20.4776 | 20.59
60.2229 | -283.7771 | 20.5242 | 20.5889 | 20.6757 | 60.2229 | 20.6757 | 20.5242 | 20.5889
61.2229 | -282.7771 | 20.5217 | 20.5844 | 20.6694 | 61.2229 | 20.6694 | 20.5217 | 20.5844
62.2229 | -281.7771 | 20.5165 | 20.5861 | 20.6764 | 62.2229 | 20.6764 | 20.5165 | 20.5861
63.2229 | -280.7771 | 20.523 | 20.5896 | 20.6729 | 63.2229 | 20.6729 | 20.523 | 20.5896
64.2229 | -279.7771 | 20.5232 | 20.5845 | 20.6719 | 64.2229 | 20.6719 | 20.5232 | 20.5845
65.2229 | -278.7771 | 20.5209 | 20.5903 | 20.6805 | 65.2229 | 20.6805 | 20.5209 | 20.5903
66.2229 | -277.7771 | 20.513 | 20.5824 | 20.6836 | 66.2229 | 20.6836 | 20.513 | 20.5824
67.2229 | -276.7771 | 20.5087 | 20.5838 | 20.6765 | 67.2229 | 20.6765 | 20.5087 | 20.5838
68.2229 | -275.7771 | 20.5072 | 20.5911 | 20.673 | 68.2229 | 20.673 | 20.5072 | 20.5911
69.2229 | -274.7771 | 20.5213 | 20.589 | 20.6674 | 69.2229 | 20.6674 | 20.5213 | 20.589
70.2229 | -273.7771 | 20.5135 | 20.5858 | 20.662 | 70.2229 | 20.662 | 20.5135 | 20.5858
71.2229 | -272.7771 | 20.5124 | 20.5849 | 20.6653 | 71.2229 | 20.6653 | 20.5124 | 20.5849
72.2229 | -271.7771 | 20.5096 | 20.5835 | 20.6631 | 72.2229 | 20.6631 | 20.5096 | 20.5835
73.2229 | -270.7771 | 20.5189 | 20.589 | 20.6697 | 73.2229 | 20.6697 | 20.5189 | 20.589
74.2229 | -269.7771 | 20.5194 | 20.5881 | 20.6704 | 74.2229 | 20.6704 | 20.5194 | 20.5881
75.2229 | -268.7771 | 20.504 | 20.5927 | 20.6701 | 75.2229 | 20.6701 | 20.504 | 20.5927
76.2229 | -267.7771 | 20.5066 | 20.5917 | 20.6645 | 76.2229 | 20.6645 | 20.5066 | 20.5917
77.2229 | -266.7771 | 20.5081 | 20.5829 | 20.6577 | 77.2229 | 20.6577 | 20.5081 | 20.5829
78.2229 | -265.7771 | 20.5027 | 20.5835 | 20.6664 | 78.2229 | 20.6664 | 20.5027 | 20.5835
79.2229 | -264.7771 | 20.5117 | 20.5813 | 20.6765 | 79.2229 | 20.6765 | 20.5117 | 20.5813
80.2229 | -263.7771 | 20.5044 | 20.5892 | 20.6719 | 80.2229 | 20.6719 | 20.5044 | 20.5892
81.2229 | -262.7771 | 20.4995 | 20.5914 | 20.6751 | 81.2229 | 20.6751 | 20.4995 | 20.5914
82.2229 | -261.7771 | 20.5063 | 20.5868 | 20.6754 | 82.2229 | 20.6754 | 20.5063 | 20.5868
83.2229 | -260.7771 | 20.4974 | 20.5867 | 20.6764 | 83.2229 | 20.6764 | 20.4974 | 20.5867
84.2229 | -259.7771 | 20.4988 | 20.5879 | 20.6678 | 84.2229 | 20.6678 | 20.4988 | 20.5879
85.2229 | -258.7771 | 20.5036 | 20.5863 | 20.6806 | 85.2229 | 20.6806 | 20.5036 | 20.5863
86.2229 | -257.7771 | 20.4967 | 20.5841 | 20.6772 | 86.2229 | 20.6772 | 20.4967 | 20.5841
87.2229 | -256.7771 | 20.4995 | 20.5857 | 20.676 | 87.2229 | 20.676 | 20.4995 | 20.5857
88.2229 | -255.7771 | 20.49 | 20.5878 | 20.6711 | 88.2229 | 20.6711 | 20.49 | 20.5878
89.2229 | -254.7771 | 20.4943 | 20.5903 | 20.6625 | 89.2229 | 20.6625 | 20.4943 | 20.5903
90.2229 | -253.7771 | 20.5088 | 20.5812 | 20.6657 | 90.2229 | 20.6657 | 20.5088 | 20.5812
91.2229 | -252.7771 | 20.5027 | 20.5908 | 20.6717 | 91.2229 | 20.6717 | 20.5027 | 20.5908
92.2229 | -251.7771 | 20.4987 | 20.593 | 20.668 | 92.2229 | 20.668 | 20.4987 | 20.593
93.2229 | -250.7771 | 20.4981 | 20.5912 | 20.6679 | 93.2229 | 20.6679 | 20.4981 | 20.5912
94.2229 | -249.7771 | 20.4964 | 20.59 | 20.6745 | 94.2229 | 20.6745 | 20.4964 | 20.59
95.2229 | -248.7771 | 20.4881 | 20.5892 | 20.6695 | 95.2229 | 20.6695 | 20.4881 | 20.5892
96.2229 | -247.7771 | 20.5024 | 20.5846 | 20.6721 | 96.2229 | 20.6721 | 20.5024 | 20.5846
97.2229 | -246.7771 | 20.5025 | 20.5811 | 20.6673 | 97.2229 | 20.6673 | 20.5025 | 20.5811
98.2229 | -245.7771 | 20.4877 | 20.5876 | 20.6782 | 98.2229 | 20.6782 | 20.4877 | 20.5876
99.2229 | -244.7771 | 20.5027 | 20.5882 | 20.6728 | 99.2229 | 20.6728 | 20.5027 | 20.5882
100.2229 | -243.7771 | 20.4942 | 20.5847 | 20.6715 | 100.2229 | 20.6715 | 20.4942 | 20.5847
101.2229 | -242.7771 | 20.4889 | 20.5837 | 20.6751 | 101.2229 | 20.6751 | 20.4889 | 20.5837
102.2229 | -241.7771 | 20.4921 | 20.5916 | 20.6847 | 102.2229 | 20.6847 | 20.4921 | 20.5916
103.2229 | -240.7771 | 20.4847 | 20.5897 | 20.674 | 103.2229 | 20.674 | 20.4847 | 20.5897
104.2229 | -239.7771 | 20.4896 | 20.5884 | 20.6762 | 104.2229 | 20.6762 | 20.4896 | 20.5884
105.2229 | -238.7771 | 20.4898 | 20.5874 | 20.6768 | 105.2229 | 20.6768 | 20.4898 | 20.5874
106.2229 | -237.7771 | 20.484 | 20.5849 | 20.6789 | 106.2229 | 20.6789 | 20.484 | 20.5849
107.2229 | -236.7771 | 20.4949 | 20.588 | 20.6849 | 107.2229 | 20.6849 | 20.4949 | 20.588
108.2229 | -235.7771 | 20.4757 | 20.5864 | 20.6683 | 108.2229 | 20.6683 | 20.4757 | 20.5864
109.2229 | -234.7771 | 20.4772 | 20.5847 | 20.6769 | 109.2229 | 20.6769 | 20.4772 | 20.5847
110.2229 | -233.7771 | 20.4887 | 20.5882 | 20.6737 | 110.2229 | 20.6737 | 20.4887 | 20.5882
111.2229 | -232.7771 | 20.4916 | 20.5899 | 20.671 | 111.2229 | 20.671 | 20.4916 | 20.5899
112.2229 | -231.7771 | 20.4832 | 20.5889 | 20.6593 | 112.2229 | 20.6593 | 20.4832 | 20.5889
113.2229 | -230.7771 | 20.4803 | 20.5881 | 20.6701 | 113.2229 | 20.6701 | 20.4803 | 20.5881
114.2229 | -229.7771 | 20.4913 | 20.5859 | 20.6797 | 114.2229 | 20.6797 | 20.4913 | 20.5859
115.2229 | -228.7771 | 20.4873 | 20.5861 | 20.6812 | 115.2229 | 20.6812 | 20.4873 | 20.5861
116.2229 | -227.7771 | 20.4826 | 20.5909 | 20.6702 | 116.2229 | 20.6702 | 20.4826 | 20.5909
117.2229 | -226.7771 | 20.4887 | 20.586 | 20.6631 | 117.2229 | 20.6631 | 20.4887 | 20.586
118.2229 | -225.7771 | 20.4774 | 20.5847 | 20.6671 | 118.2229 | 20.6671 | 20.4774 | 20.5847
119.2229 | -224.7771 | 20.4807 | 20.5905 | 20.6653 | 119.2229 | 20.6653 | 20.4807 | 20.5905
120.2229 | -223.7771 | 20.4833 | 20.5878 | 20.671 | 120.2229 | 20.671 | 20.4833 | 20.5878
121.2229 | -222.7771 | 20.4895 | 20.5845 | 20.6713 | 121.2229 | 20.6713 | 20.4895 | 20.5845
122.2229 | -221.7771 | 20.4785 | 20.5838 | 20.6727 | 122.2229 | 20.6727 | 20.4785 | 20.5838
123.2229 | -220.7771 | 20.494 | 20.5916 | 20.6679 | 123.2229 | 20.6679 | 20.494 | 20.5916
124.2229 | -219.7771 | 20.4937 | 20.5835 | 20.6739 | 124.2229 | 20.6739 | 20.4937 | 20.5835
125.2229 | -218.7771 | 20.4826 | 20.584 | 20.6768 | 125.2229 | 20.6768 | 20.4826 | 20.584
126.2229 | -217.7771 | 20.488 | 20.5865 | 20.6834 | 126.2229 | 20.6834 | 20.488 | 20.5865
127.2229 | -216.7771 | 20.4746 | 20.5891 | 20.6899 | 127.2229 | 20.6899 | 20.4746 | 20.5891
128.2229 | -215.7771 | 20.4783 | 20.588 | 20.6817 | 128.2229 | 20.6817 | 20.4783 | 20.588
129.2229 | -214.7771 | 20.4934 | 20.5806 | 20.6854 | 129.2229 | 20.6854 | 20.4934 | 20.5806
130.2229 | -213.7771 | 20.4881 | 20.5855 | 20.6745 | 130.2229 | 20.6745 | 20.4881 | 20.5855
131.2229 | -212.7771 | 20.4834 | 20.5849 | 20.6804 | 131.2229 | 20.6804 | 20.4834 | 20.5849
132.2229 | -211.7771 | 20.4827 | 20.5851 | 20.6777 | 132.2229 | 20.6777 | 20.4827 | 20.5851
133.2229 | -210.7771 | 20.4682 | 20.5893 | 20.6737 | 133.2229 | 20.6737 | 20.4682 | 20.5893
134.2229 | -209.7771 | 20.4904 | 20.5828 | 20.6766 | 134.2229 | 20.6766 | 20.4904 | 20.5828
135.2229 | -208.7771 | 20.476 | 20.5895 | 20.6831 | 135.2229 | 20.6831 | 20.476 | 20.5895
136.2229 | -207.7771 | 20.4835 | 20.5908 | 20.6772 | 136.2229 | 20.6772 | 20.4835 | 20.5908
137.2229 | -206.7771 | 20.4863 | 20.5927 | 20.6806 | 137.2229 | 20.6806 | 20.4863 | 20.5927
138.2229 | -205.7771 | 20.4816 | 20.5911 | 20.6729 | 138.2229 | 20.6729 | 20.4816 | 20.5911
139.2229 | -204.7771 | 20.4703 | 20.59 | 20.6738 | 139.2229 | 20.6738 | 20.4703 | 20.59
140.2229 | -203.7771 | 20.4716 | 20.5887 | 20.6752 | 140.2229 | 20.6752 | 20.4716 | 20.5887
141.2229 | -202.7771 | 20.4749 | 20.587 | 20.6744 | 141.2229 | 20.6744 | 20.4749 | 20.587
142.2229 | -201.7771 | 20.4759 | 20.588 | 20.6749 | 142.2229 | 20.6749 | 20.4759 | 20.588
143.2229 | -200.7771 | 20.4751 | 20.5848 | 20.6747 | 143.2229 | 20.6747 | 20.4751 | 20.5848
144.2229 | -199.7771 | 20.4712 | 20.5848 | 20.6707 | 144.2229 | 20.6707 | 20.4712 | 20.5848
145.2229 | -198.7771 | 20.4693 | 20.5894 | 20.6751 | 145.2229 | 20.6751 | 20.4693 | 20.5894
146.2229 | -197.7771 | 20.4676 | 20.584 | 20.6684 | 146.2229 | 20.6684 | 20.4676 | 20.584
147.2229 | -196.7771 | 20.4732 | 20.5879 | 20.6791 | 147.2229 | 20.6791 | 20.4732 | 20.5879
148.2229 | -195.7771 | 20.4696 | 20.5848 | 20.6717 | 148.2229 | 20.6717 | 20.4696 | 20.5848
149.2229 | -194.7771 | 20.4788 | 20.5874 | 20.6727 | 149.2229 | 20.6727 | 20.4788 | 20.5874
150.2229 | -193.7771 | 20.4703 | 20.5822 | 20.6639 | 150.2229 | 20.6639 | 20.4703 | 20.5822
151.2229 | -192.7771 | 20.4754 | 20.5884 | 20.6654 | 151.2229 | 20.6654 | 20.4754 | 20.5884
152.2229 | -191.7771 | 20.4829 | 20.5877 | 20.669 | 152.2229 | 20.669 | 20.4829 | 20.5877
153.2229 | -190.7771 | 20.4657 | 20.5861 | 20.6722 | 153.2229 | 20.6722 | 20.4657 | 20.5861
154.2229 | -189.7771 | 20.4711 | 20.596 | 20.6695 | 154.2229 | 20.6695 | 20.4711 | 20.596
155.2229 | -188.7771 | 20.4751 | 20.5931 | 20.6686 | 155.2229 | 20.6686 | 20.4751 | 20.5931
156.2229 | -187.7771 | 20.4737 | 20.582 | 20.6565 | 156.2229 | 20.6565 | 20.4737 | 20.582
157.2229 | -186.7771 | 20.4807 | 20.5897 | 20.6706 | 157.2229 | 20.6706 | 20.4807 | 20.5897
158.2229 | -185.7771 | 20.4715 | 20.5919 | 20.6655 | 158.2229 | 20.6655 | 20.4715 | 20.5919
159.2229 | -184.7771 | 20.4804 | 20.5892 | 20.6634 | 159.2229 | 20.6634 | 20.4804 | 20.5892
160.2229 | -183.7771 | 20.4593 | 20.5884 | 20.667 | 160.2229 | 20.667 | 20.4593 | 20.5884
161.2229 | -182.7771 | 20.4704 | 20.5894 | 20.6613 | 161.2229 | 20.6613 | 20.4704 | 20.5894
162.2229 | -181.7771 | 20.4633 | 20.5948 | 20.6591 | 162.2229 | 20.6591 | 20.4633 | 20.5948
163.2229 | -180.7771 | 20.4735 | 20.5892 | 20.6571 | 163.2229 | 20.6571 | 20.4735 | 20.5892
164.2229 | -179.7771 | 20.4731 | 20.5883 | 20.6643 | 164.2229 | 20.6643 | 20.4731 | 20.5883
165.2229 | -178.7771 | 20.4675 | 20.5869 | 20.673 | 165.2229 | 20.673 | 20.4675 | 20.5869
166.2229 | -177.7771 | 20.4685 | 20.5889 | 20.6655 | 166.2229 | 20.6655 | 20.4685 | 20.5889
167.2229 | -176.7771 | 20.4723 | 20.5917 | 20.6734 | 167.2229 | 20.6734 | 20.4723 | 20.5917
168.2229 | -175.7771 | 20.4731 | 20.5878 | 20.6772 | 168.2229 | 20.6772 | 20.4731 | 20.5878
169.2229 | -174.7771 | 20.4792 | 20.5946 | 20.6782 | 169.2229 | 20.6782 | 20.4792 | 20.5946
170.2229 | -173.7771 | 20.4724 | 20.5854 | 20.6841 | 170.2229 | 20.6841 | 20.4724 | 20.5854
171.2229 | -172.7771 | 20.4713 | 20.5948 | 20.6755 | 171.2229 | 20.6755 | 20.4713 | 20.5948
172.2229 | -171.7771 | 20.477 | 20.591 | 20.6671 | 172.2229 | 20.6671 | 20.477 | 20.591
173.2229 | -170.7771 | 20.4769 | 20.5852 | 20.666 | 173.2229 | 20.666 | 20.4769 | 20.5852
174.2229 | -169.7771 | 20.476 | 20.591 | 20.665 | 174.2229 | 20.665 | 20.476 | 20.591
175.2229 | -168.7771 | 20.4732 | 20.5891 | 20.6757 | 175.2229 | 20.6757 | 20.4732 | 20.5891
176.2229 | -167.7771 | 20.4549 | 20.5954 | 20.6711 | 176.2229 | 20.6711 | 20.4549 | 20.5954
177.2229 | -166.7771 | 20.459 | 20.59 | 20.6676 | 177.2229 | 20.6676 | 20.459 | 20.59
178.2229 | -165.7771 | 20.4602 | 20.5924 | 20.6777 | 178.2229 | 20.6777 | 20.4602 | 20.5924
179.2229 | -164.7771 | 20.4651 | 20.5926 | 20.6804 | 179.2229 | 20.6804 | 20.4651 | 20.5926
180.2229 | -163.7771 | 20.4696 | 20.5957 | 20.6723 | 180.2229 | 20.6723 | 20.4696 | 20.5957
181.2229 | -162.7771 | 20.4704 | 20.5873 | 20.6741 | 181.2229 | 20.6741 | 20.4704 | 20.5873
182.2229 | -161.7771 | 20.4417 | 20.5939 | 20.6761 | 182.2229 | 20.6761 | 20.4417 | 20.5939
183.2229 | -160.7771 | 20.4664 | 20.591 | 20.6713 | 183.2229 | 20.6713 | 20.4664 | 20.591
184.2229 | -159.7771 | 20.4619 | 20.592 | 20.6758 | 184.2229 | 20.6758 | 20.4619 | 20.592
185.2229 | -158.7771 | 20.4511 | 20.5867 | 20.6673 | 185.2229 | 20.6673 | 20.4511 | 20.5867
186.2229 | -157.7771 | 20.4728 | 20.5884 | 20.6807 | 186.2229 | 20.6807 | 20.4728 | 20.5884
187.2229 | -156.7771 | 20.4616 | 20.5929 | 20.666 | 187.2229 | 20.666 | 20.4616 | 20.5929
188.2229 | -155.7771 | 20.4714 | 20.5908 | 20.673 | 188.2229 | 20.673 | 20.4714 | 20.5908
189.2229 | -154.7771 | 20.4615 | 20.5931 | 20.676 | 189.2229 | 20.676 | 20.4615 | 20.5931
190.2229 | -153.7771 | 20.4626 | 20.5913 | 20.6748 | 190.2229 | 20.6748 | 20.4626 | 20.5913
191.2229 | -152.7771 | 20.4669 | 20.5939 | 20.679 | 191.2229 | 20.679 | 20.4669 | 20.5939
192.2229 | -151.7771 | 20.4652 | 20.5949 | 20.6753 | 192.2229 | 20.6753 | 20.4652 | 20.5949
193.2229 | -150.7771 | 20.4593 | 20.5928 | 20.6791 | 193.2229 | 20.6791 | 20.4593 | 20.5928
194.2229 | -149.7771 | 20.4667 | 20.5883 | 20.6743 | 194.2229 | 20.6743 | 20.4667 | 20.5883
195.2229 | -148.7771 | 20.465 | 20.5904 | 20.6805 | 195.2229 | 20.6805 | 20.465 | 20.5904
196.2229 | -147.7771 | 20.4607 | 20.5903 | 20.6852 | 196.2229 | 20.6852 | 20.4607 | 20.5903
197.2229 | -146.7771 | 20.4518 | 20.5917 | 20.6765 | 197.2229 | 20.6765 | 20.4518 | 20.5917
198.2229 | -145.7771 | 20.4615 | 20.588 | 20.6751 | 198.2229 | 20.6751 | 20.4615 | 20.588
199.2229 | -144.7771 | 20.4655 | 20.5894 | 20.6809 | 199.2229 | 20.6809 | 20.4655 | 20.5894
200.2229 | -143.7771 | 20.4587 | 20.5902 | 20.6765 | 200.2229 | 20.6765 | 20.4587 | 20.5902
201.2229 | -142.7771 | 20.4707 | 20.5927 | 20.6817 | 201.2229 | 20.6817 | 20.4707 | 20.5927
202.2229 | -141.7771 | 20.4686 | 20.5895 | 20.6772 | 202.2229 | 20.6772 | 20.4686 | 20.5895
203.2229 | -140.7771 | 20.464 | 20.5948 | 20.6691 | 203.2229 | 20.6691 | 20.464 | 20.5948
204.2229 | -139.7771 | 20.4642 | 20.5931 | 20.6706 | 204.2229 | 20.6706 | 20.4642 | 20.5931
205.2229 | -138.7771 | 20.4539 | 20.5881 | 20.6724 | 205.2229 | 20.6724 | 20.4539 | 20.5881
206.2229 | -137.7771 | 20.4466 | 20.5903 | 20.6716 | 206.2229 | 20.6716 | 20.4466 | 20.5903
207.2229 | -136.7771 | 20.4654 | 20.5879 | 20.6699 | 207.2229 | 20.6699 | 20.4654 | 20.5879
208.2229 | -135.7771 | 20.4582 | 20.5876 | 20.6767 | 208.2229 | 20.6767 | 20.4582 | 20.5876
209.2229 | -134.7771 | 20.4557 | 20.5915 | 20.6636 | 209.2229 | 20.6636 | 20.4557 | 20.5915
210.2229 | -133.7771 | 20.4654 | 20.5939 | 20.6694 | 210.2229 | 20.6694 | 20.4654 | 20.5939
211.2229 | -132.7771 | 20.468 | 20.5884 | 20.6687 | 211.2229 | 20.6687 | 20.468 | 20.5884
212.2229 | -131.7771 | 20.4607 | 20.5911 | 20.673 | 212.2229 | 20.673 | 20.4607 | 20.5911
213.2229 | -130.7771 | 20.4583 | 20.5898 | 20.6752 | 213.2229 | 20.6752 | 20.4583 | 20.5898
214.2229 | -129.7771 | 20.457 | 20.5875 | 20.6799 | 214.2229 | 20.6799 | 20.457 | 20.5875
215.2229 | -128.7771 | 20.4484 | 20.591 | 20.6795 | 215.2229 | 20.6795 | 20.4484 | 20.591
216.2229 | -127.7771 | 20.4692 | 20.5879 | 20.6764 | 216.2229 | 20.6764 | 20.4692 | 20.5879
217.2229 | -126.7771 | 20.453 | 20.5872 | 20.6792 | 217.2229 | 20.6792 | 20.453 | 20.5872
218.2229 | -125.7771 | 20.4556 | 20.5923 | 20.6873 | 218.2229 | 20.6873 | 20.4556 | 20.5923
219.2229 | -124.7771 | 20.4564 | 20.5901 | 20.6752 | 219.2229 | 20.6752 | 20.4564 | 20.5901
220.2229 | -123.7771 | 20.4529 | 20.5896 | 20.6648 | 220.2229 | 20.6648 | 20.4529 | 20.5896
221.2229 | -122.7771 | 20.4586 | 20.592 | 20.6668 | 221.2229 | 20.6668 | 20.4586 | 20.592
222.2229 | -121.7771 | 20.4591 | 20.589 | 20.6718 | 222.2229 | 20.6718 | 20.4591 | 20.589
223.2229 | -120.7771 | 20.4676 | 20.593 | 20.6718 | 223.2229 | 20.6718 | 20.4676 | 20.593
224.2229 | -119.7771 | 20.4521 | 20.5876 | 20.6699 | 224.2229 | 20.6699 | 20.4521 | 20.5876
225.2229 | -118.7771 | 20.4524 | 20.5866 | 20.6665 | 225.2229 | 20.6665 | 20.4524 | 20.5866
226.2229 | -117.7771 | 20.4501 | 20.5849 | 20.671 | 226.2229 | 20.671 | 20.4501 | 20.5849
227.2229 | -116.7771 | 20.4617 | 20.5914 | 20.6641 | 227.2229 | 20.6641 | 20.4617 | 20.5914
228.2229 | -115.7771 | 20.4478 | 20.5929 | 20.6728 | 228.2229 | 20.6728 | 20.4478 | 20.5929
229.2229 | -114.7771 | 20.4564 | 20.5891 | 20.6795 | 229.2229 | 20.6795 | 20.4564 | 20.5891
230.2229 | -113.7771 | 20.4527 | 20.587 | 20.6873 | 230.2229 | 20.6873 | 20.4527 | 20.587
231.2229 | -112.7771 | 20.4609 | 20.588 | 20.6834 | 231.2229 | 20.6834 | 20.4609 | 20.588
232.2229 | -111.7771 | 20.4482 | 20.5878 | 20.6754 | 232.2229 | 20.6754 | 20.4482 | 20.5878
233.2229 | -110.7771 | 20.4561 | 20.5841 | 20.6755 | 233.2229 | 20.6755 | 20.4561 | 20.5841
234.2229 | -109.7771 | 20.4522 | 20.5899 | 20.6773 | 234.2229 | 20.6773 | 20.4522 | 20.5899
235.2229 | -108.7771 | 20.461 | 20.5859 | 20.6705 | 235.2229 | 20.6705 | 20.461 | 20.5859
236.2229 | -107.7771 | 20.4576 | 20.5799 | 20.6764 | 236.2229 | 20.6764 | 20.4576 | 20.5799
237.2229 | -106.7771 | 20.4513 | 20.5842 | 20.6796 | 237.2229 | 20.6796 | 20.4513 | 20.5842
238.2229 | -105.7771 | 20.4617 | 20.5885 | 20.6731 | 238.2229 | 20.6731 | 20.4617 | 20.5885
239.2229 | -104.7771 | 20.4601 | 20.5871 | 20.6607 | 239.2229 | 20.6607 | 20.4601 | 20.5871
240.2229 | -103.7771 | 20.4555 | 20.5861 | 20.673 | 240.2229 | 20.673 | 20.4555 | 20.5861
241.2229 | -102.7771 | 20.4587 | 20.5893 | 20.6687 | 241.2229 | 20.6687 | 20.4587 | 20.5893
242.2229 | -101.7771 | 20.4556 | 20.5905 | 20.6742 | 242.2229 | 20.6742 | 20.4556 | 20.5905
243.2229 | -100.7771 | 20.4566 | 20.5976 | 20.6722 | 243.2229 | 20.6722 | 20.4566 | 20.5976
244.2229 | -99.7771 | 20.4417 | 20.5908 | 20.666 | 244.2229 | 20.666 | 20.4417 | 20.5908
245.2229 | -98.7771 | 20.4533 | 20.5892 | 20.6813 | 245.2229 | 20.6813 | 20.4533 | 20.5892
246.2229 | -97.7771 | 20.4547 | 20.5953 | 20.6731 | 246.2229 | 20.6731 | 20.4547 | 20.5953
247.2229 | -96.7771 | 20.4526 | 20.5887 | 20.6737 | 247.2229 | 20.6737 | 20.4526 | 20.5887
248.2229 | -95.7771 | 20.4552 | 20.5891 | 20.6736 | 248.2229 | 20.6736 | 20.4552 | 20.5891
249.2229 | -94.7771 | 20.4453 | 20.5934 | 20.6711 | 249.2229 | 20.6711 | 20.4453 | 20.5934
250.2229 | -93.7771 | 20.4511 | 20.5907 | 20.6733 | 250.2229 | 20.6733 | 20.4511 | 20.5907
251.2229 | -92.7771 | 20.4535 | 20.5855 | 20.6689 | 251.2229 | 20.6689 | 20.4535 | 20.5855
252.2229 | -91.7771 | 20.4478 | 20.5867 | 20.6787 | 252.2229 | 20.6787 | 20.4478 | 20.5867
253.2229 | -90.7771 | 20.4487 | 20.586 | 20.6696 | 253.2229 | 20.6696 | 20.4487 | 20.586
254.2229 | -89.7771 | 20.452 | 20.5831 | 20.6718 | 254.2229 | 20.6718 | 20.452 | 20.5831
255.2229 | -88.7771 | 20.4408 | 20.5873 | 20.6783 | 255.2229 | 20.6783 | 20.4408 | 20.5873
256.2229 | -87.7771 | 20.4379 | 20.5865 | 20.6713 | 256.2229 | 20.6713 | 20.4379 | 20.5865
257.2229 | -86.7771 | 20.4515 | 20.5847 | 20.6754 | 257.2229 | 20.6754 | 20.4515 | 20.5847
258.2229 | -85.7771 | 20.4544 | 20.5867 | 20.6746 | 258.2229 | 20.6746 | 20.4544 | 20.5867
259.2229 | -84.7771 | 20.4456 | 20.5887 | 20.6773 | 259.2229 | 20.6773 | 20.4456 | 20.5887
260.2229 | -83.7771 | 20.4407 | 20.5831 | 20.6666 | 260.2229 | 20.6666 | 20.4407 | 20.5831
261.2229 | -82.7771 | 20.4443 | 20.5919 | 20.6772 | 261.2229 | 20.6772 | 20.4443 | 20.5919
262.2229 | -81.7771 | 20.4433 | 20.5867 | 20.6803 | 262.2229 | 20.6803 | 20.4433 | 20.5867
263.2229 | -80.7771 | 20.442 | 20.588 | 20.6748 | 263.2229 | 20.6748 | 20.442 | 20.588
264.2229 | -79.7771 | 20.4497 | 20.5928 | 20.6732 | 264.2229 | 20.6732 | 20.4497 | 20.5928
265.2229 | -78.7771 | 20.4488 | 20.5854 | 20.6713 | 265.2229 | 20.6713 | 20.4488 | 20.5854
266.2229 | -77.7771 | 20.442 | 20.5899 | 20.6632 | 266.2229 | 20.6632 | 20.442 | 20.5899
267.2229 | -76.7771 | 20.434 | 20.5891 | 20.6798 | 267.2229 | 20.6798 | 20.434 | 20.5891
268.2229 | -75.7771 | 20.4541 | 20.5837 | 20.6802 | 268.2229 | 20.6802 | 20.4541 | 20.5837
269.2229 | -74.7771 | 20.4383 | 20.5845 | 20.6613 | 269.2229 | 20.6613 | 20.4383 | 20.5845
270.2229 | -73.7771 | 20.4432 | 20.5816 | 20.6652 | 270.2229 | 20.6652 | 20.4432 | 20.5816
271.2229 | -72.7771 | 20.4557 | 20.5839 | 20.6685 | 271.2229 | 20.6685 | 20.4557 | 20.5839
272.2229 | -71.7771 | 20.4355 | 20.5894 | 20.6655 | 272.2229 | 20.6655 | 20.4355 | 20.5894
273.2229 | -70.7771 | 20.4378 | 20.5918 | 20.673 | 273.2229 | 20.673 | 20.4378 | 20.5918
274.2229 | -69.7771 | 20.4473 | 20.5915 | 20.6753 | 274.2229 | 20.6753 | 20.4473 | 20.5915
275.2229 | -68.7771 | 20.4405 | 20.5912 | 20.671 | 275.2229 | 20.671 | 20.4405 | 20.5912
276.2229 | -67.7771 | 20.436 | 20.5867 | 20.6716 | 276.2229 | 20.6716 | 20.436 | 20.5867
277.2229 | -66.7771 | 20.4336 | 20.5896 | 20.6648 | 277.2229 | 20.6648 | 20.4336 | 20.5896
278.2229 | -65.7771 | 20.4505 | 20.5894 | 20.6693 | 278.2229 | 20.6693 | 20.4505 | 20.5894
279.2229 | -64.7771 | 20.4394 | 20.5902 | 20.6628 | 279.2229 | 20.6628 | 20.4394 | 20.5902
280.2229 | -63.7771 | 20.4412 | 20.5834 | 20.6731 | 280.2229 | 20.6731 | 20.4412 | 20.5834
281.2229 | -62.7771 | 20.431 | 20.5891 | 20.6694 | 281.2229 | 20.6694 | 20.431 | 20.5891
282.2229 | -61.7771 | 20.4294 | 20.5948 | 20.6686 | 282.2229 | 20.6686 | 20.4294 | 20.5948
283.2229 | -60.7771 | 20.4425 | 20.5885 | 20.6776 | 283.2229 | 20.6776 | 20.4425 | 20.5885
284.2229 | -59.7771 | 20.4516 | 20.5876 | 20.664 | 284.2229 | 20.664 | 20.4516 | 20.5876
285.2229 | -58.7771 | 20.4449 | 20.5847 | 20.6709 | 285.2229 | 20.6709 | 20.4449 | 20.5847
286.2229 | -57.7771 | 20.4343 | 20.5858 | 20.6696 | 286.2229 | 20.6696 | 20.4343 | 20.5858
287.2229 | -56.7771 | 20.4355 | 20.5876 | 20.6654 | 287.2229 | 20.6654 | 20.4355 | 20.5876
288.2229 | -55.7771 | 20.4385 | 20.5869 | 20.6696 | 288.2229 | 20.6696 | 20.4385 | 20.5869
289.2229 | -54.7771 | 20.4468 | 20.5918 | 20.6608 | 289.2229 | 20.6608 | 20.4468 | 20.5918
290.2229 | -53.7771 | 20.4462 | 20.5924 | 20.6701 | 290.2229 | 20.6701 | 20.4462 | 20.5924
291.2229 | -52.7771 | 20.4444 | 20.593 | 20.6641 | 291.2229 | 20.6641 | 20.4444 | 20.593
292.2229 | -51.7771 | 20.4281 | 20.5871 | 20.6604 | 292.2229 | 20.6604 | 20.4281 | 20.5871
293.2229 | -50.7771 | 20.4431 | 20.586 | 20.6692 | 293.2229 | 20.6692 | 20.4431 | 20.586
294.2229 | -49.7771 | 20.4389 | 20.5915 | 20.6685 | 294.2229 | 20.6685 | 20.4389 | 20.5915
295.2229 | -48.7771 | 20.4395 | 20.5893 | 20.6728 | 295.2229 | 20.6728 | 20.4395 | 20.5893
296.2229 | -47.7771 | 20.4391 | 20.588 | 20.6774 | 296.2229 | 20.6774 | 20.4391 | 20.588
297.2229 | -46.7771 | 20.4476 | 20.5839 | 20.6744 | 297.2229 | 20.6744 | 20.4476 | 20.5839
298.2229 | -45.7771 | 20.4227 | 20.5829 | 20.6691 | 298.2229 | 20.6691 | 20.4227 | 20.5829
299.2229 | -44.7771 | 20.4407 | 20.591 | 20.6698 | 299.2229 | 20.6698 | 20.4407 | 20.591
300.2229 | -43.7771 | 20.4377 | 20.5849 | 20.6584 | 300.2229 | 20.6584 | 20.4377 | 20.5849
301.2229 | -42.7771 | 20.438 | 20.5911 | 20.6712 | 301.2229 | 20.6712 | 20.438 | 20.5911
302.2229 | -41.7771 | 20.4482 | 20.5907 | 20.6753 | 302.2229 | 20.6753 | 20.4482 | 20.5907
303.2229 | -40.7771 | 20.4465 | 20.587 | 20.675 | 303.2229 | 20.675 | 20.4465 | 20.587
304.2229 | -39.7771 | 20.4206 | 20.592 | 20.6648 | 304.2229 | 20.6648 | 20.4206 | 20.592
305.2229 | -38.7771 | 20.4374 | 20.582 | 20.6686 | 305.2229 | 20.6686 | 20.4374 | 20.582
306.2229 | -37.7771 | 20.4454 | 20.5801 | 20.6766 | 306.2229 | 20.6766 | 20.4454 | 20.5801
307.2229 | -36.7771 | 20.441 | 20.5828 | 20.6669 | 307.2229 | 20.6669 | 20.441 | 20.5828
308.2229 | -35.7771 | 20.4259 | 20.5837 | 20.67 | 308.2229 | 20.67 | 20.4259 | 20.5837
309.2229 | -34.7771 | 20.4344 | 20.5807 | 20.6713 | 309.2229 | 20.6713 | 20.4344 | 20.5807
310.2229 | -33.7771 | 20.4341 | 20.5889 | 20.6668 | 310.2229 | 20.6668 | 20.4341 | 20.5889
311.2229 | -32.7771 | 20.4319 | 20.5877 | 20.674 | 311.2229 | 20.674 | 20.4319 | 20.5877
312.2229 | -31.7771 | 20.4308 | 20.5906 | 20.684 | 312.2229 | 20.684 | 20.4308 | 20.5906
313.2229 | -30.7771 | 20.4307 | 20.5867 | 20.6812 | 313.2229 | 20.6812 | 20.4307 | 20.5867
314.2229 | -29.7771 | 20.4304 | 20.5856 | 20.6815 | 314.2229 | 20.6815 | 20.4304 | 20.5856
315.2229 | -28.7771 | 20.4255 | 20.5891 | 20.6797 | 315.2229 | 20.6797 | 20.4255 | 20.5891
316.2229 | -27.7771 | 20.4359 | 20.5902 | 20.6865 | 316.2229 | 20.6865 | 20.4359 | 20.5902
317.2229 | -26.7771 | 20.4358 | 20.589 | 20.6851 | 317.2229 | 20.6851 | 20.4358 | 20.589
318.2229 | -25.7771 | 20.4398 | 20.5796 | 20.6838 | 318.2229 | 20.6838 | 20.4398 | 20.5796
319.2229 | -24.7771 | 20.4277 | 20.5898 | 20.6757 | 319.2229 | 20.6757 | 20.4277 | 20.5898
320.2229 | -23.7771 | 20.4323 | 20.5845 | 20.6694 | 320.2229 | 20.6694 | 20.4323 | 20.5845
321.2229 | -22.7771 | 20.4439 | 20.5809 | 20.6688 | 321.2229 | 20.6688 | 20.4439 | 20.5809
322.2229 | -21.7771 | 20.4356 | 20.588 | 20.676 | 322.2229 | 20.676 | 20.4356 | 20.588
323.2229 | -20.7771 | 20.436 | 20.5846 | 20.6666 | 323.2229 | 20.6666 | 20.436 | 20.5846
324.2229 | -19.7771 | 20.4232 | 20.5879 | 20.6661 | 324.2229 | 20.6661 | 20.4232 | 20.5879
325.2229 | -18.7771 | 20.4364 | 20.5841 | 20.6547 | 325.2229 | 20.6547 | 20.4364 | 20.5841
326.2229 | -17.7771 | 20.4356 | 20.589 | 20.6677 | 326.2229 | 20.6677 | 20.4356 | 20.589
327.2229 | -16.7771 | 20.4491 | 20.5785 | 20.668 | 327.2229 | 20.668 | 20.4491 | 20.5785
328.2229 | -15.7771 | 20.4325 | 20.5877 | 20.6707 | 328.2229 | 20.6707 | 20.4325 | 20.5877
329.2229 | -14.7771 | 20.4246 | 20.5813 | 20.6702 | 329.2229 | 20.6702 | 20.4246 | 20.5813
330.2229 | -13.7771 | 20.431 | 20.5844 | 20.6794 | 330.2229 | 20.6794 | 20.431 | 20.5844
331.2229 | -12.7771 | 20.4328 | 20.5814 | 20.6844 | 331.2229 | 20.6844 | 20.4328 | 20.5814
332.2229 | -11.7771 | 20.4282 | 20.5851 | 20.6739 | 332.2229 | 20.6739 | 20.4282 | 20.5851
333.2229 | -10.7771 | 20.4412 | 20.5836 | 20.6778 | 333.2229 | 20.6778 | 20.4412 | 20.5836
334.2229 | -9.7771 | 20.429 | 20.5921 | 20.6708 | 334.2229 | 20.6708 | 20.429 | 20.5921
335.2229 | -8.7771 | 20.4266 | 20.5857 | 20.6656 | 335.2229 | 20.6656 | 20.4266 | 20.5857
336.2229 | -7.7771 | 20.429 | 20.585 | 20.6749 | 336.2229 | 20.6749 | 20.429 | 20.585
337.2229 | -6.7771 | 20.4287 | 20.584 | 20.6698 | 337.2229 | 20.6698 | 20.4287 | 20.584
338.2229 | -5.7771 | 20.4228 | 20.5828 | 20.6715 | 338.2229 | 20.6715 | 20.4228 | 20.5828
339.2229 | -4.7771 | 20.4242 | 20.5859 | 20.6627 | 339.2229 | 20.6627 | 20.4242 | 20.5859
340.2229 | -3.7771 | 20.4306 | 20.5789 | 20.6647 | 340.2229 | 20.6647 | 20.4306 | 20.5789
341.2229 | -2.7771 | 20.4349 | 20.5939 | 20.6607 | 341.2229 | 20.6607 | 20.4349 | 20.5939
342.2229 | -1.7771 | 20.434 | 20.5826 | 20.668 | 342.2229 | 20.668 | 20.434 | 20.5826
343.2229 | -0.7771 | 20.438 | 20.5871 | 20.6797 | 343.2229 | 20.6797 | 20.438 | 20.5871
344.2229 | 0.2229 | 20.4311 | 20.5892 | 20.6699 | 344.2229 | 20.6699 | 20.4311 | 20.5892
345.2229 | 1.2229 | 20.4252 | 20.5904 | 20.6758 | 345.2229 | 20.6758 | 20.4252 | 20.5904
346.2229 | 2.2229 | 20.4357 | 20.5791 | 20.6677 | 346.2229 | 20.6677 | 20.4357 | 20.5791
347.2229 | 3.2229 | 20.4304 | 20.5878 | 20.6757 | 347.2229 | 20.6757 | 20.4304 | 20.5878
348.2229 | 4.2229 | 20.4351 | 20.5853 | 20.673 | 348.2229 | 20.673 | 20.4351 | 20.5853
349.2229 | 5.2229 | 20.4294 | 20.5849 | 20.6748 | 349.2229 | 20.6748 | 20.4294 | 20.5849
350.2229 | 6.2229 | 20.429 | 20.5871 | 20.6753 | 350.2229 | 20.6753 | 20.429 | 20.5871
351.2229 | 7.2229 | 20.4269 | 20.5881 | 20.6732 | 351.2229 | 20.6732 | 20.4269 | 20.5881
352.2229 | 8.2229 | 20.4267 | 20.5824 | 20.681 | 352.2229 | 20.681 | 20.4267 | 20.5824
353.2229 | 9.2229 | 20.4268 | 20.5875 | 20.6742 | 353.2229 | 20.6742 | 20.4268 | 20.5875
354.2229 | 10.2229 | 20.4288 | 20.5836 | 20.6731 | 354.2229 | 20.6731 | 20.4288 | 20.5836
355.2229 | 11.2229 | 20.4277 | 20.5866 | 20.7657 | 355.2229 | 20.7657 | 20.4277 | 20.5866
356.2229 | 12.2229 | 20.4031 | 20.5823 | 21.3898 | 356.2229 | 21.3898 | 20.4031 | 20.5823
357.2229 | 13.2229 | 20.4265 | 20.5851 | 22.7373 | 357.2229 | 22.7373 | 20.4265 | 20.5851
358.2229 | 14.2229 | 20.434 | 20.589 | 24.8173 | 358.2229 | 24.8173 | 20.434 | 20.589
359.2229 | 15.2229 | 20.4307 | 20.59 | 27.4825 | 359.2229 | 27.4825 | 20.4307 | 20.59
360.2229 | 16.2229 | 20.4313 | 20.592 | 30.6604 | 360.2229 | 30.6604 | 20.4313 | 20.592
361.2229 | 17.2229 | 20.4287 | 20.5873 | 34.2827 | 361.2229 | 34.2827 | 20.4287 | 20.5873
362.2229 | 18.2229 | 20.4385 | 20.5826 | 38.2507 | 362.2229 | 38.2507 | 20.4385 | 20.5826
363.2229 | 19.2229 | 20.4226 | 20.5869 | 42.5274 | 363.2229 | 42.5274 | 20.4226 | 20.5869
364.2229 | 20.2229 | 20.4341 | 20.5936 | 47.0483 | 364.2229 | 47.0483 | 20.4341 | 20.5936
365.2229 | 21.2229 | 20.4368 | 20.5906 | 51.7398 | 365.2229 | 51.7398 | 20.4368 | 20.5906
366.2229 | 22.2229 | 20.4353 | 20.5925 | 56.6205 | 366.2229 | 56.6205 | 20.4353 | 20.5925
367.2229 | 23.2229 | 20.427 | 20.5923 | 61.7115 | 367.2229 | 61.7115 | 20.427 | 20.5923
368.2229 | 24.2229 | 20.4464 | 20.5926 | 67.0117 | 368.2229 | 67.0117 | 20.4464 | 20.5926
369.2229 | 25.2229 | 20.4523 | 20.587 | 72.4258 | 369.2229 | 72.4258 | 20.4523 | 20.587
370.2229 | 26.2229 | 20.4627 | 20.5983 | 77.9234 | 370.2229 | 77.9234 | 20.4627 | 20.5983
371.2229 | 27.2229 | 20.4757 | 20.5964 | 83.5309 | 371.2229 | 83.5309 | 20.4757 | 20.5964
372.2229 | 28.2229 | 20.4814 | 20.5947 | 89.1775 | 372.2229 | 89.1775 | 20.4814 | 20.5947
373.2229 | 29.2229 | 20.5008 | 20.5985 | 94.9465 | 373.2229 | 94.9465 | 20.5008 | 20.5985
374.2229 | 30.2229 | 20.5141 | 20.6028 | 100.7903 | 374.2229 | 100.7903 | 20.5141 | 20.6028
375.2229 | 31.2229 | 20.5369 | 20.6025 | 106.7169 | 375.2229 | 106.7169 | 20.5369 | 20.6025
376.2229 | 32.2229 | 20.5649 | 20.6087 | 112.6741 | 376.2229 | 112.6741 | 20.5649 | 20.6087
377.2229 | 33.2229 | 20.5895 | 20.6172 | 118.6042 | 377.2229 | 118.6042 | 20.5895 | 20.6172
378.2229 | 34.2229 | 20.6264 | 20.6218 | 124.6012 | 378.2229 | 124.6012 | 20.6264 | 20.6218
379.2229 | 35.2229 | 20.6596 | 20.628 | 130.7106 | 379.2229 | 130.7106 | 20.6596 | 20.628
380.2229 | 36.2229 | 20.7006 | 20.6329 | 136.8185 | 380.2229 | 136.8185 | 20.7006 | 20.6329
381.2229 | 37.2229 | 20.7465 | 20.6409 | 142.8619 | 381.2229 | 142.8619 | 20.7465 | 20.6409
382.2229 | 38.2229 | 20.7716 | 20.6491 | 148.91 | 382.2229 | 148.91 | 20.7716 | 20.6491
383.2229 | 39.2229 | 20.8309 | 20.6643 | 154.9636 | 383.2229 | 154.9636 | 20.8309 | 20.6643
384.2229 | 40.2229 | 20.8949 | 20.6662 | 160.9573 | 384.2229 | 160.9573 | 20.8949 | 20.6662
385.2229 | 41.2229 | 20.9489 | 20.6875 | 166.8381 | 385.2229 | 166.8381 | 20.9489 | 20.6875
386.2229 | 42.2229 | 21.0128 | 20.705 | 172.837 | 386.2229 | 172.837 | 21.0128 | 20.705
387.2229 | 43.2229 | 21.0827 | 20.7229 | 178.8702 | 387.2229 | 178.8702 | 21.0827 | 20.7229
388.2229 | 44.2229 | 21.1502 | 20.7433 | 184.8833 | 388.2229 | 184.8833 | 21.1502 | 20.7433
389.2229 | 45.2229 | 21.2359 | 20.7714 | 191.0188 | 389.2229 | 191.0188 | 21.2359 | 20.7714
390.2229 | 46.2229 | 21.3292 | 20.7905 | 197.0223 | 390.2229 | 197.0223 | 21.3292 | 20.7905
391.2229 | 47.2229 | 21.4133 | 20.8201 | 202.9401 | 391.2229 | 202.9401 | 21.4133 | 20.8201
392.2229 | 48.2229 | 21.511 | 20.847 | 208.7994 | 392.2229 | 208.7994 | 21.511 | 20.847
393.2229 | 49.2229 | 21.6279 | 20.8707 | 214.7512 | 393.2229 | 214.7512 | 21.6279 | 20.8707
394.2229 | 50.2229 | 21.7424 | 20.9026 | 220.7401 | 394.2229 | 220.7401 | 21.7424 | 20.9026
395.2229 | 51.2229 | 21.8784 | 20.9509 | 226.6229 | 395.2229 | 226.6229 | 21.8784 | 20.9509
396.2229 | 52.2229 | 21.9966 | 20.9867 | 232.5529 | 396.2229 | 232.5529 | 21.9966 | 20.9867
397.2229 | 53.2229 | 22.1457 | 21.0309 | 238.5187 | 397.2229 | 238.5187 | 22.1457 | 21.0309
398.2229 | 54.2229 | 22.2996 | 21.0681 | 244.4378 | 398.2229 | 244.4378 | 22.2996 | 21.0681
399.2229 | 55.2229 | 22.4512 | 21.1165 | 250.3109 | 399.2229 | 250.3109 | 22.4512 | 21.1165
400.2229 | 56.2229 | 22.6271 | 21.1691 | 256.1425 | 400.2229 | 256.1425 | 22.6271 | 21.1691
401.2229 | 57.2229 | 22.7869 | 21.2296 | 261.8313 | 401.2229 | 261.8313 | 22.7869 | 21.2296
402.2229 | 58.2229 | 22.9774 | 21.2906 | 267.5417 | 402.2229 | 267.5417 | 22.9774 | 21.2906
403.2229 | 59.2229 | 23.1709 | 21.3546 | 273.1558 | 403.2229 | 273.1558 | 23.1709 | 21.3546
404.2229 | 60.2229 | 23.3722 | 21.4349 | 278.6696 | 404.2229 | 278.6696 | 23.3722 | 21.4349
405.2229 | 61.2229 | 23.6035 | 21.5151 | 284.3273 | 405.2229 | 284.3273 | 23.6035 | 21.5151
406.2229 | 62.2229 | 23.8227 | 21.595 | 289.9387 | 406.2229 | 289.9387 | 23.8227 | 21.595
407.2229 | 63.2229 | 24.0757 | 21.6796 | 295.4969 | 407.2229 | 295.4969 | 24.0757 | 21.6796
408.2229 | 64.2229 | 24.3218 | 21.7723 | 301.0076 | 408.2229 | 301.0076 | 24.3218 | 21.7723
409.2229 | 65.2229 | 24.5878 | 21.8813 | 306.4943 | 409.2229 | 306.4943 | 24.5878 | 21.8813
410.2229 | 66.2229 | 24.8702 | 21.9807 | 311.9673 | 410.2229 | 311.9673 | 24.8702 | 21.9807
411.2229 | 67.2229 | 25.1491 | 22.0933 | 317.3823 | 411.2229 | 317.3823 | 25.1491 | 22.0933
412.2229 | 68.2229 | 25.4437 | 22.214 | 322.5891 | 412.2229 | 322.5891 | 25.4437 | 22.214
413.2229 | 69.2229 | 25.7739 | 22.3378 | 327.8624 | 413.2229 | 327.8624 | 25.7739 | 22.3378
414.2229 | 70.2229 | 26.1136 | 22.4756 | 333.214 | 414.2229 | 333.214 | 26.1136 | 22.4756
415.2229 | 71.2229 | 26.4418 | 22.6051 | 338.6342 | 415.2229 | 338.6342 | 26.4418 | 22.6051
416.2229 | 72.2229 | 26.7846 | 22.7584 | 344.0177 | 416.2229 | 344.0177 | 26.7846 | 22.7584
417.2229 | 73.2229 | 27.1495 | 22.908 | 349.3795 | 417.2229 | 349.3795 | 27.1495 | 22.908
418.2229 | 74.2229 | 27.5432 | 23.0655 | 354.6301 | 418.2229 | 354.6301 | 27.5432 | 23.0655
419.2229 | 75.2229 | 27.9346 | 23.2352 | 359.7231 | 419.2229 | 359.7231 | 27.9346 | 23.2352
420.2229 | 76.2229 | 28.3378 | 23.4051 | 364.963 | 420.2229 | 364.963 | 28.3378 | 23.4051
421.2385 | 77.2385 | 28.7693 | 23.6032 | 370.372 | 421.2385 | 370.372 | 28.7693 | 23.6032
422.2854 | 78.2854 | 29.2246 | 23.8044 | 375.6316 | 422.2854 | 375.6316 | 29.2246 | 23.8044
423.2229 | 79.2229 | 29.6665 | 23.9885 | 380.3796 | 423.2229 | 380.3796 | 29.6665 | 23.9885
424.2229 | 80.2229 | 30.1238 | 24.1983 | 385.2359 | 424.2229 | 385.2359 | 30.1238 | 24.1983
425.2229 | 81.2229 | 30.6198 | 24.4128 | 389.8291 | 425.2229 | 389.8291 | 30.6198 | 24.4128
426.2229 | 82.2229 | 31.1022 | 24.641 | 393.7912 | 426.2229 | 393.7912 | 31.1022 | 24.641
427.2385 | 83.2385 | 31.6461 | 24.8844 | 397.4297 | 427.2385 | 397.4297 | 31.6461 | 24.8844
428.2229 | 84.2229 | 32.1609 | 25.1266 | 400.8574 | 428.2229 | 400.8574 | 32.1609 | 25.1266
429.3167 | 85.3167 | 32.7651 | 25.4049 | 404.4861 | 429.3167 | 404.4861 | 32.7651 | 25.4049
430.2385 | 86.2385 | 33.2824 | 25.6481 | 407.4589 | 430.2385 | 407.4589 | 33.2824 | 25.6481
431.2229 | 87.2229 | 33.8441 | 25.9252 | 410.4186 | 431.2229 | 410.4186 | 33.8441 | 25.9252
432.2385 | 88.2385 | 34.4575 | 26.2279 | 413.2819 | 432.2385 | 413.2819 | 34.4575 | 26.2279
433.2229 | 89.2229 | 35.0507 | 26.5165 | 415.7499 | 433.2229 | 415.7499 | 35.0507 | 26.5165
434.2229 | 90.2229 | 35.6851 | 26.8263 | 418.1463 | 434.2229 | 418.1463 | 35.6851 | 26.8263
435.2229 | 91.2229 | 36.3268 | 27.1441 | 420.4501 | 435.2229 | 420.4501 | 36.3268 | 27.1441
436.2229 | 92.2229 | 36.9745 | 27.4732 | 422.2566 | 436.2229 | 422.2566 | 36.9745 | 27.4732
437.2229 | 93.2229 | 37.6428 | 27.8177 | 424.1046 | 437.2229 | 424.1046 | 37.6428 | 27.8177
438.2229 | 94.2229 | 38.3247 | 28.1783 | 425.8416 | 438.2229 | 425.8416 | 38.3247 | 28.1783
439.2229 | 95.2229 | 39.0076 | 28.5384 | 427.2469 | 439.2229 | 427.2469 | 39.0076 | 28.5384
440.2229 | 96.2229 | 39.7225 | 28.9108 | 428.3758 | 440.2229 | 428.3758 | 39.7225 | 28.9108
441.2229 | 97.2229 | 40.4209 | 29.3062 | 429.2775 | 441.2229 | 429.2775 | 40.4209 | 29.3062
442.2229 | 98.2229 | 41.1593 | 29.7096 | 430.0287 | 442.2229 | 430.0287 | 41.1593 | 29.7096
443.2229 | 99.2229 | 41.9033 | 30.1197 | 430.4747 | 443.2229 | 430.4747 | 41.9033 | 30.1197
444.2229 | 100.2229 | 42.6357 | 30.5517 | 430.8466 | 444.2229 | 430.8466 | 42.6357 | 30.5517
445.2229 | 101.2229 | 43.4028 | 30.9938 | 431.1893 | 445.2229 | 431.1893 | 43.4028 | 30.9938
446.2229 | 102.2229 | 44.1634 | 31.4457 | 431.2411 | 446.2229 | 431.2411 | 44.1634 | 31.4457
447.2229 | 103.2229 | 44.9299 | 31.91 | 431.3493 | 447.2229 | 431.3493 | 44.9299 | 31.91
448.2229 | 104.2229 | 45.7097 | 32.3923 | 431.4862 | 448.2229 | 431.4862 | 45.7097 | 32.3923
449.2229 | 105.2229 | 46.5026 | 32.8831 | 431.5947 | 449.2229 | 431.5947 | 46.5026 | 32.8831
450.2229 | 106.2229 | 47.2744 | 33.38 | 431.6098 | 450.2229 | 431.6098 | 47.2744 | 33.38
451.2229 | 107.2229 | 48.0759 | 33.8894 | 431.4521 | 451.2229 | 431.4521 | 48.0759 | 33.8894
452.2229 | 108.2229 | 48.8772 | 34.4213 | 431.3725 | 452.2229 | 431.3725 | 48.8772 | 34.4213
453.2229 | 109.2229 | 49.6676 | 34.9422 | 431.4536 | 453.2229 | 431.4536 | 49.6676 | 34.9422
454.2229 | 110.2229 | 50.4672 | 35.5063 | 431.3807 | 454.2229 | 431.3807 | 50.4672 | 35.5063
455.2229 | 111.2229 | 51.273 | 36.0632 | 431.283 | 455.2229 | 431.283 | 51.273 | 36.0632
456.2229 | 112.2229 | 52.0789 | 36.6383 | 431.1849 | 456.2229 | 431.1849 | 52.0789 | 36.6383
457.2229 | 113.2229 | 52.8643 | 37.2061 | 430.9797 | 457.2229 | 430.9797 | 52.8643 | 37.2061
458.2229 | 114.2229 | 53.6713 | 37.7916 | 430.6311 | 458.2229 | 430.6311 | 53.6713 | 37.7916
459.2229 | 115.2229 | 54.4835 | 38.3787 | 430.3747 | 459.2229 | 430.3747 | 54.4835 | 38.3787
460.2229 | 116.2229 | 55.2996 | 38.9789 | 430.197 | 460.2229 | 430.197 | 55.2996 | 38.9789
461.2229 | 117.2229 | 56.084 | 39.5833 | 430.0804 | 461.2229 | 430.0804 | 56.084 | 39.5833
462.2229 | 118.2229 | 56.8783 | 40.1955 | 429.9489 | 462.2229 | 429.9489 | 56.8783 | 40.1955
463.2229 | 119.2229 | 57.6817 | 40.8093 | 429.8575 | 463.2229 | 429.8575 | 57.6817 | 40.8093
464.2229 | 120.2229 | 58.4583 | 41.4346 | 429.7029 | 464.2229 | 429.7029 | 58.4583 | 41.4346
465.2229 | 121.2229 | 59.2492 | 42.058 | 429.4929 | 465.2229 | 429.4929 | 59.2492 | 42.058
466.2229 | 122.2229 | 60.0557 | 42.6996 | 429.182 | 466.2229 | 429.182 | 60.0557 | 42.6996
467.2229 | 123.2229 | 60.8354 | 43.336 | 429.2711 | 467.2229 | 429.2711 | 60.8354 | 43.336
468.2229 | 124.2229 | 61.6163 | 43.9747 | 429.2833 | 468.2229 | 429.2833 | 61.6163 | 43.9747
469.2229 | 125.2229 | 62.403 | 44.6128 | 429.3323 | 469.2229 | 429.3323 | 62.403 | 44.6128
470.2229 | 126.2229 | 63.1681 | 45.284 | 429.4474 | 470.2229 | 429.4474 | 63.1681 | 45.284
471.2229 | 127.2229 | 63.9427 | 45.9297 | 429.6272 | 471.2229 | 429.6272 | 63.9427 | 45.9297
472.2229 | 128.2229 | 64.7369 | 46.5821 | 429.826 | 472.2229 | 429.826 | 64.7369 | 46.5821
473.2229 | 129.2229 | 65.4845 | 47.2389 | 429.8442 | 473.2229 | 429.8442 | 65.4845 | 47.2389
474.2229 | 130.2229 | 66.2498 | 47.8961 | 429.9268 | 474.2229 | 429.9268 | 66.2498 | 47.8961
475.2229 | 131.2229 | 67.0127 | 48.5531 | 430.0528 | 475.2229 | 430.0528 | 67.0127 | 48.5531
476.2229 | 132.2229 | 67.771 | 49.2111 | 430.131 | 476.2229 | 430.131 | 67.771 | 49.2111
477.2229 | 133.2229 | 68.5198 | 49.8649 | 430.3099 | 477.2229 | 430.3099 | 68.5198 | 49.8649
478.2229 | 134.2229 | 69.2674 | 50.5289 | 430.4694 | 478.2229 | 430.4694 | 69.2674 | 50.5289
479.2229 | 135.2229 | 70.0105 | 51.1919 | 430.5264 | 479.2229 | 430.5264 | 70.0105 | 51.1919
480.2229 | 136.2229 | 70.748 | 51.857 | 430.6822 | 480.2229 | 430.6822 | 70.748 | 51.857
481.2229 | 137.2229 | 71.4827 | 52.5116 | 430.7516 | 481.2229 | 430.7516 | 71.4827 | 52.5116
482.2229 | 138.2229 | 72.2163 | 53.1679 | 430.9086 | 482.2229 | 430.9086 | 72.2163 | 53.1679
483.2229 | 139.2229 | 72.9431 | 53.8215 | 431.067 | 483.2229 | 431.067 | 72.9431 | 53.8215
484.2229 | 140.2229 | 73.6938 | 54.4887 | 431.1844 | 484.2229 | 431.1844 | 73.6938 | 54.4887
485.2229 | 141.2229 | 74.4151 | 55.1547 | 431.3448 | 485.2229 | 431.3448 | 74.4151 | 55.1547
486.2229 | 142.2229 | 75.1315 | 55.8157 | 431.5359 | 486.2229 | 431.5359 | 75.1315 | 55.8157
487.2229 | 143.2229 | 75.8486 | 56.4653 | 431.5532 | 487.2229 | 431.5532 | 75.8486 | 56.4653
488.2229 | 144.2229 | 76.5597 | 57.1141 | 431.5732 | 488.2229 | 431.5732 | 76.5597 | 57.1141
489.2229 | 145.2229 | 77.2763 | 57.7691 | 431.6906 | 489.2229 | 431.6906 | 77.2763 | 57.7691
490.2229 | 146.2229 | 77.9888 | 58.4136 | 431.6732 | 490.2229 | 431.6732 | 77.9888 | 58.4136
491.2229 | 147.2229 | 78.6872 | 59.0624 | 431.7247 | 491.2229 | 431.7247 | 78.6872 | 59.0624
492.2229 | 148.2229 | 79.4005 | 59.7019 | 431.7894 | 492.2229 | 431.7894 | 79.4005 | 59.7019
493.2229 | 149.2229 | 80.1063 | 60.345 | 431.7773 | 493.2229 | 431.7773 | 80.1063 | 60.345
494.2229 | 150.2229 | 80.7982 | 60.9864 | 431.9305 | 494.2229 | 431.9305 | 80.7982 | 60.9864
495.2229 | 151.2229 | 81.4972 | 61.6332 | 432.1323 | 495.2229 | 432.1323 | 81.4972 | 61.6332
496.2229 | 152.2229 | 82.1896 | 62.2619 | 432.2294 | 496.2229 | 432.2294 | 82.1896 | 62.2619
497.2229 | 153.2229 | 82.9016 | 62.9058 | 432.4432 | 497.2229 | 432.4432 | 82.9016 | 62.9058
498.2229 | 154.2229 | 83.5895 | 63.5268 | 432.6779 | 498.2229 | 432.6779 | 83.5895 | 63.5268
499.2229 | 155.2229 | 84.2708 | 64.174 | 432.8154 | 499.2229 | 432.8154 | 84.2708 | 64.174
500.2229 | 156.2229 | 84.9649 | 64.7956 | 432.7865 | 500.2229 | 432.7865 | 84.9649 | 64.7956
501.2229 | 157.2229 | 85.6427 | 65.4131 | 432.9214 | 501.2229 | 432.9214 | 85.6427 | 65.4131
502.2229 | 158.2229 | 86.3289 | 66.0335 | 433.0614 | 502.2229 | 433.0614 | 86.3289 | 66.0335
503.2229 | 159.2229 | 87.0206 | 66.6533 | 433.0225 | 503.2229 | 433.0225 | 87.0206 | 66.6533
504.2229 | 160.2229 | 87.6877 | 67.2789 | 432.9991 | 504.2229 | 432.9991 | 87.6877 | 67.2789
505.2229 | 161.2229 | 88.3754 | 67.878 | 433.0962 | 505.2229 | 433.0962 | 88.3754 | 67.878
506.2229 | 162.2229 | 89.048 | 68.4881 | 433.1105 | 506.2229 | 433.1105 | 89.048 | 68.4881
507.2229 | 163.2229 | 89.7219 | 69.0872 | 433.1188 | 507.2229 | 433.1188 | 89.7219 | 69.0872
508.2229 | 164.2229 | 90.3975 | 69.6959 | 433.2181 | 508.2229 | 433.2181 | 90.3975 | 69.6959
509.2229 | 165.2229 | 91.0682 | 70.2956 | 433.1623 | 509.2229 | 433.1623 | 91.0682 | 70.2956
510.2229 | 166.2229 | 91.7338 | 70.8916 | 433.0955 | 510.2229 | 433.0955 | 91.7338 | 70.8916
511.2229 | 167.2229 | 92.4168 | 71.4887 | 433.0763 | 511.2229 | 433.0763 | 92.4168 | 71.4887
512.2229 | 168.2229 | 93.0899 | 72.0781 | 433.1117 | 512.2229 | 433.1117 | 93.0899 | 72.0781
513.2229 | 169.2229 | 93.7498 | 72.6581 | 433.1502 | 513.2229 | 433.1502 | 93.7498 | 72.6581
514.2229 | 170.2229 | 94.4101 | 73.2435 | 433.0964 | 514.2229 | 433.0964 | 94.4101 | 73.2435
515.2229 | 171.2229 | 95.0873 | 73.8398 | 432.9652 | 515.2229 | 432.9652 | 95.0873 | 73.8398
516.2229 | 172.2229 | 95.7458 | 74.4191 | 432.8869 | 516.2229 | 432.8869 | 95.7458 | 74.4191
517.2229 | 173.2229 | 96.4044 | 74.9928 | 432.8397 | 517.2229 | 432.8397 | 96.4044 | 74.9928
518.2229 | 174.2229 | 97.069 | 75.567 | 432.9729 | 518.2229 | 432.9729 | 97.069 | 75.567
519.2229 | 175.2229 | 97.7431 | 76.1369 | 433.0625 | 519.2229 | 433.0625 | 97.7431 | 76.1369
520.2229 | 176.2229 | 98.4062 | 76.7095 | 432.9906 | 520.2229 | 432.9906 | 98.4062 | 76.7095
521.2229 | 177.2229 | 99.0513 | 77.2661 | 432.8748 | 521.2229 | 432.8748 | 99.0513 | 77.2661
522.2229 | 178.2229 | 99.7125 | 77.8328 | 432.8388 | 522.2229 | 432.8388 | 99.7125 | 77.8328
523.2229 | 179.2229 | 100.3609 | 78.3865 | 432.7895 | 523.2229 | 432.7895 | 100.3609 | 78.3865
524.2229 | 180.2229 | 101.0235 | 78.9329 | 432.698 | 524.2229 | 432.698 | 101.0235 | 78.9329
525.2229 | 181.2229 | 101.6852 | 79.4873 | 432.7443 | 525.2229 | 432.7443 | 101.6852 | 79.4873
526.2229 | 182.2229 | 102.3407 | 80.0316 | 432.7731 | 526.2229 | 432.7731 | 102.3407 | 80.0316
527.2229 | 183.2229 | 102.9979 | 80.5848 | 432.8818 | 527.2229 | 432.8818 | 102.9979 | 80.5848
528.2229 | 184.2229 | 103.6322 | 81.1233 | 432.9319 | 528.2229 | 432.9319 | 103.6322 | 81.1233
529.2229 | 185.2229 | 104.2884 | 81.6623 | 432.8884 | 529.2229 | 432.8884 | 104.2884 | 81.6623
530.2229 | 186.2229 | 104.9454 | 82.1973 | 432.8028 | 530.2229 | 432.8028 | 104.9454 | 82.1973
531.2229 | 187.2229 | 105.5844 | 82.7319 | 432.6451 | 531.2229 | 432.6451 | 105.5844 | 82.7319
532.2229 | 188.2229 | 106.2382 | 83.2695 | 432.7363 | 532.2229 | 432.7363 | 106.2382 | 83.2695
533.2229 | 189.2229 | 106.878 | 83.8093 | 432.7133 | 533.2229 | 432.7133 | 106.878 | 83.8093
534.2229 | 190.2229 | 107.5246 | 84.33 | 432.8415 | 534.2229 | 432.8415 | 107.5246 | 84.33
535.2229 | 191.2229 | 108.1641 | 84.8539 | 432.8978 | 535.2229 | 432.8978 | 108.1641 | 84.8539
536.2229 | 192.2229 | 108.8104 | 85.3786 | 432.8228 | 536.2229 | 432.8228 | 108.8104 | 85.3786
537.2229 | 193.2229 | 109.442 | 85.897 | 432.8612 | 537.2229 | 432.8612 | 109.442 | 85.897
538.2229 | 194.2229 | 110.0852 | 86.4112 | 433.0058 | 538.2229 | 433.0058 | 110.0852 | 86.4112
539.2229 | 195.2229 | 110.727 | 86.9258 | 433.1048 | 539.2229 | 433.1048 | 110.727 | 86.9258
540.2229 | 196.2229 | 111.3811 | 87.4418 | 433.2025 | 540.2229 | 433.2025 | 111.3811 | 87.4418
541.2229 | 197.2229 | 112.0172 | 87.9494 | 433.4062 | 541.2229 | 433.4062 | 112.0172 | 87.9494
542.2229 | 198.2229 | 112.6469 | 88.4581 | 433.5916 | 542.2229 | 433.5916 | 112.6469 | 88.4581
543.2229 | 199.2229 | 113.285 | 88.9623 | 433.6646 | 543.2229 | 433.6646 | 113.285 | 88.9623
544.2229 | 200.2229 | 113.9284 | 89.4613 | 433.5635 | 544.2229 | 433.5635 | 113.9284 | 89.4613
545.2229 | 201.2229 | 114.5515 | 89.9584 | 433.7018 | 545.2229 | 433.7018 | 114.5515 | 89.9584
546.2229 | 202.2229 | 115.1872 | 90.462 | 433.7194 | 546.2229 | 433.7194 | 115.1872 | 90.462
547.2229 | 203.2229 | 115.8083 | 90.9726 | 433.8782 | 547.2229 | 433.8782 | 115.8083 | 90.9726
548.2229 | 204.2229 | 116.441 | 91.4654 | 434.0266 | 548.2229 | 434.0266 | 116.441 | 91.4654
549.2229 | 205.2229 | 117.0624 | 91.9562 | 434.0726 | 549.2229 | 434.0726 | 117.0624 | 91.9562
550.2229 | 206.2229 | 117.6778 | 92.4678 | 434.0969 | 550.2229 | 434.0969 | 117.6778 | 92.4678
551.2229 | 207.2229 | 118.3099 | 92.96 | 434.1331 | 551.2229 | 434.1331 | 118.3099 | 92.96
552.2229 | 208.2229 | 118.9178 | 93.4403 | 434.1249 | 552.2229 | 434.1249 | 118.9178 | 93.4403
553.2229 | 209.2229 | 119.5257 | 93.9292 | 434.1494 | 553.2229 | 434.1494 | 119.5257 | 93.9292
554.2229 | 210.2229 | 120.1539 | 94.4094 | 433.9431 | 554.2229 | 433.9431 | 120.1539 | 94.4094
555.2229 | 211.2229 | 120.7754 | 94.8772 | 433.7608 | 555.2229 | 433.7608 | 120.7754 | 94.8772
556.2229 | 212.2229 | 121.3899 | 95.3429 | 433.7325 | 556.2229 | 433.7325 | 121.3899 | 95.3429
557.2229 | 213.2229 | 121.9946 | 95.7935 | 433.7475 | 557.2229 | 433.7475 | 121.9946 | 95.7935
558.2229 | 214.2229 | 122.6001 | 96.2357 | 433.7566 | 558.2229 | 433.7566 | 122.6001 | 96.2357
559.2229 | 215.2229 | 123.1941 | 96.6654 | 433.8157 | 559.2229 | 433.8157 | 123.1941 | 96.6654
560.2229 | 216.2229 | 123.8036 | 97.0871 | 433.8582 | 560.2229 | 433.8582 | 123.8036 | 97.0871
561.2229 | 217.2229 | 124.4129 | 97.4881 | 433.724 | 561.2229 | 433.724 | 124.4129 | 97.4881
562.2229 | 218.2229 | 125.0051 | 97.8679 | 433.6757 | 562.2229 | 433.6757 | 125.0051 | 97.8679
563.2229 | 219.2229 | 125.6014 | 98.2386 | 433.4829 | 563.2229 | 433.4829 | 125.6014 | 98.2386
564.2229 | 220.2229 | 126.1862 | 98.5834 | 433.476 | 564.2229 | 433.476 | 126.1862 | 98.5834
565.2229 | 221.2229 | 126.772 | 98.9112 | 433.4834 | 565.2229 | 433.4834 | 126.772 | 98.9112
566.2229 | 222.2229 | 127.3517 | 99.229 | 433.3902 | 566.2229 | 433.3902 | 127.3517 | 99.229
567.2229 | 223.2229 | 127.9432 | 99.5257 | 433.279 | 567.2229 | 433.279 | 127.9432 | 99.5257
568.2229 | 224.2229 | 128.5109 | 99.8081 | 433.1992 | 568.2229 | 433.1992 | 128.5109 | 99.8081
569.2229 | 225.2229 | 129.094 | 100.08 | 433.1689 | 569.2229 | 433.1689 | 129.094 | 100.08
570.2229 | 226.2229 | 129.6538 | 100.3319 | 433.1261 | 570.2229 | 433.1261 | 129.6538 | 100.3319
571.2229 | 227.2229 | 130.2311 | 100.5811 | 433.1976 | 571.2229 | 433.1976 | 130.2311 | 100.5811
572.2229 | 228.2229 | 130.7883 | 100.8294 | 433.0411 | 572.2229 | 433.0411 | 130.7883 | 100.8294
573.2229 | 229.2229 | 131.32 | 101.0518 | 433.114 | 573.2229 | 433.114 | 131.32 | 101.0518
574.301 | 230.301 | 131.8994 | 101.2912 | 433.2936 | 574.301 | 433.2936 | 131.8994 | 101.2912
575.2854 | 231.2854 | 132.4249 | 101.5138 | 433.4465 | 575.2854 | 433.4465 | 132.4249 | 101.5138
576.2229 | 232.2229 | 132.9096 | 101.7293 | 433.5104 | 576.2229 | 433.5104 | 132.9096 | 101.7293
577.2229 | 233.2229 | 133.4204 | 101.948 | 433.5263 | 577.2229 | 433.5263 | 133.4204 | 101.948
578.2229 | 234.2229 | 133.9212 | 102.1643 | 433.5551 | 578.2229 | 433.5551 | 133.9212 | 102.1643
579.2229 | 235.2229 | 134.425 | 102.3821 | 433.4914 | 579.2229 | 433.4914 | 134.425 | 102.3821
580.2229 | 236.2229 | 134.9155 | 102.5975 | 433.463 | 580.2229 | 433.463 | 134.9155 | 102.5975
581.2229 | 237.2229 | 135.4001 | 102.8243 | 433.3388 | 581.2229 | 433.3388 | 135.4001 | 102.8243
582.2229 | 238.2229 | 135.8946 | 103.0509 | 433.2488 | 582.2229 | 433.2488 | 135.8946 | 103.0509
583.2229 | 239.2229 | 136.3624 | 103.2891 | 433.276 | 583.2229 | 433.276 | 136.3624 | 103.2891
584.2229 | 240.2229 | 136.8652 | 103.5259 | 433.1981 | 584.2229 | 433.1981 | 136.8652 | 103.5259
585.2229 | 241.2229 | 137.345 | 103.7597 | 433.2138 | 585.2229 | 433.2138 | 137.345 | 103.7597
586.2229 | 242.2229 | 137.8256 | 104.0101 | 433.0895 | 586.2229 | 433.0895 | 137.8256 | 104.0101
587.2229 | 243.2229 | 138.3143 | 104.2597 | 432.9744 | 587.2229 | 432.9744 | 138.3143 | 104.2597
588.2229 | 244.2229 | 138.7968 | 104.5188 | 432.8547 | 588.2229 | 432.8547 | 138.7968 | 104.5188
589.2229 | 245.2229 | 139.2765 | 104.7755 | 432.8602 | 589.2229 | 432.8602 | 139.2765 | 104.7755
590.2229 | 246.2229 | 139.7563 | 105.0507 | 432.8236 | 590.2229 | 432.8236 | 139.7563 | 105.0507
591.2229 | 247.2229 | 140.2488 | 105.3358 | 432.7679 | 591.2229 | 432.7679 | 140.2488 | 105.3358
592.2229 | 248.2229 | 140.7279 | 105.6095 | 432.9162 | 592.2229 | 432.9162 | 140.7279 | 105.6095
593.2229 | 249.2229 | 141.2158 | 105.8982 | 432.983 | 593.2229 | 432.983 | 141.2158 | 105.8982
594.2229 | 250.2229 | 141.6924 | 106.197 | 432.9023 | 594.2229 | 432.9023 | 141.6924 | 106.197
595.2229 | 251.2229 | 142.1672 | 106.5017 | 432.7496 | 595.2229 | 432.7496 | 142.1672 | 106.5017
596.2229 | 252.2229 | 142.6495 | 106.8098 | 432.7319 | 596.2229 | 432.7319 | 142.6495 | 106.8098
597.2229 | 253.2229 | 143.1325 | 107.1377 | 432.6995 | 597.2229 | 432.6995 | 143.1325 | 107.1377
598.2229 | 254.2229 | 143.5974 | 107.4635 | 432.7673 | 598.2229 | 432.7673 | 143.5974 | 107.4635
599.2229 | 255.2229 | 144.0924 | 107.8006 | 432.8193 | 599.2229 | 432.8193 | 144.0924 | 107.8006
600.2229 | 256.2229 | 144.5673 | 108.1474 | 432.8333 | 600.2229 | 432.8333 | 144.5673 | 108.1474
601.2229 | 257.2229 | 145.0472 | 108.5024 | 432.7539 | 601.2229 | 432.7539 | 145.0472 | 108.5024
602.2229 | 258.2229 | 145.5329 | 108.8576 | 432.8506 | 602.2229 | 432.8506 | 145.5329 | 108.8576
603.2229 | 259.2229 | 145.9949 | 109.2131 | 432.942 | 603.2229 | 432.942 | 145.9949 | 109.2131
604.2229 | 260.2229 | 146.4805 | 109.5853 | 432.9486 | 604.2229 | 432.9486 | 146.4805 | 109.5853
605.2229 | 261.2229 | 146.959 | 109.9394 | 432.8865 | 605.2229 | 432.8865 | 146.959 | 109.9394
606.2229 | 262.2229 | 147.4127 | 110.3152 | 432.782 | 606.2229 | 432.782 | 147.4127 | 110.3152
607.2229 | 263.2229 | 147.8955 | 110.6828 | 432.727 | 607.2229 | 432.727 | 147.8955 | 110.6828
608.2229 | 264.2229 | 148.3681 | 111.0604 | 432.8865 | 608.2229 | 432.8865 | 148.3681 | 111.0604
609.2229 | 265.2229 | 148.8361 | 111.4444 | 432.9221 | 609.2229 | 432.9221 | 148.8361 | 111.4444
610.2229 | 266.2229 | 149.3082 | 111.8196 | 432.7959 | 610.2229 | 432.7959 | 149.3082 | 111.8196
611.2229 | 267.2229 | 149.7904 | 112.2038 | 432.7034 | 611.2229 | 432.7034 | 149.7904 | 112.2038
612.2229 | 268.2229 | 150.255 | 112.583 | 432.5627 | 612.2229 | 432.5627 | 150.255 | 112.583
613.2229 | 269.2229 | 150.7179 | 112.9711 | 432.373 | 613.2229 | 432.373 | 150.7179 | 112.9711
614.2229 | 270.2229 | 151.183 | 113.351 | 432.3669 | 614.2229 | 432.3669 | 151.183 | 113.351
615.2229 | 271.2229 | 151.6458 | 113.7382 | 432.4029 | 615.2229 | 432.4029 | 151.6458 | 113.7382
616.2229 | 272.2229 | 152.1042 | 114.1429 | 432.413 | 616.2229 | 432.413 | 152.1042 | 114.1429
617.2229 | 273.2229 | 152.5643 | 114.5231 | 432.4918 | 617.2229 | 432.4918 | 152.5643 | 114.5231
618.2229 | 274.2229 | 153.0254 | 114.9175 | 432.3906 | 618.2229 | 432.3906 | 153.0254 | 114.9175
619.2229 | 275.2229 | 153.4717 | 115.3216 | 432.4639 | 619.2229 | 432.4639 | 153.4717 | 115.3216
620.2229 | 276.2229 | 153.9401 | 115.722 | 432.5365 | 620.2229 | 432.5365 | 153.9401 | 115.722
621.2229 | 277.2229 | 154.3906 | 116.1324 | 432.5248 | 621.2229 | 432.5248 | 154.3906 | 116.1324
622.2229 | 278.2229 | 154.8316 | 116.5315 | 432.5834 | 622.2229 | 432.5834 | 154.8316 | 116.5315
623.2229 | 279.2229 | 155.2962 | 116.9439 | 432.6127 | 623.2229 | 432.6127 | 155.2962 | 116.9439
624.2229 | 280.2229 | 155.746 | 117.3569 | 432.5984 | 624.2229 | 432.5984 | 155.746 | 117.3569
625.2229 | 281.2229 | 156.1957 | 117.7759 | 432.3345 | 625.2229 | 432.3345 | 156.1957 | 117.7759
626.2229 | 282.2229 | 156.6431 | 118.1893 | 432.2918 | 626.2229 | 432.2918 | 156.6431 | 118.1893
627.2229 | 283.2229 | 157.1031 | 118.6199 | 432.3606 | 627.2229 | 432.3606 | 157.1031 | 118.6199
628.2229 | 284.2229 | 157.5504 | 119.0457 | 432.2421 | 628.2229 | 432.2421 | 157.5504 | 119.0457
629.2229 | 285.2229 | 157.9892 | 119.4728 | 432.2626 | 629.2229 | 432.2626 | 157.9892 | 119.4728
630.2229 | 286.2229 | 158.4359 | 119.8995 | 432.2983 | 630.2229 | 432.2983 | 158.4359 | 119.8995
631.2229 | 287.2229 | 158.882 | 120.3404 | 432.2442 | 631.2229 | 432.2442 | 158.882 | 120.3404
632.2229 | 288.2229 | 159.3397 | 120.8038 | 432.2154 | 632.2229 | 432.2154 | 159.3397 | 120.8038
633.2229 | 289.2229 | 159.7779 | 121.2431 | 432.1197 | 633.2229 | 432.1197 | 159.7779 | 121.2431
634.2229 | 290.2229 | 160.2158 | 121.6962 | 432.0425 | 634.2229 | 432.0425 | 160.2158 | 121.6962
635.2229 | 291.2229 | 160.6668 | 122.136 | 432.0617 | 635.2229 | 432.0617 | 160.6668 | 122.136
636.2229 | 292.2229 | 161.0968 | 122.5954 | 431.9462 | 636.2229 | 431.9462 | 161.0968 | 122.5954
637.2229 | 293.2229 | 161.5481 | 123.0534 | 431.9529 | 637.2229 | 431.9529 | 161.5481 | 123.0534
638.2229 | 294.2229 | 161.9806 | 123.5092 | 432.1378 | 638.2229 | 432.1378 | 161.9806 | 123.5092
639.2229 | 295.2229 | 162.4179 | 123.967 | 432.3655 | 639.2229 | 432.3655 | 162.4179 | 123.967
640.2229 | 296.2229 | 162.8529 | 124.4359 | 432.4284 | 640.2229 | 432.4284 | 162.8529 | 124.4359
641.2229 | 297.2229 | 163.2788 | 124.8977 | 432.5844 | 641.2229 | 432.5844 | 163.2788 | 124.8977
642.2229 | 298.2229 | 163.7128 | 125.3641 | 432.5769 | 642.2229 | 432.5769 | 163.7128 | 125.3641
643.2229 | 299.2229 | 164.1437 | 125.8291 | 432.4314 | 643.2229 | 432.4314 | 164.1437 | 125.8291
644.2229 | 300.2229 | 164.5749 | 126.2943 | 432.4309 | 644.2229 | 432.4309 | 164.5749 | 126.2943
645.2229 | 301.2229 | 165.0077 | 126.7627 | 432.3602 | 645.2229 | 432.3602 | 165.0077 | 126.7627
646.2229 | 302.2229 | 165.4376 | 127.2301 | 432.3585 | 646.2229 | 432.3585 | 165.4376 | 127.2301
647.2229 | 303.2229 | 165.8546 | 127.7019 | 432.12 | 647.2229 | 432.12 | 165.8546 | 127.7019
648.2229 | 304.2229 | 166.2783 | 128.1668 | 432.0088 | 648.2229 | 432.0088 | 166.2783 | 128.1668
649.2229 | 305.2229 | 166.7167 | 128.6357 | 431.944 | 649.2229 | 431.944 | 166.7167 | 128.6357
650.2229 | 306.2229 | 167.129 | 129.1147 | 432.013 | 650.2229 | 432.013 | 167.129 | 129.1147
651.2229 | 307.2229 | 167.5612 | 129.5832 | 432.1832 | 651.2229 | 432.1832 | 167.5612 | 129.5832
652.2229 | 308.2229 | 167.9851 | 130.0583 | 432.1896 | 652.2229 | 432.1896 | 167.9851 | 130.0583
653.2229 | 309.2229 | 168.4031 | 130.5368 | 432.2457 | 653.2229 | 432.2457 | 168.4031 | 130.5368
654.2229 | 310.2229 | 168.8291 | 131.0131 | 432.2575 | 654.2229 | 432.2575 | 168.8291 | 131.0131
655.2229 | 311.2229 | 169.2514 | 131.489 | 432.3024 | 655.2229 | 432.3024 | 169.2514 | 131.489
656.2229 | 312.2229 | 169.6675 | 131.9708 | 432.1806 | 656.2229 | 432.1806 | 169.6675 | 131.9708
657.2229 | 313.2229 | 170.0814 | 132.4457 | 432.1158 | 657.2229 | 432.1158 | 170.0814 | 132.4457
658.2229 | 314.2229 | 170.51 | 132.9238 | 432.0526 | 658.2229 | 432.0526 | 170.51 | 132.9238
659.2229 | 315.2229 | 170.9382 | 133.4023 | 431.9655 | 659.2229 | 431.9655 | 170.9382 | 133.4023
660.2229 | 316.2229 | 171.3566 | 133.8839 | 431.9358 | 660.2229 | 431.9358 | 171.3566 | 133.8839
661.2229 | 317.2229 | 171.7722 | 134.3622 | 431.9074 | 661.2229 | 431.9074 | 171.7722 | 134.3622
662.2229 | 318.2229 | 172.1706 | 134.8483 | 431.9349 | 662.2229 | 431.9349 | 172.1706 | 134.8483
663.2229 | 319.2229 | 172.6177 | 135.3292 | 431.9639 | 663.2229 | 431.9639 | 172.6177 | 135.3292
664.2229 | 320.2229 | 173.0168 | 135.8145 | 431.9796 | 664.2229 | 431.9796 | 173.0168 | 135.8145
665.2229 | 321.2229 | 173.4291 | 136.3034 | 431.8061 | 665.2229 | 431.8061 | 173.4291 | 136.3034
666.2229 | 322.2229 | 173.8562 | 136.801 | 431.7702 | 666.2229 | 431.7702 | 173.8562 | 136.801
667.2229 | 323.2229 | 174.2516 | 137.2985 | 431.6973 | 667.2229 | 431.6973 | 174.2516 | 137.2985
668.2229 | 324.2229 | 174.6747 | 137.7917 | 431.7033 | 668.2229 | 431.7033 | 174.6747 | 137.7917
669.2229 | 325.2229 | 175.0751 | 138.3043 | 431.6933 | 669.2229 | 431.6933 | 175.0751 | 138.3043
670.2229 | 326.2229 | 175.4797 | 138.8087 | 431.6648 | 670.2229 | 431.6648 | 175.4797 | 138.8087
671.2229 | 327.2229 | 175.902 | 139.3177 | 431.6177 | 671.2229 | 431.6177 | 175.902 | 139.3177
672.2229 | 328.2229 | 176.3006 | 139.8512 | 431.5599 | 672.2229 | 431.5599 | 176.3006 | 139.8512
673.2229 | 329.2229 | 176.7268 | 140.3721 | 431.5445 | 673.2229 | 431.5445 | 176.7268 | 140.3721
674.2229 | 330.2229 | 177.1237 | 140.9051 | 431.3019 | 674.2229 | 431.3019 | 177.1237 | 140.9051
675.2229 | 331.2229 | 177.515 | 141.442 | 431.2491 | 675.2229 | 431.2491 | 177.515 | 141.442
676.2229 | 332.2229 | 177.9369 | 141.9873 | 431.1536 | 676.2229 | 431.1536 | 177.9369 | 141.9873
677.2229 | 333.2229 | 178.3572 | 142.5366 | 431.1513 | 677.2229 | 431.1513 | 178.3572 | 142.5366
678.2229 | 334.2229 | 178.7604 | 143.1021 | 431.1046 | 678.2229 | 431.1046 | 178.7604 | 143.1021
679.2229 | 335.2229 | 179.1572 | 143.6608 | 431.017 | 679.2229 | 431.017 | 179.1572 | 143.6608
680.2229 | 336.2229 | 179.5763 | 144.2289 | 431.111 | 680.2229 | 431.111 | 179.5763 | 144.2289
681.2229 | 337.2229 | 179.9771 | 144.8011 | 431.0907 | 681.2229 | 431.0907 | 179.9771 | 144.8011
682.2229 | 338.2229 | 180.3702 | 145.3852 | 431.0242 | 682.2229 | 431.0242 | 180.3702 | 145.3852
683.2229 | 339.2229 | 180.7766 | 145.9647 | 430.9254 | 683.2229 | 430.9254 | 180.7766 | 145.9647
684.2229 | 340.2229 | 181.1749 | 146.5488 | 430.942 | 684.2229 | 430.942 | 181.1749 | 146.5488
685.2229 | 341.2229 | 181.5734 | 147.1252 | 430.8129 | 685.2229 | 430.8129 | 181.5734 | 147.1252
686.2229 | 342.2229 | 181.9856 | 147.7058 | 430.743 | 686.2229 | 430.743 | 181.9856 | 147.7058
687.2229 | 343.2229 | 182.3777 | 148.2933 | 430.6802 | 687.2229 | 430.6802 | 182.3777 | 148.2933
688.2229 | 344.2229 | 182.7777 | 148.8648 | 430.694 | 688.2229 | 430.694 | 182.7777 | 148.8648
689.2229 | 345.2229 | 183.1783 | 149.4568 | 430.6416 | 689.2229 | 430.6416 | 183.1783 | 149.4568
690.2229 | 346.2229 | 183.58 | 150.0424 | 430.7401 | 690.2229 | 430.7401 | 183.58 | 150.0424
691.2229 | 347.2229 | 183.9815 | 150.6232 | 430.8415 | 691.2229 | 430.8415 | 183.9815 | 150.6232
692.2229 | 348.2229 | 184.383 | 151.1979 | 430.9238 | 692.2229 | 430.9238 | 184.383 | 151.1979
693.2229 | 349.2229 | 184.7686 | 151.7668 | 430.9166 | 693.2229 | 430.9166 | 184.7686 | 151.7668
694.2229 | 350.2229 | 185.1648 | 152.3477 | 430.9218 | 694.2229 | 430.9218 | 185.1648 | 152.3477
695.2229 | 351.2229 | 185.5649 | 152.9105 | 430.8977 | 695.2229 | 430.8977 | 185.5649 | 152.9105
696.2229 | 352.2229 | 185.9619 | 153.4754 | 430.8696 | 696.2229 | 430.8696 | 185.9619 | 153.4754
697.2229 | 353.2229 | 186.3636 | 154.0393 | 430.8691 | 697.2229 | 430.8691 | 186.3636 | 154.0393
698.2229 | 354.2229 | 186.7627 | 154.5823 | 430.8581 | 698.2229 | 430.8581 | 186.7627 | 154.5823
699.2229 | 355.2229 | 187.1584 | 155.1304 | 430.9128 | 699.2229 | 430.9128 | 187.1584 | 155.1304
700.301 | 356.301 | 187.5923 | 155.7182 | 430.8119 | 700.301 | 430.8119 | 187.5923 | 155.7182
701.2229 | 357.2229 | 187.9613 | 156.2225 | 430.6854 | 701.2229 | 430.6854 | 187.9613 | 156.2225
702.2229 | 358.2229 | 188.356 | 156.7495 | 430.6113 | 702.2229 | 430.6113 | 188.356 | 156.7495
703.2229 | 359.2229 | 188.7685 | 157.2859 | 430.5802 | 703.2229 | 430.5802 | 188.7685 | 157.2859
704.2229 | 360.2229 | 189.1639 | 157.8246 | 430.6566 | 704.2229 | 430.6566 | 189.1639 | 157.8246
705.2229 | 361.2229 | 189.5644 | 158.3431 | 430.7196 | 705.2229 | 430.7196 | 189.5644 | 158.3431
706.2229 | 362.2229 | 189.9633 | 158.8642 | 430.667 | 706.2229 | 430.667 | 189.9633 | 158.8642
707.2229 | 363.2229 | 190.375 | 159.3916 | 430.6269 | 707.2229 | 430.6269 | 190.375 | 159.3916
708.2229 | 364.2229 | 190.7671 | 159.9044 | 430.7053 | 708.2229 | 430.7053 | 190.7671 | 159.9044
709.2229 | 365.2229 | 191.1717 | 160.4103 | 430.6172 | 709.2229 | 430.6172 | 191.1717 | 160.4103
710.2229 | 366.2229 | 191.5716 | 160.9191 | 430.5362 | 710.2229 | 430.5362 | 191.5716 | 160.9191
711.2229 | 367.2229 | 191.9691 | 161.4278 | 430.4658 | 711.2229 | 430.4658 | 191.9691 | 161.4278
712.2229 | 368.2229 | 192.3767 | 161.929 | 430.3672 | 712.2229 | 430.3672 | 192.3767 | 161.929
713.2229 | 369.2229 | 192.779 | 162.4257 | 430.3202 | 713.2229 | 430.3202 | 192.779 | 162.4257
714.2229 | 370.2229 | 193.1519 | 162.9149 | 430.3545 | 714.2229 | 430.3545 | 193.1519 | 162.9149
715.2229 | 371.2229 | 193.5677 | 163.4065 | 430.4093 | 715.2229 | 430.4093 | 193.5677 | 163.4065
716.2229 | 372.2229 | 193.9764 | 163.9039 | 430.4214 | 716.2229 | 430.4214 | 193.9764 | 163.9039
717.2229 | 373.2229 | 194.3635 | 164.3899 | 430.3261 | 717.2229 | 430.3261 | 194.3635 | 164.3899
718.2229 | 374.2229 | 194.7492 | 164.8999 | 430.2646 | 718.2229 | 430.2646 | 194.7492 | 164.8999
719.2229 | 375.2229 | 195.1502 | 165.4154 | 430.2131 | 719.2229 | 430.2131 | 195.1502 | 165.4154
720.2229 | 376.2229 | 195.5446 | 165.9398 | 430.1168 | 720.2229 | 430.1168 | 195.5446 | 165.9398
721.2229 | 377.2229 | 195.9408 | 166.4546 | 430.1422 | 721.2229 | 430.1422 | 195.9408 | 166.4546
722.2229 | 378.2229 | 196.3149 | 166.9588 | 430.2369 | 722.2229 | 430.2369 | 196.3149 | 166.9588
723.2229 | 379.2229 | 196.7277 | 167.4606 | 430.3828 | 723.2229 | 430.3828 | 196.7277 | 167.4606
724.2229 | 380.2229 | 197.107 | 167.9385 | 430.3395 | 724.2229 | 430.3395 | 197.107 | 167.9385
725.2229 | 381.2229 | 197.4977 | 168.406 | 430.236 | 725.2229 | 430.236 | 197.4977 | 168.406
726.2229 | 382.2229 | 197.8795 | 168.858 | 430.2247 | 726.2229 | 430.2247 | 197.8795 | 168.858
727.2229 | 383.2229 | 198.2652 | 169.3063 | 430.1965 | 727.2229 | 430.1965 | 198.2652 | 169.3063
728.2229 | 384.2229 | 198.6375 | 169.7172 | 430.3509 | 728.2229 | 430.3509 | 198.6375 | 169.7172
729.2229 | 385.2229 | 199.0126 | 170.1171 | 430.5095 | 729.2229 | 430.5095 | 199.0126 | 170.1171
730.2229 | 386.2229 | 199.371 | 170.4919 | 430.4842 | 730.2229 | 430.4842 | 199.371 | 170.4919
731.2229 | 387.2229 | 199.7567 | 170.8572 | 430.4689 | 731.2229 | 430.4689 | 199.7567 | 170.8572
732.2229 | 388.2229 | 200.1177 | 171.2053 | 430.6077 | 732.2229 | 430.6077 | 200.1177 | 171.2053
733.2229 | 389.2229 | 200.4805 | 171.5414 | 430.7036 | 733.2229 | 430.7036 | 200.4805 | 171.5414
734.2229 | 390.2229 | 200.8483 | 171.86 | 430.7725 | 734.2229 | 430.7725 | 200.8483 | 171.86
735.2229 | 391.2229 | 201.1809 | 172.1688 | 430.8587 | 735.2229 | 430.8587 | 201.1809 | 172.1688
736.2229 | 392.2229 | 201.5475 | 172.4662 | 430.9462 | 736.2229 | 430.9462 | 201.5475 | 172.4662
737.2229 | 393.2229 | 201.9151 | 172.7488 | 430.9155 | 737.2229 | 430.9155 | 201.9151 | 172.7488
738.2229 | 394.2229 | 202.2537 | 173.0228 | 430.6908 | 738.2229 | 430.6908 | 202.2537 | 173.0228
739.2229 | 395.2229 | 202.6006 | 173.288 | 430.7846 | 739.2229 | 430.7846 | 202.6006 | 173.288
740.2229 | 396.2229 | 202.9371 | 173.5463 | 430.7888 | 740.2229 | 430.7888 | 202.9371 | 173.5463
741.2229 | 397.2229 | 203.2808 | 173.8109 | 430.8408 | 741.2229 | 430.8408 | 203.2808 | 173.8109
742.2385 | 398.2385 | 203.6156 | 174.0462 | 430.7756 | 742.2385 | 430.7756 | 203.6156 | 174.0462
743.2698 | 399.2698 | 203.9477 | 174.3038 | 430.7318 | 743.2698 | 430.7318 | 203.9477 | 174.3038
744.2229 | 400.2229 | 204.2505 | 174.5356 | 430.7266 | 744.2229 | 430.7266 | 204.2505 | 174.5356
745.3167 | 401.3167 | 204.6059 | 174.796 | 430.6284 | 745.3167 | 430.6284 | 204.6059 | 174.796
746.2854 | 402.2854 | 204.8729 | 175.0192 | 430.7197 | 746.2854 | 430.7197 | 204.8729 | 175.0192
747.2385 | 403.2385 | 205.185 | 175.2335 | 430.6545 | 747.2385 | 430.6545 | 205.185 | 175.2335
748.2385 | 404.2385 | 205.4855 | 175.4671 | 430.5257 | 748.2385 | 430.5257 | 205.4855 | 175.4671
749.2229 | 405.2229 | 205.7591 | 175.6993 | 430.5171 | 749.2229 | 430.5171 | 205.7591 | 175.6993
750.2229 | 406.2229 | 206.0724 | 175.9289 | 430.5284 | 750.2229 | 430.5284 | 206.0724 | 175.9289
751.2229 | 407.2229 | 206.3784 | 176.1484 | 430.5869 | 751.2229 | 430.5869 | 206.3784 | 176.1484
752.2229 | 408.2229 | 206.6892 | 176.3777 | 430.6141 | 752.2229 | 430.6141 | 206.6892 | 176.3777
753.2229 | 409.2229 | 206.9731 | 176.6048 | 430.5848 | 753.2229 | 430.5848 | 206.9731 | 176.6048
754.2229 | 410.2229 | 207.2738 | 176.8344 | 430.4606 | 754.2229 | 430.4606 | 207.2738 | 176.8344
755.2229 | 411.2229 | 207.5506 | 177.0643 | 430.4247 | 755.2229 | 430.4247 | 207.5506 | 177.0643
756.2229 | 412.2229 | 207.8199 | 177.2892 | 430.5225 | 756.2229 | 430.5225 | 207.8199 | 177.2892
757.2385 | 413.2385 | 208.0878 | 177.5127 | 430.6166 | 757.2385 | 430.6166 | 208.0878 | 177.5127
758.2385 | 414.2385 | 208.3124 | 177.7418 | 430.6532 | 758.2385 | 430.6532 | 208.3124 | 177.7418
759.2229 | 415.2229 | 208.6672 | 177.9624 | 430.5412 | 759.2229 | 430.5412 | 208.6672 | 177.9624
760.3167 | 416.3167 | 208.8218 | 178.2091 | 430.5134 | 760.3167 | 430.5134 | 208.8218 | 178.2091
761.2542 | 417.2542 | 208.8548 | 178.4246 | 430.4624 | 761.2542 | 430.4624 | 208.8548 | 178.4246
762.2229 | 418.2229 | 208.8508 | 178.6435 | 430.4032 | 762.2229 | 430.4032 | 208.8508 | 178.6435
763.2229 | 419.2229 | 208.8216 | 178.8833 | 430.4836 | 763.2229 | 430.4836 | 208.8216 | 178.8833
764.2229 | 420.2229 | 208.7824 | 179.1094 | 430.4501 | 764.2229 | 430.4501 | 208.7824 | 179.1094
765.426 | 421.426 | 208.7505 | 179.3854 | 430.4275 | 765.426 | 430.4275 | 208.7505 | 179.3854
766.2854 | 422.2854 | 208.7459 | 179.5908 | 430.4006 | 766.2854 | 430.4006 | 208.7459 | 179.5908
767.2229 | 423.2229 | 208.7399 | 179.8125 | 430.3923 | 767.2229 | 430.3923 | 208.7399 | 179.8125
768.2229 | 424.2229 | 208.7515 | 180.0437 | 430.329 | 768.2229 | 430.329 | 208.7515 | 180.0437
769.2229 | 425.2229 | 208.776 | 180.2736 | 430.4047 | 769.2229 | 430.4047 | 208.776 | 180.2736
770.2229 | 426.2229 | 208.809 | 180.4957 | 430.4816 | 770.2229 | 430.4816 | 208.809 | 180.4957
771.2229 | 427.2229 | 208.8477 | 180.7288 | 430.4256 | 771.2229 | 430.4256 | 208.8477 | 180.7288
772.2229 | 428.2229 | 208.9058 | 180.9579 | 430.3954 | 772.2229 | 430.3954 | 208.9058 | 180.9579
773.2698 | 429.2698 | 208.9814 | 181.1915 | 430.4656 | 773.2698 | 430.4656 | 208.9814 | 181.1915
774.2854 | 430.2854 | 209.0439 | 181.4305 | 430.5921 | 774.2854 | 430.5921 | 209.0439 | 181.4305
775.2385 | 431.2385 | 209.1391 | 181.6578 | 430.6909 | 775.2385 | 430.6909 | 209.1391 | 181.6578
776.2385 | 432.2385 | 209.2342 | 181.8873 | 430.7637 | 776.2385 | 430.7637 | 209.2342 | 181.8873
777.2229 | 433.2229 | 209.3278 | 182.1237 | 430.7853 | 777.2229 | 430.7853 | 209.3278 | 182.1237
778.2229 | 434.2229 | 209.4344 | 182.3604 | 430.7023 | 778.2229 | 430.7023 | 209.4344 | 182.3604
779.2229 | 435.2229 | 209.5427 | 182.6032 | 430.653 | 779.2229 | 430.653 | 209.5427 | 182.6032
780.2229 | 436.2229 | 209.6755 | 182.8321 | 430.6636 | 780.2229 | 430.6636 | 209.6755 | 182.8321
781.2229 | 437.2229 | 209.7959 | 183.0722 | 430.7112 | 781.2229 | 430.7112 | 209.7959 | 183.0722
782.2229 | 438.2229 | 209.9039 | 183.3157 | 430.7314 | 782.2229 | 430.7314 | 209.9039 | 183.3157
783.2229 | 439.2229 | 210.0486 | 183.5573 | 430.6859 | 783.2229 | 430.6859 | 210.0486 | 183.5573
784.2385 | 440.2385 | 210.1978 | 183.7986 | 430.5175 | 784.2385 | 430.5175 | 210.1978 | 183.7986
785.2229 | 441.2229 | 210.3373 | 184.0391 | 430.4704 | 785.2229 | 430.4704 | 210.3373 | 184.0391
786.2229 | 442.2229 | 210.4896 | 184.2864 | 430.4462 | 786.2229 | 430.4462 | 210.4896 | 184.2864
787.2229 | 443.2229 | 210.64 | 184.5287 | 430.4916 | 787.2229 | 430.4916 | 210.64 | 184.5287
788.2229 | 444.2229 | 210.799 | 184.7682 | 430.6665 | 788.2229 | 430.6665 | 210.799 | 184.7682
789.2229 | 445.2229 | 210.9336 | 185.0111 | 430.7201 | 789.2229 | 430.7201 | 210.9336 | 185.0111
790.2229 | 446.2229 | 211.0777 | 185.2644 | 430.7927 | 790.2229 | 430.7927 | 211.0777 | 185.2644
791.2229 | 447.2229 | 211.2609 | 185.511 | 430.7327 | 791.2229 | 430.7327 | 211.2609 | 185.511
792.2229 | 448.2229 | 211.4125 | 185.7631 | 430.752 | 792.2229 | 430.752 | 211.4125 | 185.7631
793.2229 | 449.2229 | 211.5904 | 186.0085 | 430.6728 | 793.2229 | 430.6728 | 211.5904 | 186.0085
794.2229 | 450.2229 | 211.7329 | 186.2683 | 430.5112 | 794.2229 | 430.5112 | 211.7329 | 186.2683
795.2229 | 451.2229 | 211.9121 | 186.52 | 430.4613 | 795.2229 | 430.4613 | 211.9121 | 186.52
796.2229 | 452.2229 | 212.0887 | 186.7659 | 430.3375 | 796.2229 | 430.3375 | 212.0887 | 186.7659
797.2229 | 453.2229 | 212.2581 | 187.0214 | 430.3006 | 797.2229 | 430.3006 | 212.2581 | 187.0214
798.2229 | 454.2229 | 212.4167 | 187.2704 | 430.4233 | 798.2229 | 430.4233 | 212.4167 | 187.2704
799.2229 | 455.2229 | 212.5976 | 187.5267 | 430.4534 | 799.2229 | 430.4534 | 212.5976 | 187.5267
800.2229 | 456.2229 | 212.7638 | 187.7864 | 430.5351 | 800.2229 | 430.5351 | 212.7638 | 187.7864
801.2229 | 457.2229 | 212.9386 | 188.0439 | 430.5148 | 801.2229 | 430.5148 | 212.9386 | 188.0439
802.2229 | 458.2229 | 213.1022 | 188.2994 | 430.5671 | 802.2229 | 430.5671 | 213.1022 | 188.2994
803.2229 | 459.2229 | 213.2935 | 188.5697 | 430.5726 | 803.2229 | 430.5726 | 213.2935 | 188.5697
804.2229 | 460.2229 | 213.4676 | 188.829 | 430.5181 | 804.2229 | 430.5181 | 213.4676 | 188.829
805.2229 | 461.2229 | 213.6421 | 189.0885 | 430.4205 | 805.2229 | 430.4205 | 213.6421 | 189.0885
806.2229 | 462.2229 | 213.8363 | 189.3477 | 430.5083 | 806.2229 | 430.5083 | 213.8363 | 189.3477
807.2229 | 463.2229 | 214.0158 | 189.6112 | 430.6071 | 807.2229 | 430.6071 | 214.0158 | 189.6112
808.2229 | 464.2229 | 214.2111 | 189.8677 | 430.7785 | 808.2229 | 430.7785 | 214.2111 | 189.8677
809.2229 | 465.2229 | 214.3857 | 190.1347 | 430.8278 | 809.2229 | 430.8278 | 214.3857 | 190.1347
810.2229 | 466.2229 | 214.5722 | 190.3952 | 430.6963 | 810.2229 | 430.6963 | 214.5722 | 190.3952
811.2229 | 467.2229 | 214.7526 | 190.6549 | 430.5056 | 811.2229 | 430.5056 | 214.7526 | 190.6549
812.2229 | 468.2229 | 214.9413 | 190.9232 | 430.4606 | 812.2229 | 430.4606 | 214.9413 | 190.9232
813.2229 | 469.2229 | 215.1241 | 191.1809 | 430.4624 | 813.2229 | 430.4624 | 215.1241 | 191.1809
814.2229 | 470.2229 | 215.3246 | 191.4512 | 430.4204 | 814.2229 | 430.4204 | 215.3246 | 191.4512
815.2229 | 471.2229 | 215.5101 | 191.7224 | 430.3826 | 815.2229 | 430.3826 | 215.5101 | 191.7224
816.2229 | 472.2229 | 215.7102 | 191.9888 | 430.3871 | 816.2229 | 430.3871 | 215.7102 | 191.9888
817.2229 | 473.2229 | 215.9108 | 192.2578 | 430.3551 | 817.2229 | 430.3551 | 215.9108 | 192.2578
818.2229 | 474.2229 | 216.1091 | 192.5172 | 430.3185 | 818.2229 | 430.3185 | 216.1091 | 192.5172
819.2229 | 475.2229 | 216.3278 | 192.7911 | 430.3796 | 819.2229 | 430.3796 | 216.3278 | 192.7911
820.2229 | 476.2229 | 216.5308 | 193.0661 | 430.3282 | 820.2229 | 430.3282 | 216.5308 | 193.0661
821.2229 | 477.2229 | 216.7474 | 193.3357 | 430.2909 | 821.2229 | 430.2909 | 216.7474 | 193.3357
822.2229 | 478.2229 | 216.952 | 193.6098 | 430.2274 | 822.2229 | 430.2274 | 216.952 | 193.6098
823.2229 | 479.2229 | 217.182 | 193.8743 | 430.0993 | 823.2229 | 430.0993 | 217.182 | 193.8743
824.2229 | 480.2229 | 217.3968 | 194.1515 | 430.2119 | 824.2229 | 430.2119 | 217.3968 | 194.1515
825.2229 | 481.2229 | 217.6158 | 194.4161 | 430.3133 | 825.2229 | 430.3133 | 217.6158 | 194.4161
826.2229 | 482.2229 | 217.832 | 194.6918 | 430.1665 | 826.2229 | 430.1665 | 217.832 | 194.6918
827.2229 | 483.2229 | 218.0664 | 194.9601 | 430.0689 | 827.2229 | 430.0689 | 218.0664 | 194.9601
828.2229 | 484.2229 | 218.2739 | 195.2338 | 429.9285 | 828.2229 | 429.9285 | 218.2739 | 195.2338
829.2229 | 485.2229 | 218.4844 | 195.5137 | 429.8908 | 829.2229 | 429.8908 | 218.4844 | 195.5137
830.2229 | 486.2229 | 218.7114 | 195.7837 | 429.826 | 830.2229 | 429.826 | 218.7114 | 195.7837
831.2229 | 487.2229 | 218.9225 | 196.0538 | 429.8513 | 831.2229 | 429.8513 | 218.9225 | 196.0538
832.2229 | 488.2229 | 219.1328 | 196.333 | 429.9123 | 832.2229 | 429.9123 | 219.1328 | 196.333
833.2229 | 489.2229 | 219.3539 | 196.6064 | 429.9389 | 833.2229 | 429.9389 | 219.3539 | 196.6064
834.2229 | 490.2229 | 219.5472 | 196.8729 | 429.9361 | 834.2229 | 429.9361 | 219.5472 | 196.8729
835.2229 | 491.2229 | 219.7422 | 197.149 | 429.9366 | 835.2229 | 429.9366 | 219.7422 | 197.149
836.2229 | 492.2229 | 219.9491 | 197.4204 | 429.8589 | 836.2229 | 429.8589 | 219.9491 | 197.4204
837.2229 | 493.2229 | 220.1159 | 197.6921 | 429.7654 | 837.2229 | 429.7654 | 220.1159 | 197.6921
838.2229 | 494.2229 | 220.2899 | 197.9729 | 429.7571 | 838.2229 | 429.7571 | 220.2899 | 197.9729
839.2229 | 495.2229 | 220.4605 | 198.2491 | 429.7418 | 839.2229 | 429.7418 | 220.4605 | 198.2491
840.2229 | 496.2229 | 220.6334 | 198.537 | 429.6905 | 840.2229 | 429.6905 | 220.6334 | 198.537
841.2229 | 497.2229 | 220.7981 | 198.8146 | 429.6674 | 841.2229 | 429.6674 | 220.7981 | 198.8146
842.2229 | 498.2229 | 220.9604 | 199.0906 | 429.5557 | 842.2229 | 429.5557 | 220.9604 | 199.0906
843.2229 | 499.2229 | 221.1087 | 199.3594 | 429.4675 | 843.2229 | 429.4675 | 221.1087 | 199.3594
844.2229 | 500.2229 | 221.2694 | 199.6316 | 429.4861 | 844.2229 | 429.4861 | 221.2694 | 199.6316
845.2229 | 501.2229 | 221.4354 | 199.9103 | 429.5533 | 845.2229 | 429.5533 | 221.4354 | 199.9103
846.2229 | 502.2229 | 221.5943 | 200.181 | 429.5575 | 846.2229 | 429.5575 | 221.5943 | 200.181
847.2229 | 503.2229 | 221.744 | 200.4613 | 429.6166 | 847.2229 | 429.6166 | 221.744 | 200.4613
848.2229 | 504.2229 | 221.904 | 200.7304 | 429.6345 | 848.2229 | 429.6345 | 221.904 | 200.7304
849.2229 | 505.2229 | 222.0618 | 201.0073 | 429.6931 | 849.2229 | 429.6931 | 222.0618 | 201.0073
850.2229 | 506.2229 | 222.2317 | 201.2721 | 429.7537 | 850.2229 | 429.7537 | 222.2317 | 201.2721
851.2229 | 507.2229 | 222.3896 | 201.5492 | 429.7444 | 851.2229 | 429.7444 | 222.3896 | 201.5492
852.2229 | 508.2229 | 222.5567 | 201.8169 | 429.7814 | 852.2229 | 429.7814 | 222.5567 | 201.8169
853.2229 | 509.2229 | 222.7233 | 202.0946 | 429.7968 | 853.2229 | 429.7968 | 222.7233 | 202.0946
854.2229 | 510.2229 | 222.8908 | 202.371 | 429.8344 | 854.2229 | 429.8344 | 222.8908 | 202.371
855.2229 | 511.2229 | 223.064 | 202.6309 | 429.9429 | 855.2229 | 429.9429 | 223.064 | 202.6309
856.2229 | 512.2229 | 223.2295 | 202.9029 | 430.0423 | 856.2229 | 430.0423 | 223.2295 | 202.9029
857.2229 | 513.2229 | 223.4073 | 203.1679 | 429.969 | 857.2229 | 429.969 | 223.4073 | 203.1679
858.2229 | 514.2229 | 223.593 | 203.4322 | 429.8861 | 858.2229 | 429.8861 | 223.593 | 203.4322
859.2229 | 515.2229 | 223.7666 | 203.7042 | 429.7855 | 859.2229 | 429.7855 | 223.7666 | 203.7042
860.2385 | 516.2385 | 223.9452 | 203.9669 | 429.8222 | 860.2385 | 429.8222 | 223.9452 | 203.9669
861.301 | 517.301 | 224.1528 | 204.2586 | 429.8182 | 861.301 | 429.8182 | 224.1528 | 204.2586
862.3167 | 518.3167 | 224.3353 | 204.52 | 429.8497 | 862.3167 | 429.8497 | 224.3353 | 204.52
863.2698 | 519.2698 | 224.5211 | 204.7719 | 429.8167 | 863.2698 | 429.8167 | 224.5211 | 204.7719
864.2542 | 520.2542 | 224.707 | 205.0253 | 429.7872 | 864.2542 | 429.7872 | 224.707 | 205.0253
865.2229 | 521.2229 | 224.9005 | 205.2747 | 429.858 | 865.2229 | 429.858 | 224.9005 | 205.2747
866.2229 | 522.2229 | 225.1003 | 205.5377 | 429.6758 | 866.2229 | 429.6758 | 225.1003 | 205.5377
867.2385 | 523.2385 | 225.2813 | 205.7984 | 429.7695 | 867.2385 | 429.7695 | 225.2813 | 205.7984
868.2229 | 524.2229 | 225.47 | 206.0506 | 429.7232 | 868.2229 | 429.7232 | 225.47 | 206.0506
869.2229 | 525.2229 | 225.6748 | 206.3106 | 429.7309 | 869.2229 | 429.7309 | 225.6748 | 206.3106
870.2229 | 526.2229 | 225.8567 | 206.5607 | 429.8763 | 870.2229 | 429.8763 | 225.8567 | 206.5607
871.2229 | 527.2229 | 226.0642 | 206.8127 | 429.956 | 871.2229 | 429.956 | 226.0642 | 206.8127
872.2229 | 528.2229 | 226.2511 | 207.0691 | 430.0213 | 872.2229 | 430.0213 | 226.2511 | 207.0691
873.2229 | 529.2229 | 226.4469 | 207.3134 | 429.9859 | 873.2229 | 429.9859 | 226.4469 | 207.3134
874.2229 | 530.2229 | 226.6479 | 207.5593 | 430.0581 | 874.2229 | 430.0581 | 226.6479 | 207.5593
875.2229 | 531.2229 | 226.8526 | 207.804 | 430.0495 | 875.2229 | 430.0495 | 226.8526 | 207.804
876.2229 | 532.2229 | 227.0436 | 208.0531 | 430.0579 | 876.2229 | 430.0579 | 227.0436 | 208.0531
877.2229 | 533.2229 | 227.2537 | 208.3003 | 430.0558 | 877.2229 | 430.0558 | 227.2537 | 208.3003
878.2229 | 534.2229 | 227.457 | 208.5426 | 430.0515 | 878.2229 | 430.0515 | 227.457 | 208.5426
879.2229 | 535.2229 | 227.6742 | 208.7982 | 429.9739 | 879.2229 | 429.9739 | 227.6742 | 208.7982
880.2229 | 536.2229 | 227.8724 | 209.0471 | 430.0202 | 880.2229 | 430.0202 | 227.8724 | 209.0471
881.2229 | 537.2229 | 228.0864 | 209.293 | 429.9877 | 881.2229 | 429.9877 | 228.0864 | 209.293
882.2229 | 538.2229 | 228.2796 | 209.5364 | 429.9479 | 882.2229 | 429.9479 | 228.2796 | 209.5364
883.2229 | 539.2229 | 228.4829 | 209.7697 | 429.9861 | 883.2229 | 429.9861 | 228.4829 | 209.7697
884.2229 | 540.2229 | 228.6851 | 210.014 | 429.9581 | 884.2229 | 429.9581 | 228.6851 | 210.014
885.2229 | 541.2229 | 228.8921 | 210.2549 | 429.827 | 885.2229 | 429.827 | 228.8921 | 210.2549
886.2229 | 542.2229 | 229.0919 | 210.5006 | 429.8557 | 886.2229 | 429.8557 | 229.0919 | 210.5006
887.2229 | 543.2229 | 229.2949 | 210.7333 | 429.8872 | 887.2229 | 429.8872 | 229.2949 | 210.7333
888.2229 | 544.2229 | 229.4929 | 210.9751 | 429.6249 | 888.2229 | 429.6249 | 229.4929 | 210.9751
889.2229 | 545.2229 | 229.7022 | 211.2128 | 429.6401 | 889.2229 | 429.6401 | 229.7022 | 211.2128
890.2229 | 546.2229 | 229.9094 | 211.4389 | 429.7386 | 890.2229 | 429.7386 | 229.9094 | 211.4389
891.2229 | 547.2229 | 230.1111 | 211.6812 | 429.7194 | 891.2229 | 429.7194 | 230.1111 | 211.6812
892.2229 | 548.2229 | 230.3312 | 211.915 | 429.6135 | 892.2229 | 429.6135 | 230.3312 | 211.915
893.2229 | 549.2229 | 230.5419 | 212.1577 | 429.3808 | 893.2229 | 429.3808 | 230.5419 | 212.1577
894.2229 | 550.2229 | 230.7455 | 212.3792 | 429.3651 | 894.2229 | 429.3651 | 230.7455 | 212.3792
895.2229 | 551.2229 | 230.959 | 212.6254 | 429.3619 | 895.2229 | 429.3619 | 230.959 | 212.6254
896.2229 | 552.2229 | 231.1755 | 212.8548 | 429.3364 | 896.2229 | 429.3364 | 231.1755 | 212.8548
897.2229 | 553.2229 | 231.3982 | 213.0866 | 429.3019 | 897.2229 | 429.3019 | 231.3982 | 213.0866
898.2229 | 554.2229 | 231.627 | 213.312 | 429.2778 | 898.2229 | 429.2778 | 231.627 | 213.312
899.2229 | 555.2229 | 231.8555 | 213.5616 | 429.1766 | 899.2229 | 429.1766 | 231.8555 | 213.5616
900.2229 | 556.2229 | 232.1015 | 213.7939 | 429.0848 | 900.2229 | 429.0848 | 232.1015 | 213.7939
901.2229 | 557.2229 | 232.3298 | 214.0434 | 429.061 | 901.2229 | 429.061 | 232.3298 | 214.0434
902.2229 | 558.2229 | 232.5726 | 214.2836 | 429.1279 | 902.2229 | 429.1279 | 232.5726 | 214.2836
903.2229 | 559.2229 | 232.8313 | 214.528 | 429.1976 | 903.2229 | 429.1976 | 232.8313 | 214.528
904.2229 | 560.2229 | 233.0701 | 214.7693 | 429.1175 | 904.2229 | 429.1175 | 233.0701 | 214.7693
905.2229 | 561.2229 | 233.3344 | 215.0148 | 429.1442 | 905.2229 | 429.1442 | 233.3344 | 215.0148
906.2229 | 562.2229 | 233.5978 | 215.2637 | 429.2377 | 906.2229 | 429.2377 | 233.5978 | 215.2637
907.2229 | 563.2229 | 233.8804 | 215.5372 | 429.2874 | 907.2229 | 429.2874 | 233.8804 | 215.5372
908.2229 | 564.2229 | 234.1688 | 215.8694 | 429.2993 | 908.2229 | 429.2993 | 234.1688 | 215.8694
909.2229 | 565.2229 | 234.4494 | 216.189 | 429.3047 | 909.2229 | 429.3047 | 234.4494 | 216.189
910.2229 | 566.2229 | 234.7443 | 216.5281 | 429.2694 | 910.2229 | 429.2694 | 234.7443 | 216.5281
911.2229 | 567.2229 | 235.0188 | 216.8659 | 429.2411 | 911.2229 | 429.2411 | 235.0188 | 216.8659
912.2229 | 568.2229 | 235.3347 | 217.216 | 429.2716 | 912.2229 | 429.2716 | 235.3347 | 217.216
913.2229 | 569.2229 | 235.6268 | 217.5748 | 429.3772 | 913.2229 | 429.3772 | 235.6268 | 217.5748
914.2229 | 570.2229 | 235.934 | 217.9512 | 429.4377 | 914.2229 | 429.4377 | 235.934 | 217.9512
915.2229 | 571.2229 | 236.235 | 218.2971 | 429.4969 | 915.2229 | 429.4969 | 236.235 | 218.2971
916.2229 | 572.2229 | 236.5349 | 218.6491 | 429.5236 | 916.2229 | 429.5236 | 236.5349 | 218.6491
917.2229 | 573.2229 | 236.8324 | 219.0124 | 429.6094 | 917.2229 | 429.6094 | 236.8324 | 219.0124
918.2229 | 574.2229 | 237.1241 | 219.3803 | 429.6707 | 918.2229 | 429.6707 | 237.1241 | 219.3803
919.2229 | 575.2229 | 237.4171 | 219.7504 | 429.6564 | 919.2229 | 429.6564 | 237.4171 | 219.7504
920.2229 | 576.2229 | 237.6968 | 220.1253 | 429.6827 | 920.2229 | 429.6827 | 237.6968 | 220.1253
921.2229 | 577.2229 | 237.9891 | 220.5109 | 429.7025 | 921.2229 | 429.7025 | 237.9891 | 220.5109
922.2229 | 578.2229 | 238.2834 | 220.8946 | 429.5668 | 922.2229 | 429.5668 | 238.2834 | 220.8946
923.2229 | 579.2229 | 238.6193 | 221.2821 | 429.3954 | 923.2229 | 429.3954 | 238.6193 | 221.2821
924.2229 | 580.2229 | 238.9871 | 221.6717 | 429.4008 | 924.2229 | 429.4008 | 238.9871 | 221.6717
925.2229 | 581.2229 | 239.5291 | 222.0625 | 429.3708 | 925.2229 | 429.3708 | 239.5291 | 222.0625
926.2229 | 582.2229 | 240.1237 | 222.46 | 429.3366 | 926.2229 | 429.3366 | 240.1237 | 222.46
927.2229 | 583.2229 | 240.7627 | 222.8563 | 429.3173 | 927.2229 | 429.3173 | 240.7627 | 222.8563
928.2229 | 584.2229 | 241.4438 | 223.2453 | 429.2494 | 928.2229 | 429.2494 | 241.4438 | 223.2453
929.2229 | 585.2229 | 242.1413 | 223.6467 | 429.2826 | 929.2229 | 429.2826 | 242.1413 | 223.6467
930.2229 | 586.2229 | 242.8669 | 224.0704 | 429.2423 | 930.2229 | 429.2423 | 242.8669 | 224.0704
931.2229 | 587.2229 | 243.6 | 224.4903 | 429.0987 | 931.2229 | 429.0987 | 243.6 | 224.4903
932.2229 | 588.2229 | 244.3523 | 224.8999 | 429.1516 | 932.2229 | 429.1516 | 244.3523 | 224.8999
933.2229 | 589.2229 | 245.1146 | 225.3081 | 429.1408 | 933.2229 | 429.1408 | 245.1146 | 225.3081
934.2229 | 590.2229 | 245.8972 | 225.7264 | 429.0356 | 934.2229 | 429.0356 | 245.8972 | 225.7264
935.2229 | 591.2229 | 246.6925 | 226.1296 | 428.9794 | 935.2229 | 428.9794 | 246.6925 | 226.1296
936.2229 | 592.2229 | 247.4899 | 226.5508 | 429.0093 | 936.2229 | 429.0093 | 247.4899 | 226.5508
937.2229 | 593.2229 | 248.2817 | 226.9686 | 428.9823 | 937.2229 | 428.9823 | 248.2817 | 226.9686
938.2229 | 594.2229 | 249.0499 | 227.3745 | 428.9689 | 938.2229 | 428.9689 | 249.0499 | 227.3745
939.2229 | 595.2229 | 249.8405 | 227.8057 | 429.0204 | 939.2229 | 429.0204 | 249.8405 | 227.8057
940.2229 | 596.2229 | 250.6387 | 228.215 | 429.0718 | 940.2229 | 429.0718 | 250.6387 | 228.215
941.2229 | 597.2229 | 251.4279 | 228.6201 | 429.1212 | 941.2229 | 429.1212 | 251.4279 | 228.6201
942.2229 | 598.2229 | 252.2224 | 229.041 | 429.1071 | 942.2229 | 429.1071 | 252.2224 | 229.041
943.2229 | 599.2229 | 252.9974 | 229.4443 | 429.1456 | 943.2229 | 429.1456 | 252.9974 | 229.4443
944.2229 | 600.2229 | 253.784 | 229.8606 | 429.2256 | 944.2229 | 429.2256 | 253.784 | 229.8606
945.2229 | 601.2229 | 254.5532 | 230.2796 | 429.1531 | 945.2229 | 429.1531 | 254.5532 | 230.2796
946.2229 | 602.2229 | 255.327 | 230.6855 | 428.8923 | 946.2229 | 428.8923 | 255.327 | 230.6855
947.2229 | 603.2229 | 256.1095 | 231.0986 | 428.7369 | 947.2229 | 428.7369 | 256.1095 | 231.0986
948.2229 | 604.2229 | 256.8946 | 231.5135 | 428.738 | 948.2229 | 428.738 | 256.8946 | 231.5135
949.2229 | 605.2229 | 257.6696 | 231.9307 | 428.7783 | 949.2229 | 428.7783 | 257.6696 | 231.9307
950.2229 | 606.2229 | 258.4682 | 232.3365 | 428.7514 | 950.2229 | 428.7514 | 258.4682 | 232.3365
951.2229 | 607.2229 | 259.2536 | 232.7483 | 428.759 | 951.2229 | 428.759 | 259.2536 | 232.7483
952.2229 | 608.2229 | 260.091 | 233.157 | 428.7601 | 952.2229 | 428.7601 | 260.091 | 233.157
953.2229 | 609.2229 | 260.9021 | 233.5784 | 428.7864 | 953.2229 | 428.7864 | 260.9021 | 233.5784
954.2229 | 610.2229 | 261.743 | 233.9922 | 428.7428 | 954.2229 | 428.7428 | 261.743 | 233.9922
955.2229 | 611.2229 | 262.5528 | 234.4037 | 428.796 | 955.2229 | 428.796 | 262.5528 | 234.4037
956.2229 | 612.2229 | 263.3736 | 234.8156 | 428.8154 | 956.2229 | 428.8154 | 263.3736 | 234.8156
957.2229 | 613.2229 | 264.1689 | 235.2227 | 428.7011 | 957.2229 | 428.7011 | 264.1689 | 235.2227
958.2229 | 614.2229 | 264.9723 | 235.6382 | 428.7085 | 958.2229 | 428.7085 | 264.9723 | 235.6382
959.2229 | 615.2229 | 265.74 | 236.0429 | 428.5542 | 959.2229 | 428.5542 | 265.74 | 236.0429
960.2229 | 616.2229 | 266.4931 | 236.4534 | 428.5022 | 960.2229 | 428.5022 | 266.4931 | 236.4534
961.2229 | 617.2229 | 267.2255 | 236.8608 | 428.4342 | 961.2229 | 428.4342 | 267.2255 | 236.8608
962.2229 | 618.2229 | 267.9402 | 237.2915 | 428.4925 | 962.2229 | 428.4925 | 267.9402 | 237.2915
963.2229 | 619.2229 | 268.6337 | 237.6964 | 428.6035 | 963.2229 | 428.6035 | 268.6337 | 237.6964
964.2229 | 620.2229 | 269.3076 | 238.106 | 428.5828 | 964.2229 | 428.5828 | 269.3076 | 238.106
965.2229 | 621.2229 | 269.9692 | 238.5191 | 428.5158 | 965.2229 | 428.5158 | 269.9692 | 238.5191
966.2854 | 622.2854 | 270.6367 | 238.9531 | 428.3175 | 966.2854 | 428.3175 | 270.6367 | 238.9531
967.2229 | 623.2229 | 271.213 | 239.3498 | 428.1895 | 967.2229 | 428.1895 | 271.213 | 239.3498
968.2385 | 624.2385 | 271.8188 | 239.7665 | 428.1611 | 968.2385 | 428.1611 | 271.8188 | 239.7665
969.2385 | 625.2385 | 272.42 | 240.1762 | 428.2627 | 969.2385 | 428.2627 | 272.42 | 240.1762
970.2385 | 626.2385 | 273.0295 | 240.5942 | 428.3017 | 970.2385 | 428.3017 | 273.0295 | 240.5942
971.2229 | 627.2229 | 273.5888 | 241.0109 | 428.2477 | 971.2229 | 428.2477 | 273.5888 | 241.0109
972.2385 | 628.2385 | 274.1529 | 241.4301 | 428.2471 | 972.2385 | 428.2471 | 274.1529 | 241.4301
973.3792 | 629.3792 | 274.7938 | 241.9098 | 428.3496 | 973.3792 | 428.3496 | 274.7938 | 241.9098
974.4104 | 630.4104 | 275.3423 | 242.3439 | 428.4683 | 974.4104 | 428.4683 | 275.3423 | 242.3439
975.2229 | 631.2229 | 275.7986 | 242.6707 | 428.6003 | 975.2229 | 428.6003 | 275.7986 | 242.6707
976.2229 | 632.2229 | 276.3213 | 243.0878 | 428.6642 | 976.2229 | 428.6642 | 276.3213 | 243.0878
977.2385 | 633.2385 | 276.8524 | 243.5082 | 428.6786 | 977.2385 | 428.6786 | 276.8524 | 243.5082
978.2698 | 634.2698 | 277.3972 | 243.9421 | 428.7092 | 978.2698 | 428.7092 | 277.3972 | 243.9421
979.2542 | 635.2542 | 277.8949 | 244.3631 | 428.7397 | 979.2542 | 428.7397 | 277.8949 | 244.3631
980.2385 | 636.2385 | 278.3845 | 244.7701 | 428.7823 | 980.2385 | 428.7823 | 278.3845 | 244.7701
981.2229 | 637.2229 | 278.8739 | 245.1768 | 428.7908 | 981.2229 | 428.7908 | 278.8739 | 245.1768
982.2229 | 638.2229 | 279.3649 | 245.5907 | 428.6028 | 982.2229 | 428.6028 | 279.3649 | 245.5907
983.2229 | 639.2229 | 279.863 | 246.0006 | 428.5166 | 983.2229 | 428.5166 | 279.863 | 246.0006
984.2542 | 640.2542 | 280.363 | 246.4312 | 428.4106 | 984.2542 | 428.4106 | 280.363 | 246.4312
985.3323 | 641.3323 | 280.8568 | 246.8764 | 428.5445 | 985.3323 | 428.5445 | 280.8568 | 246.8764
986.4417 | 642.4417 | 281.3782 | 247.3231 | 428.6172 | 986.4417 | 428.6172 | 281.3782 | 247.3231
987.3167 | 643.3167 | 281.7814 | 247.6866 | 428.6553 | 987.3167 | 428.6553 | 281.7814 | 247.6866
988.2698 | 644.2698 | 282.2431 | 248.0783 | 428.6567 | 988.2698 | 428.6567 | 282.2431 | 248.0783
989.2385 | 645.2385 | 282.708 | 248.4746 | 428.784 | 989.2385 | 428.784 | 282.708 | 248.4746
990.2229 | 646.2229 | 283.196 | 248.8748 | 428.8503 | 990.2229 | 428.8503 | 283.196 | 248.8748
991.2229 | 647.2229 | 283.6714 | 249.2844 | 429.0056 | 991.2229 | 429.0056 | 283.6714 | 249.2844
992.2229 | 648.2229 | 284.1635 | 249.689 | 429.0519 | 992.2229 | 429.0519 | 284.1635 | 249.689
993.2229 | 649.2229 | 284.6484 | 250.0981 | 428.8346 | 993.2229 | 428.8346 | 284.6484 | 250.0981
994.2229 | 650.2229 | 285.1494 | 250.4954 | 428.9471 | 994.2229 | 428.9471 | 285.1494 | 250.4954
995.2229 | 651.2229 | 285.6776 | 250.8958 | 428.9539 | 995.2229 | 428.9539 | 285.6776 | 250.8958
996.2229 | 652.2229 | 286.1821 | 251.3107 | 428.865 | 996.2229 | 428.865 | 286.1821 | 251.3107
997.2229 | 653.2229 | 286.6927 | 251.7181 | 428.6709 | 997.2229 | 428.6709 | 286.6927 | 251.7181
998.2229 | 654.2229 | 287.2048 | 252.1241 | 428.6062 | 998.2229 | 428.6062 | 287.2048 | 252.1241
999.2229 | 655.2229 | 287.706 | 252.5346 | 428.553 | 999.2229 | 428.553 | 287.706 | 252.5346
1000.2229 | 656.2229 | 288.2034 | 252.9237 | 428.6219 | 1000.2229 | 428.6219 | 288.2034 | 252.9237
1001.2229 | 657.2229 | 288.7009 | 253.322 | 428.5548 | 1001.2229 | 428.5548 | 288.7009 | 253.322
1002.2229 | 658.2229 | 289.1891 | 253.7306 | 428.3641 | 1002.2229 | 428.3641 | 289.1891 | 253.7306
1003.2229 | 659.2229 | 289.7092 | 254.1411 | 428.2997 | 1003.2229 | 428.2997 | 289.7092 | 254.1411
1004.2229 | 660.2229 | 290.2126 | 254.5436 | 428.4191 | 1004.2229 | 428.4191 | 290.2126 | 254.5436
1005.2229 | 661.2229 | 290.7242 | 254.9517 | 428.6131 | 1005.2229 | 428.6131 | 290.7242 | 254.9517
1006.2229 | 662.2229 | 291.2378 | 255.359 | 428.7147 | 1006.2229 | 428.7147 | 291.2378 | 255.359
1007.2229 | 663.2229 | 291.7756 | 255.767 | 428.7388 | 1007.2229 | 428.7388 | 291.7756 | 255.767
1008.2229 | 664.2229 | 292.2976 | 256.174 | 428.7162 | 1008.2229 | 428.7162 | 292.2976 | 256.174
1009.2229 | 665.2229 | 292.851 | 256.5951 | 428.7425 | 1009.2229 | 428.7425 | 292.851 | 256.5951
1010.2229 | 666.2229 | 293.3921 | 257.0149 | 428.8414 | 1010.2229 | 428.8414 | 293.3921 | 257.0149
1011.2229 | 667.2229 | 293.9452 | 257.4311 | 428.8826 | 1011.2229 | 428.8826 | 293.9452 | 257.4311
1012.2229 | 668.2229 | 294.5063 | 257.852 | 428.9285 | 1012.2229 | 428.9285 | 294.5063 | 257.852
1013.2229 | 669.2229 | 295.0547 | 258.2727 | 429.1125 | 1013.2229 | 429.1125 | 295.0547 | 258.2727
1014.2229 | 670.2229 | 295.621 | 258.6919 | 429.1538 | 1014.2229 | 429.1538 | 295.621 | 258.6919
1015.2229 | 671.2229 | 296.2014 | 259.1112 | 429.2636 | 1015.2229 | 429.2636 | 296.2014 | 259.1112
1016.2229 | 672.2229 | 296.7858 | 259.5407 | 429.3452 | 1016.2229 | 429.3452 | 296.7858 | 259.5407
1017.2229 | 673.2229 | 297.3857 | 259.9626 | 429.2206 | 1017.2229 | 429.2206 | 297.3857 | 259.9626
1018.2229 | 674.2229 | 297.9791 | 260.3979 | 429.184 | 1018.2229 | 429.184 | 297.9791 | 260.3979
1019.2229 | 675.2229 | 298.5985 | 260.829 | 429.1576 | 1019.2229 | 429.1576 | 298.5985 | 260.829
1020.2229 | 676.2229 | 299.2052 | 261.2655 | 429.0233 | 1020.2229 | 429.0233 | 299.2052 | 261.2655
1021.2229 | 677.2229 | 299.8282 | 261.7015 | 428.971 | 1021.2229 | 428.971 | 299.8282 | 261.7015
1022.2229 | 678.2229 | 300.4596 | 262.1404 | 428.939 | 1022.2229 | 428.939 | 300.4596 | 262.1404
1023.2229 | 679.2229 | 301.1016 | 262.5855 | 428.7058 | 1023.2229 | 428.7058 | 301.1016 | 262.5855
1024.2229 | 680.2229 | 301.7592 | 263.0227 | 428.7317 | 1024.2229 | 428.7317 | 301.7592 | 263.0227
1025.2229 | 681.2229 | 302.4045 | 263.4701 | 428.8625 | 1025.2229 | 428.8625 | 302.4045 | 263.4701
1026.2229 | 682.2229 | 303.0761 | 263.9134 | 428.7699 | 1026.2229 | 428.7699 | 303.0761 | 263.9134
1027.2229 | 683.2229 | 303.7276 | 264.3599 | 428.7274 | 1027.2229 | 428.7274 | 303.7276 | 264.3599
1028.2229 | 684.2229 | 304.4406 | 264.8152 | 428.6059 | 1028.2229 | 428.6059 | 304.4406 | 264.8152
1029.2229 | 685.2229 | 305.1074 | 265.275 | 428.6692 | 1029.2229 | 428.6692 | 305.1074 | 265.275
1030.3792 | 686.3792 | 305.9076 | 265.7972 | 428.6867 | 1030.3792 | 428.6867 | 305.9076 | 265.7972
1031.3792 | 687.3792 | 306.6319 | 266.2642 | 428.5609 | 1031.3792 | 428.5609 | 306.6319 | 266.2642
1032.2385 | 688.2385 | 307.2462 | 266.6518 | 428.5786 | 1032.2385 | 428.5786 | 307.2462 | 266.6518
1033.2229 | 689.2229 | 307.9682 | 267.1133 | 428.5925 | 1033.2229 | 428.5925 | 307.9682 | 267.1133
1034.2229 | 690.2229 | 308.7223 | 267.5691 | 428.5108 | 1034.2229 | 428.5108 | 308.7223 | 267.5691
1035.2229 | 691.2229 | 309.475 | 268.0265 | 428.4514 | 1035.2229 | 428.4514 | 309.475 | 268.0265
1036.2229 | 692.2229 | 310.2292 | 268.4952 | 428.4234 | 1036.2229 | 428.4234 | 310.2292 | 268.4952
1037.2229 | 693.2229 | 311.0021 | 268.9513 | 428.5399 | 1037.2229 | 428.5399 | 311.0021 | 268.9513
1038.2229 | 694.2229 | 311.804 | 269.4257 | 428.556 | 1038.2229 | 428.556 | 311.804 | 269.4257
1039.2229 | 695.2229 | 312.5934 | 269.8962 | 428.6251 | 1039.2229 | 428.6251 | 312.5934 | 269.8962
1040.2229 | 696.2229 | 313.4097 | 270.3718 | 428.7025 | 1040.2229 | 428.7025 | 313.4097 | 270.3718
1041.2229 | 697.2229 | 314.2421 | 270.8513 | 428.6726 | 1041.2229 | 428.6726 | 314.2421 | 270.8513
1042.2229 | 698.2229 | 315.058 | 271.3284 | 428.6043 | 1042.2229 | 428.6043 | 315.058 | 271.3284
1043.2229 | 699.2229 | 315.8878 | 271.8089 | 428.512 | 1043.2229 | 428.512 | 315.8878 | 271.8089
1044.2229 | 700.2229 | 316.7297 | 272.303 | 428.344 | 1044.2229 | 428.344 | 316.7297 | 272.303
1045.2229 | 701.2229 | 317.5866 | 272.7917 | 428.3046 | 1045.2229 | 428.3046 | 317.5866 | 272.7917
1046.2229 | 702.2229 | 318.4558 | 273.2859 | 428.1565 | 1046.2229 | 428.1565 | 318.4558 | 273.2859
1047.2229 | 703.2229 | 319.354 | 273.7868 | 428.0464 | 1047.2229 | 428.0464 | 319.354 | 273.7868
1048.2229 | 704.2229 | 320.2307 | 274.293 | 428.0841 | 1048.2229 | 428.0841 | 320.2307 | 274.293
1049.2229 | 705.2229 | 321.1352 | 274.7954 | 428.0501 | 1049.2229 | 428.0501 | 321.1352 | 274.7954
1050.2229 | 706.2229 | 322.0415 | 275.2993 | 428.049 | 1050.2229 | 428.049 | 322.0415 | 275.2993
1051.2229 | 707.2229 | 322.9338 | 275.8099 | 427.984 | 1051.2229 | 427.984 | 322.9338 | 275.8099
1052.2229 | 708.2229 | 323.8118 | 276.3198 | 427.9026 | 1052.2229 | 427.9026 | 323.8118 | 276.3198
1053.2229 | 709.2229 | 324.7276 | 276.8317 | 427.8954 | 1053.2229 | 427.8954 | 324.7276 | 276.8317
1054.2229 | 710.2229 | 325.634 | 277.3537 | 427.8666 | 1054.2229 | 427.8666 | 325.634 | 277.3537
1055.3635 | 711.3635 | 326.6766 | 277.9468 | 427.9472 | 1055.3635 | 427.9472 | 326.6766 | 277.9468
1056.2385 | 712.2385 | 327.4751 | 278.4068 | 428.0081 | 1056.2385 | 428.0081 | 327.4751 | 278.4068
1057.2229 | 713.2229 | 328.3696 | 278.9312 | 428.0969 | 1057.2229 | 428.0969 | 328.3696 | 278.9312
1058.301 | 714.301 | 329.371 | 279.5 | 428.1492 | 1058.301 | 428.1492 | 329.371 | 279.5
1059.2385 | 715.2385 | 330.2563 | 280.0181 | 428.3218 | 1059.2385 | 428.3218 | 330.2563 | 280.0181
1060.2229 | 716.2229 | 331.1732 | 280.5552 | 428.3605 | 1060.2229 | 428.3605 | 331.1732 | 280.5552
1061.2229 | 717.2229 | 332.1257 | 281.1024 | 428.2715 | 1061.2229 | 428.2715 | 332.1257 | 281.1024
1062.2229 | 718.2229 | 333.1005 | 281.6593 | 428.1013 | 1062.2229 | 428.1013 | 333.1005 | 281.6593
1063.2229 | 719.2229 | 334.0607 | 282.1946 | 428.1501 | 1063.2229 | 428.1501 | 334.0607 | 282.1946
1064.2229 | 720.2229 | 335.0069 | 282.7647 | 428.1283 | 1064.2229 | 428.1283 | 335.0069 | 282.7647
1065.2229 | 721.2229 | 335.9817 | 283.335 | 428.1013 | 1065.2229 | 428.1013 | 335.9817 | 283.335
1066.2229 | 722.2229 | 336.9581 | 283.9036 | 428.0749 | 1066.2229 | 428.0749 | 336.9581 | 283.9036
1067.2229 | 723.2229 | 337.9334 | 284.4817 | 428.0378 | 1067.2229 | 428.0378 | 337.9334 | 284.4817
1068.2229 | 724.2229 | 338.9267 | 285.0742 | 427.9707 | 1068.2229 | 427.9707 | 338.9267 | 285.0742
1069.2229 | 725.2229 | 339.9206 | 285.6624 | 427.9545 | 1069.2229 | 427.9545 | 339.9206 | 285.6624
1070.2229 | 726.2229 | 340.92 | 286.2499 | 427.9302 | 1070.2229 | 427.9302 | 340.92 | 286.2499
1071.2229 | 727.2229 | 341.935 | 286.839 | 427.8172 | 1071.2229 | 427.8172 | 341.935 | 286.839
1072.2229 | 728.2229 | 342.9211 | 287.4457 | 427.8821 | 1072.2229 | 427.8821 | 342.9211 | 287.4457
1073.2229 | 729.2229 | 343.9574 | 288.0382 | 427.9036 | 1073.2229 | 427.9036 | 343.9574 | 288.0382
1074.2229 | 730.2229 | 344.9741 | 288.6524 | 427.9784 | 1074.2229 | 427.9784 | 344.9741 | 288.6524
1075.2229 | 731.2229 | 345.9884 | 289.2711 | 427.9383 | 1075.2229 | 427.9383 | 345.9884 | 289.2711
1076.2229 | 732.2229 | 347.0249 | 289.8863 | 427.8334 | 1076.2229 | 427.8334 | 347.0249 | 289.8863
1077.2229 | 733.2229 | 348.0622 | 290.5097 | 427.8431 | 1077.2229 | 427.8431 | 348.0622 | 290.5097
1078.2229 | 734.2229 | 349.0984 | 291.1369 | 428.0665 | 1078.2229 | 428.0665 | 349.0984 | 291.1369
1079.2229 | 735.2229 | 350.1716 | 291.7662 | 428.1745 | 1079.2229 | 428.1745 | 350.1716 | 291.7662
1080.2229 | 736.2229 | 351.2226 | 292.4121 | 428.2451 | 1080.2229 | 428.2451 | 351.2226 | 292.4121
1081.2229 | 737.2229 | 352.3083 | 293.0563 | 428.1928 | 1081.2229 | 428.1928 | 352.3083 | 293.0563
1082.2229 | 738.2229 | 353.375 | 293.715 | 428.2159 | 1082.2229 | 428.2159 | 353.375 | 293.715
1083.2229 | 739.2229 | 354.4358 | 294.3713 | 428.2262 | 1083.2229 | 428.2262 | 354.4358 | 294.3713
1084.2229 | 740.2229 | 355.4993 | 295.0378 | 428.2124 | 1084.2229 | 428.2124 | 355.4993 | 295.0378
1085.2229 | 741.2229 | 356.5998 | 295.7127 | 428.2831 | 1085.2229 | 428.2831 | 356.5998 | 295.7127
1086.2229 | 742.2229 | 357.6847 | 296.3799 | 428.2748 | 1086.2229 | 428.2748 | 357.6847 | 296.3799
1087.2229 | 743.2229 | 358.7788 | 297.0489 | 428.0981 | 1087.2229 | 428.0981 | 358.7788 | 297.0489
1088.2229 | 744.2229 | 359.854 | 297.7232 | 427.9869 | 1088.2229 | 427.9869 | 359.854 | 297.7232
1089.2229 | 745.2229 | 360.9483 | 298.4097 | 427.9242 | 1089.2229 | 427.9242 | 360.9483 | 298.4097
1090.2229 | 746.2229 | 362.0111 | 299.0841 | 428.05 | 1090.2229 | 428.05 | 362.0111 | 299.0841
1091.2229 | 747.2229 | 363.075 | 299.7769 | 428.1268 | 1091.2229 | 428.1268 | 363.075 | 299.7769
1092.2229 | 748.2229 | 364.127 | 300.4686 | 428.0508 | 1092.2229 | 428.0508 | 364.127 | 300.4686
1093.2229 | 749.2229 | 365.16 | 301.1702 | 427.9618 | 1093.2229 | 427.9618 | 365.16 | 301.1702
1094.2229 | 750.2229 | 366.2094 | 301.8752 | 428.1095 | 1094.2229 | 428.1095 | 366.2094 | 301.8752
1095.2229 | 751.2229 | 367.232 | 302.5594 | 428.1721 | 1095.2229 | 428.1721 | 367.232 | 302.5594
1096.2229 | 752.2229 | 368.247 | 303.2611 | 428.1486 | 1096.2229 | 428.1486 | 368.247 | 303.2611
1097.2229 | 753.2229 | 369.257 | 303.9668 | 428.1434 | 1097.2229 | 428.1434 | 369.257 | 303.9668
1098.2229 | 754.2229 | 370.2763 | 304.6822 | 428.0283 | 1098.2229 | 428.0283 | 370.2763 | 304.6822
1099.2229 | 755.2229 | 371.257 | 305.3875 | 427.9165 | 1099.2229 | 427.9165 | 371.257 | 305.3875
1100.2229 | 756.2229 | 372.2264 | 306.0996 | 427.8121 | 1100.2229 | 427.8121 | 372.2264 | 306.0996
1101.2229 | 757.2229 | 373.1817 | 306.8212 | 427.8837 | 1101.2229 | 427.8837 | 373.1817 | 306.8212
1102.2229 | 758.2229 | 374.1373 | 307.5462 | 427.8593 | 1102.2229 | 427.8593 | 374.1373 | 307.5462
1103.2229 | 759.2229 | 375.0769 | 308.2642 | 427.859 | 1103.2229 | 427.859 | 375.0769 | 308.2642
1104.2229 | 760.2229 | 375.9953 | 308.9894 | 427.8233 | 1104.2229 | 427.8233 | 375.9953 | 308.9894
1105.2229 | 761.2229 | 376.9161 | 309.7178 | 427.795 | 1105.2229 | 427.795 | 376.9161 | 309.7178
1106.2229 | 762.2229 | 377.8285 | 310.4376 | 427.8359 | 1106.2229 | 427.8359 | 377.8285 | 310.4376
1107.2229 | 763.2229 | 378.7386 | 311.1695 | 427.9094 | 1107.2229 | 427.9094 | 378.7386 | 311.1695
1108.2229 | 764.2229 | 379.6374 | 311.8966 | 427.8832 | 1108.2229 | 427.8832 | 379.6374 | 311.8966
1109.2229 | 765.2229 | 380.526 | 312.6226 | 427.7765 | 1109.2229 | 427.7765 | 380.526 | 312.6226
1110.2229 | 766.2229 | 381.4015 | 313.3596 | 427.7048 | 1110.2229 | 427.7048 | 381.4015 | 313.3596
1111.2229 | 767.2229 | 382.2582 | 314.0827 | 427.5673 | 1111.2229 | 427.5673 | 382.2582 | 314.0827
1112.2229 | 768.2229 | 383.0917 | 314.8095 | 427.466 | 1112.2229 | 427.466 | 383.0917 | 314.8095
1113.2229 | 769.2229 | 383.9448 | 315.529 | 427.3568 | 1113.2229 | 427.3568 | 383.9448 | 315.529
1114.2229 | 770.2229 | 384.7663 | 316.2518 | 427.142 | 1114.2229 | 427.142 | 384.7663 | 316.2518
1115.2229 | 771.2229 | 385.5821 | 316.9627 | 426.8649 | 1115.2229 | 426.8649 | 385.5821 | 316.9627
1116.2229 | 772.2229 | 386.3765 | 317.6655 | 426.7911 | 1116.2229 | 426.7911 | 386.3765 | 317.6655
1117.2229 | 773.2229 | 387.1649 | 318.3729 | 426.8132 | 1117.2229 | 426.8132 | 387.1649 | 318.3729
1118.2229 | 774.2229 | 387.9781 | 319.0861 | 426.8266 | 1118.2229 | 426.8266 | 387.9781 | 319.0861
1119.2229 | 775.2229 | 388.7435 | 319.7893 | 426.7939 | 1119.2229 | 426.7939 | 388.7435 | 319.7893
1120.2229 | 776.2229 | 389.5017 | 320.4922 | 426.9472 | 1120.2229 | 426.9472 | 389.5017 | 320.4922
1121.2229 | 777.2229 | 390.2555 | 321.193 | 426.933 | 1121.2229 | 426.933 | 390.2555 | 321.193
1122.2229 | 778.2229 | 390.9913 | 321.889 | 426.843 | 1122.2229 | 426.843 | 390.9913 | 321.889
1123.2229 | 779.2229 | 391.7245 | 322.5868 | 426.9033 | 1123.2229 | 426.9033 | 391.7245 | 322.5868
1124.2229 | 780.2229 | 392.4556 | 323.2861 | 426.8962 | 1124.2229 | 426.8962 | 392.4556 | 323.2861
1125.2229 | 781.2229 | 393.1622 | 323.987 | 426.8764 | 1125.2229 | 426.8764 | 393.1622 | 323.987
1126.2229 | 782.2229 | 393.8724 | 324.6664 | 426.9829 | 1126.2229 | 426.9829 | 393.8724 | 324.6664
1127.2229 | 783.2229 | 394.568 | 325.3508 | 427.0564 | 1127.2229 | 427.0564 | 394.568 | 325.3508
1128.2229 | 784.2229 | 395.2625 | 326.032 | 427.1089 | 1128.2229 | 427.1089 | 395.2625 | 326.032
1129.2229 | 785.2229 | 395.9563 | 326.708 | 427.1648 | 1129.2229 | 427.1648 | 395.9563 | 326.708
1130.2229 | 786.2229 | 396.6232 | 327.3922 | 427.1898 | 1130.2229 | 427.1898 | 396.6232 | 327.3922
1131.2229 | 787.2229 | 397.3132 | 328.0621 | 427.3041 | 1131.2229 | 427.3041 | 397.3132 | 328.0621
1132.2229 | 788.2229 | 397.9753 | 328.7324 | 427.2373 | 1132.2229 | 427.2373 | 397.9753 | 328.7324
1133.2229 | 789.2229 | 398.6471 | 329.4046 | 427.3866 | 1133.2229 | 427.3866 | 398.6471 | 329.4046
1134.2229 | 790.2229 | 399.2965 | 330.0649 | 427.5884 | 1134.2229 | 427.5884 | 399.2965 | 330.0649
1135.2229 | 791.2229 | 399.9611 | 330.7294 | 427.6958 | 1135.2229 | 427.6958 | 399.9611 | 330.7294
1136.2229 | 792.2229 | 400.6206 | 331.3869 | 427.7143 | 1136.2229 | 427.7143 | 400.6206 | 331.3869
1137.2229 | 793.2229 | 401.2778 | 332.0495 | 427.5984 | 1137.2229 | 427.5984 | 401.2778 | 332.0495
1138.2229 | 794.2229 | 401.947 | 332.7091 | 427.5996 | 1138.2229 | 427.5996 | 401.947 | 332.7091
1139.2229 | 795.2229 | 402.6133 | 333.3574 | 427.6355 | 1139.2229 | 427.6355 | 402.6133 | 333.3574
1140.2229 | 796.2229 | 403.2603 | 333.9963 | 427.6935 | 1140.2229 | 427.6935 | 403.2603 | 333.9963
1141.2229 | 797.2229 | 403.9162 | 334.6505 | 427.7695 | 1141.2229 | 427.7695 | 403.9162 | 334.6505
1142.2229 | 798.2229 | 404.565 | 335.2778 | 427.8814 | 1142.2229 | 427.8814 | 404.565 | 335.2778
1143.2229 | 799.2229 | 405.2083 | 335.9218 | 428.0278 | 1143.2229 | 428.0278 | 405.2083 | 335.9218
1144.2229 | 800.2229 | 405.8335 | 336.554 | 428.0812 | 1144.2229 | 428.0812 | 405.8335 | 336.554
1145.2229 | 801.2229 | 406.4722 | 337.1685 | 428.2094 | 1145.2229 | 428.2094 | 406.4722 | 337.1685
1146.2385 | 802.2385 | 407.0777 | 337.7965 | 428.3129 | 1146.2385 | 428.3129 | 407.0777 | 337.7965
1147.2229 | 803.2229 | 407.7026 | 338.4072 | 428.3014 | 1147.2229 | 428.3014 | 407.7026 | 338.4072
1148.3948 | 804.3948 | 408.3912 | 339.1259 | 428.3705 | 1148.3948 | 428.3705 | 408.3912 | 339.1259
1149.2698 | 805.2698 | 408.9317 | 339.6511 | 428.3691 | 1149.2698 | 428.3691 | 408.9317 | 339.6511
1150.2229 | 806.2229 | 409.4895 | 340.2251 | 428.3656 | 1150.2229 | 428.3656 | 409.4895 | 340.2251
1151.2229 | 807.2229 | 410.1018 | 340.8169 | 428.2701 | 1151.2229 | 428.2701 | 410.1018 | 340.8169
1152.2229 | 808.2229 | 410.7313 | 341.423 | 428.1814 | 1152.2229 | 428.1814 | 410.7313 | 341.423
1153.2229 | 809.2229 | 411.3912 | 342.0036 | 428.2746 | 1153.2229 | 428.2746 | 411.3912 | 342.0036
1154.2229 | 810.2229 | 412.039 | 342.6036 | 428.3942 | 1154.2229 | 428.3942 | 412.039 | 342.6036
1155.2229 | 811.2229 | 412.6956 | 343.1762 | 428.4311 | 1155.2229 | 428.4311 | 412.6956 | 343.1762
1156.2229 | 812.2229 | 413.377 | 343.7525 | 428.4213 | 1156.2229 | 428.4213 | 413.377 | 343.7525
1157.2229 | 813.2229 | 414.0488 | 344.3255 | 428.4968 | 1157.2229 | 428.4968 | 414.0488 | 344.3255
1158.2229 | 814.2229 | 414.7466 | 344.8878 | 428.498 | 1158.2229 | 428.498 | 414.7466 | 344.8878
1159.2229 | 815.2229 | 415.4449 | 345.4589 | 428.3415 | 1159.2229 | 428.3415 | 415.4449 | 345.4589
1160.2229 | 816.2229 | 416.1607 | 346.0273 | 428.0601 | 1160.2229 | 428.0601 | 416.1607 | 346.0273
1161.2229 | 817.2229 | 416.877 | 346.5874 | 427.8488 | 1161.2229 | 427.8488 | 416.877 | 346.5874
1162.2229 | 818.2229 | 417.5928 | 347.1488 | 427.7586 | 1162.2229 | 427.7586 | 417.5928 | 347.1488
1163.2229 | 819.2229 | 418.3182 | 347.7043 | 427.7981 | 1163.2229 | 427.7981 | 418.3182 | 347.7043
1164.2229 | 820.2229 | 419.0444 | 348.2534 | 427.8521 | 1164.2229 | 427.8521 | 419.0444 | 348.2534
1165.301 | 821.301 | 419.8125 | 348.8445 | 427.889 | 1165.301 | 427.889 | 419.8125 | 348.8445
1166.3479 | 822.3479 | 420.6002 | 349.4271 | 427.8326 | 1166.3479 | 427.8326 | 420.6002 | 349.4271
1167.2229 | 823.2229 | 421.2406 | 349.9122 | 427.6779 | 1167.2229 | 427.6779 | 421.2406 | 349.9122
1168.2385 | 824.2385 | 421.9976 | 350.4567 | 427.6686 | 1168.2385 | 427.6686 | 421.9976 | 350.4567
1169.4885 | 825.4885 | 422.9403 | 351.1308 | 427.6454 | 1169.4885 | 427.6454 | 422.9403 | 351.1308
1170.2385 | 826.2385 | 423.486 | 351.5362 | 427.5728 | 1170.2385 | 427.5728 | 423.486 | 351.5362
1171.2385 | 827.2385 | 424.2205 | 352.0752 | 427.3292 | 1171.2385 | 427.3292 | 424.2205 | 352.0752
1172.2385 | 828.2385 | 424.9739 | 352.5978 | 427.2073 | 1172.2385 | 427.2073 | 424.9739 | 352.5978
1173.2229 | 829.2229 | 425.6887 | 353.1207 | 427.0863 | 1173.2229 | 427.0863 | 425.6887 | 353.1207
1174.2229 | 830.2229 | 426.4129 | 353.6481 | 426.9522 | 1174.2229 | 426.9522 | 426.4129 | 353.6481
1175.2229 | 831.2229 | 427.1295 | 354.1612 | 426.9942 | 1175.2229 | 426.9942 | 427.1295 | 354.1612
1176.2229 | 832.2229 | 427.8249 | 354.6921 | 426.8876 | 1176.2229 | 426.8876 | 427.8249 | 354.6921
1177.2229 | 833.2229 | 428.5226 | 355.2053 | 426.7601 | 1177.2229 | 426.7601 | 428.5226 | 355.2053
1178.2229 | 834.2229 | 429.227 | 355.7167 | 426.7135 | 1178.2229 | 426.7135 | 429.227 | 355.7167
1179.2229 | 835.2229 | 429.9176 | 356.2326 | 426.8404 | 1179.2229 | 426.8404 | 429.9176 | 356.2326
1180.2229 | 836.2229 | 430.5766 | 356.7322 | 427.0691 | 1180.2229 | 427.0691 | 430.5766 | 356.7322
1181.2229 | 837.2229 | 431.2299 | 357.2484 | 427.202 | 1181.2229 | 427.202 | 431.2299 | 357.2484
1182.2229 | 838.2229 | 431.8699 | 357.733 | 427.1907 | 1182.2229 | 427.1907 | 431.8699 | 357.733
1183.2229 | 839.2229 | 432.5145 | 358.2349 | 427.3349 | 1183.2229 | 427.3349 | 432.5145 | 358.2349
1184.2229 | 840.2229 | 433.1504 | 358.7261 | 427.3981 | 1184.2229 | 427.3981 | 433.1504 | 358.7261
1185.2229 | 841.2229 | 433.7956 | 359.2188 | 427.4538 | 1185.2229 | 427.4538 | 433.7956 | 359.2188
1186.2229 | 842.2229 | 434.4423 | 359.7068 | 427.366 | 1186.2229 | 427.366 | 434.4423 | 359.7068
1187.2229 | 843.2229 | 435.0678 | 360.1975 | 427.3086 | 1187.2229 | 427.3086 | 435.0678 | 360.1975
1188.3635 | 844.3635 | 435.7755 | 360.7326 | 427.237 | 1188.3635 | 427.237 | 435.7755 | 360.7326
1189.3792 | 845.3792 | 436.4579 | 361.2237 | 427.2447 | 1189.3792 | 427.2447 | 436.4579 | 361.2237
1190.3167 | 846.3167 | 437.0536 | 361.6657 | 427.3131 | 1190.3167 | 427.3131 | 437.0536 | 361.6657
1191.2542 | 847.2542 | 437.6086 | 362.1126 | 427.4469 | 1191.2542 | 427.4469 | 437.6086 | 362.1126
1192.2385 | 848.2385 | 438.1463 | 362.569 | 427.5026 | 1192.2385 | 427.5026 | 438.1463 | 362.569
1193.2229 | 849.2229 | 438.6588 | 363.0325 | 427.5599 | 1193.2229 | 427.5599 | 438.6588 | 363.0325
1194.2229 | 850.2229 | 439.1625 | 363.497 | 427.4655 | 1194.2229 | 427.4655 | 439.1625 | 363.497
1195.2229 | 851.2229 | 439.6596 | 363.954 | 427.5262 | 1195.2229 | 427.5262 | 439.6596 | 363.954
1196.2229 | 852.2229 | 440.147 | 364.4089 | 427.5269 | 1196.2229 | 427.5269 | 440.147 | 364.4089
1197.2229 | 853.2229 | 440.6095 | 364.847 | 427.4952 | 1197.2229 | 427.4952 | 440.6095 | 364.847
1198.2229 | 854.2229 | 441.0696 | 365.2979 | 427.4976 | 1198.2229 | 427.4976 | 441.0696 | 365.2979
1199.2229 | 855.2229 | 441.5387 | 365.7553 | 427.5811 | 1199.2229 | 427.5811 | 441.5387 | 365.7553
1200.2229 | 856.2229 | 442.0129 | 366.1927 | 427.5781 | 1200.2229 | 427.5781 | 442.0129 | 366.1927
1201.2229 | 857.2229 | 442.4493 | 366.6368 | 427.5921 | 1201.2229 | 427.5921 | 442.4493 | 366.6368
1202.2229 | 858.2229 | 442.8826 | 367.0815 | 427.6022 | 1202.2229 | 427.6022 | 442.8826 | 367.0815
1203.2229 | 859.2229 | 443.3446 | 367.5156 | 427.8477 | 1203.2229 | 427.8477 | 443.3446 | 367.5156
1204.2229 | 860.2229 | 443.7718 | 367.9432 | 427.9065 | 1204.2229 | 427.9065 | 443.7718 | 367.9432
1205.2229 | 861.2229 | 444.2187 | 368.3717 | 427.9363 | 1205.2229 | 427.9363 | 444.2187 | 368.3717
1206.2229 | 862.2229 | 444.655 | 368.7946 | 427.9093 | 1206.2229 | 427.9093 | 444.655 | 368.7946
1207.2229 | 863.2229 | 445.097 | 369.2196 | 427.8899 | 1207.2229 | 427.8899 | 445.097 | 369.2196
1208.2229 | 864.2229 | 445.5491 | 369.6604 | 427.8494 | 1208.2229 | 427.8494 | 445.5491 | 369.6604
1209.2229 | 865.2229 | 445.9691 | 370.0708 | 427.7528 | 1209.2229 | 427.7528 | 445.9691 | 370.0708
1210.2229 | 866.2229 | 446.4261 | 370.4931 | 427.7015 | 1210.2229 | 427.7015 | 446.4261 | 370.4931
1211.2229 | 867.2229 | 446.8824 | 370.9123 | 427.5994 | 1211.2229 | 427.5994 | 446.8824 | 370.9123
1212.2229 | 868.2229 | 447.3465 | 371.3307 | 427.5528 | 1212.2229 | 427.5528 | 447.3465 | 371.3307
1213.2229 | 869.2229 | 447.8363 | 371.7496 | 427.7132 | 1213.2229 | 427.7132 | 447.8363 | 371.7496
1214.2229 | 870.2229 | 448.3097 | 372.1724 | 427.7655 | 1214.2229 | 427.7655 | 448.3097 | 372.1724
1215.2229 | 871.2229 | 448.7963 | 372.5949 | 427.7449 | 1215.2229 | 427.7449 | 448.7963 | 372.5949
1216.2229 | 872.2229 | 449.2807 | 373.01 | 427.7207 | 1216.2229 | 427.7207 | 449.2807 | 373.01
1217.2229 | 873.2229 | 449.7631 | 373.4223 | 427.7906 | 1217.2229 | 427.7906 | 449.7631 | 373.4223
1218.2229 | 874.2229 | 450.2324 | 373.8411 | 427.7557 | 1218.2229 | 427.7557 | 450.2324 | 373.8411
1219.2229 | 875.2229 | 450.6822 | 374.245 | 427.7979 | 1219.2229 | 427.7979 | 450.6822 | 374.245
1220.2229 | 876.2229 | 451.1582 | 374.6574 | 427.6137 | 1220.2229 | 427.6137 | 451.1582 | 374.6574
1221.2229 | 877.2229 | 451.5883 | 375.0706 | 427.5007 | 1221.2229 | 427.5007 | 451.5883 | 375.0706
1222.2229 | 878.2229 | 452.0054 | 375.4832 | 427.4553 | 1222.2229 | 427.4553 | 452.0054 | 375.4832
1223.2229 | 879.2229 | 452.3918 | 375.8792 | 427.4051 | 1223.2229 | 427.4051 | 452.3918 | 375.8792
1224.2229 | 880.2229 | 452.7833 | 376.2973 | 427.3116 | 1224.2229 | 427.3116 | 452.7833 | 376.2973
1225.2229 | 881.2229 | 453.1327 | 376.6947 | 427.4011 | 1225.2229 | 427.4011 | 453.1327 | 376.6947
1226.2229 | 882.2229 | 453.4732 | 377.1017 | 427.4234 | 1226.2229 | 427.4234 | 453.4732 | 377.1017
1227.2229 | 883.2229 | 453.8037 | 377.5104 | 427.5081 | 1227.2229 | 427.5081 | 453.8037 | 377.5104
1228.2229 | 884.2229 | 454.1195 | 377.915 | 427.5862 | 1228.2229 | 427.5862 | 454.1195 | 377.915
1229.2229 | 885.2229 | 454.4324 | 378.3267 | 427.4224 | 1229.2229 | 427.4224 | 454.4324 | 378.3267
1230.2229 | 886.2229 | 454.7306 | 378.7269 | 427.3589 | 1230.2229 | 427.3589 | 454.7306 | 378.7269
1231.2229 | 887.2229 | 455.0188 | 379.1252 | 427.1685 | 1231.2229 | 427.1685 | 455.0188 | 379.1252
1232.2229 | 888.2229 | 455.3257 | 379.5172 | 427.1429 | 1232.2229 | 427.1429 | 455.3257 | 379.5172
1233.2229 | 889.2229 | 455.614 | 379.902 | 427.0465 | 1233.2229 | 427.0465 | 455.614 | 379.902
1234.2229 | 890.2229 | 455.9329 | 380.2922 | 427.0986 | 1234.2229 | 427.0986 | 455.9329 | 380.2922
1235.2229 | 891.2229 | 456.222 | 380.6797 | 427.1177 | 1235.2229 | 427.1177 | 456.222 | 380.6797
1236.2229 | 892.2229 | 456.5108 | 381.0624 | 427.1394 | 1236.2229 | 427.1394 | 456.5108 | 381.0624
1237.2229 | 893.2229 | 456.8348 | 381.4425 | 427.0526 | 1237.2229 | 427.0526 | 456.8348 | 381.4425
1238.2229 | 894.2229 | 457.1412 | 381.822 | 426.9455 | 1238.2229 | 426.9455 | 457.1412 | 381.822
1239.2229 | 895.2229 | 457.4537 | 382.1969 | 426.8657 | 1239.2229 | 426.8657 | 457.4537 | 382.1969
1240.2229 | 896.2229 | 457.7634 | 382.5795 | 426.912 | 1240.2229 | 426.912 | 457.7634 | 382.5795
1241.2229 | 897.2229 | 458.0211 | 382.9561 | 426.9609 | 1241.2229 | 426.9609 | 458.0211 | 382.9561
1242.2229 | 898.2229 | 458.2924 | 383.3369 | 427.0354 | 1242.2229 | 427.0354 | 458.2924 | 383.3369
1243.3323 | 899.3323 | 458.5554 | 383.741 | 426.9967 | 1243.3323 | 426.9967 | 458.5554 | 383.741
1244.551 | 900.551 | 458.8606 | 384.1982 | 426.8885 | 1244.551 | 426.8885 | 458.8606 | 384.1982
1245.2229 | 901.2229 | 459.0101 | 384.4488 | 426.8477 | 1245.2229 | 426.8477 | 459.0101 | 384.4488
1246.2229 | 902.2229 | 459.2332 | 384.8091 | 426.7828 | 1246.2229 | 426.7828 | 459.2332 | 384.8091
1247.2229 | 903.2229 | 459.4658 | 385.1888 | 426.8003 | 1247.2229 | 426.8003 | 459.4658 | 385.1888
1248.2229 | 904.2229 | 459.6909 | 385.545 | 426.8321 | 1248.2229 | 426.8321 | 459.6909 | 385.545
1249.2229 | 905.2229 | 459.9521 | 385.9125 | 426.8744 | 1249.2229 | 426.8744 | 459.9521 | 385.9125
1250.2229 | 906.2229 | 460.2016 | 386.272 | 426.9298 | 1250.2229 | 426.9298 | 460.2016 | 386.272
1251.2229 | 907.2229 | 460.5019 | 386.6345 | 426.9868 | 1251.2229 | 426.9868 | 460.5019 | 386.6345
1252.2229 | 908.2229 | 460.7889 | 386.9971 | 426.9817 | 1252.2229 | 426.9817 | 460.7889 | 386.9971
1253.2229 | 909.2229 | 461.0915 | 387.3664 | 426.9379 | 1253.2229 | 426.9379 | 461.0915 | 387.3664
1254.2229 | 910.2229 | 461.3952 | 387.7273 | 426.8076 | 1254.2229 | 426.8076 | 461.3952 | 387.7273
1255.2229 | 911.2229 | 461.7005 | 388.0995 | 426.8705 | 1255.2229 | 426.8705 | 461.7005 | 388.0995
1256.2229 | 912.2229 | 461.985 | 388.4537 | 426.9582 | 1256.2229 | 426.9582 | 461.985 | 388.4537
1257.2229 | 913.2229 | 462.2659 | 388.8108 | 426.9971 | 1257.2229 | 426.9971 | 462.2659 | 388.8108
1258.2229 | 914.2229 | 462.547 | 389.1676 | 427.033 | 1258.2229 | 427.033 | 462.547 | 389.1676
1259.2229 | 915.2229 | 462.7996 | 389.5153 | 426.9552 | 1259.2229 | 426.9552 | 462.7996 | 389.5153
1260.2229 | 916.2229 | 463.0537 | 389.8662 | 426.8814 | 1260.2229 | 426.8814 | 463.0537 | 389.8662
1261.2229 | 917.2229 | 463.2896 | 390.2085 | 426.7944 | 1261.2229 | 426.7944 | 463.2896 | 390.2085
1262.2229 | 918.2229 | 463.5383 | 390.5627 | 426.7641 | 1262.2229 | 426.7641 | 463.5383 | 390.5627
1263.2229 | 919.2229 | 463.7888 | 390.902 | 426.7653 | 1263.2229 | 426.7653 | 463.7888 | 390.902
1264.2229 | 920.2229 | 464.01 | 391.244 | 426.7609 | 1264.2229 | 426.7609 | 464.01 | 391.244
1265.2229 | 921.2229 | 464.2293 | 391.5893 | 426.7207 | 1265.2229 | 426.7207 | 464.2293 | 391.5893
1266.2854 | 922.2854 | 464.4406 | 391.9484 | 426.5688 | 1266.2854 | 426.5688 | 464.4406 | 391.9484
1267.301 | 923.301 | 464.6421 | 392.3061 | 426.6102 | 1267.301 | 426.6102 | 464.6421 | 392.3061
1268.301 | 924.301 | 464.7946 | 392.6379 | 426.7025 | 1268.301 | 426.7025 | 464.7946 | 392.6379
1269.2542 | 925.2542 | 464.9616 | 392.9572 | 426.7946 | 1269.2542 | 426.7946 | 464.9616 | 392.9572
1270.2385 | 926.2385 | 465.1187 | 393.2893 | 426.7841 | 1270.2385 | 426.7841 | 465.1187 | 393.2893
1271.2698 | 927.2698 | 465.2707 | 393.6275 | 426.7654 | 1271.2698 | 426.7654 | 465.2707 | 393.6275
1272.301 | 928.301 | 465.4107 | 393.9745 | 426.7706 | 1272.301 | 426.7706 | 465.4107 | 393.9745
1273.2542 | 929.2542 | 465.5176 | 394.2826 | 426.7429 | 1273.2542 | 426.7429 | 465.5176 | 394.2826
1274.2229 | 930.2229 | 465.6642 | 394.6034 | 426.8018 | 1274.2229 | 426.8018 | 465.6642 | 394.6034
1275.2385 | 931.2385 | 465.8018 | 394.9364 | 426.9359 | 1275.2385 | 426.9359 | 465.8018 | 394.9364
1276.2229 | 932.2229 | 465.9473 | 395.2629 | 426.9195 | 1276.2229 | 426.9195 | 465.9473 | 395.2629
1277.2229 | 933.2229 | 466.1031 | 395.586 | 426.8165 | 1277.2229 | 426.8165 | 466.1031 | 395.586
1278.2229 | 934.2229 | 466.2833 | 395.9139 | 426.7179 | 1278.2229 | 426.7179 | 466.2833 | 395.9139
1279.2229 | 935.2229 | 466.4662 | 396.225 | 426.7866 | 1279.2229 | 426.7866 | 466.4662 | 396.225
1280.2229 | 936.2229 | 466.6096 | 396.5568 | 426.8896 | 1280.2229 | 426.8896 | 466.6096 | 396.5568
1281.2229 | 937.2229 | 466.815 | 396.8706 | 427.0178 | 1281.2229 | 427.0178 | 466.815 | 396.8706
1282.2229 | 938.2229 | 466.9764 | 397.1994 | 427.0238 | 1282.2229 | 427.0238 | 466.9764 | 397.1994
1283.2229 | 939.2229 | 467.1299 | 397.521 | 426.822 | 1283.2229 | 426.822 | 467.1299 | 397.521
1284.2229 | 940.2229 | 467.2996 | 397.8384 | 426.8184 | 1284.2229 | 426.8184 | 467.2996 | 397.8384
1285.2229 | 941.2229 | 467.4587 | 398.1553 | 426.8241 | 1285.2229 | 426.8241 | 467.4587 | 398.1553
1286.2229 | 942.2229 | 467.6134 | 398.4727 | 426.7761 | 1286.2229 | 426.7761 | 467.6134 | 398.4727
1287.2229 | 943.2229 | 467.7793 | 398.7911 | 426.6696 | 1287.2229 | 426.6696 | 467.7793 | 398.7911
1288.2229 | 944.2229 | 467.9481 | 399.1064 | 426.5569 | 1288.2229 | 426.5569 | 467.9481 | 399.1064
1289.2229 | 945.2229 | 468.1175 | 399.4193 | 426.5666 | 1289.2229 | 426.5666 | 468.1175 | 399.4193
1290.2229 | 946.2229 | 468.2994 | 399.7417 | 426.6242 | 1290.2229 | 426.6242 | 468.2994 | 399.7417
1291.2229 | 947.2229 | 468.5068 | 400.052 | 426.6113 | 1291.2229 | 426.6113 | 468.5068 | 400.052
1292.2229 | 948.2229 | 468.6945 | 400.3711 | 426.5728 | 1292.2229 | 426.5728 | 468.6945 | 400.3711
1293.2229 | 949.2229 | 468.8827 | 400.6818 | 426.5166 | 1293.2229 | 426.5166 | 468.8827 | 400.6818
1294.2229 | 950.2229 | 469.0001 | 400.9918 | 426.4247 | 1294.2229 | 426.4247 | 469.0001 | 400.9918
1295.2229 | 951.2229 | 469.1865 | 401.3096 | 426.4642 | 1295.2229 | 426.4642 | 469.1865 | 401.3096
1296.2229 | 952.2229 | 469.3727 | 401.6153 | 426.5822 | 1296.2229 | 426.5822 | 469.3727 | 401.6153
1297.2229 | 953.2229 | 469.5975 | 401.9516 | 426.4215 | 1297.2229 | 426.4215 | 469.5975 | 401.9516
1298.2229 | 954.2229 | 469.8214 | 402.274 | 426.2852 | 1298.2229 | 426.2852 | 469.8214 | 402.274
1299.2229 | 955.2229 | 470.0782 | 402.5826 | 426.2594 | 1299.2229 | 426.2594 | 470.0782 | 402.5826
1300.3167 | 956.3167 | 470.3244 | 402.9236 | 426.2584 | 1300.3167 | 426.2584 | 470.3244 | 402.9236
1301.2698 | 957.2698 | 470.5582 | 403.2164 | 426.2516 | 1301.2698 | 426.2516 | 470.5582 | 403.2164
1302.2229 | 958.2229 | 470.7134 | 403.52 | 426.1155 | 1302.2229 | 426.1155 | 470.7134 | 403.52
1303.2229 | 959.2229 | 470.9457 | 403.8342 | 426.0959 | 1303.2229 | 426.0959 | 470.9457 | 403.8342
1304.2229 | 960.2229 | 471.1505 | 404.1508 | 426.0501 | 1304.2229 | 426.0501 | 471.1505 | 404.1508
1305.2229 | 961.2229 | 471.3469 | 404.464 | 426.1406 | 1305.2229 | 426.1406 | 471.3469 | 404.464
1306.2229 | 962.2229 | 471.5363 | 404.7659 | 426.1228 | 1306.2229 | 426.1228 | 471.5363 | 404.7659
1307.2229 | 963.2229 | 471.6853 | 405.0736 | 426.0374 | 1307.2229 | 426.0374 | 471.6853 | 405.0736
1308.2229 | 964.2229 | 471.815 | 405.3772 | 425.9834 | 1308.2229 | 425.9834 | 471.815 | 405.3772
1309.2229 | 965.2229 | 471.9409 | 405.6818 | 426.051 | 1309.2229 | 426.051 | 471.9409 | 405.6818
1310.2229 | 966.2229 | 472.0517 | 405.9866 | 425.977 | 1310.2229 | 425.977 | 472.0517 | 405.9866
1311.2229 | 967.2229 | 472.1798 | 406.2846 | 425.9217 | 1311.2229 | 425.9217 | 472.1798 | 406.2846
1312.2229 | 968.2229 | 472.3121 | 406.5966 | 425.973 | 1312.2229 | 425.973 | 472.3121 | 406.5966
1313.2229 | 969.2229 | 472.4628 | 406.8954 | 426.0689 | 1313.2229 | 426.0689 | 472.4628 | 406.8954
1314.2229 | 970.2229 | 472.5929 | 407.1979 | 426.0383 | 1314.2229 | 426.0383 | 472.5929 | 407.1979
1315.2229 | 971.2229 | 472.7354 | 407.497 | 425.876 | 1315.2229 | 425.876 | 472.7354 | 407.497
1316.2229 | 972.2229 | 472.8844 | 407.8039 | 425.7097 | 1316.2229 | 425.7097 | 472.8844 | 407.8039
1317.2229 | 973.2229 | 473.0292 | 408.1031 | 425.7533 | 1317.2229 | 425.7533 | 473.0292 | 408.1031
1318.2229 | 974.2229 | 473.158 | 408.401 | 425.7954 | 1318.2229 | 425.7954 | 473.158 | 408.401
1319.2229 | 975.2229 | 473.2837 | 408.6977 | 425.6937 | 1319.2229 | 425.6937 | 473.2837 | 408.6977
1320.2229 | 976.2229 | 473.4074 | 409.0046 | 425.5732 | 1320.2229 | 425.5732 | 473.4074 | 409.0046
1321.2229 | 977.2229 | 473.4766 | 409.3012 | 425.5793 | 1321.2229 | 425.5793 | 473.4766 | 409.3012
1322.2229 | 978.2229 | 473.53 | 409.6036 | 425.6347 | 1322.2229 | 425.6347 | 473.53 | 409.6036
1323.2229 | 979.2229 | 473.5693 | 409.8829 | 425.7349 | 1323.2229 | 425.7349 | 473.5693 | 409.8829
1324.2229 | 980.2229 | 473.6063 | 410.1761 | 425.876 | 1324.2229 | 425.876 | 473.6063 | 410.1761
1325.2229 | 981.2229 | 473.636 | 410.4674 | 425.8371 | 1325.2229 | 425.8371 | 473.636 | 410.4674
1326.2229 | 982.2229 | 473.6758 | 410.757 | 425.9343 | 1326.2229 | 425.9343 | 473.6758 | 410.757
1327.2229 | 983.2229 | 473.7218 | 411.0476 | 425.7956 | 1327.2229 | 425.7956 | 473.7218 | 411.0476
1328.2229 | 984.2229 | 473.7713 | 411.3418 | 425.7183 | 1328.2229 | 425.7183 | 473.7713 | 411.3418
1329.2229 | 985.2229 | 473.8377 | 411.626 | 425.7861 | 1329.2229 | 425.7861 | 473.8377 | 411.626
1330.2229 | 986.2229 | 473.8877 | 411.9254 | 425.83 | 1330.2229 | 425.83 | 473.8877 | 411.9254
1331.2229 | 987.2229 | 473.9233 | 412.2262 | 425.9234 | 1331.2229 | 425.9234 | 473.9233 | 412.2262
1332.2229 | 988.2229 | 473.7759 | 412.5314 | 425.9486 | 1332.2229 | 425.9486 | 473.7759 | 412.5314
1333.2229 | 989.2229 | 473.757 | 412.8377 | 425.9066 | 1333.2229 | 425.9066 | 473.757 | 412.8377
1334.2229 | 990.2229 | 473.825 | 413.1518 | 426.0262 | 1334.2229 | 426.0262 | 473.825 | 413.1518
1335.2229 | 991.2229 | 473.9088 | 413.4575 | 425.9488 | 1335.2229 | 425.9488 | 473.9088 | 413.4575
1336.2229 | 992.2229 | 474.0261 | 413.7656 | 426.0066 | 1336.2229 | 426.0066 | 474.0261 | 413.7656
1337.2229 | 993.2229 | 474.1358 | 414.0687 | 426.0632 | 1337.2229 | 426.0632 | 474.1358 | 414.0687
1338.2229 | 994.2229 | 474.2622 | 414.3746 | 425.9712 | 1338.2229 | 425.9712 | 474.2622 | 414.3746
1339.2229 | 995.2229 | 474.4075 | 414.6801 | 425.8635 | 1339.2229 | 425.8635 | 474.4075 | 414.6801
1340.2229 | 996.2229 | 474.5482 | 414.9887 | 425.902 | 1340.2229 | 425.902 | 474.5482 | 414.9887
1341.2229 | 997.2229 | 474.6984 | 415.2932 | 425.9904 | 1341.2229 | 425.9904 | 474.6984 | 415.2932
1342.2229 | 998.2229 | 474.8474 | 415.6027 | 425.9613 | 1342.2229 | 425.9613 | 474.8474 | 415.6027
1343.2229 | 999.2229 | 475.0181 | 415.9237 | 425.969 | 1343.2229 | 425.969 | 475.0181 | 415.9237
1344.2229 | 1000.2229 | 475.1612 | 416.2316 | 425.9005 | 1344.2229 | 425.9005 | 475.1612 | 416.2316
1345.2229 | 1001.2229 | 475.2901 | 416.534 | 425.7987 | 1345.2229 | 425.7987 | 475.2901 | 416.534
1346.2229 | 1002.2229 | 475.4278 | 416.8382 | 425.9395 | 1346.2229 | 425.9395 | 475.4278 | 416.8382
1347.2229 | 1003.2229 | 475.5367 | 417.1325 | 425.9878 | 1347.2229 | 425.9878 | 475.5367 | 417.1325
1348.2229 | 1004.2229 | 475.6324 | 417.4267 | 425.9347 | 1348.2229 | 425.9347 | 475.6324 | 417.4267
1349.2229 | 1005.2229 | 475.7332 | 417.7203 | 426.0604 | 1349.2229 | 426.0604 | 475.7332 | 417.7203
1350.2229 | 1006.2229 | 475.8315 | 418.0029 | 426.411 | 1350.2229 | 426.411 | 475.8315 | 418.0029
1351.2229 | 1007.2229 | 475.9329 | 418.2805 | 426.5255 | 1351.2229 | 426.5255 | 475.9329 | 418.2805
1352.2229 | 1008.2229 | 476.0355 | 418.552 | 426.5415 | 1352.2229 | 426.5415 | 476.0355 | 418.552
1353.2229 | 1009.2229 | 476.1197 | 418.8236 | 426.524 | 1353.2229 | 426.524 | 476.1197 | 418.8236
1354.2229 | 1010.2229 | 476.1921 | 419.0837 | 426.546 | 1354.2229 | 426.546 | 476.1921 | 419.0837
1355.2229 | 1011.2229 | 476.2183 | 419.3551 | 426.6923 | 1355.2229 | 426.6923 | 476.2183 | 419.3551
1356.2229 | 1012.2229 | 476.2184 | 419.6161 | 426.9348 | 1356.2229 | 426.9348 | 476.2184 | 419.6161
1357.2229 | 1013.2229 | 476.2288 | 419.8952 | 427.0115 | 1357.2229 | 427.0115 | 476.2288 | 419.8952
1358.2229 | 1014.2229 | 476.2162 | 420.1671 | 427.096 | 1358.2229 | 427.096 | 476.2162 | 420.1671
1359.2229 | 1015.2229 | 476.135 | 420.4301 | 427.1681 | 1359.2229 | 427.1681 | 476.135 | 420.4301
1360.3948 | 1016.3948 | 476.0709 | 420.7422 | 427.3513 | 1360.3948 | 427.3513 | 476.0709 | 420.7422
1361.2229 | 1017.2229 | 476.0337 | 420.9646 | 427.4194 | 1361.2229 | 427.4194 | 476.0337 | 420.9646
1362.2229 | 1018.2229 | 476.0154 | 421.2329 | 427.4182 | 1362.2229 | 427.4182 | 476.0154 | 421.2329
1363.2229 | 1019.2229 | 475.9691 | 421.5008 | 427.2656 | 1363.2229 | 427.2656 | 475.9691 | 421.5008
1364.2229 | 1020.2229 | 475.9545 | 421.7801 | 427.1929 | 1364.2229 | 427.1929 | 475.9545 | 421.7801
1365.2229 | 1021.2229 | 475.9114 | 422.0578 | 427.0921 | 1365.2229 | 427.0921 | 475.9114 | 422.0578
1366.2229 | 1022.2229 | 475.895 | 422.3369 | 427.144 | 1366.2229 | 427.144 | 475.895 | 422.3369
1367.2229 | 1023.2229 | 475.8715 | 422.6222 | 427.1972 | 1367.2229 | 427.1972 | 475.8715 | 422.6222
1368.2229 | 1024.2229 | 475.8829 | 422.9079 | 427.2245 | 1368.2229 | 427.2245 | 475.8829 | 422.9079
1369.2229 | 1025.2229 | 475.8845 | 423.1966 | 427.2324 | 1369.2229 | 427.2324 | 475.8845 | 423.1966
1370.2229 | 1026.2229 | 475.8961 | 423.4618 | 427.2681 | 1370.2229 | 427.2681 | 475.8961 | 423.4618
1371.2229 | 1027.2229 | 475.9468 | 423.732 | 427.2795 | 1371.2229 | 427.2795 | 475.9468 | 423.732
1372.2229 | 1028.2229 | 475.9678 | 423.9984 | 427.0545 | 1372.2229 | 427.0545 | 475.9678 | 423.9984
1373.2229 | 1029.2229 | 476.048 | 424.2662 | 426.7467 | 1373.2229 | 426.7467 | 476.048 | 424.2662
1374.2229 | 1030.2229 | 476.1314 | 424.5216 | 426.7282 | 1374.2229 | 426.7282 | 476.1314 | 424.5216
1375.2229 | 1031.2229 | 476.1805 | 424.7804 | 426.7529 | 1375.2229 | 426.7529 | 476.1805 | 424.7804
1376.2229 | 1032.2229 | 476.2367 | 425.0449 | 426.7088 | 1376.2229 | 426.7088 | 476.2367 | 425.0449
1377.2229 | 1033.2229 | 476.2739 | 425.2892 | 426.7625 | 1377.2229 | 426.7625 | 476.2739 | 425.2892
1378.2229 | 1034.2229 | 476.288 | 425.5444 | 426.774 | 1378.2229 | 426.774 | 476.288 | 425.5444
1379.2229 | 1035.2229 | 476.2796 | 425.7784 | 426.7471 | 1379.2229 | 426.7471 | 476.2796 | 425.7784
1380.2229 | 1036.2229 | 476.2782 | 426.0277 | 426.6404 | 1380.2229 | 426.6404 | 476.2782 | 426.0277
1381.2229 | 1037.2229 | 476.277 | 426.2644 | 426.3632 | 1381.2229 | 426.3632 | 476.277 | 426.2644
1382.2229 | 1038.2229 | 476.2952 | 426.5048 | 426.2628 | 1382.2229 | 426.2628 | 476.2952 | 426.5048
1383.2229 | 1039.2229 | 476.3454 | 426.7431 | 426.226 | 1383.2229 | 426.226 | 476.3454 | 426.7431
1384.2229 | 1040.2229 | 476.4077 | 426.9892 | 426.2782 | 1384.2229 | 426.2782 | 476.4077 | 426.9892
1385.2229 | 1041.2229 | 476.4804 | 427.2239 | 426.2926 | 1385.2229 | 426.2926 | 476.4804 | 427.2239
1386.2229 | 1042.2229 | 476.5704 | 427.455 | 426.1665 | 1386.2229 | 426.1665 | 476.5704 | 427.455
1387.2229 | 1043.2229 | 476.6605 | 427.6817 | 426.0837 | 1387.2229 | 426.0837 | 476.6605 | 427.6817
1388.2229 | 1044.2229 | 476.7577 | 427.9 | 426.0378 | 1388.2229 | 426.0378 | 476.7577 | 427.9
1389.2229 | 1045.2229 | 476.8555 | 428.11 | 425.9783 | 1389.2229 | 425.9783 | 476.8555 | 428.11
1390.2229 | 1046.2229 | 476.9263 | 428.3113 | 426.0498 | 1390.2229 | 426.0498 | 476.9263 | 428.3113
1391.2229 | 1047.2229 | 477.005 | 428.5263 | 426.071 | 1391.2229 | 426.071 | 477.005 | 428.5263
1392.2229 | 1048.2229 | 477.1097 | 428.7271 | 426.0331 | 1392.2229 | 426.0331 | 477.1097 | 428.7271
1393.2229 | 1049.2229 | 477.2406 | 428.9229 | 426.0925 | 1393.2229 | 426.0925 | 477.2406 | 428.9229
1394.2229 | 1050.2229 | 477.3512 | 429.1199 | 426.2273 | 1394.2229 | 426.2273 | 477.3512 | 429.1199
1395.2229 | 1051.2229 | 477.4869 | 429.307 | 426.3501 | 1395.2229 | 426.3501 | 477.4869 | 429.307
1396.2229 | 1052.2229 | 477.6383 | 429.4986 | 426.3918 | 1396.2229 | 426.3918 | 477.6383 | 429.4986
1397.2229 | 1053.2229 | 477.7584 | 429.6711 | 426.2888 | 1397.2229 | 426.2888 | 477.7584 | 429.6711
1398.2229 | 1054.2229 | 477.917 | 429.8559 | 426.0914 | 1398.2229 | 426.0914 | 477.917 | 429.8559
1399.2229 | 1055.2229 | 478.0615 | 430.0451 | 425.9695 | 1399.2229 | 425.9695 | 478.0615 | 430.0451
1400.3635 | 1056.3635 | 478.2032 | 430.2595 | 426.1315 | 1400.3635 | 426.1315 | 478.2032 | 430.2595
1401.2542 | 1057.2542 | 478.3378 | 430.4189 | 426.2321 | 1401.2542 | 426.2321 | 478.3378 | 430.4189
1402.3323 | 1058.3323 | 478.4966 | 430.631 | 426.1626 | 1402.3323 | 426.1626 | 478.4966 | 430.631
1403.2542 | 1059.2542 | 478.6289 | 430.8076 | 426.0487 | 1403.2542 | 426.0487 | 478.6289 | 430.8076
1404.4417 | 1060.4417 | 478.7689 | 431.041 | 426.0441 | 1404.4417 | 426.0441 | 478.7689 | 431.041
1405.4573 | 1061.4573 | 478.8854 | 431.2399 | 426.3248 | 1405.4573 | 426.3248 | 478.8854 | 431.2399
1406.301 | 1062.301 | 478.9541 | 431.414 | 426.3959 | 1406.301 | 426.3959 | 478.9541 | 431.414
1407.2229 | 1063.2229 | 479.0234 | 431.597 | 426.4751 | 1407.2229 | 426.4751 | 479.0234 | 431.597
1408.2698 | 1064.2698 | 479.0455 | 431.802 | 426.6466 | 1408.2698 | 426.6466 | 479.0455 | 431.802
1409.2385 | 1065.2385 | 479.0461 | 431.9949 | 426.7357 | 1409.2385 | 426.7357 | 479.0461 | 431.9949
1410.3323 | 1066.3323 | 478.9874 | 432.2127 | 426.8602 | 1410.3323 | 426.8602 | 478.9874 | 432.2127
1411.2542 | 1067.2542 | 478.9415 | 432.3889 | 426.9033 | 1411.2542 | 426.9033 | 478.9415 | 432.3889
1412.3167 | 1068.3167 | 478.8968 | 432.5976 | 426.805 | 1412.3167 | 426.805 | 478.8968 | 432.5976
1413.2542 | 1069.2542 | 478.8275 | 432.7904 | 426.7185 | 1413.2542 | 426.7185 | 478.8275 | 432.7904
1414.2385 | 1070.2385 | 478.7802 | 432.99 | 426.7321 | 1414.2385 | 426.7321 | 478.7802 | 432.99
1415.2229 | 1071.2229 | 478.7436 | 433.1932 | 426.7084 | 1415.2229 | 426.7084 | 478.7436 | 433.1932
1416.2229 | 1072.2229 | 478.7341 | 433.3938 | 426.7091 | 1416.2229 | 426.7091 | 478.7341 | 433.3938
1417.2229 | 1073.2229 | 478.7235 | 433.5919 | 426.8182 | 1417.2229 | 426.8182 | 478.7235 | 433.5919
1418.2229 | 1074.2229 | 478.7371 | 433.7755 | 426.8608 | 1418.2229 | 426.8608 | 478.7371 | 433.7755
1419.2229 | 1075.2229 | 478.7158 | 433.9798 | 426.9588 | 1419.2229 | 426.9588 | 478.7158 | 433.9798
1420.2229 | 1076.2229 | 478.7257 | 434.1674 | 427.0229 | 1420.2229 | 427.0229 | 478.7257 | 434.1674
1421.2229 | 1077.2229 | 478.7629 | 434.3623 | 427.1988 | 1421.2229 | 427.1988 | 478.7629 | 434.3623
1422.2229 | 1078.2229 | 478.8049 | 434.5447 | 427.2584 | 1422.2229 | 427.2584 | 478.8049 | 434.5447
1423.2229 | 1079.2229 | 478.8419 | 434.7356 | 427.245 | 1423.2229 | 427.245 | 478.8419 | 434.7356
1424.2229 | 1080.2229 | 478.8928 | 434.9174 | 427.1427 | 1424.2229 | 427.1427 | 478.8928 | 434.9174
1425.2229 | 1081.2229 | 478.9435 | 435.1024 | 427.0958 | 1425.2229 | 427.0958 | 478.9435 | 435.1024
1426.2229 | 1082.2229 | 479.0081 | 435.2924 | 427.0845 | 1426.2229 | 427.0845 | 479.0081 | 435.2924
1427.2229 | 1083.2229 | 479.0659 | 435.4719 | 427.057 | 1427.2229 | 427.057 | 479.0659 | 435.4719
1428.2229 | 1084.2229 | 479.1537 | 435.6471 | 426.918 | 1428.2229 | 426.918 | 479.1537 | 435.6471
1429.2229 | 1085.2229 | 479.2729 | 435.8225 | 426.8782 | 1429.2229 | 426.8782 | 479.2729 | 435.8225
1430.2229 | 1086.2229 | 479.3764 | 436.0052 | 426.9349 | 1430.2229 | 426.9349 | 479.3764 | 436.0052
1431.2229 | 1087.2229 | 479.5182 | 436.1889 | 427.0071 | 1431.2229 | 427.0071 | 479.5182 | 436.1889
1432.2229 | 1088.2229 | 479.659 | 436.3836 | 427.0781 | 1432.2229 | 427.0781 | 479.659 | 436.3836
1433.2229 | 1089.2229 | 479.7973 | 436.5817 | 426.9679 | 1433.2229 | 426.9679 | 479.7973 | 436.5817
1434.2229 | 1090.2229 | 479.9531 | 436.7811 | 426.9307 | 1434.2229 | 426.9307 | 479.9531 | 436.7811
1435.2229 | 1091.2229 | 480.1027 | 436.9959 | 426.9167 | 1435.2229 | 426.9167 | 480.1027 | 436.9959
1436.2229 | 1092.2229 | 480.2633 | 437.2255 | 426.8086 | 1436.2229 | 426.8086 | 480.2633 | 437.2255
1437.2229 | 1093.2229 | 480.4003 | 437.445 | 426.7459 | 1437.2229 | 426.7459 | 480.4003 | 437.445
1438.2229 | 1094.2229 | 480.5695 | 437.6721 | 426.6461 | 1438.2229 | 426.6461 | 480.5695 | 437.6721
1439.2229 | 1095.2229 | 480.7369 | 437.8976 | 426.5105 | 1439.2229 | 426.5105 | 480.7369 | 437.8976
1440.2229 | 1096.2229 | 480.8881 | 438.1205 | 426.4145 | 1440.2229 | 426.4145 | 480.8881 | 438.1205
1441.2229 | 1097.2229 | 481.0402 | 438.3389 | 426.4101 | 1441.2229 | 426.4101 | 481.0402 | 438.3389
1442.2229 | 1098.2229 | 481.2374 | 438.5596 | 426.5593 | 1442.2229 | 426.5593 | 481.2374 | 438.5596
1443.2229 | 1099.2229 | 481.4133 | 438.7903 | 426.5948 | 1443.2229 | 426.5948 | 481.4133 | 438.7903
1444.2229 | 1100.2229 | 481.6225 | 439.0201 | 426.4369 | 1444.2229 | 426.4369 | 481.6225 | 439.0201
1445.2229 | 1101.2229 | 481.8249 | 439.2569 | 426.358 | 1445.2229 | 426.358 | 481.8249 | 439.2569
1446.2229 | 1102.2229 | 482.0203 | 439.4879 | 426.1979 | 1446.2229 | 426.1979 | 482.0203 | 439.4879
1447.2229 | 1103.2229 | 482.2507 | 439.7351 | 426.0698 | 1447.2229 | 426.0698 | 482.2507 | 439.7351
1448.2229 | 1104.2229 | 482.4805 | 439.9842 | 426.1151 | 1448.2229 | 426.1151 | 482.4805 | 439.9842
1449.2229 | 1105.2229 | 482.7297 | 440.2299 | 426.1939 | 1449.2229 | 426.1939 | 482.7297 | 440.2299
1450.2229 | 1106.2229 | 482.9323 | 440.4817 | 426.1477 | 1450.2229 | 426.1477 | 482.9323 | 440.4817
1451.2229 | 1107.2229 | 483.1415 | 440.7349 | 426.2086 | 1451.2229 | 426.2086 | 483.1415 | 440.7349
1452.2229 | 1108.2229 | 483.3305 | 440.9912 | 426.1886 | 1452.2229 | 426.1886 | 483.3305 | 440.9912
1453.2229 | 1109.2229 | 483.5265 | 441.2405 | 426.0959 | 1453.2229 | 426.0959 | 483.5265 | 441.2405
1454.2229 | 1110.2229 | 483.7208 | 441.4841 | 426.0794 | 1454.2229 | 426.0794 | 483.7208 | 441.4841
1455.2229 | 1111.2229 | 483.9241 | 441.7319 | 426.1792 | 1455.2229 | 426.1792 | 483.9241 | 441.7319
1456.2229 | 1112.2229 | 484.1131 | 441.9834 | 426.1553 | 1456.2229 | 426.1553 | 484.1131 | 441.9834
1457.2229 | 1113.2229 | 484.32 | 442.2308 | 426.1562 | 1457.2229 | 426.1562 | 484.32 | 442.2308
1458.2229 | 1114.2229 | 484.5615 | 442.4762 | 426.2124 | 1458.2229 | 426.2124 | 484.5615 | 442.4762
1459.2229 | 1115.2229 | 484.781 | 442.7257 | 426.2517 | 1459.2229 | 426.2517 | 484.781 | 442.7257
1460.2229 | 1116.2229 | 484.9845 | 442.954 | 426.3169 | 1460.2229 | 426.3169 | 484.9845 | 442.954
1461.2229 | 1117.2229 | 485.2194 | 443.1894 | 426.4023 | 1461.2229 | 426.4023 | 485.2194 | 443.1894
1462.2229 | 1118.2229 | 485.4551 | 443.4383 | 426.4027 | 1462.2229 | 426.4027 | 485.4551 | 443.4383
1463.2229 | 1119.2229 | 485.7117 | 443.6726 | 426.3849 | 1463.2229 | 426.3849 | 485.7117 | 443.6726
1464.2229 | 1120.2229 | 485.9349 | 443.9072 | 426.4381 | 1464.2229 | 426.4381 | 485.9349 | 443.9072
1465.2229 | 1121.2229 | 486.1895 | 444.1187 | 426.4995 | 1465.2229 | 426.4995 | 486.1895 | 444.1187
1466.2229 | 1122.2229 | 486.4251 | 444.3439 | 426.483 | 1466.2229 | 426.483 | 486.4251 | 444.3439
1467.2229 | 1123.2229 | 486.6428 | 444.5685 | 426.344 | 1467.2229 | 426.344 | 486.6428 | 444.5685
1468.2229 | 1124.2229 | 486.8531 | 444.7958 | 426.2823 | 1468.2229 | 426.2823 | 486.8531 | 444.7958
1469.2229 | 1125.2229 | 487.0608 | 445.0298 | 426.2924 | 1469.2229 | 426.2924 | 487.0608 | 445.0298
1470.2229 | 1126.2229 | 487.2738 | 445.2438 | 426.2772 | 1470.2229 | 426.2772 | 487.2738 | 445.2438
1471.2229 | 1127.2229 | 487.4715 | 445.4717 | 426.3032 | 1471.2229 | 426.3032 | 487.4715 | 445.4717
1472.2229 | 1128.2229 | 487.643 | 445.6979 | 426.3016 | 1472.2229 | 426.3016 | 487.643 | 445.6979
1473.2229 | 1129.2229 | 487.8374 | 445.9162 | 426.3443 | 1473.2229 | 426.3443 | 487.8374 | 445.9162
1474.2229 | 1130.2229 | 488.004 | 446.1316 | 426.3256 | 1474.2229 | 426.3256 | 488.004 | 446.1316
1475.2229 | 1131.2229 | 488.1998 | 446.3486 | 426.2299 | 1475.2229 | 426.2299 | 488.1998 | 446.3486
1476.2229 | 1132.2229 | 488.3624 | 446.5708 | 426.1731 | 1476.2229 | 426.1731 | 488.3624 | 446.5708
1477.2229 | 1133.2229 | 488.5621 | 446.7755 | 426.2148 | 1477.2229 | 426.2148 | 488.5621 | 446.7755
1478.2229 | 1134.2229 | 488.7259 | 446.989 | 426.1901 | 1478.2229 | 426.1901 | 488.7259 | 446.989
1479.2229 | 1135.2229 | 488.9033 | 447.1843 | 426.2054 | 1479.2229 | 426.2054 | 488.9033 | 447.1843
1480.2229 | 1136.2229 | 489.0366 | 447.3782 | 426.17 | 1480.2229 | 426.17 | 489.0366 | 447.3782
1481.2229 | 1137.2229 | 489.1539 | 447.5725 | 426.1129 | 1481.2229 | 426.1129 | 489.1539 | 447.5725
1482.2229 | 1138.2229 | 489.2999 | 447.7669 | 426.2231 | 1482.2229 | 426.2231 | 489.2999 | 447.7669
1483.2229 | 1139.2229 | 489.4325 | 447.9689 | 426.2906 | 1483.2229 | 426.2906 | 489.4325 | 447.9689
1484.2229 | 1140.2229 | 489.5426 | 448.1818 | 426.3989 | 1484.2229 | 426.3989 | 489.5426 | 448.1818
1485.2229 | 1141.2229 | 489.598 | 448.3939 | 426.5379 | 1485.2229 | 426.5379 | 489.598 | 448.3939
1486.2229 | 1142.2229 | 489.6576 | 448.607 | 426.63 | 1486.2229 | 426.63 | 489.6576 | 448.607
1487.2229 | 1143.2229 | 489.6943 | 448.8259 | 426.7353 | 1487.2229 | 426.7353 | 489.6943 | 448.8259
1488.2229 | 1144.2229 | 489.7422 | 449.0359 | 426.8544 | 1488.2229 | 426.8544 | 489.7422 | 449.0359
1489.2229 | 1145.2229 | 489.7791 | 449.2578 | 426.8758 | 1489.2229 | 426.8758 | 489.7791 | 449.2578
1490.2229 | 1146.2229 | 489.8453 | 449.4744 | 427.0206 | 1490.2229 | 427.0206 | 489.8453 | 449.4744
1491.2229 | 1147.2229 | 489.9605 | 449.6982 | 427.0947 | 1491.2229 | 427.0947 | 489.9605 | 449.6982
1492.2229 | 1148.2229 | 490.0913 | 449.9195 | 427.0395 | 1492.2229 | 427.0395 | 490.0913 | 449.9195
1493.2229 | 1149.2229 | 490.2411 | 450.1574 | 426.9648 | 1493.2229 | 426.9648 | 490.2411 | 450.1574
1494.2229 | 1150.2229 | 490.3927 | 450.3701 | 426.9594 | 1494.2229 | 426.9594 | 490.3927 | 450.3701
1495.2229 | 1151.2229 | 490.5571 | 450.5844 | 426.8808 | 1495.2229 | 426.8808 | 490.5571 | 450.5844
1496.2229 | 1152.2229 | 490.7137 | 450.8085 | 426.7625 | 1496.2229 | 426.7625 | 490.7137 | 450.8085
1497.2229 | 1153.2229 | 490.8771 | 451.0241 | 426.8309 | 1497.2229 | 426.8309 | 490.8771 | 451.0241
1498.2229 | 1154.2229 | 491.035 | 451.2261 | 426.813 | 1498.2229 | 426.813 | 491.035 | 451.2261
1499.2229 | 1155.2229 | 491.1398 | 451.4055 | 426.8356 | 1499.2229 | 426.8356 | 491.1398 | 451.4055
1500.2229 | 1156.2229 | 491.2259 | 451.6027 | 426.8021 | 1500.2229 | 426.8021 | 491.2259 | 451.6027
1501.2229 | 1157.2229 | 491.3029 | 451.7921 | 426.7796 | 1501.2229 | 426.7796 | 491.3029 | 451.7921
1502.2229 | 1158.2229 | 491.3582 | 451.9776 | 426.8063 | 1502.2229 | 426.8063 | 491.3582 | 451.9776
1503.2229 | 1159.2229 | 491.3888 | 452.1674 | 426.8618 | 1503.2229 | 426.8618 | 491.3888 | 452.1674
1504.2854 | 1160.2854 | 491.4049 | 452.3639 | 426.8304 | 1504.2854 | 426.8304 | 491.4049 | 452.3639
1505.2229 | 1161.2229 | 491.5017 | 452.5389 | 426.8015 | 1505.2229 | 426.8015 | 491.5017 | 452.5389
1506.3323 | 1162.3323 | 491.5813 | 452.7679 | 426.7086 | 1506.3323 | 426.7086 | 491.5813 | 452.7679
1507.2542 | 1163.2542 | 491.6567 | 452.9284 | 426.7529 | 1507.2542 | 426.7529 | 491.6567 | 452.9284
1508.3167 | 1164.3167 | 491.7447 | 453.1201 | 426.8453 | 1508.3167 | 426.8453 | 491.7447 | 453.1201
1509.2854 | 1165.2854 | 491.8951 | 453.272 | 426.7476 | 1509.2854 | 426.7476 | 491.8951 | 453.272
1510.2542 | 1166.2542 | 492.0168 | 453.411 | 426.7413 | 1510.2542 | 426.7413 | 492.0168 | 453.411
1511.2385 | 1167.2385 | 492.1504 | 453.5471 | 426.7535 | 1511.2385 | 426.7535 | 492.1504 | 453.5471
1512.2385 | 1168.2385 | 492.2671 | 453.6753 | 426.7367 | 1512.2385 | 426.7367 | 492.2671 | 453.6753
1513.2229 | 1169.2229 | 492.3689 | 453.7824 | 426.7153 | 1513.2229 | 426.7153 | 492.3689 | 453.7824
1514.2229 | 1170.2229 | 492.4729 | 453.8837 | 426.6438 | 1514.2229 | 426.6438 | 492.4729 | 453.8837
1515.2229 | 1171.2229 | 492.58 | 453.9591 | 426.5117 | 1515.2229 | 426.5117 | 492.58 | 453.9591
1516.2229 | 1172.2229 | 492.6734 | 454.0334 | 426.3624 | 1516.2229 | 426.3624 | 492.6734 | 454.0334
1517.2229 | 1173.2229 | 492.81 | 454.0965 | 426.3812 | 1517.2229 | 426.3812 | 492.81 | 454.0965
1518.2229 | 1174.2229 | 492.8854 | 454.1475 | 426.4862 | 1518.2229 | 426.4862 | 492.8854 | 454.1475
1519.2229 | 1175.2229 | 493.021 | 454.1973 | 426.3747 | 1519.2229 | 426.3747 | 493.021 | 454.1973
1520.2229 | 1176.2229 | 493.138 | 454.2386 | 426.2201 | 1520.2229 | 426.2201 | 493.138 | 454.2386
1521.2229 | 1177.2229 | 493.2654 | 454.2853 | 425.9759 | 1521.2229 | 425.9759 | 493.2654 | 454.2853
1522.2229 | 1178.2229 | 493.3318 | 454.3048 | 426.0485 | 1522.2229 | 426.0485 | 493.3318 | 454.3048
1523.2229 | 1179.2229 | 493.4861 | 454.3056 | 426.0992 | 1523.2229 | 426.0992 | 493.4861 | 454.3056
1524.2229 | 1180.2229 | 493.6711 | 454.3283 | 425.9772 | 1524.2229 | 425.9772 | 493.6711 | 454.3283
1525.2229 | 1181.2229 | 493.8319 | 454.3632 | 425.9042 | 1525.2229 | 425.9042 | 493.8319 | 454.3632
1526.2229 | 1182.2229 | 494.032 | 454.3435 | 426.0392 | 1526.2229 | 426.0392 | 494.032 | 454.3435
1527.2229 | 1183.2229 | 494.2006 | 454.2869 | 426.0549 | 1527.2229 | 426.0549 | 494.2006 | 454.2869
1528.2229 | 1184.2229 | 494.3504 | 454.2303 | 426.0972 | 1528.2229 | 426.0972 | 494.3504 | 454.2303
1529.2229 | 1185.2229 | 494.4299 | 454.1584 | 426.123 | 1529.2229 | 426.123 | 494.4299 | 454.1584
1530.2229 | 1186.2229 | 494.5297 | 454.0761 | 426.0737 | 1530.2229 | 426.0737 | 494.5297 | 454.0761
1531.2229 | 1187.2229 | 494.6439 | 453.9384 | 426.0626 | 1531.2229 | 426.0626 | 494.6439 | 453.9384
1532.2229 | 1188.2229 | 494.7579 | 453.768 | 426.0975 | 1532.2229 | 426.0975 | 494.7579 | 453.768
1533.2229 | 1189.2229 | 494.8829 | 453.5882 | 426.2784 | 1533.2229 | 426.2784 | 494.8829 | 453.5882
1534.2229 | 1190.2229 | 494.9984 | 453.409 | 426.4238 | 1534.2229 | 426.4238 | 494.9984 | 453.409
1535.2229 | 1191.2229 | 495.0955 | 453.2219 | 426.357 | 1535.2229 | 426.357 | 495.0955 | 453.2219
1536.2229 | 1192.2229 | 495.2229 | 453.0115 | 426.3009 | 1536.2229 | 426.3009 | 495.2229 | 453.0115
1537.2229 | 1193.2229 | 495.3583 | 452.8056 | 426.2936 | 1537.2229 | 426.2936 | 495.3583 | 452.8056
1538.2229 | 1194.2229 | 495.4834 | 452.5891 | 426.2171 | 1538.2229 | 426.2171 | 495.4834 | 452.5891
1539.2229 | 1195.2229 | 495.6016 | 452.3569 | 426.4329 | 1539.2229 | 426.4329 | 495.6016 | 452.3569
1540.2229 | 1196.2229 | 495.6604 | 452.1445 | 426.7596 | 1540.2229 | 426.7596 | 495.6604 | 452.1445
1541.2229 | 1197.2229 | 495.6805 | 451.9212 | 427.062 | 1541.2229 | 427.062 | 495.6805 | 451.9212
1542.2229 | 1198.2229 | 495.674 | 451.6784 | 427.2777 | 1542.2229 | 427.2777 | 495.674 | 451.6784
1543.2229 | 1199.2229 | 495.6343 | 451.4393 | 427.396 | 1543.2229 | 427.396 | 495.6343 | 451.4393
1544.2229 | 1200.2229 | 495.6206 | 451.2091 | 427.3831 | 1544.2229 | 427.3831 | 495.6206 | 451.2091
1545.2229 | 1201.2229 | 495.5754 | 450.9648 | 427.4937 | 1545.2229 | 427.4937 | 495.5754 | 450.9648
1546.2229 | 1202.2229 | 495.519 | 450.7194 | 427.5484 | 1546.2229 | 427.5484 | 495.519 | 450.7194
1547.2229 | 1203.2229 | 495.4778 | 450.475 | 427.4985 | 1547.2229 | 427.4985 | 495.4778 | 450.475
1548.2229 | 1204.2229 | 495.4165 | 450.2268 | 427.3736 | 1548.2229 | 427.3736 | 495.4165 | 450.2268
1549.2229 | 1205.2229 | 495.2791 | 449.989 | 427.4565 | 1549.2229 | 427.4565 | 495.2791 | 449.989
1550.2229 | 1206.2229 | 495.182 | 449.7404 | 427.6017 | 1550.2229 | 427.6017 | 495.182 | 449.7404
1551.2229 | 1207.2229 | 495.0395 | 449.5 | 427.5926 | 1551.2229 | 427.5926 | 495.0395 | 449.5
1552.2229 | 1208.2229 | 494.9397 | 449.2566 | 427.6 | 1552.2229 | 427.6 | 494.9397 | 449.2566
1553.2229 | 1209.2229 | 494.8448 | 449.0187 | 427.4958 | 1553.2229 | 427.4958 | 494.8448 | 449.0187
1554.2229 | 1210.2229 | 494.7636 | 448.7682 | 427.3987 | 1554.2229 | 427.3987 | 494.7636 | 448.7682
1555.2229 | 1211.2229 | 494.7009 | 448.5256 | 427.3735 | 1555.2229 | 427.3735 | 494.7009 | 448.5256
1556.2229 | 1212.2229 | 494.6522 | 448.2859 | 427.3929 | 1556.2229 | 427.3929 | 494.6522 | 448.2859
1557.2229 | 1213.2229 | 494.6075 | 448.0562 | 427.3955 | 1557.2229 | 427.3955 | 494.6075 | 448.0562
1558.2229 | 1214.2229 | 494.6208 | 447.8188 | 427.2635 | 1558.2229 | 427.2635 | 494.6208 | 447.8188
1559.2229 | 1215.2229 | 494.6652 | 447.5893 | 427.1576 | 1559.2229 | 427.1576 | 494.6652 | 447.5893
1560.2229 | 1216.2229 | 494.7981 | 447.3644 | 427.1562 | 1560.2229 | 427.1562 | 494.7981 | 447.3644
1561.2229 | 1217.2229 | 494.9764 | 447.1525 | 427.1338 | 1561.2229 | 427.1338 | 494.9764 | 447.1525
1562.2229 | 1218.2229 | 495.1502 | 446.9472 | 427.0451 | 1562.2229 | 427.0451 | 495.1502 | 446.9472
1563.2229 | 1219.2229 | 495.2937 | 446.7451 | 426.9435 | 1563.2229 | 426.9435 | 495.2937 | 446.7451
1564.2229 | 1220.2229 | 495.4753 | 446.5518 | 426.911 | 1564.2229 | 426.911 | 495.4753 | 446.5518
1565.2229 | 1221.2229 | 495.6299 | 446.3747 | 426.7817 | 1565.2229 | 426.7817 | 495.6299 | 446.3747
1566.2229 | 1222.2229 | 495.7797 | 446.1913 | 426.8037 | 1566.2229 | 426.8037 | 495.7797 | 446.1913
1567.2229 | 1223.2229 | 495.8762 | 446.0273 | 426.7523 | 1567.2229 | 426.7523 | 495.8762 | 446.0273
1568.2229 | 1224.2229 | 495.9491 | 445.8643 | 426.8307 | 1568.2229 | 426.8307 | 495.9491 | 445.8643
1569.2229 | 1225.2229 | 496.0976 | 445.7049 | 426.8401 | 1569.2229 | 426.8401 | 496.0976 | 445.7049
1570.2229 | 1226.2229 | 496.1909 | 445.549 | 426.7533 | 1570.2229 | 426.7533 | 496.1909 | 445.549
1571.2229 | 1227.2229 | 496.3019 | 445.4082 | 426.7955 | 1571.2229 | 426.7955 | 496.3019 | 445.4082
1572.2229 | 1228.2229 | 496.3825 | 445.2674 | 426.8248 | 1572.2229 | 426.8248 | 496.3825 | 445.2674
1573.2229 | 1229.2229 | 496.4603 | 445.1427 | 426.8996 | 1573.2229 | 426.8996 | 496.4603 | 445.1427
1574.2229 | 1230.2229 | 496.5009 | 445.0287 | 426.8539 | 1574.2229 | 426.8539 | 496.5009 | 445.0287
1575.2229 | 1231.2229 | 496.5767 | 444.9233 | 426.8924 | 1575.2229 | 426.8924 | 496.5767 | 444.9233
1576.2229 | 1232.2229 | 496.6633 | 444.8198 | 426.8481 | 1576.2229 | 426.8481 | 496.6633 | 444.8198
1577.2229 | 1233.2229 | 496.7328 | 444.7084 | 426.9351 | 1577.2229 | 426.9351 | 496.7328 | 444.7084
1578.2229 | 1234.2229 | 496.8181 | 444.6189 | 427.0584 | 1578.2229 | 427.0584 | 496.8181 | 444.6189
1579.2229 | 1235.2229 | 496.8642 | 444.5382 | 427.2009 | 1579.2229 | 427.2009 | 496.8642 | 444.5382
1580.2229 | 1236.2229 | 496.932 | 444.4639 | 427.2476 | 1580.2229 | 427.2476 | 496.932 | 444.4639
1581.2229 | 1237.2229 | 496.9496 | 444.3935 | 427.2842 | 1581.2229 | 427.2842 | 496.9496 | 444.3935
1582.2229 | 1238.2229 | 496.9601 | 444.3225 | 427.3931 | 1582.2229 | 427.3931 | 496.9601 | 444.3225
1583.2229 | 1239.2229 | 496.9643 | 444.2589 | 427.3225 | 1583.2229 | 427.3225 | 496.9643 | 444.2589
1584.2229 | 1240.2229 | 496.9576 | 444.2169 | 427.2861 | 1584.2229 | 427.2861 | 496.9576 | 444.2169
1585.2229 | 1241.2229 | 496.9028 | 444.1601 | 427.2788 | 1585.2229 | 427.2788 | 496.9028 | 444.1601
1586.2229 | 1242.2229 | 496.8883 | 444.1224 | 427.3607 | 1586.2229 | 427.3607 | 496.8883 | 444.1224
1587.2229 | 1243.2229 | 496.7925 | 444.0771 | 427.4564 | 1587.2229 | 427.4564 | 496.7925 | 444.0771
1588.2229 | 1244.2229 | 496.712 | 444.0257 | 427.4301 | 1588.2229 | 427.4301 | 496.712 | 444.0257
1589.2229 | 1245.2229 | 496.644 | 443.9981 | 427.4992 | 1589.2229 | 427.4992 | 496.644 | 443.9981
1590.2229 | 1246.2229 | 496.5871 | 443.9528 | 427.7 | 1590.2229 | 427.7 | 496.5871 | 443.9528
1591.2229 | 1247.2229 | 496.4547 | 443.9217 | 427.6895 | 1591.2229 | 427.6895 | 496.4547 | 443.9217
1592.2229 | 1248.2229 | 496.363 | 443.8851 | 427.6791 | 1592.2229 | 427.6791 | 496.363 | 443.8851
1593.2229 | 1249.2229 | 496.2524 | 443.8533 | 427.7318 | 1593.2229 | 427.7318 | 496.2524 | 443.8533
1594.2229 | 1250.2229 | 496.0939 | 443.8289 | 427.6501 | 1594.2229 | 427.6501 | 496.0939 | 443.8289
1595.2229 | 1251.2229 | 496.0553 | 443.814 | 427.5794 | 1595.2229 | 427.5794 | 496.0553 | 443.814
1596.2229 | 1252.2229 | 495.9774 | 443.7915 | 427.6172 | 1596.2229 | 427.6172 | 495.9774 | 443.7915
1597.2229 | 1253.2229 | 495.9489 | 443.7618 | 427.6255 | 1597.2229 | 427.6255 | 495.9489 | 443.7618
1598.2229 | 1254.2229 | 495.9481 | 443.7406 | 427.6538 | 1598.2229 | 427.6538 | 495.9481 | 443.7406
1599.2229 | 1255.2229 | 495.8986 | 443.7311 | 427.7739 | 1599.2229 | 427.7739 | 495.8986 | 443.7311
1600.2229 | 1256.2229 | 495.8674 | 443.6975 | 427.9034 | 1600.2229 | 427.9034 | 495.8674 | 443.6975
1601.2229 | 1257.2229 | 495.8034 | 443.6885 | 428.0214 | 1601.2229 | 428.0214 | 495.8034 | 443.6885
1602.2229 | 1258.2229 | 495.6872 | 443.6676 | 428.0524 | 1602.2229 | 428.0524 | 495.6872 | 443.6676
1603.2542 | 1259.2542 | 495.627 | 443.6543 | 428.1178 | 1603.2542 | 428.1178 | 495.627 | 443.6543
1604.2229 | 1260.2229 | 495.4933 | 443.6369 | 428.1961 | 1604.2229 | 428.1961 | 495.4933 | 443.6369
1605.2229 | 1261.2229 | 495.4402 | 443.6232 | 428.1064 | 1605.2229 | 428.1064 | 495.4402 | 443.6232
1606.2229 | 1262.2229 | 495.3767 | 443.6271 | 428.0536 | 1606.2229 | 428.0536 | 495.3767 | 443.6271
1607.2229 | 1263.2229 | 495.3073 | 443.6194 | 428.0837 | 1607.2229 | 428.0837 | 495.3073 | 443.6194
1608.2229 | 1264.2229 | 495.2636 | 443.6159 | 428.1272 | 1608.2229 | 428.1272 | 495.2636 | 443.6159
1609.2229 | 1265.2229 | 495.1865 | 443.6147 | 428.1303 | 1609.2229 | 428.1303 | 495.1865 | 443.6147
1610.2229 | 1266.2229 | 495.2077 | 443.625 | 428.0669 | 1610.2229 | 428.0669 | 495.2077 | 443.625
1611.2229 | 1267.2229 | 495.2323 | 443.6225 | 427.9262 | 1611.2229 | 427.9262 | 495.2323 | 443.6225
1612.2229 | 1268.2229 | 495.2223 | 443.6453 | 427.7938 | 1612.2229 | 427.7938 | 495.2223 | 443.6453
1613.2229 | 1269.2229 | 495.1873 | 443.6521 | 427.6828 | 1613.2229 | 427.6828 | 495.1873 | 443.6521
1614.2229 | 1270.2229 | 495.2468 | 443.6661 | 427.6331 | 1614.2229 | 427.6331 | 495.2468 | 443.6661
1615.2229 | 1271.2229 | 495.2886 | 443.6682 | 427.5686 | 1615.2229 | 427.5686 | 495.2886 | 443.6682
1616.2229 | 1272.2229 | 495.3806 | 443.6784 | 427.5137 | 1616.2229 | 427.5137 | 495.3806 | 443.6784
1617.2229 | 1273.2229 | 495.4854 | 443.6968 | 427.4405 | 1617.2229 | 427.4405 | 495.4854 | 443.6968
1618.2229 | 1274.2229 | 495.6783 | 443.7184 | 427.4473 | 1618.2229 | 427.4473 | 495.6783 | 443.7184
1619.2229 | 1275.2229 | 495.8753 | 443.7438 | 427.4222 | 1619.2229 | 427.4222 | 495.8753 | 443.7438
1620.2229 | 1276.2229 | 496.1021 | 443.7619 | 427.4443 | 1620.2229 | 427.4443 | 496.1021 | 443.7619
1621.2229 | 1277.2229 | 496.3467 | 443.7811 | 427.5029 | 1621.2229 | 427.5029 | 496.3467 | 443.7811
1622.2229 | 1278.2229 | 496.6423 | 443.8063 | 427.4711 | 1622.2229 | 427.4711 | 496.6423 | 443.8063
1623.2229 | 1279.2229 | 496.9393 | 443.8386 | 427.2977 | 1623.2229 | 427.2977 | 496.9393 | 443.8386
1624.2229 | 1280.2229 | 497.225 | 443.8681 | 427.2054 | 1624.2229 | 427.2054 | 497.225 | 443.8681
1625.2229 | 1281.2229 | 497.5496 | 443.9136 | 427.1407 | 1625.2229 | 427.1407 | 497.5496 | 443.9136
1626.2229 | 1282.2229 | 497.8482 | 443.9492 | 427.1394 | 1626.2229 | 427.1394 | 497.8482 | 443.9492
1627.2229 | 1283.2229 | 498.184 | 443.9941 | 427.0475 | 1627.2229 | 427.0475 | 498.184 | 443.9941
1628.2229 | 1284.2229 | 498.5 | 444.043 | 427.0219 | 1628.2229 | 427.0219 | 498.5 | 444.043
1629.2229 | 1285.2229 | 498.8943 | 444.0976 | 427.1026 | 1629.2229 | 427.1026 | 498.8943 | 444.0976
1630.2229 | 1286.2229 | 499.1907 | 444.1406 | 427.1436 | 1630.2229 | 427.1436 | 499.1907 | 444.1406
1631.2229 | 1287.2229 | 499.5548 | 444.1792 | 427.0398 | 1631.2229 | 427.0398 | 499.5548 | 444.1792
1632.2229 | 1288.2229 | 499.8684 | 444.2219 | 426.9887 | 1632.2229 | 426.9887 | 499.8684 | 444.2219
1633.2229 | 1289.2229 | 500.0757 | 444.2701 | 426.7581 | 1633.2229 | 426.7581 | 500.0757 | 444.2701
1634.2229 | 1290.2229 | 500.3688 | 444.3133 | 426.6339 | 1634.2229 | 426.6339 | 500.3688 | 444.3133
1635.2229 | 1291.2229 | 500.5811 | 444.3632 | 426.6993 | 1635.2229 | 426.6993 | 500.5811 | 444.3632
1636.2229 | 1292.2229 | 500.9008 | 444.4123 | 426.7655 | 1636.2229 | 426.7655 | 500.9008 | 444.4123
1637.2229 | 1293.2229 | 501.131 | 444.4624 | 426.8035 | 1637.2229 | 426.8035 | 501.131 | 444.4624
1638.2229 | 1294.2229 | 501.4568 | 444.5029 | 426.8524 | 1638.2229 | 426.8524 | 501.4568 | 444.5029
1639.2229 | 1295.2229 | 501.6959 | 444.5584 | 426.9831 | 1639.2229 | 426.9831 | 501.6959 | 444.5584
1640.2229 | 1296.2229 | 501.9487 | 444.6227 | 426.9798 | 1640.2229 | 426.9798 | 501.9487 | 444.6227
1641.2229 | 1297.2229 | 502.2435 | 444.6856 | 427.0425 | 1641.2229 | 427.0425 | 502.2435 | 444.6856
1642.2229 | 1298.2229 | 502.516 | 444.7445 | 427.0174 | 1642.2229 | 427.0174 | 502.516 | 444.7445
1643.2229 | 1299.2229 | 502.8586 | 444.8041 | 427.0904 | 1643.2229 | 427.0904 | 502.8586 | 444.8041
1644.2229 | 1300.2229 | 503.2123 | 444.8829 | 427.0563 | 1644.2229 | 427.0563 | 503.2123 | 444.8829
1645.2229 | 1301.2229 | 503.518 | 444.9456 | 427.0108 | 1645.2229 | 427.0108 | 503.518 | 444.9456
1646.2229 | 1302.2229 | 503.8607 | 445.018 | 427.0951 | 1646.2229 | 427.0951 | 503.8607 | 445.018
1647.2229 | 1303.2229 | 504.1847 | 445.0893 | 427.1676 | 1647.2229 | 427.1676 | 504.1847 | 445.0893
1648.2229 | 1304.2229 | 504.5085 | 445.1639 | 427.2962 | 1648.2229 | 427.2962 | 504.5085 | 445.1639
1649.2229 | 1305.2229 | 504.8326 | 445.228 | 427.4383 | 1649.2229 | 427.4383 | 504.8326 | 445.228
1650.2229 | 1306.2229 | 505.1029 | 445.2955 | 427.4497 | 1650.2229 | 427.4497 | 505.1029 | 445.2955
1651.2229 | 1307.2229 | 505.4554 | 445.3662 | 427.4851 | 1651.2229 | 427.4851 | 505.4554 | 445.3662
1652.2229 | 1308.2229 | 505.7511 | 445.4482 | 427.3556 | 1652.2229 | 427.3556 | 505.7511 | 445.4482
1653.2229 | 1309.2229 | 506.0082 | 445.5201 | 427.3594 | 1653.2229 | 427.3594 | 506.0082 | 445.5201
1654.2229 | 1310.2229 | 506.3102 | 445.5754 | 427.4639 | 1654.2229 | 427.4639 | 506.3102 | 445.5754
1655.2229 | 1311.2229 | 506.6197 | 445.6429 | 427.5305 | 1655.2229 | 427.5305 | 506.6197 | 445.6429
1656.2229 | 1312.2229 | 506.8613 | 445.6937 | 427.5601 | 1656.2229 | 427.5601 | 506.8613 | 445.6937
1657.2229 | 1313.2229 | 507.2173 | 445.7451 | 427.5595 | 1657.2229 | 427.5595 | 507.2173 | 445.7451
1658.2229 | 1314.2229 | 507.5334 | 445.8123 | 427.542 | 1658.2229 | 427.542 | 507.5334 | 445.8123
1659.2229 | 1315.2229 | 507.7835 | 445.8819 | 427.4659 | 1659.2229 | 427.4659 | 507.7835 | 445.8819
1660.2229 | 1316.2229 | 508.0821 | 445.9491 | 427.3562 | 1660.2229 | 427.3562 | 508.0821 | 445.9491
1661.2229 | 1317.2229 | 508.4356 | 446.0279 | 427.3975 | 1661.2229 | 427.3975 | 508.4356 | 446.0279
1662.2229 | 1318.2229 | 508.7195 | 446.0993 | 427.4607 | 1662.2229 | 427.4607 | 508.7195 | 446.0993
1663.2229 | 1319.2229 | 508.9654 | 446.1666 | 427.4935 | 1663.2229 | 427.4935 | 508.9654 | 446.1666
1664.2229 | 1320.2229 | 509.2767 | 446.229 | 427.5351 | 1664.2229 | 427.5351 | 509.2767 | 446.229
1665.2229 | 1321.2229 | 509.478 | 446.2758 | 427.5388 | 1665.2229 | 427.5388 | 509.478 | 446.2758
1666.2229 | 1322.2229 | 509.8107 | 446.3326 | 427.4007 | 1666.2229 | 427.4007 | 509.8107 | 446.3326
1667.2229 | 1323.2229 | 510.0452 | 446.3858 | 427.2132 | 1667.2229 | 427.2132 | 510.0452 | 446.3858
1668.2229 | 1324.2229 | 510.2714 | 446.4401 | 426.9517 | 1668.2229 | 426.9517 | 510.2714 | 446.4401
1669.2229 | 1325.2229 | 510.5449 | 446.4879 | 426.7969 | 1669.2229 | 426.7969 | 510.5449 | 446.4879
1670.2229 | 1326.2229 | 510.7098 | 446.5259 | 426.7647 | 1670.2229 | 426.7647 | 510.7098 | 446.5259
1671.2229 | 1327.2229 | 510.9584 | 446.5518 | 426.779 | 1671.2229 | 426.779 | 510.9584 | 446.5518
1672.2229 | 1328.2229 | 511.1629 | 446.5909 | 426.7462 | 1672.2229 | 426.7462 | 511.1629 | 446.5909
1673.2229 | 1329.2229 | 511.2862 | 446.6271 | 426.6817 | 1673.2229 | 426.6817 | 511.2862 | 446.6271
1674.2229 | 1330.2229 | 511.3491 | 446.6593 | 426.6952 | 1674.2229 | 426.6952 | 511.3491 | 446.6593
1675.2385 | 1331.2385 | 511.4663 | 446.7051 | 426.6775 | 1675.2385 | 426.6775 | 511.4663 | 446.7051
1676.426 | 1332.426 | 511.555 | 446.7467 | 426.6532 | 1676.426 | 426.6532 | 511.555 | 446.7467
1677.2229 | 1333.2229 | 511.586 | 446.7886 | 426.5779 | 1677.2229 | 426.5779 | 511.586 | 446.7886
1678.2385 | 1334.2385 | 511.6682 | 446.8378 | 426.4952 | 1678.2385 | 426.4952 | 511.6682 | 446.8378
1679.2229 | 1335.2229 | 511.6992 | 446.9021 | 426.4849 | 1679.2229 | 426.4849 | 511.6992 | 446.9021
1680.2229 | 1336.2229 | 511.6976 | 446.9633 | 426.473 | 1680.2229 | 426.473 | 511.6976 | 446.9633
1681.2229 | 1337.2229 | 511.8208 | 447.0167 | 426.4516 | 1681.2229 | 426.4516 | 511.8208 | 447.0167
1682.2229 | 1338.2229 | 511.9415 | 447.092 | 426.3485 | 1682.2229 | 426.3485 | 511.9415 | 447.092
1683.2229 | 1339.2229 | 512.0502 | 447.1721 | 426.3048 | 1683.2229 | 426.3048 | 512.0502 | 447.1721
1684.2229 | 1340.2229 | 512.122 | 447.2362 | 426.3355 | 1684.2229 | 426.3355 | 512.122 | 447.2362
1685.2229 | 1341.2229 | 512.172 | 447.3054 | 426.4008 | 1685.2229 | 426.4008 | 512.172 | 447.3054
1686.2229 | 1342.2229 | 512.3086 | 447.3722 | 426.3543 | 1686.2229 | 426.3543 | 512.3086 | 447.3722
1687.2229 | 1343.2229 | 512.4402 | 447.4375 | 426.2476 | 1687.2229 | 426.2476 | 512.4402 | 447.4375
1688.2229 | 1344.2229 | 512.5129 | 447.516 | 426.0798 | 1688.2229 | 426.0798 | 512.5129 | 447.516
1689.2229 | 1345.2229 | 512.5493 | 447.5778 | 426.1538 | 1689.2229 | 426.1538 | 512.5493 | 447.5778
1690.2229 | 1346.2229 | 512.5849 | 447.6492 | 426.3082 | 1690.2229 | 426.3082 | 512.5849 | 447.6492
1691.2229 | 1347.2229 | 512.6684 | 447.7167 | 426.233 | 1691.2229 | 426.233 | 512.6684 | 447.7167
1692.2229 | 1348.2229 | 512.6835 | 447.7733 | 426.0993 | 1692.2229 | 426.0993 | 512.6835 | 447.7733
1693.2229 | 1349.2229 | 512.7141 | 447.83 | 426.1863 | 1693.2229 | 426.1863 | 512.7141 | 447.83
1694.2229 | 1350.2229 | 512.6267 | 447.88 | 426.279 | 1694.2229 | 426.279 | 512.6267 | 447.88
1695.2229 | 1351.2229 | 512.5781 | 447.9395 | 426.3163 | 1695.2229 | 426.3163 | 512.5781 | 447.9395
1696.2229 | 1352.2229 | 512.5035 | 447.9886 | 426.4459 | 1696.2229 | 426.4459 | 512.5035 | 447.9886
1697.2229 | 1353.2229 | 512.4254 | 448.0529 | 426.6532 | 1697.2229 | 426.6532 | 512.4254 | 448.0529
1698.2229 | 1354.2229 | 512.3289 | 448.1103 | 426.7969 | 1698.2229 | 426.7969 | 512.3289 | 448.1103
1699.2229 | 1355.2229 | 512.3536 | 448.1755 | 426.6977 | 1699.2229 | 426.6977 | 512.3536 | 448.1755
1700.2229 | 1356.2229 | 512.2746 | 448.242 | 426.5142 | 1700.2229 | 426.5142 | 512.2746 | 448.242
1701.2229 | 1357.2229 | 512.3573 | 448.3041 | 426.481 | 1701.2229 | 426.481 | 512.3573 | 448.3041
1702.2229 | 1358.2229 | 512.299 | 448.3726 | 426.4734 | 1702.2229 | 426.4734 | 512.299 | 448.3726
1703.2229 | 1359.2229 | 512.3177 | 448.4434 | 426.4462 | 1703.2229 | 426.4462 | 512.3177 | 448.4434
1704.2229 | 1360.2229 | 512.2964 | 448.5115 | 426.5186 | 1704.2229 | 426.5186 | 512.2964 | 448.5115
1705.2229 | 1361.2229 | 512.259 | 448.585 | 426.597 | 1705.2229 | 426.597 | 512.259 | 448.585
1706.2229 | 1362.2229 | 512.266 | 448.6634 | 426.6673 | 1706.2229 | 426.6673 | 512.266 | 448.6634
1707.2229 | 1363.2229 | 512.2801 | 448.7303 | 426.6652 | 1707.2229 | 426.6652 | 512.2801 | 448.7303
1708.2229 | 1364.2229 | 512.3304 | 448.8034 | 426.7979 | 1708.2229 | 426.7979 | 512.3304 | 448.8034
1709.2229 | 1365.2229 | 512.3949 | 448.8768 | 426.7799 | 1709.2229 | 426.7799 | 512.3949 | 448.8768
1710.2229 | 1366.2229 | 512.371 | 448.9543 | 426.7706 | 1710.2229 | 426.7706 | 512.371 | 448.9543
1711.2229 | 1367.2229 | 512.439 | 449.0283 | 426.8016 | 1711.2229 | 426.8016 | 512.439 | 449.0283
1712.2229 | 1368.2229 | 512.4899 | 449.1109 | 426.8605 | 1712.2229 | 426.8605 | 512.4899 | 449.1109
1713.2229 | 1369.2229 | 512.6256 | 449.1833 | 426.826 | 1713.2229 | 426.826 | 512.6256 | 449.1833
1714.2229 | 1370.2229 | 512.6468 | 449.273 | 426.7495 | 1714.2229 | 426.7495 | 512.6468 | 449.273
1715.2229 | 1371.2229 | 512.6749 | 449.3376 | 426.5496 | 1715.2229 | 426.5496 | 512.6749 | 449.3376
1716.2229 | 1372.2229 | 512.7671 | 449.4239 | 426.436 | 1716.2229 | 426.436 | 512.7671 | 449.4239
1717.2229 | 1373.2229 | 512.731 | 449.5099 | 426.3099 | 1717.2229 | 426.3099 | 512.731 | 449.5099
1718.2229 | 1374.2229 | 512.7169 | 449.5923 | 426.3215 | 1718.2229 | 426.3215 | 512.7169 | 449.5923
1719.2229 | 1375.2229 | 512.7974 | 449.6656 | 426.3295 | 1719.2229 | 426.3295 | 512.7974 | 449.6656
1720.2229 | 1376.2229 | 512.7826 | 449.7366 | 426.2353 | 1720.2229 | 426.2353 | 512.7826 | 449.7366
1721.2229 | 1377.2229 | 512.8271 | 449.8069 | 426.1601 | 1721.2229 | 426.1601 | 512.8271 | 449.8069
1722.2854 | 1378.2854 | 512.8382 | 449.8812 | 426.2203 | 1722.2854 | 426.2203 | 512.8382 | 449.8812
1723.2854 | 1379.2854 | 512.839 | 449.9463 | 426.2028 | 1723.2854 | 426.2028 | 512.839 | 449.9463
1724.2385 | 1380.2385 | 512.8316 | 450.0094 | 426.1791 | 1724.2385 | 426.1791 | 512.8316 | 450.0094
1725.2229 | 1381.2229 | 512.9866 | 450.0735 | 426.2263 | 1725.2229 | 426.2263 | 512.9866 | 450.0735
1726.2229 | 1382.2229 | 512.9441 | 450.1447 | 426.2519 | 1726.2229 | 426.2519 | 512.9441 | 450.1447
1727.3479 | 1383.3479 | 512.9593 | 450.2102 | 426.3803 | 1727.3479 | 426.3803 | 512.9593 | 450.2102
1728.301 | 1384.301 | 512.9752 | 450.268 | 426.3327 | 1728.301 | 426.3327 | 512.9752 | 450.268
1729.2385 | 1385.2385 | 512.9134 | 450.3186 | 426.2278 | 1729.2385 | 426.2278 | 512.9134 | 450.3186
1730.2229 | 1386.2229 | 512.9879 | 450.3845 | 426.1564 | 1730.2229 | 426.1564 | 512.9879 | 450.3845
1731.2229 | 1387.2229 | 513.0868 | 450.4285 | 426.1757 | 1731.2229 | 426.1757 | 513.0868 | 450.4285
1732.2229 | 1388.2229 | 513.1324 | 450.4809 | 426.0791 | 1732.2229 | 426.0791 | 513.1324 | 450.4809
1733.2854 | 1389.2854 | 513.0557 | 450.5282 | 425.9868 | 1733.2854 | 425.9868 | 513.0557 | 450.5282
1734.2698 | 1390.2698 | 513.1939 | 450.5989 | 425.9929 | 1734.2698 | 425.9929 | 513.1939 | 450.5989
1735.2385 | 1391.2385 | 513.1714 | 450.6444 | 426.0771 | 1735.2385 | 426.0771 | 513.1714 | 450.6444
1736.301 | 1392.301 | 513.3026 | 450.712 | 426.2125 | 1736.301 | 426.2125 | 513.3026 | 450.712
1737.2385 | 1393.2385 | 513.3107 | 450.7597 | 426.2026 | 1737.2385 | 426.2026 | 513.3107 | 450.7597
1738.2229 | 1394.2229 | 513.3112 | 450.8165 | 426.0929 | 1738.2229 | 426.0929 | 513.3112 | 450.8165
1739.2229 | 1395.2229 | 513.3251 | 450.8725 | 426.2552 | 1739.2229 | 426.2552 | 513.3251 | 450.8725
1740.2229 | 1396.2229 | 513.3627 | 450.9211 | 426.4027 | 1740.2229 | 426.4027 | 513.3627 | 450.9211
1741.2229 | 1397.2229 | 513.3833 | 450.9775 | 426.4614 | 1741.2229 | 426.4614 | 513.3833 | 450.9775
1742.2229 | 1398.2229 | 513.5033 | 451.0305 | 426.59 | 1742.2229 | 426.59 | 513.5033 | 451.0305
1743.2229 | 1399.2229 | 513.522 | 451.0985 | 426.7957 | 1743.2229 | 426.7957 | 513.522 | 451.0985
1744.2229 | 1400.2229 | 513.6344 | 451.1538 | 426.8159 | 1744.2229 | 426.8159 | 513.6344 | 451.1538
1745.2229 | 1401.2229 | 513.7585 | 451.2139 | 426.7865 | 1745.2229 | 426.7865 | 513.7585 | 451.2139
1746.2229 | 1402.2229 | 513.7749 | 451.2836 | 426.8967 | 1746.2229 | 426.8967 | 513.7749 | 451.2836
1747.2229 | 1403.2229 | 513.8233 | 451.3519 | 426.9666 | 1747.2229 | 426.9666 | 513.8233 | 451.3519
1748.2229 | 1404.2229 | 513.9674 | 451.4097 | 426.9888 | 1748.2229 | 426.9888 | 513.9674 | 451.4097
1749.2229 | 1405.2229 | 514.0599 | 451.4762 | 426.8544 | 1749.2229 | 426.8544 | 514.0599 | 451.4762
1750.2229 | 1406.2229 | 514.0736 | 451.5314 | 426.7385 | 1750.2229 | 426.7385 | 514.0736 | 451.5314
1751.2229 | 1407.2229 | 514.2428 | 451.5958 | 426.7361 | 1751.2229 | 426.7361 | 514.2428 | 451.5958
1752.2229 | 1408.2229 | 514.2941 | 451.6742 | 426.8928 | 1752.2229 | 426.8928 | 514.2941 | 451.6742
1753.2229 | 1409.2229 | 514.3989 | 451.728 | 426.9652 | 1753.2229 | 426.9652 | 514.3989 | 451.728
1754.2229 | 1410.2229 | 514.385 | 451.7873 | 427.0288 | 1754.2229 | 427.0288 | 514.385 | 451.7873
1755.2229 | 1411.2229 | 514.4356 | 451.8487 | 427.0554 | 1755.2229 | 427.0554 | 514.4356 | 451.8487
1756.2229 | 1412.2229 | 514.4917 | 451.8908 | 427.1419 | 1756.2229 | 427.1419 | 514.4917 | 451.8908
1757.2229 | 1413.2229 | 514.4104 | 451.9553 | 427.1354 | 1757.2229 | 427.1354 | 514.4104 | 451.9553
1758.2229 | 1414.2229 | 514.418 | 452.0042 | 427.0482 | 1758.2229 | 427.0482 | 514.418 | 452.0042
1759.2229 | 1415.2229 | 514.4758 | 452.0399 | 427.0173 | 1759.2229 | 427.0173 | 514.4758 | 452.0399
1760.2229 | 1416.2229 | 514.4961 | 452.096 | 427.0964 | 1760.2229 | 427.0964 | 514.4961 | 452.096
1761.2229 | 1417.2229 | 514.4445 | 452.1478 | 427.096 | 1761.2229 | 427.096 | 514.4445 | 452.1478
1762.2229 | 1418.2229 | 514.4902 | 452.2 | 427.0431 | 1762.2229 | 427.0431 | 514.4902 | 452.2
1763.2229 | 1419.2229 | 514.458 | 452.2583 | 426.9867 | 1763.2229 | 426.9867 | 514.458 | 452.2583
1764.2229 | 1420.2229 | 514.476 | 452.2949 | 426.9799 | 1764.2229 | 426.9799 | 514.476 | 452.2949
1765.2229 | 1421.2229 | 514.4303 | 452.3411 | 426.9856 | 1765.2229 | 426.9856 | 514.4303 | 452.3411
1766.2229 | 1422.2229 | 514.3754 | 452.3777 | 426.9643 | 1766.2229 | 426.9643 | 514.3754 | 452.3777
1767.2229 | 1423.2229 | 514.349 | 452.4159 | 427.0343 | 1767.2229 | 427.0343 | 514.349 | 452.4159
1768.2229 | 1424.2229 | 514.292 | 452.4684 | 426.982 | 1768.2229 | 426.982 | 514.292 | 452.4684
1769.2229 | 1425.2229 | 514.1742 | 452.4975 | 427.0164 | 1769.2229 | 427.0164 | 514.1742 | 452.4975
1770.2229 | 1426.2229 | 514.067 | 452.5475 | 426.9967 | 1770.2229 | 426.9967 | 514.067 | 452.5475
1771.2229 | 1427.2229 | 514.086 | 452.5964 | 426.9554 | 1771.2229 | 426.9554 | 514.086 | 452.5964
1772.2229 | 1428.2229 | 514.0244 | 452.642 | 426.939 | 1772.2229 | 426.939 | 514.0244 | 452.642
1773.2229 | 1429.2229 | 513.9698 | 452.6802 | 426.888 | 1773.2229 | 426.888 | 513.9698 | 452.6802
1774.2229 | 1430.2229 | 513.9302 | 452.7308 | 426.9224 | 1774.2229 | 426.9224 | 513.9302 | 452.7308
1775.2229 | 1431.2229 | 513.8309 | 452.7569 | 426.9354 | 1775.2229 | 426.9354 | 513.8309 | 452.7569
1776.2229 | 1432.2229 | 513.7295 | 452.8034 | 426.9809 | 1776.2229 | 426.9809 | 513.7295 | 452.8034
1777.2229 | 1433.2229 | 513.66 | 452.8424 | 427.1325 | 1777.2229 | 427.1325 | 513.66 | 452.8424
1778.2229 | 1434.2229 | 513.6159 | 452.8955 | 427.2335 | 1778.2229 | 427.2335 | 513.6159 | 452.8955
1779.2229 | 1435.2229 | 513.5008 | 452.9423 | 427.303 | 1779.2229 | 427.303 | 513.5008 | 452.9423
1780.2229 | 1436.2229 | 513.4761 | 452.9775 | 427.2274 | 1780.2229 | 427.2274 | 513.4761 | 452.9775
1781.2229 | 1437.2229 | 513.3824 | 453.0049 | 427.3545 | 1781.2229 | 427.3545 | 513.3824 | 453.0049
1782.2229 | 1438.2229 | 513.3901 | 453.0503 | 427.4308 | 1782.2229 | 427.4308 | 513.3901 | 453.0503
1783.2229 | 1439.2229 | 513.2238 | 453.072 | 427.3085 | 1783.2229 | 427.3085 | 513.2238 | 453.072
1784.2229 | 1440.2229 | 513.3189 | 453.1318 | 427.3075 | 1784.2229 | 427.3075 | 513.3189 | 453.1318
1785.2229 | 1441.2229 | 513.2009 | 453.1907 | 427.2561 | 1785.2229 | 427.2561 | 513.2009 | 453.1907
1786.2229 | 1442.2229 | 513.0644 | 453.2431 | 427.1833 | 1786.2229 | 427.1833 | 513.0644 | 453.2431
1787.2229 | 1443.2229 | 513.1456 | 453.317 | 427.1372 | 1787.2229 | 427.1372 | 513.1456 | 453.317
1788.2229 | 1444.2229 | 513.1236 | 453.378 | 427.0871 | 1788.2229 | 427.0871 | 513.1236 | 453.378
1789.2229 | 1445.2229 | 513.172 | 453.4492 | 427.0279 | 1789.2229 | 427.0279 | 513.172 | 453.4492
1790.2229 | 1446.2229 | 513.0551 | 453.5207 | 426.9977 | 1790.2229 | 426.9977 | 513.0551 | 453.5207
1791.2229 | 1447.2229 | 513.2078 | 453.6158 | 426.9881 | 1791.2229 | 426.9881 | 513.2078 | 453.6158
1792.2229 | 1448.2229 | 513.2665 | 453.688 | 426.9644 | 1792.2229 | 426.9644 | 513.2665 | 453.688
1793.2229 | 1449.2229 | 513.3632 | 453.7544 | 426.9021 | 1793.2229 | 426.9021 | 513.3632 | 453.7544
1794.2229 | 1450.2229 | 513.4165 | 453.8324 | 426.8161 | 1794.2229 | 426.8161 | 513.4165 | 453.8324
1795.2229 | 1451.2229 | 513.5075 | 453.9298 | 426.9266 | 1795.2229 | 426.9266 | 513.5075 | 453.9298
1796.2229 | 1452.2229 | 513.6505 | 453.9929 | 426.9204 | 1796.2229 | 426.9204 | 513.6505 | 453.9929
1797.2229 | 1453.2229 | 513.8205 | 454.0734 | 426.9119 | 1797.2229 | 426.9119 | 513.8205 | 454.0734
1798.2229 | 1454.2229 | 513.9792 | 454.1193 | 427.0112 | 1798.2229 | 427.0112 | 513.9792 | 454.1193
1799.2229 | 1455.2229 | 513.9921 | 454.1908 | 426.9475 | 1799.2229 | 426.9475 | 513.9921 | 454.1908
1800.2229 | 1456.2229 | 514.1394 | 454.244 | 426.9287 | 1800.2229 | 426.9287 | 514.1394 | 454.244
1801.2229 | 1457.2229 | 514.1963 | 454.2921 | 426.9251 | 1801.2229 | 426.9251 | 514.1963 | 454.2921
1802.2229 | 1458.2229 | 514.2137 | 454.3669 | 426.8881 | 1802.2229 | 426.8881 | 514.2137 | 454.3669
1803.2229 | 1459.2229 | 514.2347 | 454.4147 | 426.9491 | 1803.2229 | 426.9491 | 514.2347 | 454.4147
1804.2229 | 1460.2229 | 514.2367 | 454.4874 | 426.9268 | 1804.2229 | 426.9268 | 514.2367 | 454.4874
1805.2229 | 1461.2229 | 514.2398 | 454.5458 | 426.8702 | 1805.2229 | 426.8702 | 514.2398 | 454.5458
1806.2229 | 1462.2229 | 514.2569 | 454.6064 | 426.7849 | 1806.2229 | 426.7849 | 514.2569 | 454.6064
1807.2229 | 1463.2229 | 514.2358 | 454.6626 | 426.752 | 1807.2229 | 426.752 | 514.2358 | 454.6626
1808.2229 | 1464.2229 | 514.0637 | 454.7082 | 426.7088 | 1808.2229 | 426.7088 | 514.0637 | 454.7082
1809.2229 | 1465.2229 | 514.3487 | 454.7579 | 426.8052 | 1809.2229 | 426.8052 | 514.3487 | 454.7579
1810.2229 | 1466.2229 | 514.2915 | 454.8178 | 426.7924 | 1810.2229 | 426.7924 | 514.2915 | 454.8178
1811.2229 | 1467.2229 | 514.4351 | 454.8544 | 426.7654 | 1811.2229 | 426.7654 | 514.4351 | 454.8544
1812.2229 | 1468.2229 | 514.4749 | 454.9007 | 426.7429 | 1812.2229 | 426.7429 | 514.4749 | 454.9007
1813.2229 | 1469.2229 | 514.5916 | 454.97 | 426.7156 | 1813.2229 | 426.7156 | 514.5916 | 454.97
1814.2229 | 1470.2229 | 514.6379 | 455.0163 | 426.5694 | 1814.2229 | 426.5694 | 514.6379 | 455.0163
1815.2229 | 1471.2229 | 514.706 | 455.0779 | 426.5423 | 1815.2229 | 426.5423 | 514.706 | 455.0779
1816.2229 | 1472.2229 | 514.6665 | 455.132 | 426.5299 | 1816.2229 | 426.5299 | 514.6665 | 455.132
1817.2229 | 1473.2229 | 514.6468 | 455.1797 | 426.5421 | 1817.2229 | 426.5421 | 514.6468 | 455.1797
1818.2229 | 1474.2229 | 514.5938 | 455.2314 | 426.5782 | 1818.2229 | 426.5782 | 514.5938 | 455.2314
1819.2229 | 1475.2229 | 514.4656 | 455.2763 | 426.6838 | 1819.2229 | 426.6838 | 514.4656 | 455.2763
1820.2229 | 1476.2229 | 514.3613 | 455.347 | 426.5942 | 1820.2229 | 426.5942 | 514.3613 | 455.347
1821.2229 | 1477.2229 | 514.2238 | 455.4423 | 426.4596 | 1821.2229 | 426.4596 | 514.2238 | 455.4423
1822.2229 | 1478.2229 | 514.2209 | 455.473 | 426.4428 | 1822.2229 | 426.4428 | 514.2209 | 455.473
1823.2229 | 1479.2229 | 514.1449 | 455.4908 | 426.3773 | 1823.2229 | 426.3773 | 514.1449 | 455.4908
1824.2229 | 1480.2229 | 514.0809 | 455.5518 | 426.3217 | 1824.2229 | 426.3217 | 514.0809 | 455.5518
1825.2229 | 1481.2229 | 514.137 | 455.6183 | 426.1999 | 1825.2229 | 426.1999 | 514.137 | 455.6183
1826.2229 | 1482.2229 | 514.1764 | 455.6775 | 426.1092 | 1826.2229 | 426.1092 | 514.1764 | 455.6775
1827.2229 | 1483.2229 | 514.1919 | 455.7097 | 426.1103 | 1827.2229 | 426.1103 | 514.1919 | 455.7097
1828.2229 | 1484.2229 | 514.307 | 455.752 | 426.1101 | 1828.2229 | 426.1101 | 514.307 | 455.752
1829.2229 | 1485.2229 | 514.4522 | 455.8088 | 425.9343 | 1829.2229 | 425.9343 | 514.4522 | 455.8088
1830.2229 | 1486.2229 | 514.4853 | 455.8343 | 425.7698 | 1830.2229 | 425.7698 | 514.4853 | 455.8343
1831.2229 | 1487.2229 | 514.5932 | 455.8748 | 425.7649 | 1831.2229 | 425.7649 | 514.5932 | 455.8748
1832.2229 | 1488.2229 | 514.7509 | 455.9313 | 425.6856 | 1832.2229 | 425.6856 | 514.7509 | 455.9313
1833.2229 | 1489.2229 | 514.897 | 455.967 | 425.7072 | 1833.2229 | 425.7072 | 514.897 | 455.967
1834.2229 | 1490.2229 | 514.9555 | 456.015 | 425.6166 | 1834.2229 | 425.6166 | 514.9555 | 456.015
1835.2229 | 1491.2229 | 514.9386 | 456.0636 | 425.5657 | 1835.2229 | 425.5657 | 514.9386 | 456.0636
1836.2229 | 1492.2229 | 514.9237 | 456.0808 | 425.5557 | 1836.2229 | 425.5557 | 514.9237 | 456.0808
1837.2229 | 1493.2229 | 514.9984 | 456.1204 | 425.5147 | 1837.2229 | 425.5147 | 514.9984 | 456.1204
1838.2229 | 1494.2229 | 515.0132 | 456.1898 | 425.6172 | 1838.2229 | 425.6172 | 515.0132 | 456.1898
1839.2229 | 1495.2229 | 514.9943 | 456.1546 | 425.7432 | 1839.2229 | 425.7432 | 514.9943 | 456.1546
1840.2229 | 1496.2229 | 515.0954 | 456.2009 | 425.8651 | 1840.2229 | 425.8651 | 515.0954 | 456.2009
1841.2229 | 1497.2229 | 515.0519 | 456.2176 | 425.8692 | 1841.2229 | 425.8692 | 515.0519 | 456.2176
1842.2229 | 1498.2229 | 515.0273 | 456.2499 | 426.0229 | 1842.2229 | 426.0229 | 515.0273 | 456.2499
1843.2229 | 1499.2229 | 515.0176 | 456.2912 | 426.0931 | 1843.2229 | 426.0931 | 515.0176 | 456.2912
1844.2229 | 1500.2229 | 514.9428 | 456.2883 | 426.2516 | 1844.2229 | 426.2516 | 514.9428 | 456.2883
1845.2385 | 1501.2385 | 514.9591 | 456.2971 | 426.2017 | 1845.2385 | 426.2017 | 514.9591 | 456.2971
1846.2229 | 1502.2229 | 514.7656 | 456.3589 | 426.3307 | 1846.2229 | 426.3307 | 514.7656 | 456.3589
1847.2229 | 1503.2229 | 514.6599 | 456.4053 | 426.4019 | 1847.2229 | 426.4019 | 514.6599 | 456.4053
1848.2229 | 1504.2229 | 514.5205 | 456.344 | 426.3802 | 1848.2229 | 426.3802 | 514.5205 | 456.344
1849.2229 | 1505.2229 | 514.5191 | 456.4274 | 426.2642 | 1849.2229 | 426.2642 | 514.5191 | 456.4274