## Test Conditions
DESIREE-FIRE Test Number 20 - Circuit Simulator Data Only
Test Date: | 2009-08-11
DCSim DAQ Start Time | 8:59
DCSim Time for Synchronization | 9:17
Heat Source Synchronization | 0:03 | hour:minutes:seconds
Heat Source DAQ Start Time | 9:13
Fire Time | 9:28
Offset | 0:29 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1765 | seconds
Heat Source Offset | 0:15 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 903 | seconds
Heat Source Stop Time | 9:39
Test Duration | 0:11 | hour:minutes:seconds
| 646 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | Armored Cable, 8c, 12AWG |  | Channel 3 and Channel 4 thermocouples are below the outer jacketing material on either side of the monitored temperature cable. Channel 5 thermocouple is below the armor on top of the thermocouple cable. | Channel 4, TC25 in the Temperature Data File
SOV 2 | Armored Cable, 8c, 12AWG |  | Channel 3 and Channel 4 thermocouples are below the outer jacketing material on either side of the monitored temperature cable. Channel 5 thermocouple is below the armor on top of the thermocouple cable. | Channel 4, TC25 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.35938 | 123.2071 | -66.7648 | 56.2592 | -0.012133 | -0.0014786 | 0.0015427 | 0.053132 | -0.0013653 | 0.060548 | -0.0070964 | -3.8406e-05 | -0.00016665 | 0.064518 | 0.0049316 | 0.066461 | -66.7793 | 0.051771 | -66.7048 | 56.174 | 55.9823 | 56.0467 | -66.7917 | -66.7291 | 0.03241 | -66.7682 | 56.0658 | 56.1932 | 56.1872 | -66.8546 | -0.026893 | -0.085149 | -0.014486 | 0.060032 | 0.086925 | -0.27687 | -0.21245 | -0.089789 | -0.19339 | 0.035762 | -0.003322 | 0.086467 | -0.065996 | -0.071951 | 122.9388 | 122.7471 | 122.8115 | 66.8166 | -123.0509 | 122.8306 | 122.958 | 122.952 | 66.7972 | -123.1138
0.64062 | 123.2758 | -66.7099 | 56.2454 | -0.012133 | -0.001265 | 0.0011155 | 0.053132 | -0.0017927 | 0.060548 | -0.0070964 | -3.8406e-05 | -0.00059405 | 0.064731 | 0.004718 | 0.066461 | -66.7793 | 0.028878 | -66.6773 | 56.1557 | 55.8861 | 56.0101 | -66.5765 | -66.7199 | 0.018674 | -66.7727 | 56.0703 | 56.2023 | 55.7706 | -66.8546 | 0.13339 | -0.089729 | -0.069418 | 0.032569 | -0.10082 | -0.35929 | -0.23535 | -0.14472 | -0.17507 | -0.010012 | -0.062832 | 0.081889 | -0.043105 | -0.47487 | 122.8656 | 122.596 | 122.72 | 66.7388 | -122.8219 | 122.7802 | 122.9122 | 122.4805 | 66.7286 | -123.1
1.6406 | 123.175 | -66.7786 | 56.25 | -0.0045023 | -0.0010512 | 0.0013291 | 0.052705 | -0.0011517 | 0.060975 | -0.0070964 | -0.00046581 | -0.00016665 | 0.064731 | 0.0045042 | 0.066461 | -66.7793 | 0.033457 | -66.6911 | 56.1511 | 55.8907 | 56.0101 | -66.6864 | -66.7199 | 0.027831 | -66.7819 | 56.0703 | 56.1977 | 55.7843 | -66.8638 | 0.092155 | -0.098886 | -0.000754 | 0.087499 | -0.004656 | -0.35929 | -0.23993 | -0.085215 | -0.17965 | 0.058652 | -0.003326 | 0.081889 | -0.052262 | -0.46571 | 122.9297 | 122.6693 | 122.7886 | 66.812 | -122.9364 | 122.8489 | 122.9763 | 122.5629 | 66.8064 | -123.1138
2.6406 | 123.3032 | -66.7282 | 56.218 | 0.0031287 | -0.0014786 | 0.0011155 | 0.052919 | -0.0011517 | 0.060761 | -0.0070964 | 0.00038879 | 4.695e-05 | 0.064304 | 0.0045042 | 0.066461 | -66.7747 | 0.0243 | -66.6911 | 56.1465 | 55.8816 | 56.0101 | -66.6452 | -66.7199 | 0.023253 | -66.7727 | 56.0612 | 56.1932 | 55.7889 | -66.8638 | 0.083011 | -0.071421 | -0.046529 | 0.037145 | -0.045866 | -0.3364 | -0.20788 | -0.13557 | -0.15677 | 0.008298 | -0.044522 | 0.091047 | -0.024798 | -0.42909 | 122.8747 | 122.6098 | 122.7383 | 66.7525 | -122.8632 | 122.7894 | 122.9214 | 122.5171 | 66.7515 | -123.0817
3.6406 | 123.1567 | -66.7786 | 56.282 | -0.0045023 | -0.0016924 | 0.0013291 | 0.052491 | -0.0015791 | 0.060548 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.064731 | 0.0051452 | 0.066247 | -66.7839 | 0.033457 | -66.6911 | 56.1603 | 55.8999 | 56.0147 | -66.6635 | -66.7245 | 0.023253 | -66.7773 | 56.0566 | 56.1932 | 55.798 | -66.8638 | 0.11505 | -0.12177 | -0.005332 | 0.087499 | -0.02755 | -0.38217 | -0.26739 | -0.085215 | -0.22543 | 0.054073 | 0.001253 | 0.086468 | -0.088884 | -0.48402 | 122.9388 | 122.6784 | 122.7932 | 66.812 | -122.9456 | 122.8352 | 122.9717 | 122.5766 | 66.8018 | -123.1458
4.6406 | 123.2483 | -66.7557 | 56.2454 | -0.012133 | -0.001265 | 0.0011155 | 0.052705 | -0.0013653 | 0.060548 | -0.0070964 | 0.00017519 | -0.00059405 | 0.06409 | 0.004718 | 0.066461 | -66.7793 | 0.028878 | -66.6865 | 56.1511 | 55.8953 | 56.0147 | -66.7322 | -66.7245 | 0.023253 | -66.7682 | 56.0612 | 56.1886 | 55.8804 | -66.8592 | 0.023477 | -0.094308 | -0.023642 | 0.069189 | 0.045712 | -0.35013 | -0.23077 | -0.10352 | -0.18423 | 0.031185 | -0.012478 | 0.091046 | -0.056841 | -0.36498 | 122.9068 | 122.651 | 122.7703 | 66.7846 | -122.9776 | 122.8169 | 122.9443 | 122.6361 | 66.7789 | -123.1046
5.6406 | 123.2117 | -66.7419 | 56.2683 | -0.0045023 | -0.0016924 | 0.0013291 | 0.052491 | -0.0013653 | 0.060975 | 0.00053414 | 0.00017519 | 4.695e-05 | 0.064518 | 0.0049316 | 0.066461 | -66.7793 | 0.033457 | -66.6911 | 56.1648 | 55.8953 | 56.0238 | -66.7047 | -66.7199 | 0.027831 | -66.7682 | 56.0658 | 56.1977 | 55.8575 | -66.8638 | 0.037218 | -0.10346 | -0.037375 | 0.050878 | 0.01366 | -0.37302 | -0.2445 | -0.12184 | -0.20254 | 0.022031 | -0.026211 | 0.095625 | -0.070573 | -0.41077 | 122.9068 | 122.6372 | 122.7658 | 66.7754 | -122.973 | 122.8077 | 122.9397 | 122.5995 | 66.7698 | -123.1321
6.6406 | 123.2758 | -66.7191 | 56.2134 | -0.0045023 | -0.0014786 | 0.0011155 | 0.052705 | -0.0011517 | 0.060548 | -0.014727 | 0.00038879 | 4.695e-05 | 0.064518 | 0.0049316 | 0.066461 | -66.7793 | 0.028878 | -66.6865 | 56.1603 | 55.8907 | 56.0238 | -66.691 | -66.7199 | 0.023253 | -66.7682 | 56.0612 | 56.1932 | 55.8163 | -66.8592 | 0.028067 | -0.053108 | -0.060263 | 0.032568 | 0.004501 | -0.32267 | -0.18957 | -0.14015 | -0.15219 | -0.000857 | -0.049099 | 0.091046 | -0.02022 | -0.39704 | 122.8793 | 122.6098 | 122.7429 | 66.7479 | -122.9044 | 122.7802 | 122.9122 | 122.5354 | 66.7423 | -123.0726
7.6406 | 123.2254 | -66.7374 | 56.282 | -0.019764 | -0.0014786 | 0.0011155 | 0.052491 | -0.0015791 | 0.060334 | -0.0070964 | -0.00025221 | 4.695e-05 | 0.064304 | 0.0051452 | 0.066461 | -66.7747 | 0.038035 | -66.6911 | 56.1557 | 55.8953 | 56.0238 | -66.7001 | -66.7199 | 0.03241 | -66.7727 | 56.0658 | 56.1932 | 55.8163 | -66.8546 | 0.03722 | -0.12635 | -0.037373 | 0.046301 | 0.009081 | -0.38675 | -0.25823 | -0.11726 | -0.21627 | 0.017454 | -0.035366 | 0.081889 | -0.088884 | -0.46571 | 122.8931 | 122.6327 | 122.7612 | 66.7754 | -122.9822 | 122.8031 | 122.9305 | 122.5537 | 66.7698 | -123.1367
8.6406 | 123.3032 | -66.7099 | 56.2408 | 0.0031287 | -0.0016924 | 0.0013291 | 0.052705 | -0.00093808 | 0.060334 | -0.0070964 | -3.8406e-05 | -0.00038025 | 0.064518 | 0.0049316 | 0.066675 | -66.7702 | 0.033457 | -66.6865 | 56.1511 | 55.9044 | 56.0192 | -66.7047 | -66.7199 | 0.018674 | -66.7682 | 56.0612 | 56.1932 | 55.8438 | -66.8592 | 0.005175 | -0.089731 | -0.060261 | 0.023413 | 0.018238 | -0.3364 | -0.22161 | -0.1493 | -0.17965 | -0.010012 | -0.058254 | 0.091046 | -0.047686 | -0.39704 | 122.861 | 122.6143 | 122.7291 | 66.7434 | -122.9456 | 122.7711 | 122.9031 | 122.5537 | 66.7286 | -123.1
9.6406 | 123.1888 | -66.7694 | 56.2683 | -0.012133 | -0.001265 | 0.0011155 | 0.052705 | -0.0013653 | 0.060334 | -0.0070964 | 0.00017519 | -0.00016665 | 0.064731 | 0.0049316 | 0.066675 | -66.7747 | 0.038035 | -66.6865 | 56.1511 | 55.8999 | 56.0284 | -66.6727 | -66.7245 | 0.023253 | -66.7682 | 56.0566 | 56.2023 | 55.885 | -66.8546 | 0.096736 | -0.1172 | -0.00533 | 0.082922 | -0.013814 | -0.36844 | -0.23992 | -0.085212 | -0.2117 | 0.044918 | 0.001255 | 0.086467 | -0.065994 | -0.38329 | 122.9205 | 122.6693 | 122.7978 | 66.8074 | -122.941 | 122.826 | 122.9717 | 122.6544 | 66.7927 | -123.1229
10.6406 | 123.2712 | -66.7465 | 56.2408 | -0.012133 | -0.0016924 | 0.0011155 | 0.052919 | -0.0011517 | 0.060334 | 0.00053414 | -3.8406e-05 | -0.00038025 | 0.064518 | 0.0049316 | 0.066888 | -66.7793 | 0.028878 | -66.6865 | 56.1511 | 55.9044 | 56.0284 | -66.6727 | -66.7245 | 0.03241 | -66.7727 | 56.0566 | 56.2023 | 55.8209 | -66.8638 | 0.073848 | -0.089731 | -0.032797 | 0.060034 | -0.013814 | -0.3364 | -0.21246 | -0.11726 | -0.18423 | 0.02203 | -0.026211 | 0.091047 | -0.038528 | -0.41993 | 122.8976 | 122.651 | 122.7749 | 66.7754 | -122.9135 | 122.8031 | 122.9488 | 122.5674 | 66.7789 | -123.1046
11.6406 | 123.1888 | -66.7694 | 56.282 | 0.0031287 | -0.0014786 | 0.0011155 | 0.052919 | -0.0011517 | 0.060548 | -0.0070964 | 0.00017519 | -0.00059405 | 0.064304 | 0.0051452 | 0.066675 | -66.7793 | 0.028878 | -66.6819 | 56.1511 | 55.909 | 56.0238 | -66.6635 | -66.7199 | 0.018674 | -66.7727 | 56.0703 | 56.1886 | 55.8255 | -66.8592 | 0.10589 | -0.13093 | -0.009909 | 0.0875 | -0.018394 | -0.37302 | -0.25823 | -0.089791 | -0.2117 | 0.049497 | -0.003323 | 0.086468 | -0.093462 | -0.45655 | 122.9205 | 122.6784 | 122.7932 | 66.7983 | -122.9456 | 122.8398 | 122.958 | 122.5949 | 66.7881 | -123.1412
12.6406 | 123.23 | -66.7465 | 56.2363 | 0.0031287 | -0.0014786 | 0.00090168 | 0.052919 | -0.0013653 | 0.060761 | 0.00053414 | -3.8406e-05 | -0.00038025 | 0.064304 | 0.0051452 | 0.066461 | -66.7747 | 0.033457 | -66.6728 | 56.1511 | 55.9044 | 56.0192 | -66.691 | -66.7245 | 0.023253 | -66.7727 | 56.0566 | 56.1977 | 55.8163 | -66.8592 | 0.055533 | -0.085153 | -0.028218 | 0.073769 | 0.018236 | -0.33182 | -0.21704 | -0.11268 | -0.17965 | 0.02203 | -0.026211 | 0.086468 | -0.038529 | -0.41993 | 122.8976 | 122.651 | 122.7658 | 66.78 | -122.9273 | 122.8031 | 122.9443 | 122.5629 | 66.7698 | -123.0955
13.6406 | 123.2117 | -66.7557 | 56.25 | -0.0045023 | -0.0014786 | 0.0011155 | 0.052705 | -0.0011517 | 0.060761 | 0.0081646 | -0.00025221 | -0.00016665 | 0.063877 | 0.005359 | 0.066675 | -66.7702 | 0.033457 | -66.6682 | 56.1557 | 55.8953 | 56.0238 | -66.6956 | -66.7199 | 0.023253 | -66.7636 | 56.0658 | 56.1886 | 55.8026 | -66.8684 | 0.060109 | -0.094307 | -0.014485 | 0.087502 | 0.027393 | -0.35471 | -0.22619 | -0.11268 | -0.18423 | 0.035764 | -0.007899 | 0.10478 | -0.061419 | -0.4474 | 122.9114 | 122.651 | 122.7795 | 66.7891 | -122.9456 | 122.8214 | 122.9443 | 122.5583 | 66.7789 | -123.1184
14.6406 | 123.2803 | -66.7282 | 56.2225 | -0.0045023 | -0.0014786 | 0.0013291 | 0.053132 | -0.0011517 | 0.060761 | -0.0070964 | 0.00017519 | -0.00016665 | 0.064518 | 0.0051452 | 0.066247 | -66.7702 | 0.033457 | -66.6773 | 56.1511 | 55.8999 | 56.0238 | -66.6727 | -66.7245 | 0.014095 | -66.7727 | 56.0703 | 56.1932 | 55.8209 | -66.8546 | 0.055537 | -0.07142 | -0.041951 | 0.050879 | -0.004658 | -0.32266 | -0.19872 | -0.12641 | -0.15219 | 0.003719 | -0.044522 | 0.081889 | -0.029375 | -0.40162 | 122.8793 | 122.6281 | 122.752 | 66.7617 | -122.8952 | 122.7986 | 122.9214 | 122.5491 | 66.7423 | -123.0772
15.6406 | 123.2025 | -66.7465 | 56.2958 | -0.0045023 | -0.0014786 | 0.0015427 | 0.052919 | -0.0015791 | 0.060548 | -0.022357 | -3.8406e-05 | 4.695e-05 | 0.064304 | 0.0049316 | 0.066675 | -66.7747 | 0.033457 | -66.6728 | 56.1603 | 55.9044 | 56.0238 | -66.6131 | -66.7153 | 0.018674 | -66.7727 | 56.0612 | 56.1932 | 55.8118 | -66.85 | 0.13337 | -0.1355 | -0.028218 | 0.073769 | -0.059605 | -0.39133 | -0.27197 | -0.10352 | -0.23459 | 0.031187 | -0.026211 | 0.07731 | -0.10262 | -0.48402 | 122.9068 | 122.651 | 122.7703 | 66.78 | -122.9089 | 122.8077 | 122.9397 | 122.5583 | 66.7652 | -123.1458
16.6406 | 123.3032 | -66.7557 | 56.2225 | 0.0031287 | -0.0016924 | 0.0011155 | 0.052919 | -0.0011517 | 0.060761 | -0.0070964 | -3.8406e-05 | -0.00059405 | 0.064304 | 0.0049316 | 0.066675 | -66.7747 | 0.033457 | -66.6636 | 56.1511 | 55.9044 | 56.0284 | -66.7047 | -66.7199 | 0.023253 | -66.7682 | 56.0658 | 56.1886 | 55.8072 | -66.8638 | 0.050951 | -0.07142 | -0.019063 | 0.09208 | 0.041129 | -0.31809 | -0.19415 | -0.1081 | -0.15677 | 0.035764 | -0.012478 | 0.095625 | -0.033953 | -0.41535 | 122.9068 | 122.6601 | 122.7841 | 66.7891 | -122.9273 | 122.8214 | 122.9443 | 122.5629 | 66.7789 | -123.0863
17.6406 | 123.1567 | -66.7786 | 56.2729 | -0.012133 | -0.0021196 | 0.0015427 | 0.052919 | -0.0011517 | 0.060761 | -0.0070964 | 0.00017519 | -0.00016665 | 0.06409 | 0.005359 | 0.066461 | -66.7702 | 0.033457 | -66.6728 | 56.1557 | 55.9044 | 56.0284 | -66.7139 | -66.7153 | 0.027831 | -66.7682 | 56.0612 | 56.1932 | 55.853 | -66.8638 | 0.064681 | -0.1172 | 0.008403 | 0.10581 | 0.041131 | -0.36844 | -0.2445 | -0.085215 | -0.2117 | 0.06323 | 0.01041 | 0.095625 | -0.079729 | -0.41992 | 122.9343 | 122.683 | 122.807 | 66.812 | -122.9868 | 122.8398 | 122.9717 | 122.6315 | 66.8064 | -123.1367
18.6406 | 123.2483 | -66.7236 | 56.218 | 0.0031287 | -0.0016924 | 0.0013291 | 0.053132 | -0.0013653 | 0.060548 | 0.0081646 | -3.8406e-05 | 4.695e-05 | 0.064731 | 0.0049316 | 0.066461 | -66.7793 | 0.028878 | -66.6682 | 56.1557 | 55.9044 | 56.0284 | -66.6956 | -66.7199 | 0.023253 | -66.7682 | 56.0658 | 56.1932 | 55.8209 | -66.8638 | 0.028066 | -0.062264 | -0.055685 | 0.055459 | 0.027393 | -0.31351 | -0.18957 | -0.14015 | -0.15219 | 0.003721 | -0.044521 | 0.095625 | -0.024798 | -0.39704 | 122.8793 | 122.6281 | 122.752 | 66.7525 | -122.9135 | 122.7894 | 122.9168 | 122.5445 | 66.7469 | -123.0817
19.6406 | 123.2712 | -66.7328 | 56.2592 | 0.01076 | -0.0016924 | 0.0013291 | 0.052919 | -0.0015791 | 0.060334 | 0.0081646 | -3.8406e-05 | 4.695e-05 | 0.064304 | 0.0049316 | 0.066461 | -66.7793 | 0.0243 | -66.659 | 56.1465 | 55.8953 | 56.0284 | -66.7001 | -66.7199 | 0.027831 | -66.7682 | 56.0703 | 56.184 | 55.8118 | -66.8592 | 0.032642 | -0.11262 | -0.04653 | 0.073771 | 0.041129 | -0.36386 | -0.23077 | -0.12641 | -0.18881 | 0.012876 | -0.035366 | 0.091046 | -0.075153 | -0.4474 | 122.8793 | 122.6281 | 122.7612 | 66.7571 | -122.9593 | 122.8031 | 122.9168 | 122.5445 | 66.7606 | -123.1184
20.6406 | 123.3215 | -66.7419 | 56.2546 | -0.0045023 | -0.0014786 | 0.00090168 | 0.052705 | -0.0011517 | 0.060334 | -0.014727 | 0.00038879 | -0.00038025 | 0.06409 | 0.0051452 | 0.066247 | -66.7747 | 0.038035 | -66.6728 | 56.1511 | 55.8999 | 56.0238 | -66.7276 | -66.7199 | 0.027831 | -66.7682 | 56.0566 | 56.1886 | 55.8072 | -66.8638 | 0.014323 | -0.10346 | -0.032796 | 0.069191 | 0.054868 | -0.35471 | -0.23077 | -0.12184 | -0.19797 | 0.022031 | -0.026211 | 0.095625 | -0.065997 | -0.4474 | 122.8931 | 122.6418 | 122.7658 | 66.78 | -122.9822 | 122.7986 | 122.9305 | 122.5491 | 66.7698 | -123.1184
21.7344 | 123.1567 | -66.7328 | 56.2912 | 0.0031287 | -0.001906 | 0.0011155 | 0.052705 | -0.0011517 | 0.060548 | 0.00053414 | 0.00017519 | -0.00016665 | 0.064518 | 0.0051452 | 0.066034 | -66.7702 | 0.028878 | -66.6728 | 56.1557 | 55.909 | 56.0284 | -66.6864 | -66.7291 | 0.027831 | -66.7682 | 56.0612 | 56.1886 | 55.853 | -66.8638 | 0.046379 | -0.13551 | -0.037373 | 0.060036 | 0.013657 | -0.38217 | -0.26281 | -0.13099 | -0.23001 | 0.003718 | -0.035366 | 0.095625 | -0.10262 | -0.43823 | 122.8885 | 122.6418 | 122.7612 | 66.7617 | -122.9776 | 122.794 | 122.9214 | 122.5858 | 66.7606 | -123.155
22.6719 | 123.3078 | -66.6733 | 56.2408 | 0.0031287 | -0.001265 | 0.00090168 | 0.052705 | -0.0013653 | 0.060761 | 0.00053414 | -0.00025221 | 4.695e-05 | 0.064304 | 0.0055726 | 0.066461 | -66.7656 | 0.033457 | -66.6728 | 56.1603 | 55.8999 | 56.0192 | -66.7093 | -66.7199 | 0.014095 | -66.7773 | 56.0658 | 56.184 | 55.8072 | -66.8638 | -0.036025 | -0.080574 | -0.092304 | 0.000527 | 0.036552 | -0.34098 | -0.22161 | -0.1905 | -0.17508 | -0.046633 | -0.10403 | 0.086468 | -0.056843 | -0.43366 | 122.8336 | 122.5731 | 122.6925 | 66.7067 | -122.9501 | 122.739 | 122.8573 | 122.4805 | 66.6874 | -123.1046
23.6875 | 123.1613 | -66.7557 | 56.282 | 0.0031287 | -0.0016924 | 0.0011155 | 0.052919 | -0.00093808 | 0.060975 | -0.0070964 | -3.8406e-05 | -0.00016665 | 0.064518 | 0.0049316 | 0.066461 | -66.7702 | 0.033457 | -66.6728 | 56.1557 | 55.9044 | 56.0284 | -66.6864 | -66.7153 | 0.03241 | -66.7682 | 56.0658 | 56.1886 | 55.8072 | -66.8638 | 0.069267 | -0.12635 | -0.014485 | 0.082924 | 0.013657 | -0.37759 | -0.25366 | -0.1081 | -0.21627 | 0.040342 | -0.012478 | 0.095625 | -0.093462 | -0.47486 | 122.9114 | 122.6601 | 122.7841 | 66.7891 | -122.9685 | 122.8214 | 122.9443 | 122.5629 | 66.7881 | -123.1458
24.6406 | 123.1567 | -66.7831 | 56.2729 | -0.0045023 | -0.0016924 | 0.0013291 | 0.052491 | -0.0017927 | 0.060548 | -0.014727 | -3.8406e-05 | -0.00038025 | 0.064518 | 0.005359 | 0.066675 | -66.7839 | 0.038035 | -66.659 | 56.1511 | 55.909 | 56.0284 | -66.6452 | -66.7199 | 0.027831 | -66.7727 | 56.0658 | 56.1932 | 55.8438 | -66.8638 | 0.13794 | -0.12177 | -0.000754 | 0.12412 | -0.013818 | -0.36386 | -0.2445 | -0.080637 | -0.20712 | 0.06323 | 0.01041 | 0.091047 | -0.079729 | -0.42908 | 122.9343 | 122.6922 | 122.8115 | 66.8212 | -122.9181 | 122.8489 | 122.9763 | 122.6269 | 66.811 | -123.1367
25.6406 | 123.2254 | -66.7328 | 56.3095 | -0.0045023 | -0.0014786 | 0.0015427 | 0.052919 | -0.0013653 | 0.060548 | 0.0081646 | 0.00017519 | -0.00016665 | 0.064518 | 0.0051452 | 0.066247 | -66.7702 | 0.028878 | -66.6682 | 56.1557 | 55.909 | 56.033 | -66.6498 | -66.7199 | 0.018674 | -66.7636 | 56.052 | 56.1932 | 55.8301 | -66.8638 | 0.08301 | -0.15382 | -0.037373 | 0.064614 | -0.018396 | -0.40048 | -0.27654 | -0.13099 | -0.25748 | 0.012876 | -0.030787 | 0.1002 | -0.11635 | -0.47944 | 122.8885 | 122.6418 | 122.7658 | 66.7617 | -122.9593 | 122.7848 | 122.9259 | 122.5629 | 66.7515 | -123.1733
26.6406 | 123.1613 | -66.7603 | 56.2683 | -0.012133 | -0.0014786 | 0.0011155 | 0.052705 | -0.00093808 | 0.060761 | -0.022357 | -3.8406e-05 | 0.00026075 | 0.064518 | 0.0051452 | 0.066461 | -66.7747 | 0.033457 | -66.6728 | 56.1557 | 55.909 | 56.0238 | -66.6315 | -66.7245 | 0.027831 | -66.7636 | 56.0658 | 56.1932 | 55.8209 | -66.8592 | 0.12879 | -0.11262 | -0.014485 | 0.087502 | -0.04129 | -0.35928 | -0.2445 | -0.098946 | -0.20254 | 0.035763 | -0.003321 | 0.095625 | -0.075152 | -0.4474 | 122.9159 | 122.6693 | 122.7841 | 66.7937 | -122.8998 | 122.826 | 122.9534 | 122.5812 | 66.7881 | -123.1275
27.6406 | 123.1842 | -66.774 | 56.3004 | -0.0045023 | -0.0014786 | 0.00090168 | 0.052919 | -0.0013653 | 0.060548 | 0.0081646 | -3.8406e-05 | 0.00026075 | 0.064304 | 0.0055726 | 0.066034 | -66.7702 | 0.038035 | -66.6682 | 56.1557 | 55.8999 | 56.0375 | -66.7185 | -66.7245 | 0.023253 | -66.7682 | 56.0566 | 56.1886 | 55.8347 | -66.8592 | 0.055525 | -0.14466 | 0.003826 | 0.10581 | 0.050288 | -0.40048 | -0.26281 | -0.085213 | -0.24374 | 0.049496 | 0.005833 | 0.091046 | -0.11177 | -0.4657 | 122.9297 | 122.6739 | 122.8115 | 66.812 | -123.0188 | 122.8306 | 122.9626 | 122.6086 | 66.7972 | -123.1596
28.6406 | 123.2117 | -66.7603 | 56.2546 | 0.0031287 | -0.0010512 | 0.0013291 | 0.053132 | -0.0011517 | 0.060334 | -0.014727 | -3.8406e-05 | -0.00016665 | 0.064304 | 0.0051452 | 0.066247 | -66.7702 | 0.033457 | -66.6682 | 56.1603 | 55.8999 | 56.0284 | -66.6635 | -66.7199 | 0.023253 | -66.7682 | 56.0612 | 56.1886 | 55.8163 | -66.8638 | 0.096739 | -0.094307 | -0.009907 | 0.09208 | -0.004659 | -0.35471 | -0.22619 | -0.10352 | -0.19339 | 0.040342 | -0.0079 | 0.095625 | -0.065997 | -0.43824 | 122.9205 | 122.6601 | 122.7886 | 66.7937 | -122.9181 | 122.8214 | 122.9488 | 122.5766 | 66.7835 | -123.1184
29.6406 | 123.1979 | -66.7603 | 56.2775 | -0.0045023 | -0.0014786 | 0.0015427 | 0.052491 | -0.0011517 | 0.060548 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.064304 | 0.005359 | 0.066461 | -66.7702 | 0.033457 | -66.6728 | 56.1603 | 55.8999 | 56.0238 | -66.6727 | -66.7199 | 0.027831 | -66.7682 | 56.0566 | 56.1932 | 55.8209 | -66.8638 | 0.087581 | -0.11719 | -0.009907 | 0.087502 | -7.9e-05 | -0.3776 | -0.25366 | -0.10352 | -0.22085 | 0.040342 | -0.0079 | 0.095625 | -0.084307 | -0.45655 | 122.9205 | 122.6601 | 122.7841 | 66.7937 | -122.9501 | 122.8169 | 122.9534 | 122.5812 | 66.7881 | -123.1412
30.6406 | 123.1613 | -66.7831 | 56.2775 | 0.0031287 | -0.0014786 | 0.00090168 | 0.052919 | -0.0011517 | 0.060761 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.063877 | 0.0055726 | 0.066247 | -66.7656 | 0.042614 | -66.6636 | 56.1603 | 55.8999 | 56.033 | -66.6727 | -66.7291 | 0.027831 | -66.7636 | 56.0658 | 56.1932 | 55.8347 | -66.8638 | 0.11047 | -0.11719 | 0.017559 | 0.11955 | 0.009077 | -0.3776 | -0.2445 | -0.080637 | -0.2117 | 0.054072 | 0.019567 | 0.1002 | -0.084307 | -0.44281 | 122.9434 | 122.683 | 122.8161 | 66.8258 | -122.9501 | 122.8489 | 122.9763 | 122.6178 | 66.811 | -123.1412
31.6406 | 123.2391 | -66.7236 | 56.2454 | -0.0045023 | -0.001906 | 0.0015427 | 0.053346 | -0.0011517 | 0.060334 | -0.014727 | 0.00017519 | 4.695e-05 | 0.06409 | 0.005359 | 0.066675 | -66.7747 | 0.028878 | -66.6728 | 56.1511 | 55.9044 | 56.0375 | -66.691 | -66.7153 | 0.027831 | -66.759 | 56.0612 | 56.184 | 55.8667 | -66.8684 | 0.032645 | -0.094308 | -0.051106 | 0.050881 | 0.018236 | -0.34097 | -0.20788 | -0.14472 | -0.18423 | 0.008299 | -0.035363 | 0.10936 | -0.06142 | -0.37872 | 122.8747 | 122.6281 | 122.7612 | 66.7525 | -122.9364 | 122.7848 | 122.9076 | 122.5903 | 66.7515 | -123.1138
32.6406 | 123.1613 | -66.7877 | 56.2912 | -0.0045023 | -0.0016924 | 0.0011155 | 0.052705 | -0.0013653 | 0.060761 | -0.0070964 | 0.00017519 | -0.00016665 | 0.06409 | 0.0051452 | 0.066034 | -66.7747 | 0.028878 | -66.6682 | 56.1603 | 55.909 | 56.0284 | -66.6086 | -66.7153 | 0.027831 | -66.7727 | 56.0612 | 56.1932 | 55.8072 | -66.8638 | 0.17915 | -0.13093 | 0.012981 | 0.11955 | -0.059606 | -0.38217 | -0.26281 | -0.076059 | -0.23001 | 0.072386 | 0.014988 | 0.091047 | -0.09804 | -0.48402 | 122.948 | 122.6967 | 122.8161 | 66.8166 | -122.8998 | 122.8489 | 122.9809 | 122.5949 | 66.8156 | -123.155
33.6406 | 123.2117 | -66.7465 | 56.2683 | 0.0031287 | -0.0014786 | 0.0011155 | 0.053132 | -0.0013653 | 0.060548 | -0.0070964 | 0.00017519 | -0.00038025 | 0.06409 | 0.0051452 | 0.066675 | -66.7702 | 0.028878 | -66.6682 | 56.1603 | 55.909 | 56.0284 | -66.6681 | -66.7245 | 0.023253 | -66.7682 | 56.0658 | 56.1932 | 55.8163 | -66.8638 | 0.078427 | -0.10804 | -0.02364 | 0.078347 | -8e-05 | -0.35928 | -0.23992 | -0.11726 | -0.20254 | 0.02203 | -0.021633 | 0.095625 | -0.075152 | -0.45197 | 122.9068 | 122.6555 | 122.7749 | 66.7754 | -122.9364 | 122.8123 | 122.9397 | 122.5629 | 66.7698 | -123.1321
34.6406 | 123.2346 | -66.7191 | 56.25 | 0.0031287 | -0.0014786 | 0.0013291 | 0.053132 | -0.0013653 | 0.060975 | -0.0070964 | 0.00038879 | -0.00038025 | 0.06409 | 0.0051452 | 0.066675 | -66.7747 | 0.033457 | -66.6728 | 56.1557 | 55.9044 | 56.0284 | -66.6635 | -66.7245 | 0.023253 | -66.7727 | 56.0658 | 56.1977 | 55.8209 | -66.8638 | 0.05554 | -0.094307 | -0.055684 | 0.046303 | -0.009237 | -0.34555 | -0.22161 | -0.14472 | -0.18423 | -0.005436 | -0.053677 | 0.091047 | -0.052262 | -0.42909 | 122.8747 | 122.6235 | 122.7474 | 66.7525 | -122.9135 | 122.7848 | 122.9168 | 122.54 | 66.7423 | -123.1138
35.6406 | 123.1979 | -66.7145 | 56.2912 | 0.0031287 | -0.001906 | 0.0015427 | 0.053132 | -0.00093808 | 0.06012 | 0.0081646 | 0.00038879 | 4.695e-05 | 0.064518 | 0.0049316 | 0.066247 | -66.7702 | 0.028878 | -66.6682 | 56.1557 | 55.909 | 56.0284 | -66.7414 | -66.7245 | 0.027831 | -66.7682 | 56.0658 | 56.1886 | 55.8621 | -66.8638 | -0.026878 | -0.13551 | -0.055683 | 0.046304 | 0.073182 | -0.38217 | -0.26281 | -0.1493 | -0.22543 | -0.010013 | -0.053676 | 0.095625 | -0.10262 | -0.42908 | 122.8702 | 122.6235 | 122.7429 | 66.7434 | -123.0326 | 122.7802 | 122.9031 | 122.5766 | 66.7423 | -123.155
36.6406 | 123.262 | -66.7191 | 56.2363 | -0.0045023 | -0.0014786 | 0.0013291 | 0.052919 | -0.0015791 | 0.060334 | -0.0070964 | -3.8406e-05 | 0.00026075 | 0.06409 | 0.0055726 | 0.066247 | -66.7793 | 0.038035 | -66.6636 | 56.1557 | 55.909 | 56.0238 | -66.6589 | -66.7245 | 0.027831 | -66.7682 | 56.0658 | 56.1886 | 55.853 | -66.8592 | 0.060119 | -0.080574 | -0.060263 | 0.055459 | -0.00466 | -0.32724 | -0.21246 | -0.14015 | -0.1705 | -0.005436 | -0.049099 | 0.091046 | -0.047686 | -0.3833 | 122.8747 | 122.6281 | 122.7429 | 66.7571 | -122.8952 | 122.7848 | 122.9076 | 122.572 | 66.7469 | -123.0955
37.6562 | 123.2391 | -66.7374 | 56.282 | 0.0031287 | -0.0014786 | 0.0013291 | 0.052491 | -0.0011517 | 0.060761 | -0.0070964 | -0.00025221 | -0.00016665 | 0.06409 | 0.0055726 | 0.066461 | -66.7793 | 0.028878 | -66.6636 | 56.1603 | 55.9044 | 56.033 | -66.6773 | -66.7153 | 0.027831 | -66.7727 | 56.0566 | 56.1932 | 55.8438 | -66.8592 | 0.060114 | -0.12177 | -0.041952 | 0.07377 | 0.013656 | -0.37759 | -0.24908 | -0.12183 | -0.22543 | 0.022032 | -0.035366 | 0.086468 | -0.088884 | -0.43823 | 122.8976 | 122.6418 | 122.7703 | 66.7662 | -122.9593 | 122.794 | 122.9305 | 122.5812 | 66.7652 | -123.1412
38.6406 | 123.2117 | -66.7465 | 56.2637 | 0.0031287 | -0.001265 | 0.0011155 | 0.052491 | -0.0013653 | 0.060548 | 0.00053414 | 0.00017519 | -0.00016665 | 0.064304 | 0.0051452 | 0.066461 | -66.7793 | 0.033457 | -66.6682 | 56.1603 | 55.9136 | 56.033 | -66.6498 | -66.7153 | 0.023253 | -66.7727 | 56.0658 | 56.184 | 55.8347 | -66.8638 | 0.096743 | -0.10346 | -0.032797 | 0.078347 | -0.018396 | -0.35013 | -0.23077 | -0.11726 | -0.19796 | 0.031187 | -0.026211 | 0.091047 | -0.079731 | -0.42908 | 122.9068 | 122.6601 | 122.7795 | 66.78 | -122.9135 | 122.8123 | 122.9305 | 122.5812 | 66.7698 | -123.1275
39.6406 | 123.143 | -66.774 | 56.2866 | 0.0031287 | -0.0014786 | 0.0011155 | 0.052705 | -0.0011517 | 0.060548 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.064304 | 0.0055726 | 0.066247 | -66.7793 | 0.033457 | -66.6636 | 56.1557 | 55.909 | 56.033 | -66.7093 | -66.7153 | 0.03241 | -66.7636 | 56.0612 | 56.1932 | 55.8072 | -66.8684 | 0.064683 | -0.13093 | -0.005331 | 0.11039 | 0.045708 | -0.37759 | -0.25365 | -0.094371 | -0.22543 | 0.058653 | 0.010412 | 0.10478 | -0.093462 | -0.47944 | 122.9297 | 122.683 | 122.807 | 66.8074 | -122.9959 | 122.8352 | 122.9671 | 122.5812 | 66.8064 | -123.155
40.6406 | 123.1613 | -66.7694 | 56.2637 | -0.0045023 | -0.0014786 | 0.0015427 | 0.052491 | -0.0015791 | 0.060761 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.063877 | 0.005359 | 0.066034 | -66.7702 | 0.0243 | -66.6682 | 56.1465 | 55.9044 | 56.033 | -66.7459 | -66.7153 | 0.023253 | -66.7636 | 56.0658 | 56.1932 | 55.8804 | -66.8592 | 0.023474 | -0.1172 | -0.000752 | 0.10124 | 0.077761 | -0.35928 | -0.23077 | -0.089791 | -0.19796 | 0.054075 | 0.005834 | 0.095625 | -0.070574 | -0.3833 | 122.9159 | 122.6739 | 122.8024 | 66.7937 | -123.0097 | 122.8352 | 122.9626 | 122.6498 | 66.7927 | -123.1229
41.6406 | 123.2071 | -66.7969 | 56.2592 | 0.0031287 | -0.0016924 | 0.0011155 | 0.053132 | -0.0011517 | 0.060334 | -0.0070964 | -3.8406e-05 | -0.00016665 | 0.063877 | 0.0055726 | 0.066461 | -66.7702 | 0.028878 | -66.6728 | 56.1557 | 55.9044 | 56.0238 | -66.7185 | -66.7199 | 0.03241 | -66.7636 | 56.0612 | 56.1932 | 55.8255 | -66.8546 | 0.078413 | -0.10346 | 0.026714 | 0.12412 | 0.04571 | -0.35471 | -0.23535 | -0.057746 | -0.19796 | 0.076963 | 0.0333 | 0.091046 | -0.065996 | -0.43366 | 122.9526 | 122.7013 | 122.8207 | 66.8258 | -122.9776 | 122.8581 | 122.99 | 122.6224 | 66.8293 | -123.1138
42.6406 | 123.1613 | -66.7419 | 56.2592 | -0.019764 | -0.0014786 | 0.0011155 | 0.052705 | -0.0013653 | 0.060548 | 0.0081646 | 0.00017519 | 4.695e-05 | 0.064304 | 0.0055726 | 0.066034 | -66.7702 | 0.028878 | -66.6682 | 56.1603 | 55.9044 | 56.033 | -66.7368 | -66.7199 | 0.023253 | -66.7682 | 56.0658 | 56.1932 | 55.8163 | -66.8638 | 0.005165 | -0.098884 | -0.028218 | 0.073769 | 0.068604 | -0.35471 | -0.22619 | -0.12184 | -0.19339 | 0.022031 | -0.026211 | 0.095625 | -0.065996 | -0.44282 | 122.9022 | 122.6464 | 122.7749 | 66.7708 | -122.9959 | 122.8077 | 122.9351 | 122.5583 | 66.7652 | -123.1229
43.6406 | 123.1888 | -66.7694 | 56.2866 | -0.0045023 | -0.0014786 | 0.0017565 | 0.052705 | -0.00093808 | 0.060761 | 0.00053414 | 0.00017519 | -0.00016665 | 0.064518 | 0.005359 | 0.066247 | -66.7747 | 0.028878 | -66.6636 | 56.1557 | 55.909 | 56.0284 | -66.7368 | -66.7199 | 0.018674 | -66.7544 | 56.0658 | 56.1886 | 55.8347 | -66.8592 | 0.032631 | -0.13093 | -0.00533 | 0.10581 | 0.073182 | -0.37759 | -0.25823 | -0.089791 | -0.22085 | 0.049497 | 0.014991 | 0.10478 | -0.09804 | -0.45197 | 122.9251 | 122.6784 | 122.7978 | 66.7983 | -123.0234 | 122.8352 | 122.958 | 122.6041 | 66.7881 | -123.1458
44.6406 | 123.1613 | -66.7831 | 56.2958 | 0.0031287 | -0.001906 | 0.0013291 | 0.052919 | -0.0011517 | 0.060761 | 0.0081646 | 0.00017519 | -0.00016665 | 0.06409 | 0.0055726 | 0.066461 | -66.7747 | 0.028878 | -66.6636 | 56.1694 | 55.9044 | 56.0238 | -66.7047 | -66.7245 | 0.023253 | -66.7636 | 56.0566 | 56.184 | 55.8072 | -66.8638 | 0.078417 | -0.12635 | 0.008403 | 0.11955 | 0.041129 | -0.39133 | -0.27197 | -0.080637 | -0.23916 | 0.058651 | 0.019567 | 0.1002 | -0.11177 | -0.4886 | 122.9526 | 122.6876 | 122.807 | 66.812 | -123.0005 | 122.8398 | 122.9671 | 122.5903 | 66.8064 | -123.1596
45.6406 | 123.262 | -66.7145 | 56.3049 | 0.0031287 | -0.0014786 | 0.0011155 | 0.052705 | -0.0013653 | 0.060334 | -0.0070964 | -3.8406e-05 | -0.00038025 | 0.064518 | 0.0051452 | 0.066247 | -66.7747 | 0.028878 | -66.6728 | 56.1465 | 55.9044 | 56.0238 | -66.7414 | -66.7199 | 0.018674 | -66.7636 | 56.0566 | 56.1886 | 55.8575 | -66.8638 | -0.026878 | -0.1584 | -0.060261 | 0.041726 | 0.068604 | -0.40048 | -0.28112 | -0.1493 | -0.24832 | -0.005434 | -0.049097 | 0.1002 | -0.11635 | -0.44739 | 122.861 | 122.6189 | 122.7383 | 66.7434 | -123.0463 | 122.7711 | 122.9031 | 122.572 | 66.7332 | -123.1687
46.6406 | 123.1934 | -66.7419 | 56.2775 | -0.0045023 | -0.0014786 | 0.0013291 | 0.052705 | -0.0013653 | 0.060334 | 0.00053414 | -0.00025221 | 0.00026075 | 0.064304 | 0.005359 | 0.066461 | -66.7702 | 0.042614 | -66.6728 | 56.1557 | 55.9044 | 56.033 | -66.7047 | -66.7245 | 0.023253 | -66.7636 | 56.0612 | 56.1932 | 55.8575 | -66.8684 | 0.037218 | -0.12177 | -0.028218 | 0.069191 | 0.031973 | -0.37302 | -0.2445 | -0.12641 | -0.21628 | 0.017452 | -0.021632 | 0.10478 | -0.084307 | -0.41992 | 122.8976 | 122.6464 | 122.7749 | 66.7846 | -122.9822 | 122.8031 | 122.9351 | 122.5995 | 66.7652 | -123.1458
47.6406 | 123.1384 | -66.7374 | 56.2866 | -0.012133 | -0.0014786 | 0.0015427 | 0.052919 | -0.0013653 | 0.060334 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.0055726 | 0.066461 | -66.7747 | 0.028878 | -66.6636 | 56.1557 | 55.8999 | 56.033 | -66.7459 | -66.7199 | 0.027831 | -66.7636 | 56.0612 | 56.1977 | 55.8575 | -66.8592 | -0.008569 | -0.13093 | -0.037373 | 0.07377 | 0.082339 | -0.38675 | -0.25365 | -0.12183 | -0.22543 | 0.017454 | -0.026209 | 0.095625 | -0.088883 | -0.42908 | 122.8931 | 122.6372 | 122.7703 | 66.7662 | -123.0326 | 122.7986 | 122.9351 | 122.5949 | 66.7652 | -123.1458
48.6406 | 123.2117 | -66.7374 | 56.2637 | 0.0031287 | -0.0021196 | 0.00090168 | 0.052919 | -0.0013653 | 0.060548 | 0.0081646 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.0057862 | 0.066675 | -66.7656 | 0.028878 | -66.659 | 56.1557 | 55.909 | 56.033 | -66.6727 | -66.7108 | 0.027831 | -66.7636 | 56.0566 | 56.1932 | 55.8209 | -66.8592 | 0.064693 | -0.10804 | -0.028217 | 0.078349 | 0.013656 | -0.35471 | -0.23077 | -0.12183 | -0.20712 | 0.026611 | -0.026209 | 0.095625 | -0.070574 | -0.44282 | 122.8931 | 122.6464 | 122.7703 | 66.7662 | -122.9364 | 122.794 | 122.9305 | 122.5583 | 66.7652 | -123.1229
49.6406 | 123.1659 | -66.7557 | 56.3004 | 0.0031287 | -0.001906 | 0.0013291 | 0.052705 | -0.0011517 | 0.060334 | 0.0081646 | 0.00038879 | 4.695e-05 | 0.064304 | 0.0051452 | 0.066247 | -66.7702 | 0.0243 | -66.6682 | 56.1557 | 55.909 | 56.0284 | -66.7093 | -66.7199 | 0.023253 | -66.7636 | 56.0612 | 56.1932 | 55.8163 | -66.8638 | 0.046372 | -0.14466 | -0.014485 | 0.087502 | 0.04113 | -0.39133 | -0.27197 | -0.1081 | -0.23916 | 0.035764 | -0.007899 | 0.1002 | -0.10719 | -0.48402 | 122.9114 | 122.6647 | 122.7841 | 66.78 | -123.0097 | 122.8169 | 122.9488 | 122.572 | 66.7789 | -123.1641
50.6406 | 123.2117 | -66.7603 | 56.3049 | -0.012133 | -0.0016924 | 0.0013291 | 0.052491 | -0.0013653 | 0.060334 | 0.00053414 | 0.00060239 | 4.695e-05 | 0.06409 | 0.005359 | 0.066675 | -66.7702 | 0.033457 | -66.6682 | 56.1557 | 55.8999 | 56.0375 | -66.6635 | -66.7108 | 0.018674 | -66.7636 | 56.0566 | 56.1886 | 55.8392 | -66.8592 | 0.096739 | -0.14924 | -0.009907 | 0.09208 | -0.004659 | -0.40506 | -0.26739 | -0.098946 | -0.24832 | 0.049499 | -0.003321 | 0.095625 | -0.11635 | -0.4657 | 122.9159 | 122.6601 | 122.7978 | 66.7937 | -122.9684 | 122.8169 | 122.9488 | 122.5995 | 66.7789 | -123.1641
51.6406 | 123.2025 | -66.7374 | 56.2454 | 0.01076 | -0.0014786 | 0.0013291 | 0.052705 | -0.0013653 | 0.060548 | -0.0070964 | 0.00038879 | -0.00038025 | 0.06409 | 0.0057862 | 0.066461 | -66.7702 | 0.0243 | -66.6682 | 56.1511 | 55.9044 | 56.0284 | -66.7001 | -66.7153 | 0.027831 | -66.7682 | 56.0703 | 56.1886 | 55.8621 | -66.8546 | 0.03722 | -0.094308 | -0.032795 | 0.069192 | 0.031972 | -0.34097 | -0.21703 | -0.11726 | -0.17507 | 0.022032 | -0.030788 | 0.086467 | -0.056841 | -0.3833 | 122.8885 | 122.6418 | 122.7658 | 66.7617 | -122.9456 | 122.8077 | 122.9259 | 122.5995 | 66.7652 | -123.1
52.6406 | 123.2666 | -66.7557 | 56.3187 | 0.0031287 | -0.001906 | 0.00090168 | 0.052705 | -0.0011517 | 0.060334 | -0.0070964 | 0.00038879 | 4.695e-05 | 0.064304 | 0.005359 | 0.066247 | -66.7793 | 0.033457 | -66.6682 | 56.1557 | 55.9136 | 56.0238 | -66.691 | -66.7199 | 0.036989 | -66.759 | 56.0612 | 56.1886 | 55.8575 | -66.8638 | 0.064688 | -0.16297 | -0.023642 | 0.087502 | 0.022814 | -0.40506 | -0.29486 | -0.1081 | -0.25747 | 0.035764 | -0.00332 | 0.10478 | -0.13008 | -0.46112 | 122.9114 | 122.6693 | 122.7795 | 66.7891 | -123.0097 | 122.8169 | 122.9443 | 122.6132 | 66.7927 | -123.1824
53.6406 | 123.1384 | -66.7374 | 56.3095 | 0.0031287 | -0.001265 | 0.00090168 | 0.052705 | -0.0015791 | 0.060334 | -0.014727 | -3.8406e-05 | 4.695e-05 | 0.064304 | 0.0055726 | 0.06582 | -66.7702 | 0.0243 | -66.6636 | 56.1603 | 55.909 | 56.033 | -66.6818 | -66.7108 | 0.023253 | -66.7636 | 56.0612 | 56.1794 | 55.8392 | -66.8684 | 0.055536 | -0.14924 | -0.032795 | 0.07377 | 0.018234 | -0.40048 | -0.27654 | -0.13099 | -0.24832 | 0.026611 | -0.026209 | 0.10478 | -0.13009 | -0.47028 | 122.8976 | 122.6464 | 122.7703 | 66.7617 | -122.9913 | 122.7986 | 122.9168 | 122.5766 | 66.7606 | -123.1779
54.6562 | 123.3032 | -66.6916 | 56.2683 | 0.0031287 | -0.001906 | 0.0011155 | 0.052705 | -0.0013653 | 0.06012 | 0.015795 | 0.00038879 | 4.695e-05 | 0.064518 | 0.0055726 | 0.066675 | -66.7702 | 0.033457 | -66.6636 | 56.1511 | 55.9044 | 56.0375 | -66.7001 | -66.7199 | 0.023253 | -66.7636 | 56.0658 | 56.1886 | 55.8072 | -66.8592 | -0.008557 | -0.1172 | -0.078572 | 0.027993 | 0.03655 | -0.36386 | -0.23076 | -0.16761 | -0.20254 | -0.028323 | -0.071986 | 0.095625 | -0.07973 | -0.46113 | 122.8427 | 122.596 | 122.7291 | 66.725 | -122.9685 | 122.7574 | 122.8802 | 122.4988 | 66.7148 | -123.1275
55.6406 | 123.1659 | -66.7557 | 56.3095 | -0.0045023 | -0.001906 | 0.0015427 | 0.052491 | -0.0011517 | 0.060761 | -0.0070964 | 0.00038879 | -0.00038025 | 0.06409 | 0.0055726 | 0.066247 | -66.7747 | 0.033457 | -66.6636 | 56.1557 | 55.9044 | 56.0284 | -66.7368 | -66.7199 | 0.027831 | -66.7682 | 56.0566 | 56.184 | 55.8347 | -66.8729 | 0.018898 | -0.15382 | -0.019063 | 0.09208 | 0.073182 | -0.40506 | -0.28112 | -0.11726 | -0.2529 | 0.035764 | -0.012478 | 0.10478 | -0.12551 | -0.47486 | 122.9114 | 122.6601 | 122.7841 | 66.7891 | -123.0463 | 122.8123 | 122.9397 | 122.5903 | 66.7835 | -123.1824
56.6406 | 123.2346 | -66.7191 | 56.25 | -0.0045023 | -0.001265 | 0.0011155 | 0.052919 | -0.0011517 | 0.06012 | -0.0070964 | 0.00038879 | 4.695e-05 | 0.064518 | 0.0055726 | 0.066461 | -66.7702 | 0.042614 | -66.6636 | 56.1511 | 55.8953 | 56.0238 | -66.6727 | -66.7199 | 0.018674 | -66.7636 | 56.0566 | 56.184 | 55.8347 | -66.8592 | 0.046382 | -0.098886 | -0.051106 | 0.055459 | 0.009077 | -0.35471 | -0.22619 | -0.14015 | -0.19339 | -0.000857 | -0.04452 | 0.095625 | -0.065998 | -0.41535 | 122.8702 | 122.6143 | 122.7429 | 66.7617 | -122.9227 | 122.7757 | 122.9031 | 122.5537 | 66.7377 | -123.1092
57.6406 | 123.1705 | -66.7557 | 56.3187 | -0.0045023 | -0.001906 | 0.0011155 | 0.052919 | -0.0011517 | 0.060334 | 0.0081646 | 0.00017519 | -0.00016665 | 0.064304 | 0.0055726 | 0.066461 | -66.7656 | 0.033457 | -66.6682 | 56.1557 | 55.8999 | 56.0238 | -66.7276 | -66.7245 | 0.023253 | -66.7682 | 56.0612 | 56.1886 | 55.8804 | -66.8638 | 0.028056 | -0.16297 | -0.009907 | 0.087502 | 0.059446 | -0.4188 | -0.29486 | -0.1081 | -0.25747 | 0.031185 | -0.012478 | 0.095625 | -0.13008 | -0.43823 | 122.9114 | 122.6555 | 122.7795 | 66.7891 | -123.0463 | 122.8169 | 122.9443 | 122.6361 | 66.7789 | -123.1824
58.6406 | 123.1979 | -66.7511 | 56.3049 | -0.0045023 | -0.001906 | 0.0011155 | 0.052705 | -0.0011517 | 0.060548 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.06409 | 0.0055726 | 0.066461 | -66.7656 | 0.0243 | -66.6728 | 56.1511 | 55.9044 | 56.0284 | -66.6864 | -66.7108 | 0.027831 | -66.759 | 56.0612 | 56.1886 | 55.8072 | -66.8592 | 0.06469 | -0.15382 | -0.014484 | 0.078347 | 0.013657 | -0.40048 | -0.27654 | -0.1081 | -0.24374 | 0.040344 | -0.007897 | 0.1002 | -0.11635 | -0.49775 | 122.9022 | 122.6555 | 122.7795 | 66.7754 | -122.9913 | 122.8123 | 122.9397 | 122.5583 | 66.7789 | -123.1641
59.6406 | 123.1247 | -66.7328 | 56.3004 | -0.012133 | -0.001906 | 0.0013291 | 0.052919 | -0.00093808 | 0.06012 | 0.00053414 | 0.00038879 | -0.00016665 | 0.06409 | 0.005359 | 0.066034 | -66.7702 | 0.033457 | -66.6682 | 56.1465 | 55.909 | 56.0238 | -66.7139 | -66.7153 | 0.03241 | -66.7682 | 56.0566 | 56.1932 | 55.8575 | -66.8684 | 0.018905 | -0.15382 | -0.037373 | 0.064614 | 0.045709 | -0.39133 | -0.27654 | -0.13557 | -0.24374 | 0.017454 | -0.035366 | 0.1002 | -0.10719 | -0.44281 | 122.8793 | 122.6418 | 122.7566 | 66.7662 | -123.0142 | 122.7894 | 122.9259 | 122.5903 | 66.7652 | -123.1687
60.6406 | 123.2025 | -66.7511 | 56.3049 | 0.0031287 | -0.0016924 | 0.0011155 | 0.052919 | -0.0013653 | 0.060548 | 0.0081646 | -0.00025221 | -0.00016665 | 0.064304 | 0.0057862 | 0.066461 | -66.7656 | 0.033457 | -66.6636 | 56.1511 | 55.8953 | 56.0284 | -66.7139 | -66.7245 | 0.03241 | -66.759 | 56.0703 | 56.1886 | 55.8438 | -66.8729 | 0.037216 | -0.15382 | -0.014484 | 0.087503 | 0.050287 | -0.40964 | -0.27654 | -0.12184 | -0.23459 | 0.026608 | -0.007897 | 0.11394 | -0.11635 | -0.46112 | 122.9022 | 122.6464 | 122.7795 | 66.7846 | -123.0188 | 122.8214 | 122.9397 | 122.5949 | 66.7835 | -123.1779
61.6406 | 123.1796 | -66.7465 | 56.2866 | -0.0045023 | -0.0014786 | 0.00090168 | 0.052919 | -0.0011517 | 0.060334 | -0.0070964 | 0.00038879 | -0.00016665 | 0.064304 | 0.0055726 | 0.066247 | -66.761 | 0.033457 | -66.6636 | 56.1557 | 55.9044 | 56.0284 | -66.723 | -66.7153 | 0.027831 | -66.7727 | 56.0703 | 56.184 | 55.8118 | -66.8638 | 0.02348 | -0.13093 | -0.014483 | 0.082925 | 0.059445 | -0.38217 | -0.25823 | -0.11726 | -0.21627 | 0.031187 | -0.026211 | 0.091047 | -0.10262 | -0.47486 | 122.9022 | 122.651 | 122.7749 | 66.78 | -123.0097 | 122.8169 | 122.9305 | 122.5583 | 66.7744 | -123.1504
62.6406 | 123.1796 | -66.7465 | 56.3141 | 0.0031287 | -0.0021196 | 0.0011155 | 0.052919 | -0.0015791 | 0.060548 | -0.0070964 | 0.00038879 | 4.695e-05 | 0.064304 | 0.0057862 | 0.066034 | -66.7702 | 0.033457 | -66.6728 | 56.1557 | 55.909 | 56.0284 | -66.6818 | -66.7153 | 0.018674 | -66.759 | 56.0612 | 56.1886 | 55.8804 | -66.8684 | 0.064691 | -0.15839 | -0.02364 | 0.073769 | 0.009078 | -0.40506 | -0.2857 | -0.12184 | -0.2529 | 0.031187 | -0.012475 | 0.10936 | -0.12551 | -0.43365 | 122.9022 | 122.6555 | 122.7749 | 66.78 | -122.9959 | 122.8077 | 122.9351 | 122.627 | 66.7652 | -123.1824
63.6406 | 123.2071 | -66.7236 | 56.3232 | 0.0031287 | -0.001906 | 0.0015427 | 0.052705 | -0.0011517 | 0.060548 | -0.0070964 | 0.00038879 | -0.00016665 | 0.064518 | 0.0057862 | 0.066247 | -66.7702 | 0.028878 | -66.6682 | 56.1557 | 55.9044 | 56.0284 | -66.6956 | -66.7245 | 0.018674 | -66.7636 | 56.0566 | 56.1886 | 55.8026 | -66.8592 | 0.028066 | -0.16755 | -0.046528 | 0.055459 | 0.027393 | -0.41879 | -0.29485 | -0.13557 | -0.26663 | -0.000858 | -0.039942 | 0.095625 | -0.13466 | -0.52064 | 122.8793 | 122.6281 | 122.752 | 66.7525 | -123.0188 | 122.7802 | 122.9122 | 122.5262 | 66.7423 | -123.1824
64.6406 | 123.1888 | -66.7145 | 56.2866 | -0.0045023 | -0.0016924 | 0.0011155 | 0.052491 | -0.0011517 | 0.060334 | 0.00053414 | 0.00038879 | -0.00016665 | 0.06409 | 0.006 | 0.066247 | -66.7656 | 0.0243 | -66.6682 | 56.1557 | 55.9136 | 56.0284 | -66.6818 | -66.7199 | 0.023253 | -66.759 | 56.0566 | 56.1886 | 55.8804 | -66.8729 | 0.032648 | -0.13093 | -0.051105 | 0.046304 | 0.013656 | -0.37301 | -0.25823 | -0.15846 | -0.23001 | -0.005434 | -0.044518 | 0.11394 | -0.09804 | -0.40618 | 122.8702 | 122.6281 | 122.7429 | 66.7388 | -122.9685 | 122.7711 | 122.9031 | 122.5949 | 66.7377 | -123.1596
65.6406 | 123.2895 | -66.7053 | 56.2592 | 0.0031287 | -0.001906 | 0.0013291 | 0.052705 | -0.0011517 | 0.060334 | 0.0081646 | 0.00060239 | 4.695e-05 | 0.06409 | 0.0055726 | 0.066247 | -66.7747 | 0.028878 | -66.6682 | 56.1557 | 55.8999 | 56.0238 | -66.6727 | -66.7199 | 0.023253 | -66.7682 | 56.0612 | 56.184 | 55.8118 | -66.8684 | 0.032649 | -0.10346 | -0.069417 | 0.037148 | 0.004499 | -0.35928 | -0.23535 | -0.16304 | -0.19796 | -0.01459 | -0.062832 | 0.1002 | -0.075153 | -0.4474 | 122.861 | 122.6052 | 122.7291 | 66.7342 | -122.9318 | 122.7665 | 122.8893 | 122.5171 | 66.7286 | -123.1275
66.7031 | 123.1476 | -66.7419 | 56.3141 | -0.0045023 | -0.001906 | 0.0011155 | 0.052705 | -0.0013653 | 0.060334 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.0055726 | 0.066247 | -66.7702 | 0.028878 | -66.6636 | 56.1557 | 55.9044 | 56.0375 | -66.6406 | -66.7199 | 0.027831 | -66.759 | 56.0612 | 56.1932 | 55.8438 | -66.8684 | 0.10132 | -0.15839 | -0.028218 | 0.078347 | -0.022976 | -0.40964 | -0.27654 | -0.12641 | -0.2529 | 0.022031 | -0.017053 | 0.10936 | -0.12093 | -0.47028 | 122.8976 | 122.6464 | 122.7795 | 66.7708 | -122.9547 | 122.8031 | 122.9351 | 122.5858 | 66.7698 | -123.1824
67.6406 | 123.2254 | -66.7099 | 56.2775 | -0.0045023 | -0.001906 | 0.0013291 | 0.052705 | -0.0011517 | 0.060548 | 0.00053414 | 0.00060239 | -0.00038025 | 0.063877 | 0.0055726 | 0.066247 | -66.7702 | 0.038035 | -66.6636 | 56.1511 | 55.9044 | 56.033 | -66.7276 | -66.7199 | 0.023253 | -66.759 | 56.0566 | 56.184 | 55.8301 | -66.8592 | -0.01772 | -0.12635 | -0.060261 | 0.046304 | 0.064024 | -0.37302 | -0.2445 | -0.1493 | -0.22085 | -0.010012 | -0.049096 | 0.1002 | -0.093464 | -0.44739 | 122.861 | 122.6143 | 122.7429 | 66.7479 | -123.0051 | 122.7665 | 122.8939 | 122.54 | 66.7332 | -123.1367
68.6406 | 123.175 | -66.7511 | 56.3187 | -0.012133 | -0.0021196 | 0.00090168 | 0.052491 | -0.0013653 | 0.060334 | 0.0081646 | 0.00017519 | 4.695e-05 | 0.064304 | 0.0057862 | 0.066461 | -66.7656 | 0.038035 | -66.6682 | 56.1557 | 55.909 | 56.033 | -66.6727 | -66.7153 | 0.027831 | -66.7727 | 56.0703 | 56.1932 | 55.8575 | -66.8729 | 0.078426 | -0.16297 | -0.014484 | 0.082925 | 0.004499 | -0.40964 | -0.2857 | -0.12184 | -0.24832 | 0.035765 | -0.021633 | 0.1002 | -0.12551 | -0.46112 | 122.9068 | 122.6601 | 122.7841 | 66.7891 | -122.9913 | 122.8214 | 122.9443 | 122.6086 | 66.7789 | -123.1916
69.6406 | 123.2849 | -66.6824 | 56.2637 | 0.01076 | -0.0016924 | 0.0013291 | 0.052705 | -0.0011517 | 0.060334 | 0.0081646 | 0.00017519 | 4.695e-05 | 0.064304 | 0.0055726 | 0.066461 | -66.7656 | 0.038035 | -66.6728 | 56.1465 | 55.9044 | 56.033 | -66.691 | -66.7108 | 0.027831 | -66.7636 | 56.0658 | 56.1886 | 55.8392 | -66.8592 | -0.008554 | -0.1172 | -0.083149 | 0.009682 | 0.018236 | -0.35928 | -0.23077 | -0.17677 | -0.19796 | -0.028321 | -0.081141 | 0.095625 | -0.075152 | -0.4245 | 122.829 | 122.5869 | 122.7154 | 66.7205 | -122.9547 | 122.7482 | 122.871 | 122.5217 | 66.7103 | -123.1229
70.6406 | 123.1659 | -66.7694 | 56.3049 | 0.0031287 | -0.001906 | 0.00090168 | 0.052705 | -0.00093808 | 0.06012 | 0.0081646 | -3.8406e-05 | -0.00016665 | 0.064304 | 0.006 | 0.066247 | -66.7656 | 0.028878 | -66.6636 | 56.1557 | 55.9044 | 56.033 | -66.6589 | -66.7245 | 0.023253 | -66.759 | 56.0566 | 56.1932 | 55.8667 | -66.8638 | 0.11047 | -0.14924 | 0.003826 | 0.10581 | -0.00466 | -0.40048 | -0.27197 | -0.09437 | -0.24832 | 0.044918 | 0.010413 | 0.10478 | -0.11177 | -0.43823 | 122.9251 | 122.6739 | 122.8024 | 66.7983 | -122.9639 | 122.826 | 122.9626 | 122.6361 | 66.7927 | -123.1687
71.6406 | 123.2803 | -66.6962 | 56.2912 | 0.01076 | -0.0016924 | 0.00090168 | 0.052705 | -0.0013653 | 0.059907 | 0.00053414 | 0.00017519 | -0.00016665 | 0.06409 | 0.0055726 | 0.066461 | -66.761 | 0.028878 | -66.6636 | 56.1557 | 55.9044 | 56.0284 | -66.7459 | -66.7245 | 0.023253 | -66.759 | 56.0566 | 56.2023 | 55.8438 | -66.8638 | -0.049768 | -0.13551 | -0.064837 | 0.032571 | 0.082339 | -0.38675 | -0.26281 | -0.16761 | -0.23459 | -0.028324 | -0.062829 | 0.10478 | -0.088882 | -0.44739 | 122.8519 | 122.6006 | 122.7246 | 66.725 | -123.0371 | 122.7528 | 122.8985 | 122.54 | 66.7194 | -123.155
72.6406 | 123.2666 | -66.7007 | 56.2546 | 0.0031287 | -0.001906 | 0.0013291 | 0.053132 | -0.0015791 | 0.06012 | 0.00053414 | 0.00017519 | 4.695e-05 | 0.064304 | 0.0057862 | 0.06582 | -66.7747 | 0.028878 | -66.6636 | 56.1511 | 55.909 | 56.033 | -66.6818 | -66.7153 | 0.023253 | -66.7636 | 56.0566 | 56.1932 | 55.8026 | -66.8638 | 0.018915 | -0.10346 | -0.073994 | 0.037149 | 0.018234 | -0.34555 | -0.22161 | -0.16303 | -0.19797 | -0.014589 | -0.06283 | 0.1002 | -0.061419 | -0.45198 | 122.8519 | 122.6098 | 122.7337 | 66.7296 | -122.9364 | 122.7574 | 122.8939 | 122.5033 | 66.724 | -123.1184
73.6406 | 123.2941 | -66.687 | 56.2729 | 0.0031287 | -0.001906 | 0.0013291 | 0.052705 | -0.0015791 | 0.060334 | 0.00053414 | 0.00017519 | 4.695e-05 | 0.064304 | 0.0057862 | 0.066034 | -66.7656 | 0.028878 | -66.6682 | 56.1603 | 55.9044 | 56.033 | -66.6818 | -66.7108 | 0.023253 | -66.7636 | 56.0612 | 56.1886 | 55.8026 | -66.8638 | 0.005182 | -0.11262 | -0.078571 | 0.018838 | 0.013656 | -0.36844 | -0.23992 | -0.17677 | -0.2117 | -0.023743 | -0.076563 | 0.1002 | -0.084307 | -0.47029 | 122.8473 | 122.5915 | 122.72 | 66.7159 | -122.9547 | 122.7482 | 122.8756 | 122.4896 | 66.7103 | -123.1367
74.6406 | 123.1522 | -66.7374 | 56.3141 | -0.0045023 | -0.001906 | 0.0011155 | 0.052491 | -0.0017927 | 0.060548 | 0.00053414 | -3.8406e-05 | 0.00026075 | 0.064518 | 0.0057862 | 0.066247 | -66.7702 | 0.033457 | -66.6682 | 56.1511 | 55.8999 | 56.0284 | -66.7322 | -66.7199 | 0.023253 | -66.7544 | 56.0612 | 56.1932 | 55.8301 | -66.8684 | 0.005167 | -0.16297 | -0.032795 | 0.069192 | 0.064025 | -0.41422 | -0.2857 | -0.13099 | -0.2529 | 0.017454 | -0.017052 | 0.11394 | -0.12093 | -0.48401 | 122.8885 | 122.6372 | 122.7658 | 66.7708 | -123.0463 | 122.7986 | 122.9305 | 122.5674 | 66.7606 | -123.1824
75.6406 | 123.3032 | -66.6687 | 56.2775 | 0.0031287 | -0.0014786 | 0.0013291 | 0.052705 | -0.0011517 | 0.060334 | 0.00053414 | 0.00060239 | -0.00016665 | 0.063877 | 0.0057862 | 0.066247 | -66.7702 | 0.033457 | -66.6682 | 56.1603 | 55.9044 | 56.0284 | -66.7093 | -66.7199 | 0.027831 | -66.7636 | 56.0612 | 56.1932 | 55.8759 | -66.8638 | -0.040603 | -0.11719 | -0.10146 | 0.000527 | 0.04113 | -0.37302 | -0.24908 | -0.19508 | -0.21628 | -0.051211 | -0.094874 | 0.1002 | -0.084307 | -0.40161 | 122.829 | 122.5731 | 122.6971 | 66.7022 | -122.9868 | 122.7299 | 122.8619 | 122.5446 | 66.6965 | -123.1412
76.6406 | 123.1796 | -66.7191 | 56.2958 | 0.01076 | -0.0023334 | 0.0011155 | 0.052919 | -0.0013653 | 0.060761 | 0.00053414 | 0.00017519 | -0.00038025 | 0.064518 | 0.0057862 | 0.066034 | -66.7747 | 0.042614 | -66.6819 | 56.1923 | 55.9548 | 56.065 | -66.8009 | -66.7336 | 0.036989 | -66.7636 | 56.0612 | 56.1932 | 56.1918 | -66.8684 | -0.081827 | -0.10346 | -0.055684 | 0.037146 | 0.11897 | -0.34096 | -0.23076 | -0.1493 | -0.23459 | -0.014594 | -0.04452 | 0.10478 | -0.10262 | -0.10399 | 122.9114 | 122.6739 | 122.7841 | 66.7617 | -123.0967 | 122.7802 | 122.9122 | 122.9108 | 66.756 | -123.1641
77.6406 | 123.2941 | -66.6916 | 56.2546 | -0.0045023 | -0.0014786 | 0.0011155 | 0.053132 | -0.00093808 | 0.060334 | 0.015795 | 0.00038879 | -0.00016665 | 0.064304 | 0.0062136 | 0.066461 | -66.7656 | 0.038035 | -66.6682 | 56.174 | 55.9365 | 56.0559 | -66.7871 | -66.7062 | 0.036989 | -66.7773 | 56.0612 | 56.2023 | 56.2055 | -66.8775 | -0.095557 | -0.080572 | -0.073994 | 0.023415 | 0.11897 | -0.31808 | -0.19872 | -0.18593 | -0.19339 | -0.014587 | -0.085722 | 0.1002 | -0.052261 | -0.04906 | 122.8656 | 122.6281 | 122.7474 | 66.7296 | -123.0417 | 122.7528 | 122.8939 | 122.8971 | 66.7286 | -123.1321
78.6406 | 123.1979 | -66.7145 | 56.2729 | 0.01076 | -0.0016924 | 0.0015427 | 0.052705 | -0.0015791 | 0.059907 | 0.015795 | 0.00038879 | 4.695e-05 | 0.06409 | 0.0057862 | 0.066461 | -66.7702 | 0.038035 | -66.6636 | 56.1786 | 55.9319 | 56.0604 | -66.7963 | -66.7199 | 0.027831 | -66.7636 | 56.0658 | 56.1886 | 56.2055 | -66.8592 | -0.081826 | -0.094304 | -0.055683 | 0.050882 | 0.13271 | -0.34097 | -0.21245 | -0.14472 | -0.20712 | -0.005434 | -0.049097 | 0.095625 | -0.084307 | -0.06737 | 122.8931 | 122.6464 | 122.7749 | 66.7525 | -123.0692 | 122.7802 | 122.9031 | 122.92 | 66.7423 | -123.1321
79.6406 | 123.2483 | -66.7099 | 56.2637 | 0.0031287 | -0.001906 | 0.0011155 | 0.052919 | -0.0011517 | 0.060334 | 0.00053414 | 0.00017519 | -0.00038025 | 0.064304 | 0.006 | 0.066034 | -66.7747 | 0.042614 | -66.6773 | 56.174 | 55.9319 | 56.0604 | -66.7963 | -66.7153 | 0.03241 | -66.7544 | 56.0612 | 56.2023 | 56.2055 | -66.8729 | -0.086404 | -0.089727 | -0.064839 | 0.032569 | 0.11897 | -0.33181 | -0.20329 | -0.16304 | -0.20254 | -0.005434 | -0.044518 | 0.11852 | -0.061416 | -0.058215 | 122.8839 | 122.6418 | 122.7703 | 66.7525 | -123.06 | 122.7711 | 122.9122 | 122.9154 | 66.7423 | -123.1367
80.6406 | 123.262 | -66.7007 | 56.2775 | -0.012133 | -0.0023334 | 0.0013291 | 0.052705 | -0.0013653 | 0.06012 | 0.0081646 | 0.00038879 | 4.695e-05 | 0.064304 | 0.0057862 | 0.066461 | -66.7702 | 0.033457 | -66.6773 | 56.174 | 55.9457 | 56.065 | -66.7963 | -66.7199 | 0.03241 | -66.7544 | 56.0612 | 56.1977 | 56.2147 | -66.8592 | -0.095559 | -0.10346 | -0.069416 | 0.023414 | 0.11897 | -0.33181 | -0.21245 | -0.15846 | -0.21628 | -0.019167 | -0.053673 | 0.10478 | -0.079728 | -0.062791 | 122.8748 | 122.6464 | 122.7658 | 66.7342 | -123.0738 | 122.7619 | 122.8985 | 122.9154 | 66.7332 | -123.1367
81.6406 | 123.3261 | -66.6824 | 56.2546 | -0.0045023 | -0.001906 | 0.00090168 | 0.053132 | -0.0011517 | 0.06012 | 0.0081646 | 0.00060239 | 4.695e-05 | 0.06409 | 0.006 | 0.066461 | -66.7747 | 0.047193 | -66.6773 | 56.174 | 55.9365 | 56.065 | -66.7963 | -66.7245 | 0.03241 | -66.759 | 56.0566 | 56.1977 | 56.2147 | -66.8684 | -0.11387 | -0.080572 | -0.092305 | 0.005103 | 0.11897 | -0.31808 | -0.18956 | -0.18592 | -0.19797 | -0.042057 | -0.076562 | 0.10936 | -0.05684 | -0.039903 | 122.8564 | 122.6189 | 122.7475 | 66.7296 | -123.0509 | 122.739 | 122.8802 | 122.8971 | 66.7148 | -123.1229
82.6406 | 123.2346 | -66.6962 | 56.2729 | -0.0045023 | -0.0021196 | 0.0015427 | 0.052705 | -0.0013653 | 0.060548 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.064304 | 0.006 | 0.066034 | -66.7702 | 0.038035 | -66.6773 | 56.1877 | 55.9457 | 56.0696 | -66.8009 | -66.7291 | 0.036989 | -66.7544 | 56.0612 | 56.1932 | 56.2147 | -66.8684 | -0.10471 | -0.085147 | -0.073994 | 0.018836 | 0.12355 | -0.32723 | -0.20329 | -0.17219 | -0.2117 | -0.032903 | -0.058251 | 0.11394 | -0.079729 | -0.058213 | 122.8839 | 122.6418 | 122.7658 | 66.7342 | -123.0738 | 122.7574 | 122.8893 | 122.9108 | 66.7332 | -123.1412
83.6406 | 123.2941 | -66.7145 | 56.2454 | -0.0045023 | -0.002547 | 0.00090168 | 0.052919 | -0.0017927 | 0.060761 | 0.0081646 | 0.00017519 | -0.00016665 | 0.064731 | 0.006 | 0.066034 | -66.7656 | 0.047193 | -66.6819 | 56.1923 | 55.9502 | 56.0696 | -66.8055 | -66.7291 | 0.036989 | -66.759 | 56.0566 | 56.1932 | 56.2238 | -66.8684 | -0.090983 | -0.053102 | -0.051105 | 0.032569 | 0.12355 | -0.29518 | -0.17583 | -0.15388 | -0.18881 | -0.014592 | -0.044518 | 0.10936 | -0.052263 | -0.02159 | 122.9068 | 122.6647 | 122.7841 | 66.7617 | -123.0509 | 122.7711 | 122.9076 | 122.9383 | 66.7515 | -123.1138
84.6406 | 123.2254 | -66.6916 | 56.2546 | 0.01076 | -0.0023334 | 0.0015427 | 0.052705 | -0.0017927 | 0.060975 | 0.0081646 | -0.00025221 | -0.00016665 | 0.064304 | 0.0057862 | 0.066461 | -66.7656 | 0.042614 | -66.6911 | 56.1923 | 56.0006 | 56.0742 | -66.8146 | -66.7336 | 0.03241 | -66.759 | 56.0612 | 56.1932 | 56.2193 | -66.8592 | -0.12303 | -0.062258 | -0.073994 | 0.000524 | 0.12355 | -0.25397 | -0.1804 | -0.16761 | -0.19339 | -0.04206 | -0.067407 | 0.1002 | -0.061419 | -0.035324 | 122.8839 | 122.6922 | 122.7658 | 66.7342 | -123.0692 | 122.7528 | 122.8847 | 122.9108 | 66.724 | -123.1138
85.6406 | 123.262 | -66.7007 | 56.2683 | -0.012133 | -0.0016924 | 0.0011155 | 0.052919 | -0.0011517 | 0.06012 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.064518 | 0.006 | 0.066675 | -66.7656 | 0.038035 | -66.6728 | 56.1786 | 55.9319 | 56.065 | -66.7963 | -66.7199 | 0.023253 | -66.7682 | 56.0566 | 56.1886 | 56.2101 | -66.8729 | -0.095559 | -0.089727 | -0.064838 | 0.027993 | 0.12355 | -0.33639 | -0.20329 | -0.17219 | -0.2117 | -0.019167 | -0.067409 | 0.10478 | -0.07973 | -0.058214 | 122.8793 | 122.6327 | 122.7658 | 66.7388 | -123.0646 | 122.7574 | 122.8893 | 122.9108 | 66.724 | -123.1412
86.6406 | 123.2758 | -66.687 | 56.2592 | -0.0045023 | -0.001906 | 0.0011155 | 0.052919 | -0.0013653 | 0.060334 | 0.0081646 | 0.00017519 | 4.695e-05 | 0.063877 | 0.006 | 0.066247 | -66.7702 | 0.038035 | -66.659 | 56.1648 | 55.9319 | 56.0559 | -66.778 | -66.7199 | 0.023253 | -66.7682 | 56.0658 | 56.1932 | 56.1277 | -66.8638 | -0.090976 | -0.094306 | -0.083149 | 0.027995 | 0.11897 | -0.32723 | -0.20329 | -0.17677 | -0.19339 | -0.0329 | -0.081142 | 0.095625 | -0.065996 | -0.13147 | 122.8519 | 122.6189 | 122.7429 | 66.725 | -123.0371 | 122.7528 | 122.8802 | 122.8147 | 66.7103 | -123.1229
87.7031 | 123.2483 | -66.7282 | 56.2363 | -0.0045023 | -0.0021196 | 0.0011155 | 0.053346 | -0.0011517 | 0.06012 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.064304 | 0.0057862 | 0.066034 | -66.7702 | 0.038035 | -66.6682 | 56.1511 | 55.9182 | 56.033 | -66.7688 | -66.7153 | 0.018674 | -66.759 | 56.0612 | 56.1932 | 56.178 | -66.8638 | -0.04062 | -0.085153 | -0.041951 | 0.060036 | 0.10066 | -0.31808 | -0.2033 | -0.13557 | -0.17508 | 0.012876 | -0.030786 | 0.10478 | -0.043108 | -0.058221 | 122.8793 | 122.6464 | 122.7612 | 66.7662 | -123.0051 | 122.7894 | 122.9214 | 122.9063 | 66.7469 | -123.1
88.6406 | 123.2712 | -66.7007 | 56.2729 | 0.0031287 | -0.001906 | 0.0013291 | 0.053132 | -0.0013653 | 0.06012 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.06409 | 0.0062136 | 0.066247 | -66.7702 | 0.0243 | -66.6636 | 56.1557 | 56.0052 | 56.033 | -66.7505 | -66.7199 | 0.023253 | -66.7682 | 56.0566 | 56.1932 | 56.1552 | -66.8638 | -0.049769 | -0.1172 | -0.069416 | 0.037149 | 0.086918 | -0.2677 | -0.23992 | -0.16303 | -0.21628 | -0.019167 | -0.067409 | 0.095625 | -0.079729 | -0.11774 | 122.8564 | 122.7059 | 122.7337 | 66.725 | -123.0234 | 122.7574 | 122.8939 | 122.8559 | 66.724 | -123.1367
89.6406 | 123.2437 | -66.6824 | 56.2729 | 0.0031287 | -0.001906 | 0.0011155 | 0.053346 | -0.0015791 | 0.060548 | -0.0070964 | -3.8406e-05 | -0.00038025 | 0.064304 | 0.0062136 | 0.066247 | -66.7702 | 0.033457 | -66.6636 | 56.1511 | 55.9869 | 56.0375 | -66.7505 | -66.7108 | 0.018674 | -66.759 | 56.0612 | 56.1886 | 56.1368 | -66.8729 | -0.06808 | -0.12177 | -0.087727 | 0.018838 | 0.086918 | -0.28602 | -0.23534 | -0.1905 | -0.2117 | -0.028321 | -0.076562 | 0.11394 | -0.084307 | -0.13605 | 122.8335 | 122.6693 | 122.72 | 66.7159 | -123.0234 | 122.7436 | 122.871 | 122.8193 | 66.7011 | -123.1458
90.6406 | 123.262 | -66.6779 | 56.2637 | -0.0045023 | -0.001906 | 0.0013291 | 0.053132 | -0.0017927 | 0.06012 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.063663 | 0.006 | 0.066461 | -66.7702 | 0.042614 | -66.6682 | 56.1603 | 56.0601 | 56.033 | -66.7414 | -66.7062 | 0.023253 | -66.7636 | 56.0566 | 56.1886 | 56.1185 | -66.8729 | -0.0635 | -0.10346 | -0.092305 | 0.009682 | 0.073182 | -0.2036 | -0.23077 | -0.19508 | -0.20712 | -0.02832 | -0.085719 | 0.10936 | -0.075152 | -0.14521 | 122.8381 | 122.738 | 122.7108 | 66.7205 | -123.0051 | 122.7345 | 122.8664 | 122.7964 | 66.7011 | -123.1367
91.6406 | 123.262 | -66.7145 | 56.2454 | 0.0031287 | -0.0021196 | 0.0013291 | 0.053346 | -0.0015791 | 0.06012 | -0.0070964 | -3.8406e-05 | 4.695e-05 | 0.063663 | 0.006 | 0.066247 | -66.7702 | 0.028878 | -66.6636 | 56.1603 | 55.9777 | 56.0375 | -66.6635 | -66.7108 | 0.023253 | -66.7544 | 56.0612 | 56.184 | 55.9262 | -66.8684 | 0.050963 | -0.085151 | -0.055683 | 0.050882 | -8.1e-05 | -0.26771 | -0.20788 | -0.15388 | -0.18423 | 0.003723 | -0.03994 | 0.11394 | -0.06142 | -0.3192 | 122.8747 | 122.6922 | 122.752 | 66.7434 | -122.9089 | 122.7757 | 122.8985 | 122.6407 | 66.7377 | -123.1138
92.6406 | 123.2849 | -66.6779 | 56.2729 | 0.0031287 | -0.0021196 | 0.0013291 | 0.052919 | -0.0011517 | 0.060334 | 0.0081646 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.0057862 | 0.066034 | -66.7656 | 0.033457 | -66.6682 | 56.1557 | 55.9777 | 56.0284 | -66.7368 | -66.7245 | 0.023253 | -66.759 | 56.0566 | 56.1977 | 56.0819 | -66.8729 | -0.058922 | -0.1172 | -0.087727 | 0.009682 | 0.068604 | -0.29518 | -0.2445 | -0.19508 | -0.21628 | -0.046635 | -0.08114 | 0.11394 | -0.07515 | -0.19099 | 122.8335 | 122.6556 | 122.7062 | 66.7113 | -123.0097 | 122.7345 | 122.8756 | 122.7598 | 66.7011 | -123.1458
93.6406 | 123.23 | -66.7191 | 56.25 | 0.0031287 | -0.0023334 | 0.0013291 | 0.053346 | -0.0015791 | 0.060334 | 0.015795 | -0.00025221 | 4.695e-05 | 0.06409 | 0.0064274 | 0.066247 | -66.7702 | 0.028878 | -66.6682 | 56.1648 | 55.9686 | 56.0421 | -66.7459 | -66.7199 | 0.023253 | -66.759 | 56.0658 | 56.1977 | 56.0819 | -66.8684 | -0.02688 | -0.085151 | -0.051106 | 0.050881 | 0.077761 | -0.28145 | -0.20788 | -0.1493 | -0.18423 | -0.000857 | -0.039941 | 0.10936 | -0.052262 | -0.1681 | 122.8839 | 122.6876 | 122.7612 | 66.7479 | -122.9959 | 122.7848 | 122.9168 | 122.801 | 66.7423 | -123.1184
94.6406 | 123.317 | -66.6779 | 56.2454 | 0.0031287 | -0.001906 | 0.0011155 | 0.053132 | -0.0013653 | 0.060548 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.0062136 | 0.066247 | -66.7656 | 0.028878 | -66.6682 | 56.1557 | 55.964 | 56.0375 | -66.7276 | -66.7199 | 0.014095 | -66.759 | 56.0658 | 56.184 | 56.0773 | -66.8638 | -0.049764 | -0.089729 | -0.087727 | 0.009682 | 0.059446 | -0.28145 | -0.20788 | -0.18592 | -0.17965 | -0.042056 | -0.08114 | 0.10478 | -0.06142 | -0.1681 | 122.8335 | 122.6418 | 122.7154 | 66.7067 | -122.973 | 122.7436 | 122.8619 | 122.7552 | 66.692 | -123.1092
95.6406 | 123.23 | -66.6916 | 56.2683 | 0.0031287 | -0.0023334 | 0.00090168 | 0.052919 | -0.0017927 | 0.060548 | -0.0070964 | -3.8406e-05 | -0.00038025 | 0.064518 | 0.0057862 | 0.066034 | -66.7702 | 0.033457 | -66.6636 | 56.1557 | 55.9731 | 56.0375 | -66.7322 | -66.7199 | 0.023253 | -66.7636 | 56.0612 | 56.1932 | 56.0773 | -66.8684 | -0.04061 | -0.11262 | -0.078572 | 0.027993 | 0.068603 | -0.29518 | -0.23076 | -0.17677 | -0.20712 | -0.028323 | -0.071986 | 0.10478 | -0.075152 | -0.19099 | 122.8473 | 122.6647 | 122.7291 | 66.725 | -123.0005 | 122.7528 | 122.8847 | 122.7689 | 66.7148 | -123.1367
96.6406 | 123.0652 | -66.7053 | 56.2729 | -0.0045023 | -0.0023334 | 0.0013291 | 0.052919 | -0.0013653 | 0.060334 | 0.00053414 | -3.8406e-05 | -0.00038025 | 0.064304 | 0.006 | 0.066461 | -66.761 | 0.033457 | -66.6636 | 56.1557 | 55.964 | 56.0375 | -66.7322 | -66.7199 | 0.018674 | -66.759 | 56.0566 | 56.1932 | 56.059 | -66.8592 | -0.026877 | -0.1172 | -0.055682 | 0.041726 | 0.068603 | -0.30891 | -0.23534 | -0.15388 | -0.21628 | -0.01459 | -0.053674 | 0.1002 | -0.079729 | -0.21389 | 122.861 | 122.6693 | 122.7429 | 66.7388 | -123.0051 | 122.7619 | 122.8985 | 122.7643 | 66.724 | -123.1321
97.6406 | 123.2712 | -66.7236 | 56.2729 | -0.012133 | -0.002547 | 0.00090168 | 0.052705 | -0.0015791 | 0.060334 | -0.0070964 | -0.00025221 | 0.00026075 | 0.064304 | 0.006 | 0.066034 | -66.7702 | 0.028878 | -66.6682 | 56.1603 | 55.964 | 56.033 | -66.7322 | -66.7245 | 0.018674 | -66.7636 | 56.0612 | 56.1977 | 56.0682 | -66.8684 | -0.008566 | -0.11262 | -0.046528 | 0.055459 | 0.064025 | -0.30891 | -0.23992 | -0.14472 | -0.2117 | -0.000858 | -0.039942 | 0.10478 | -0.07515 | -0.20473 | 122.8839 | 122.6876 | 122.7566 | 66.7525 | -123.0051 | 122.7848 | 122.9214 | 122.7918 | 66.7423 | -123.1412
98.6406 | 123.2758 | -66.7053 | 56.2775 | -0.0045023 | -0.002547 | 0.00090168 | 0.052705 | -0.0015791 | 0.060548 | 0.00053414 | -0.00046581 | -0.00038025 | 0.06409 | 0.006 | 0.066247 | -66.7747 | 0.028878 | -66.6728 | 56.1511 | 55.9594 | 56.0284 | -66.7322 | -66.7153 | 0.023253 | -66.7636 | 56.0566 | 56.1886 | 56.0636 | -66.8638 | -0.026877 | -0.12635 | -0.069417 | 0.03257 | 0.059447 | -0.31807 | -0.24908 | -0.15846 | -0.22085 | -0.010012 | -0.058253 | 0.1002 | -0.088885 | -0.21388 | 122.8564 | 122.6647 | 122.7337 | 66.7342 | -123.0097 | 122.7619 | 122.8939 | 122.7689 | 66.7286 | -123.1412
99.6406 | 123.0881 | -66.7099 | 56.2729 | -0.012133 | -0.0027606 | 0.0013291 | 0.053132 | -0.0015791 | 0.060548 | 0.0081646 | -0.00046581 | 4.695e-05 | 0.06409 | 0.006 | 0.066461 | -66.7702 | 0.033457 | -66.6682 | 56.1603 | 55.9548 | 56.0284 | -66.7276 | -66.7108 | 0.018674 | -66.7636 | 56.0566 | 56.1932 | 56.059 | -66.8638 | -0.01772 | -0.11262 | -0.060261 | 0.041726 | 0.059446 | -0.31807 | -0.2445 | -0.15388 | -0.21628 | -0.000855 | -0.053675 | 0.1002 | -0.079729 | -0.21389 | 122.8702 | 122.6647 | 122.7383 | 66.7434 | -123.0005 | 122.7665 | 122.9031 | 122.7689 | 66.7286 | -123.1367
100.6406 | 123.2574 | -66.7145 | 56.2546 | -0.0045023 | -0.002547 | 0.00090168 | 0.053346 | -0.0017927 | 0.060548 | 0.0081646 | -0.00046581 | 4.695e-05 | 0.06409 | 0.006 | 0.066034 | -66.7656 | 0.033457 | -66.6636 | 56.1557 | 55.964 | 56.033 | -66.723 | -66.7199 | 0.023253 | -66.759 | 56.0612 | 56.1886 | 56.059 | -66.8546 | -0.008563 | -0.098885 | -0.051105 | 0.050882 | 0.059445 | -0.2906 | -0.22161 | -0.14014 | -0.19339 | -0.005434 | -0.044518 | 0.095625 | -0.065997 | -0.19558 | 122.8702 | 122.6785 | 122.7474 | 66.7479 | -122.9776 | 122.7757 | 122.9031 | 122.7735 | 66.7377 | -123.1092
101.6406 | 123.2117 | -66.7145 | 56.2729 | -0.0045023 | -0.002547 | 0.0013291 | 0.052705 | -0.0015791 | 0.060548 | 0.00053414 | -0.00025221 | -0.00016665 | 0.06409 | 0.0057862 | 0.066034 | -66.7656 | 0.028878 | -66.6636 | 56.1557 | 55.9594 | 56.0284 | -66.7322 | -66.7245 | 0.014095 | -66.759 | 56.0566 | 56.1932 | 56.0682 | -66.8684 | -0.017721 | -0.1172 | -0.051105 | 0.050882 | 0.068603 | -0.31349 | -0.2445 | -0.15388 | -0.21628 | -0.010013 | -0.044518 | 0.10936 | -0.079729 | -0.20473 | 122.8702 | 122.6739 | 122.7429 | 66.7434 | -123.0051 | 122.7711 | 122.9076 | 122.7826 | 66.7286 | -123.1412
102.6406 | 123.2437 | -66.6687 | 56.2637 | -0.0045023 | -0.0023334 | 0.0011155 | 0.052705 | -0.0015791 | 0.060548 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.064304 | 0.0057862 | 0.066461 | -66.7656 | 0.028878 | -66.6636 | 56.1511 | 55.9686 | 56.0421 | -66.7414 | -66.7153 | 0.018674 | -66.7544 | 56.0566 | 56.1932 | 56.0773 | -66.8638 | -0.072655 | -0.11262 | -0.096882 | 0.005105 | 0.07776 | -0.29518 | -0.22161 | -0.19508 | -0.20712 | -0.046633 | -0.085717 | 0.10936 | -0.070574 | -0.18642 | 122.8198 | 122.6373 | 122.7108 | 66.6976 | -123.0051 | 122.7253 | 122.8619 | 122.746 | 66.6874 | -123.1275
103.6406 | 123.2666 | -66.7099 | 56.2729 | 0.0031287 | -0.002547 | 0.0013291 | 0.052705 | -0.0011517 | 0.06012 | 0.0081646 | 0.00017519 | 0.00026075 | 0.064304 | 0.0062136 | 0.066461 | -66.7656 | 0.033457 | -66.6682 | 56.1511 | 55.9686 | 56.0467 | -66.7368 | -66.7153 | 0.023253 | -66.7544 | 56.052 | 56.1932 | 56.0727 | -66.8638 | -0.026878 | -0.12177 | -0.055683 | 0.041726 | 0.068604 | -0.30433 | -0.22619 | -0.15388 | -0.22086 | -0.005434 | -0.044518 | 0.10936 | -0.079729 | -0.20015 | 122.861 | 122.6785 | 122.7566 | 66.7434 | -123.0097 | 122.7619 | 122.9031 | 122.7826 | 66.7332 | -123.1367
104.6406 | 123.2712 | -66.7191 | 56.2454 | -0.012133 | -0.0016924 | 0.0011155 | 0.052705 | -0.0013653 | 0.06012 | 0.00053414 | 0.00017519 | -0.00016665 | 0.064518 | 0.006 | 0.066034 | -66.7656 | 0.033457 | -66.6682 | 56.1603 | 55.9777 | 56.0375 | -66.7368 | -66.7153 | 0.027831 | -66.7636 | 56.0612 | 56.184 | 56.0819 | -66.8638 | -0.017723 | -0.085151 | -0.046528 | 0.050881 | 0.068604 | -0.26771 | -0.20788 | -0.14472 | -0.18423 | 0.003721 | -0.04452 | 0.1002 | -0.06142 | -0.16353 | 122.8793 | 122.6968 | 122.7566 | 66.7525 | -122.9822 | 122.7802 | 122.9031 | 122.801 | 66.7469 | -123.1092
105.6406 | 123.2758 | -66.7145 | 56.2546 | -0.012133 | -0.0021196 | 0.0011155 | 0.052919 | -0.0013653 | 0.06012 | 0.00053414 | 0.00038879 | 4.695e-05 | 0.063877 | 0.0064274 | 0.066247 | -66.761 | 0.0243 | -66.6682 | 56.1603 | 55.9777 | 56.0284 | -66.7414 | -66.7153 | 0.027831 | -66.7544 | 56.0612 | 56.1932 | 56.0819 | -66.8638 | -0.026878 | -0.094307 | -0.046526 | 0.046304 | 0.073182 | -0.27687 | -0.22619 | -0.1493 | -0.19339 | -0.000856 | -0.03994 | 0.10936 | -0.061419 | -0.17268 | 122.8747 | 122.6922 | 122.7429 | 66.7388 | -122.9959 | 122.7757 | 122.9076 | 122.7964 | 66.7423 | -123.1184
106.6406 | 123.2849 | -66.6962 | 56.2683 | 0.01076 | -0.0023334 | 0.0015427 | 0.052705 | -0.0015791 | 0.059693 | 0.00053414 | 0.00038879 | 4.695e-05 | 0.06409 | 0.0062136 | 0.066247 | -66.7702 | 0.033457 | -66.6682 | 56.1603 | 55.9777 | 56.0375 | -66.7459 | -66.7153 | 0.027831 | -66.759 | 56.0566 | 56.184 | 56.0911 | -66.8684 | -0.049768 | -0.10804 | -0.073994 | 0.027993 | 0.077761 | -0.2906 | -0.23076 | -0.17219 | -0.2117 | -0.019167 | -0.062829 | 0.10936 | -0.084309 | -0.17726 | 122.8564 | 122.6739 | 122.7337 | 66.7296 | -123.0142 | 122.7528 | 122.8802 | 122.7872 | 66.724 | -123.1367
107.6406 | 123.2941 | -66.7236 | 56.2454 | -0.0045023 | -0.0023334 | 0.00090168 | 0.052705 | -0.0015791 | 0.06012 | -0.0070964 | -3.8406e-05 | -0.00016665 | 0.064304 | 0.006 | 0.066034 | -66.761 | 0.033457 | -66.6728 | 56.1648 | 55.9731 | 56.033 | -66.7322 | -66.7153 | 0.027831 | -66.759 | 56.0658 | 56.1886 | 56.0911 | -66.8684 | -0.008566 | -0.080573 | -0.037371 | 0.050881 | 0.059447 | -0.27229 | -0.21245 | -0.14472 | -0.17965 | 0.008299 | -0.035363 | 0.10936 | -0.056841 | -0.15437 | 122.8885 | 122.6968 | 122.7566 | 66.7571 | -122.9776 | 122.7894 | 122.9122 | 122.8147 | 66.7515 | -123.1138
108.6406 | 123.2208 | -66.7191 | 56.25 | 0.0031287 | -0.0023334 | 0.0011155 | 0.052919 | -0.0015791 | 0.06012 | 0.00053414 | 0.00017519 | 0.00047435 | 0.064304 | 0.0064274 | 0.066247 | -66.7702 | 0.033457 | -66.6544 | 56.1603 | 55.9686 | 56.0375 | -66.7459 | -66.7153 | 0.018674 | -66.7682 | 56.0566 | 56.1932 | 56.1048 | -66.8729 | -0.02688 | -0.089729 | -0.051106 | 0.064616 | 0.091496 | -0.28145 | -0.21245 | -0.15388 | -0.19339 | 0.003721 | -0.049099 | 0.10478 | -0.056841 | -0.14521 | 122.8793 | 122.6876 | 122.7566 | 66.7525 | -122.9959 | 122.7757 | 122.9122 | 122.8238 | 66.7377 | -123.1229
109.6406 | 123.2437 | -66.7145 | 56.2592 | -0.012133 | -0.001906 | 0.0011155 | 0.053132 | -0.0011517 | 0.06012 | -0.0070964 | -3.8406e-05 | 0.00026075 | 0.06409 | 0.0064274 | 0.066247 | -66.7656 | 0.028878 | -66.6636 | 56.1603 | 55.9869 | 56.0375 | -66.7414 | -66.7108 | 0.027831 | -66.7636 | 56.0612 | 56.184 | 56.0636 | -66.8684 | -0.026878 | -0.098884 | -0.051105 | 0.050882 | 0.07776 | -0.27229 | -0.22161 | -0.15388 | -0.19796 | 0.003723 | -0.049097 | 0.10478 | -0.075153 | -0.19557 | 122.8747 | 122.7013 | 122.752 | 66.7434 | -123.0005 | 122.7757 | 122.8985 | 122.7781 | 66.7423 | -123.1275
110.6406 | 123.2666 | -66.7099 | 56.2729 | -0.012133 | -0.0021196 | 0.0011155 | 0.052919 | -0.0011517 | 0.059907 | 0.00053414 | -3.8406e-05 | -0.00038025 | 0.063877 | 0.0064274 | 0.066247 | -66.7656 | 0.028878 | -66.6636 | 56.1603 | 55.9823 | 56.0375 | -66.7368 | -66.7108 | 0.018674 | -66.7636 | 56.0658 | 56.184 | 56.0865 | -66.8638 | -0.026878 | -0.11262 | -0.055683 | 0.046304 | 0.073182 | -0.2906 | -0.23534 | -0.15388 | -0.20712 | -0.000855 | -0.053675 | 0.1002 | -0.088886 | -0.18641 | 122.8702 | 122.6922 | 122.7474 | 66.7388 | -123.0097 | 122.7757 | 122.8939 | 122.7964 | 66.7286 | -123.1367
111.6406 | 123.2437 | -66.7145 | 56.2592 | -0.0045023 | -0.0023334 | 0.0013291 | 0.053346 | -0.0015791 | 0.06012 | -0.0070964 | 0.00038879 | 4.695e-05 | 0.063877 | 0.006641 | 0.066034 | -66.7564 | 0.033457 | -66.659 | 56.1603 | 55.9777 | 56.033 | -66.7459 | -66.7108 | 0.023253 | -66.7453 | 56.0566 | 56.1932 | 56.0132 | -66.8684 | -0.031457 | -0.098884 | -0.041948 | 0.055461 | 0.086918 | -0.28144 | -0.22619 | -0.15388 | -0.20254 | 0.003723 | -0.030782 | 0.1231 | -0.065996 | -0.24594 | 122.8747 | 122.6922 | 122.7474 | 66.7479 | -123.0051 | 122.7711 | 122.9076 | 122.7277 | 66.7377 | -123.1275
112.6406 | 123.2803 | -66.7191 | 56.2683 | 0.0031287 | -0.0023334 | 0.00090168 | 0.053132 | -0.0015791 | 0.06012 | 0.00053414 | 0.00017519 | 4.695e-05 | 0.064304 | 0.006 | 0.066247 | -66.761 | 0.033457 | -66.6636 | 56.1603 | 55.9823 | 56.0375 | -66.7368 | -66.7108 | 0.018674 | -66.759 | 56.052 | 56.1932 | 55.9171 | -66.8638 | -0.017723 | -0.10804 | -0.041949 | 0.055459 | 0.073182 | -0.28602 | -0.23076 | -0.14472 | -0.21628 | 0.0083 | -0.039941 | 0.10478 | -0.075152 | -0.35124 | 122.8793 | 122.7013 | 122.7566 | 66.7525 | -123.0051 | 122.7711 | 122.9122 | 122.6361 | 66.7377 | -123.1321
113.6406 | 123.2941 | -66.7007 | 56.2317 | 0.0031287 | -0.0023334 | 0.0013291 | 0.053346 | -0.0013653 | 0.059907 | 0.00053414 | 0.00017519 | -0.00016665 | 0.06409 | 0.0062136 | 0.066247 | -66.761 | 0.038035 | -66.659 | 56.1603 | 55.9823 | 56.033 | -66.7414 | -66.7199 | 0.018674 | -66.759 | 56.0658 | 56.1932 | 55.9903 | -66.8684 | -0.040611 | -0.071418 | -0.060259 | 0.041728 | 0.082339 | -0.2494 | -0.19872 | -0.16761 | -0.16592 | -0.019167 | -0.058251 | 0.10936 | -0.03853 | -0.24137 | 122.861 | 122.683 | 122.7337 | 66.7388 | -122.973 | 122.7665 | 122.8939 | 122.6911 | 66.7194 | -123.1
114.6406 | 123.2117 | -66.7053 | 56.2592 | -0.012133 | -0.0023334 | 0.0011155 | 0.052919 | -0.0013653 | 0.06012 | -0.014727 | 0.00038879 | -0.00016665 | 0.063877 | 0.0062136 | 0.06582 | -66.761 | 0.033457 | -66.6728 | 56.1557 | 55.9823 | 56.033 | -66.7459 | -66.7199 | 0.023253 | -66.759 | 56.0612 | 56.1886 | 55.9674 | -66.8638 | -0.040613 | -0.10346 | -0.055682 | 0.03257 | 0.073183 | -0.27687 | -0.22619 | -0.15846 | -0.19796 | -0.01459 | -0.053674 | 0.10478 | -0.070574 | -0.29172 | 122.861 | 122.6876 | 122.7383 | 66.7388 | -123.0051 | 122.7665 | 122.8939 | 122.6728 | 66.7286 | -123.1229
115.6406 | 123.2437 | -66.7282 | 56.25 | -0.0045023 | -0.0023334 | 0.0011155 | 0.052919 | -0.0015791 | 0.06012 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.063877 | 0.0064274 | 0.066247 | -66.761 | 0.0243 | -66.659 | 56.1511 | 55.9777 | 56.0375 | -66.7368 | -66.7153 | 0.023253 | -66.7544 | 56.052 | 56.1932 | 55.8804 | -66.8729 | -0.008568 | -0.098886 | -0.032794 | 0.069193 | 0.077761 | -0.27229 | -0.21245 | -0.14473 | -0.19797 | 0.012876 | -0.026208 | 0.11852 | -0.056841 | -0.36956 | 122.8793 | 122.7059 | 122.7658 | 66.7525 | -122.9868 | 122.7802 | 122.9214 | 122.6086 | 66.7515 | -123.1229
116.6406 | 123.2529 | -66.7099 | 56.282 | 0.0031287 | -0.0023334 | 0.0015427 | 0.052919 | -0.0017927 | 0.059693 | 0.0081646 | 0.00038879 | -0.00016665 | 0.06409 | 0.0064274 | 0.066247 | -66.761 | 0.033457 | -66.6544 | 56.1557 | 55.9731 | 56.033 | -66.7368 | -66.7062 | 0.027831 | -66.759 | 56.0612 | 56.1886 | 55.9216 | -66.8729 | -0.026878 | -0.12635 | -0.051104 | 0.055461 | 0.082339 | -0.30891 | -0.24908 | -0.16304 | -0.22085 | 0.003724 | -0.049096 | 0.11394 | -0.093462 | -0.3604 | 122.8656 | 122.683 | 122.7429 | 66.7434 | -123.0188 | 122.7711 | 122.8985 | 122.6315 | 66.7377 | -123.155
117.6406 | 123.262 | -66.7145 | 56.2408 | 0.0031287 | -0.002547 | 0.0011155 | 0.053132 | -0.0013653 | 0.06012 | 0.00053414 | 0.00017519 | 4.695e-05 | 0.064304 | 0.0062136 | 0.066247 | -66.7702 | 0.0243 | -66.6636 | 56.1648 | 55.9777 | 56.033 | -66.7414 | -66.7199 | 0.018674 | -66.7636 | 56.0612 | 56.1932 | 55.9995 | -66.8638 | -0.026878 | -0.075996 | -0.055683 | 0.050882 | 0.07776 | -0.26313 | -0.20788 | -0.1493 | -0.17965 | -0.005434 | -0.049097 | 0.1002 | -0.047686 | -0.24136 | 122.8793 | 122.6922 | 122.7474 | 66.7388 | -122.9822 | 122.7757 | 122.9076 | 122.714 | 66.7332 | -123.1046
118.6406 | 123.2529 | -66.7191 | 56.2775 | 0.0031287 | -0.0023334 | 0.0011155 | 0.053346 | -0.0015791 | 0.060334 | -0.014727 | 0.00038879 | -0.00016665 | 0.064304 | 0.0064274 | 0.066034 | -66.761 | 0.038035 | -66.659 | 56.1648 | 55.9777 | 56.033 | -66.7368 | -66.7153 | 0.023253 | -66.7544 | 56.0566 | 56.1886 | 55.9491 | -66.8684 | -0.017723 | -0.11262 | -0.041949 | 0.060038 | 0.077761 | -0.29975 | -0.2445 | -0.1493 | -0.22085 | 0.003721 | -0.035363 | 0.11394 | -0.088885 | -0.32835 | 122.8839 | 122.6968 | 122.752 | 66.7571 | -123.0142 | 122.7757 | 122.9076 | 122.6682 | 66.7423 | -123.1458
119.6406 | 123.2666 | -66.7007 | 56.2363 | 0.0031287 | -0.0023334 | 0.0011155 | 0.052705 | -0.0013653 | 0.06012 | -0.0070964 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.0064274 | 0.06582 | -66.7564 | 0.028878 | -66.6544 | 56.1557 | 55.9823 | 56.0375 | -66.7414 | -66.7153 | 0.027831 | -66.7544 | 56.0566 | 56.1886 | 55.9537 | -66.8638 | -0.040611 | -0.080574 | -0.055681 | 0.046306 | 0.086917 | -0.25398 | -0.19872 | -0.16303 | -0.17965 | -0.014589 | -0.053673 | 0.10936 | -0.047686 | -0.28257 | 122.8564 | 122.683 | 122.7383 | 66.7296 | -122.9776 | 122.7574 | 122.8893 | 122.6544 | 66.7286 | -123.1
120.6406 | 123.2208 | -66.7053 | 56.2729 | -0.0045023 | -0.002547 | 0.0011155 | 0.053346 | -0.0017927 | 0.059693 | -0.0070964 | 0.00017519 | -0.00038025 | 0.06409 | 0.0064274 | 0.066247 | -66.7564 | 0.028878 | -66.6682 | 56.1511 | 55.9823 | 56.0375 | -66.7368 | -66.7153 | 0.014095 | -66.7544 | 56.0703 | 56.1932 | 55.9354 | -66.8775 | -0.031456 | -0.12177 | -0.051104 | 0.037148 | 0.068604 | -0.2906 | -0.23534 | -0.17219 | -0.20254 | -0.010012 | -0.049096 | 0.1231 | -0.079729 | -0.33751 | 122.8564 | 122.6876 | 122.7429 | 66.7342 | -123.0097 | 122.7757 | 122.8985 | 122.6407 | 66.7194 | -123.1504
121.6406 | 123.2117 | -66.7145 | 56.2546 | -0.0045023 | -0.0021196 | 0.0015427 | 0.053132 | -0.0013653 | 0.06012 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.06409 | 0.0064274 | 0.066034 | -66.7656 | 0.033457 | -66.6636 | 56.1603 | 55.9777 | 56.0467 | -66.7368 | -66.7108 | 0.023253 | -66.7544 | 56.0612 | 56.1932 | 55.9491 | -66.8638 | -0.0223 | -0.094307 | -0.051105 | 0.050882 | 0.073182 | -0.27687 | -0.20788 | -0.1493 | -0.19339 | 0.003723 | -0.03994 | 0.10936 | -0.061419 | -0.30546 | 122.8747 | 122.6922 | 122.7612 | 66.7479 | -122.9914 | 122.7757 | 122.9076 | 122.6636 | 66.7377 | -123.1184
122.6406 | 123.2208 | -66.7007 | 56.2546 | -0.0045023 | -0.0021196 | 0.0013291 | 0.052919 | -0.0013653 | 0.059907 | -0.014727 | 0.00017519 | 4.695e-05 | 0.064304 | 0.0064274 | 0.066461 | -66.7564 | 0.033457 | -66.6636 | 56.1603 | 55.9777 | 56.0375 | -66.7459 | -66.7108 | 0.018674 | -66.7498 | 56.0703 | 56.1886 | 55.8942 | -66.8729 | -0.04519 | -0.094307 | -0.055681 | 0.037149 | 0.082339 | -0.27687 | -0.21703 | -0.17219 | -0.18423 | -0.01001 | -0.049094 | 0.1231 | -0.065997 | -0.36041 | 122.861 | 122.6785 | 122.7383 | 66.7342 | -123.0005 | 122.7711 | 122.8893 | 122.5949 | 66.7194 | -123.1275
123.6406 | 123.3032 | -66.7374 | 56.2454 | -0.0045023 | -0.002547 | 0.0011155 | 0.053132 | -0.0011517 | 0.060334 | 0.00053414 | 0.00017519 | 4.695e-05 | 0.063877 | 0.0064274 | 0.066034 | -66.7656 | 0.033457 | -66.6544 | 56.1557 | 55.9777 | 56.0284 | -66.7459 | -66.7108 | 0.018674 | -66.759 | 56.0612 | 56.1886 | 55.9445 | -66.8729 | -0.008569 | -0.089729 | -0.028217 | 0.082927 | 0.091496 | -0.26771 | -0.21703 | -0.13557 | -0.18423 | 0.026611 | -0.02163 | 0.11394 | -0.056841 | -0.30088 | 122.8931 | 122.7151 | 122.7658 | 66.7708 | -122.9914 | 122.7986 | 122.9259 | 122.6819 | 66.756 | -123.1184
124.6406 | 123.262 | -66.6916 | 56.2683 | 0.0031287 | -0.002547 | 0.00090168 | 0.053346 | -0.0015791 | 0.06012 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.06409 | 0.006 | 0.06582 | -66.761 | 0.028878 | -66.6728 | 56.1603 | 55.9777 | 56.0375 | -66.7368 | -66.7153 | 0.027831 | -66.759 | 56.0612 | 56.1932 | 55.94 | -66.8684 | -0.045189 | -0.10804 | -0.069415 | 0.018837 | 0.064026 | -0.2906 | -0.23076 | -0.17677 | -0.20712 | -0.023745 | -0.067407 | 0.10936 | -0.075152 | -0.32835 | 122.8519 | 122.6693 | 122.7291 | 66.7205 | -123.0051 | 122.7528 | 122.8847 | 122.6315 | 66.7194 | -123.1367
125.6406 | 123.2895 | -66.7236 | 56.2546 | -0.0045023 | -0.002547 | 0.0013291 | 0.053346 | -0.0011517 | 0.06012 | -0.0070964 | 0.00038879 | -0.00016665 | 0.06409 | 0.0062136 | 0.066461 | -66.7564 | 0.033457 | -66.659 | 56.1557 | 55.9823 | 56.0375 | -66.7505 | -66.7108 | 0.018674 | -66.759 | 56.0658 | 56.1886 | 55.9903 | -66.8684 | -0.026881 | -0.098885 | -0.032793 | 0.064616 | 0.091497 | -0.27229 | -0.21703 | -0.14472 | -0.18881 | 0.012878 | -0.035363 | 0.10936 | -0.065997 | -0.26425 | 122.8793 | 122.7059 | 122.7612 | 66.7571 | -123.0051 | 122.7894 | 122.9122 | 122.714 | 66.7423 | -123.1229
126.6406 | 123.2803 | -66.6824 | 56.2225 | 0.0031287 | -0.002547 | 0.0013291 | 0.052491 | -0.0015791 | 0.06012 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.06409 | 0.0062136 | 0.065606 | -66.761 | 0.028878 | -66.6636 | 56.1557 | 55.9869 | 56.0375 | -66.7459 | -66.7108 | 0.027831 | -66.759 | 56.0566 | 56.1886 | 55.9308 | -66.8684 | -0.063501 | -0.066841 | -0.07857 | 0.018838 | 0.082339 | -0.23567 | -0.18499 | -0.18592 | -0.16592 | -0.028321 | -0.076562 | 0.10936 | -0.033953 | -0.29173 | 122.8381 | 122.6693 | 122.72 | 66.7113 | -122.9685 | 122.739 | 122.871 | 122.6132 | 66.7103 | -123.0909
127.6406 | 123.1338 | -66.7511 | 56.2958 | -0.0045023 | -0.002547 | 0.0011155 | 0.052705 | -0.0015791 | 0.060334 | -0.0070964 | 0.00038879 | 4.695e-05 | 0.064304 | 0.0064274 | 0.066247 | -66.7564 | 0.033457 | -66.6682 | 56.1603 | 55.9823 | 56.0375 | -66.7459 | -66.7153 | 0.027831 | -66.7453 | 56.0612 | 56.1932 | 56.0407 | -66.8684 | 0.005164 | -0.1355 | -0.005327 | 0.082925 | 0.077761 | -0.31349 | -0.25823 | -0.11726 | -0.23459 | 0.035765 | 0.005839 | 0.1231 | -0.10262 | -0.25509 | 122.9114 | 122.7334 | 122.7886 | 66.7846 | -123.0417 | 122.8123 | 122.9443 | 122.7918 | 66.7789 | -123.1641
128.6406 | 123.2758 | -66.7007 | 56.2363 | 0.01076 | -0.0023334 | 0.0011155 | 0.053132 | -0.0015791 | 0.06012 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.06409 | 0.0062136 | 0.066247 | -66.7656 | 0.042614 | -66.6636 | 56.1694 | 55.9731 | 56.0375 | -66.7368 | -66.7153 | 0.014095 | -66.759 | 56.0566 | 56.1886 | 56.0315 | -66.8729 | -0.036033 | -0.066839 | -0.064838 | 0.037149 | 0.073182 | -0.26313 | -0.19872 | -0.17219 | -0.17965 | -0.014589 | -0.058251 | 0.11394 | -0.047686 | -0.20474 | 122.8702 | 122.6739 | 122.7383 | 66.7434 | -122.973 | 122.7574 | 122.8893 | 122.7323 | 66.7148 | -123.1092
129.6406 | 123.2666 | -66.7328 | 56.2317 | -0.0045023 | -0.0023334 | 0.0013291 | 0.052705 | -0.0017927 | 0.059907 | 0.0081646 | 0.00017519 | 0.00026075 | 0.06409 | 0.0064274 | 0.066247 | -66.7564 | 0.033457 | -66.6544 | 56.1603 | 55.9777 | 56.033 | -66.7368 | -66.7153 | 0.023253 | -66.7453 | 56.0612 | 56.1886 | 56.059 | -66.8638 | -0.00399 | -0.071418 | -0.023638 | 0.078349 | 0.082339 | -0.25398 | -0.19872 | -0.13099 | -0.1705 | 0.017454 | -0.012472 | 0.11852 | -0.043108 | -0.17269 | 122.8931 | 122.7105 | 122.7658 | 66.7662 | -122.9685 | 122.794 | 122.9214 | 122.7918 | 66.756 | -123.0955
130.6406 | 123.262 | -66.7236 | 56.2317 | -0.0045023 | -0.002547 | 0.0011155 | 0.052919 | -0.0013653 | 0.06012 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.06409 | 0.006641 | 0.066034 | -66.761 | 0.038035 | -66.6682 | 56.1603 | 55.9823 | 56.033 | -66.7414 | -66.7153 | 0.027831 | -66.759 | 56.052 | 56.184 | 56.0544 | -66.8729 | -0.017723 | -0.071418 | -0.037371 | 0.055459 | 0.073182 | -0.2494 | -0.19872 | -0.1493 | -0.17966 | 0.008299 | -0.035363 | 0.11394 | -0.047687 | -0.17727 | 122.8839 | 122.7059 | 122.7566 | 66.7617 | -122.973 | 122.7757 | 122.9076 | 122.7781 | 66.7515 | -123.1046
131.6406 | 123.1796 | -66.7557 | 56.2592 | 0.0031287 | -0.0027606 | 0.0013291 | 0.052491 | -0.0017927 | 0.06012 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.06409 | 0.0062136 | 0.066247 | -66.7564 | 0.028878 | -66.659 | 56.1648 | 55.9777 | 56.0375 | -66.7368 | -66.7153 | 0.027831 | -66.7498 | 56.0475 | 56.1932 | 56.0911 | -66.8729 | 0.018898 | -0.094306 | -0.00075 | 0.096659 | 0.077761 | -0.28144 | -0.22161 | -0.11726 | -0.2117 | 0.040342 | 0.005837 | 0.1231 | -0.065996 | -0.1681 | 122.9205 | 122.7334 | 122.7932 | 66.7846 | -122.9959 | 122.8031 | 122.9488 | 122.8467 | 66.7835 | -123.1321
132.6406 | 123.2895 | -66.7007 | 56.2271 | -0.0045023 | -0.0027606 | 0.0011155 | 0.052491 | -0.0013653 | 0.059907 | 0.00053414 | -0.00025221 | 4.695e-05 | 0.063663 | 0.0064274 | 0.066034 | -66.7564 | 0.038035 | -66.6636 | 56.1557 | 55.9777 | 56.0467 | -66.7459 | -66.7199 | 0.023253 | -66.759 | 56.0612 | 56.1932 | 56.0911 | -66.8684 | -0.04519 | -0.071419 | -0.055681 | 0.037149 | 0.082339 | -0.2494 | -0.18041 | -0.16761 | -0.16592 | -0.019167 | -0.058251 | 0.10936 | -0.033953 | -0.13606 | 122.8564 | 122.6785 | 122.7474 | 66.7388 | -122.973 | 122.7619 | 122.8939 | 122.7918 | 66.724 | -123.0955
133.6406 | 123.1338 | -66.7648 | 56.2637 | -0.0045023 | -0.0027606 | 0.0013291 | 0.052705 | -0.0015791 | 0.059907 | 0.00053414 | 0.00017519 | -0.00038025 | 0.064304 | 0.0064274 | 0.066034 | -66.7564 | 0.033457 | -66.6636 | 56.1603 | 55.9777 | 56.033 | -66.7276 | -66.7108 | 0.018674 | -66.7636 | 56.0566 | 56.2023 | 56.0911 | -66.8729 | 0.037212 | -0.10346 | 0.008406 | 0.10124 | 0.064024 | -0.28602 | -0.23077 | -0.1081 | -0.20712 | 0.054077 | 0.001257 | 0.10936 | -0.061416 | -0.17268 | 122.9251 | 122.7425 | 122.7978 | 66.7983 | -122.9914 | 122.8214 | 122.9671 | 122.8559 | 66.7835 | -123.1367
134.6406 | 123.2529 | -66.7328 | 56.2912 | 0.0031287 | -0.0023334 | 0.0015427 | 0.052705 | -0.0015791 | 0.059907 | -0.0070964 | 0.00038879 | 4.695e-05 | 0.063877 | 0.0068546 | 0.066034 | -66.7656 | 0.028878 | -66.6636 | 56.1694 | 55.9731 | 56.0375 | -66.7414 | -66.7153 | 0.023253 | -66.7544 | 56.052 | 56.2023 | 56.0911 | -66.8684 | -0.008568 | -0.12177 | -0.032795 | 0.069192 | 0.07776 | -0.31807 | -0.25365 | -0.13557 | -0.23917 | 0.017454 | -0.02163 | 0.11394 | -0.088882 | -0.20015 | 122.9022 | 122.7059 | 122.7703 | 66.7617 | -123.0326 | 122.7848 | 122.9351 | 122.8238 | 66.756 | -123.1596
135.6406 | 123.143 | -66.7511 | 56.2958 | -0.0045023 | -0.002547 | 0.0015427 | 0.052705 | -0.0011517 | 0.060334 | 0.00053414 | 0.00017519 | -0.00016665 | 0.063877 | 0.0064274 | 0.066034 | -66.7518 | 0.033457 | -66.6636 | 56.1648 | 55.9777 | 56.0421 | -66.7459 | -66.7108 | 0.03241 | -66.759 | 56.0612 | 56.1886 | 56.0865 | -66.8684 | 0.005164 | -0.13093 | -0.000748 | 0.087503 | 0.082339 | -0.31806 | -0.25365 | -0.11726 | -0.23459 | 0.040344 | -0.007897 | 0.10936 | -0.10719 | -0.2093 | 122.9159 | 122.7288 | 122.7932 | 66.7846 | -123.0417 | 122.8123 | 122.9397 | 122.8376 | 66.7835 | -123.1641
136.6406 | 123.2895 | -66.7007 | 56.2317 | -0.012133 | -0.0027606 | 0.0011155 | 0.052491 | -0.0013653 | 0.059907 | 0.0081646 | 0.00017519 | -0.00016665 | 0.06409 | 0.0068546 | 0.06582 | -66.761 | 0.028878 | -66.6682 | 56.1603 | 55.9777 | 56.0421 | -66.7276 | -66.7108 | 0.018674 | -66.759 | 56.0566 | 56.1932 | 56.0865 | -66.8775 | -0.026875 | -0.071418 | -0.060259 | 0.032571 | 0.059446 | -0.25398 | -0.18957 | -0.17677 | -0.17508 | -0.01001 | -0.058251 | 0.11852 | -0.03853 | -0.14522 | 122.861 | 122.6785 | 122.7429 | 66.7296 | -122.9593 | 122.7574 | 122.8939 | 122.7872 | 66.7194 | -123.1092
137.6406 | 123.1247 | -66.7328 | 56.2958 | -0.012133 | -0.002547 | 0.0011155 | 0.052705 | -0.0013653 | 0.06012 | 0.00053414 | 0.00017519 | 4.695e-05 | 0.06409 | 0.0064274 | 0.066034 | -66.7564 | 0.033457 | -66.6682 | 56.1603 | 55.9731 | 56.0421 | -66.7368 | -66.7153 | 0.023253 | -66.7498 | 56.0612 | 56.1886 | 56.1002 | -66.8729 | -0.00399 | -0.1355 | -0.023638 | 0.064614 | 0.068604 | -0.32264 | -0.25365 | -0.14015 | -0.23459 | 0.017454 | -0.017051 | 0.1231 | -0.10719 | -0.19557 | 122.8931 | 122.7059 | 122.7749 | 66.7662 | -123.0326 | 122.794 | 122.9214 | 122.833 | 66.756 | -123.1687
138.6406 | 123.2025 | -66.7465 | 56.2454 | -0.012133 | -0.0027606 | 0.0011155 | 0.052705 | -0.0011517 | 0.060548 | -0.0070964 | -0.00025221 | -0.00016665 | 0.063663 | 0.006641 | 0.066034 | -66.761 | 0.038035 | -66.6636 | 56.1603 | 55.9731 | 56.0375 | -66.7322 | -66.7108 | 0.023253 | -66.7544 | 56.0612 | 56.2069 | 56.0819 | -66.8729 | 0.014322 | -0.085151 | -0.014483 | 0.082925 | 0.068603 | -0.27229 | -0.20788 | -0.12641 | -0.18423 | 0.035766 | -0.007897 | 0.11852 | -0.038527 | -0.16353 | 122.9068 | 122.7197 | 122.7841 | 66.7846 | -122.9776 | 122.8077 | 122.9534 | 122.8284 | 66.7698 | -123.1184
139.6406 | 123.1796 | -66.7191 | 56.25 | 0.0031287 | -0.0027606 | 0.00090168 | 0.052491 | -0.0017927 | 0.060334 | 0.00053414 | 0.00038879 | -0.00016665 | 0.06409 | 0.006641 | 0.06582 | -66.761 | 0.038035 | -66.6636 | 56.1648 | 55.9731 | 56.033 | -66.7322 | -66.7153 | 0.023253 | -66.7544 | 56.0566 | 56.2023 | 56.0911 | -66.8729 | -0.013144 | -0.085151 | -0.041949 | 0.055459 | 0.068603 | -0.27687 | -0.21703 | -0.15388 | -0.19339 | 0.003721 | -0.035363 | 0.11852 | -0.047683 | -0.15895 | 122.8839 | 122.6922 | 122.752 | 66.7571 | -122.9822 | 122.7757 | 122.9214 | 122.8101 | 66.7423 | -123.1229
140.6406 | 123.1659 | -66.7465 | 56.2775 | -0.012133 | -0.002547 | 0.0015427 | 0.052491 | -0.0015791 | 0.059907 | -0.0070964 | 0.00017519 | 0.00026075 | 0.064304 | 0.006641 | 0.06582 | -66.761 | 0.033457 | -66.6636 | 56.1694 | 55.9686 | 56.0421 | -66.7368 | -66.7062 | 0.018674 | -66.7544 | 56.0566 | 56.1932 | 56.0865 | -66.8638 | 0.009743 | -0.10804 | -0.014483 | 0.082925 | 0.073182 | -0.30891 | -0.23534 | -0.11726 | -0.22085 | 0.040345 | -0.007897 | 0.10936 | -0.084307 | -0.19099 | 122.9159 | 122.7151 | 122.7886 | 66.78 | -123.0142 | 122.8031 | 122.9397 | 122.833 | 66.7652 | -123.1412
141.6406 | 123.1979 | -66.7236 | 56.2592 | 0.0031287 | -0.0027606 | 0.0013291 | 0.052491 | -0.0015791 | 0.06012 | 0.00053414 | 0.00017519 | -0.00038025 | 0.064304 | 0.006641 | 0.066247 | -66.7564 | 0.028878 | -66.6636 | 56.1648 | 55.9823 | 56.033 | -66.7322 | -66.7199 | 0.018674 | -66.7544 | 56.0612 | 56.1977 | 56.0911 | -66.8729 | -0.008566 | -0.094306 | -0.032793 | 0.060037 | 0.068603 | -0.27687 | -0.22619 | -0.1493 | -0.19796 | 0.003721 | -0.030785 | 0.11852 | -0.061417 | -0.1681 | 122.8885 | 122.7059 | 122.7566 | 66.7525 | -122.9914 | 122.7848 | 122.9214 | 122.8147 | 66.7423 | -123.1321
142.6406 | 123.1705 | -66.7557 | 56.2592 | -0.0045023 | -0.0027606 | 0.0013291 | 0.052491 | -0.0017927 | 0.059907 | 0.0081646 | 0.00017519 | -0.00038025 | 0.064304 | 0.006641 | 0.06582 | -66.761 | 0.033457 | -66.6636 | 56.1557 | 55.9731 | 56.0421 | -66.7414 | -66.7199 | 0.027831 | -66.759 | 56.0566 | 56.1977 | 56.0865 | -66.8684 | 0.01432 | -0.10346 | -0.005328 | 0.09208 | 0.07776 | -0.28602 | -0.21703 | -0.11268 | -0.20254 | 0.035764 | -0.00332 | 0.10936 | -0.061417 | -0.17268 | 122.9114 | 122.7288 | 122.7978 | 66.7891 | -123.0005 | 122.8123 | 122.9534 | 122.8422 | 66.7835 | -123.1275
143.6406 | 123.1522 | -66.7374 | 56.2637 | -0.012133 | -0.003188 | 0.0011155 | 0.052278 | -0.0013653 | 0.059907 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.064518 | 0.0064274 | 0.066034 | -66.7564 | 0.038035 | -66.6636 | 56.1603 | 55.9777 | 56.0513 | -66.7414 | -66.7153 | 0.023253 | -66.7544 | 56.0612 | 56.1977 | 56.0956 | -66.8684 | -0.00399 | -0.10346 | -0.01906 | 0.07377 | 0.07776 | -0.28602 | -0.21245 | -0.13099 | -0.20254 | 0.022032 | -0.017052 | 0.11394 | -0.065995 | -0.1681 | 122.8976 | 122.7151 | 122.7886 | 66.7754 | -123.0051 | 122.7986 | 122.9351 | 122.833 | 66.7606 | -123.1321
144.6406 | 123.2849 | -66.7053 | 56.2546 | 0.0031287 | -0.0027606 | 0.0013291 | 0.052919 | -0.0013653 | 0.059907 | -0.0070964 | -3.8406e-05 | 4.695e-05 | 0.06409 | 0.0068546 | 0.066034 | -66.7564 | 0.038035 | -66.659 | 56.1603 | 55.9731 | 56.0375 | -66.7322 | -66.7108 | 0.023253 | -66.7544 | 56.0612 | 56.1977 | 56.0911 | -66.8638 | -0.026877 | -0.094307 | -0.051104 | 0.046305 | 0.073182 | -0.28145 | -0.21703 | -0.15846 | -0.19339 | -0.005433 | -0.049096 | 0.10936 | -0.05684 | -0.16352 | 122.8656 | 122.6785 | 122.7429 | 66.7434 | -122.9868 | 122.7665 | 122.9031 | 122.7964 | 66.7286 | -123.1184
145.6406 | 123.1705 | -66.7374 | 56.2775 | -0.0045023 | -0.0027606 | 0.0013291 | 0.052705 | -0.0017927 | 0.060334 | -0.0070964 | -3.8406e-05 | -0.00038025 | 0.064304 | 0.0068546 | 0.066247 | -66.761 | 0.033457 | -66.6636 | 56.1648 | 55.9777 | 56.0467 | -66.723 | -66.7108 | 0.023253 | -66.7498 | 56.0612 | 56.1977 | 56.0956 | -66.8638 | 0.014325 | -0.11262 | -0.023638 | 0.07377 | 0.059445 | -0.29975 | -0.23076 | -0.12641 | -0.21628 | 0.026611 | -0.012473 | 0.11394 | -0.079728 | -0.18183 | 122.9022 | 122.7151 | 122.7841 | 66.7708 | -123.0005 | 122.7986 | 122.9351 | 122.833 | 66.7606 | -123.1412
146.6406 | 123.1384 | -66.7557 | 56.2454 | 0.0031287 | -0.0027606 | 0.0013291 | 0.052705 | -0.0017927 | 0.06012 | 0.015795 | -3.8406e-05 | -0.00059405 | 0.063877 | 0.006641 | 0.066034 | -66.7518 | 0.028878 | -66.6636 | 56.1557 | 55.9731 | 56.0421 | -66.7414 | -66.7108 | 0.023253 | -66.7498 | 56.0658 | 56.1977 | 56.0956 | -66.8684 | 0.01432 | -0.089729 | 0.003829 | 0.09208 | 0.07776 | -0.27229 | -0.2033 | -0.11268 | -0.17965 | 0.044921 | 0.005837 | 0.11852 | -0.047684 | -0.14979 | 122.9114 | 122.7288 | 122.7978 | 66.7846 | -122.9868 | 122.8214 | 122.9534 | 122.8513 | 66.7789 | -123.1138
147.6406 | 123.2437 | -66.7053 | 56.2317 | -0.0045023 | -0.0029744 | 0.0011155 | 0.052919 | -0.0015791 | 0.06012 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.063877 | 0.006641 | 0.066034 | -66.761 | 0.033457 | -66.659 | 56.1557 | 55.9731 | 56.0375 | -66.723 | -66.7153 | 0.027831 | -66.759 | 56.0612 | 56.1977 | 56.0865 | -66.8775 | -0.017719 | -0.075996 | -0.055682 | 0.046305 | 0.064024 | -0.25856 | -0.19414 | -0.17219 | -0.1705 | -0.010012 | -0.053674 | 0.11852 | -0.033951 | -0.14522 | 122.861 | 122.6785 | 122.7429 | 66.7388 | -122.9547 | 122.7665 | 122.9031 | 122.7918 | 66.7332 | -123.1092
148.6406 | 123.1476 | -66.7465 | 56.2958 | -0.012133 | -0.0027606 | 0.0013291 | 0.052278 | -0.0013653 | 0.060548 | -0.0070964 | -0.00025221 | -0.00038025 | 0.06409 | 0.0068546 | 0.066034 | -66.761 | 0.033457 | -66.6682 | 56.1694 | 55.9731 | 56.0421 | -66.7459 | -66.7199 | 0.027831 | -66.7544 | 56.0612 | 56.1977 | 56.0911 | -66.8775 | 0.000586 | -0.12635 | -0.014483 | 0.078347 | 0.077761 | -0.32264 | -0.25365 | -0.13099 | -0.23459 | 0.026609 | -0.007897 | 0.1231 | -0.098038 | -0.20472 | 122.9159 | 122.7197 | 122.7886 | 66.78 | -123.0417 | 122.8077 | 122.9443 | 122.8376 | 66.7744 | -123.1733
149.6406 | 123.2117 | -66.7053 | 56.2546 | 0.0031287 | -0.0023334 | 0.0013291 | 0.052491 | -0.0015791 | 0.059907 | 0.0081646 | 0.00038879 | 4.695e-05 | 0.063877 | 0.006641 | 0.066034 | -66.7564 | 0.033457 | -66.6682 | 56.1603 | 55.9777 | 56.0421 | -66.7276 | -66.7108 | 0.023253 | -66.759 | 56.0612 | 56.2023 | 56.0865 | -66.8684 | -0.022298 | -0.094307 | -0.051104 | 0.037148 | 0.059446 | -0.27687 | -0.21245 | -0.16304 | -0.19339 | -0.005433 | -0.053674 | 0.10936 | -0.052261 | -0.1681 | 122.8656 | 122.683 | 122.7474 | 66.7388 | -122.9822 | 122.7665 | 122.9076 | 122.7918 | 66.7286 | -123.1229
150.6406 | 123.1979 | -66.7465 | 56.2317 | -0.012133 | -0.0027606 | 0.0013291 | 0.052705 | -0.0015791 | 0.059907 | -0.0070964 | 0.00017519 | -0.00016665 | 0.063877 | 0.0068546 | 0.06582 | -66.7564 | 0.033457 | -66.6636 | 56.1603 | 55.9777 | 56.0421 | -66.7368 | -66.7108 | 0.023253 | -66.7544 | 56.052 | 56.1886 | 56.0911 | -66.8684 | 0.009743 | -0.071418 | -0.009905 | 0.082925 | 0.073182 | -0.25398 | -0.18957 | -0.12184 | -0.17966 | 0.035766 | -0.007897 | 0.11394 | -0.043108 | -0.14064 | 122.9068 | 122.7242 | 122.7886 | 66.78 | -122.9685 | 122.7986 | 122.9351 | 122.8376 | 66.7698 | -123.1
151.6406 | 123.1842 | -66.7557 | 56.2683 | -0.0045023 | -0.0029744 | 0.0011155 | 0.052491 | -0.0015791 | 0.06012 | -0.0070964 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.0070684 | 0.066461 | -66.7564 | 0.033457 | -66.6682 | 56.1648 | 55.9823 | 56.0421 | -66.7505 | -66.7108 | 0.023253 | -66.7453 | 56.0612 | 56.1977 | 56.1002 | -66.8729 | 0.005162 | -0.10346 | -0.00075 | 0.087502 | 0.08234 | -0.28602 | -0.22619 | -0.11726 | -0.20712 | 0.044921 | 0.010416 | 0.12768 | -0.070573 | -0.1681 | 122.9205 | 122.738 | 122.7978 | 66.7891 | -123.0188 | 122.8169 | 122.9534 | 122.8559 | 66.7789 | -123.1412
152.6406 | 123.2849 | -66.6916 | 56.2546 | 0.01076 | -0.0027606 | 0.0013291 | 0.052705 | -0.0015791 | 0.059907 | -0.0070964 | -3.8406e-05 | 4.695e-05 | 0.064518 | 0.006641 | 0.066034 | -66.7518 | 0.019721 | -66.6682 | 56.1557 | 55.9823 | 56.0375 | -66.7459 | -66.7108 | 0.018674 | -66.7544 | 56.0612 | 56.1932 | 56.0911 | -66.8684 | -0.054346 | -0.098885 | -0.060258 | 0.023415 | 0.077761 | -0.27229 | -0.21703 | -0.17677 | -0.19339 | -0.019166 | -0.062829 | 0.11394 | -0.061419 | -0.16352 | 122.8473 | 122.6739 | 122.7291 | 66.7113 | -123.0005 | 122.7528 | 122.8847 | 122.7826 | 66.7103 | -123.1229
153.6406 | 123.1888 | -66.7191 | 56.2683 | 0.0031287 | -0.0027606 | 0.0011155 | 0.052278 | -0.0017927 | 0.059693 | -0.0070964 | 0.00017519 | -0.00016665 | 0.06409 | 0.0070684 | 0.06582 | -66.7518 | 0.033457 | -66.6636 | 56.1603 | 55.9823 | 56.0375 | -66.7459 | -66.7062 | 0.027831 | -66.7498 | 56.0612 | 56.2023 | 56.0956 | -66.8729 | -0.02688 | -0.10804 | -0.032792 | 0.055459 | 0.082339 | -0.28602 | -0.23076 | -0.15388 | -0.20712 | 0.012879 | -0.030784 | 0.1231 | -0.065994 | -0.17268 | 122.8793 | 122.7013 | 122.7566 | 66.7525 | -123.0142 | 122.7802 | 122.9214 | 122.8147 | 66.7469 | -123.1412
154.6562 | 123.2849 | -66.7007 | 56.2317 | 0.0031287 | -0.0027606 | 0.0015427 | 0.052705 | -0.0017927 | 0.059907 | -0.0070964 | -3.8406e-05 | 4.695e-05 | 0.06409 | 0.007282 | 0.066247 | -66.7564 | 0.042614 | -66.6636 | 56.1603 | 55.9823 | 56.0421 | -66.7185 | -66.7153 | 0.023253 | -66.7498 | 56.0566 | 56.2023 | 56.0865 | -66.8638 | -0.017717 | -0.071418 | -0.055681 | 0.037149 | 0.054866 | -0.2494 | -0.18957 | -0.16303 | -0.17508 | -0.014589 | -0.049094 | 0.11394 | -0.029372 | -0.14522 | 122.861 | 122.683 | 122.7429 | 66.7434 | -122.9502 | 122.7574 | 122.9031 | 122.7872 | 66.724 | -123.0955
155.6406 | 123.1934 | -66.7282 | 56.2637 | 0.0031287 | -0.0034016 | 0.0015427 | 0.052491 | -0.0017927 | 0.06012 | 0.00053414 | -3.8406e-05 | -0.00038025 | 0.06409 | 0.0068546 | 0.066034 | -66.7473 | 0.033457 | -66.6682 | 56.1694 | 55.9823 | 56.0375 | -66.7414 | -66.7199 | 0.027831 | -66.7453 | 56.0566 | 56.1977 | 56.0865 | -66.8729 | -0.013146 | -0.094305 | -0.019059 | 0.060036 | 0.073182 | -0.28144 | -0.22619 | -0.14473 | -0.20712 | 0.008298 | -0.01705 | 0.12768 | -0.065995 | -0.17726 | 122.8976 | 122.7105 | 122.7658 | 66.7617 | -123.0051 | 122.7848 | 122.9259 | 122.8147 | 66.756 | -123.1367
156.6406 | 123.262 | -66.7145 | 56.1951 | -0.0045023 | -0.0027606 | 0.0013291 | 0.052705 | -0.0015791 | 0.060334 | 0.0081646 | -0.00025221 | -0.00016665 | 0.063877 | 0.0068546 | 0.066247 | -66.761 | 0.028878 | -66.6682 | 56.1557 | 55.9823 | 56.0467 | -66.7185 | -66.7153 | 0.023253 | -66.7498 | 56.052 | 56.1932 | 56.0819 | -66.8729 | -0.003984 | -0.039375 | -0.046526 | 0.046304 | 0.050288 | -0.21278 | -0.14836 | -0.15846 | -0.14303 | -0.000856 | -0.035361 | 0.1231 | -0.001909 | -0.11317 | 122.8702 | 122.6968 | 122.7612 | 66.7434 | -122.9135 | 122.7665 | 122.9076 | 122.7964 | 66.7377 | -123.068
157.6406 | 123.2849 | -66.6962 | 56.1996 | 0.0031287 | -0.0027606 | 0.0013291 | 0.052705 | -0.0017927 | 0.06012 | 0.00053414 | 0.00017519 | -0.00038025 | 0.06409 | 0.0068546 | 0.066034 | -66.761 | 0.033457 | -66.6636 | 56.1648 | 55.9777 | 56.0467 | -66.7322 | -66.7153 | 0.027831 | -66.7544 | 56.0612 | 56.1932 | 56.0682 | -66.8684 | -0.036032 | -0.034797 | -0.064837 | 0.032571 | 0.068603 | -0.22193 | -0.15294 | -0.17219 | -0.13846 | -0.019167 | -0.058251 | 0.11394 | -0.006487 | -0.13149 | 122.861 | 122.6739 | 122.7429 | 66.7296 | -122.9318 | 122.7574 | 122.8893 | 122.7643 | 66.724 | -123.068
158.6406 | 123.2346 | -66.7099 | 56.2454 | -0.0045023 | -0.0029744 | 0.0015427 | 0.052705 | -0.0020063 | 0.059907 | -0.014727 | -3.8406e-05 | 4.695e-05 | 0.06409 | 0.0064274 | 0.066034 | -66.7564 | 0.038035 | -66.6636 | 56.1603 | 55.9731 | 56.0375 | -66.7322 | -66.7108 | 0.018674 | -66.7453 | 56.0566 | 56.2023 | 56.0773 | -66.8729 | -0.022299 | -0.085151 | -0.046526 | 0.046304 | 0.068603 | -0.27229 | -0.20788 | -0.16304 | -0.18881 | -0.000855 | -0.03536 | 0.12768 | -0.043105 | -0.1681 | 122.8702 | 122.683 | 122.7474 | 66.7479 | -122.9776 | 122.7665 | 122.9122 | 122.7872 | 66.7286 | -123.1184
159.6562 | 122.9324 | -66.7923 | 56.2225 | -0.0045023 | -0.0029744 | 0.0015427 | 0.052705 | -0.0017927 | 0.059907 | -0.0070964 | -0.00025221 | 0.00026075 | 0.063877 | 0.0068546 | 0.066247 | -66.761 | 0.028878 | -66.659 | 56.1648 | 55.9777 | 56.0421 | -66.7459 | -66.7153 | 0.018674 | -66.7498 | 56.0658 | 56.1977 | 56.0956 | -66.8729 | 0.046362 | -0.057685 | 0.031293 | 0.13328 | 0.086918 | -0.24482 | -0.18041 | -0.080639 | -0.15677 | 0.076963 | 0.042458 | 0.1231 | -0.024796 | -0.1269 | 122.9571 | 122.77 | 122.8344 | 66.8212 | -122.9685 | 122.8581 | 122.99 | 122.8879 | 66.811 | -123.0955
160.6406 | 123.2986 | -66.7053 | 56.218 | -0.0045023 | -0.0027606 | 0.0011155 | 0.053132 | -0.0015791 | 0.06012 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.063877 | 0.0068546 | 0.066034 | -66.7518 | 0.033457 | -66.659 | 56.1557 | 55.9686 | 56.0421 | -66.7414 | -66.7108 | 0.023253 | -66.7453 | 56.052 | 56.1977 | 56.0865 | -66.8684 | -0.036034 | -0.062264 | -0.046525 | 0.046305 | 0.082339 | -0.2494 | -0.17583 | -0.16304 | -0.16592 | -0.005433 | -0.039938 | 0.1231 | -0.020219 | -0.13148 | 122.861 | 122.6739 | 122.7474 | 66.7388 | -122.9593 | 122.7574 | 122.9031 | 122.7918 | 66.7286 | -123.0863
161.6406 | 123.1338 | -66.7374 | 56.282 | -0.0045023 | -0.0027606 | 0.0015427 | 0.052491 | -0.0017927 | 0.060334 | -0.0070964 | -3.8406e-05 | 4.695e-05 | 0.06409 | 0.0068546 | 0.066034 | -66.7518 | 0.033457 | -66.6636 | 56.1648 | 55.9777 | 56.0513 | -66.7505 | -66.7108 | 0.023253 | -66.7544 | 56.052 | 56.1932 | 56.0865 | -66.8729 | -0.013148 | -0.11719 | -0.014481 | 0.07377 | 0.086918 | -0.30433 | -0.23076 | -0.13557 | -0.23001 | 0.026611 | -0.017052 | 0.11852 | -0.088884 | -0.19557 | 122.9022 | 122.7151 | 122.7886 | 66.7708 | -123.0326 | 122.7894 | 122.9305 | 122.8238 | 66.7606 | -123.155
162.6406 | 123.2803 | -66.687 | 56.2637 | -0.012133 | -0.003188 | 0.0013291 | 0.052705 | -0.0017927 | 0.06012 | -0.0070964 | 0.00017519 | -0.00038025 | 0.06409 | 0.007282 | 0.066034 | -66.7564 | 0.033457 | -66.659 | 56.1648 | 55.9823 | 56.0467 | -66.7368 | -66.7062 | 0.014095 | -66.7498 | 56.0612 | 56.1977 | 56.0865 | -66.8684 | -0.049766 | -0.098884 | -0.069414 | 0.027995 | 0.077761 | -0.28144 | -0.21703 | -0.18135 | -0.20254 | -0.019164 | -0.062827 | 0.11852 | -0.065995 | -0.17726 | 122.8519 | 122.6693 | 122.7337 | 66.7205 | -123.0005 | 122.7482 | 122.8847 | 122.7735 | 66.7011 | -123.1321
163.6406 | 123.1522 | -66.7419 | 56.2363 | -0.035026 | -0.0029744 | 0.0011155 | 0.052491 | -0.0015791 | 0.059907 | 0.00053414 | 0.00038879 | 4.695e-05 | 0.064304 | 0.0068546 | 0.066034 | -66.7564 | 0.033457 | -66.6636 | 56.1648 | 55.9777 | 56.0421 | -66.723 | -66.7108 | 0.014095 | -66.7544 | 56.0566 | 56.1977 | 56.0911 | -66.8684 | 0.018902 | -0.071418 | -0.014483 | 0.078347 | 0.059445 | -0.25856 | -0.19414 | -0.12641 | -0.17965 | 0.031188 | -0.012475 | 0.11394 | -0.038529 | -0.14521 | 122.9068 | 122.7197 | 122.7841 | 66.7754 | -122.9593 | 122.7986 | 122.9397 | 122.833 | 66.756 | -123.1046
164.6562 | 123.23 | -66.7282 | 56.2271 | -0.012133 | -0.002547 | 0.0011155 | 0.052705 | -0.0013653 | 0.059907 | 0.00053414 | 0.00017519 | 4.695e-05 | 0.063877 | 0.0070684 | 0.066247 | -66.7564 | 0.038035 | -66.6544 | 56.1648 | 55.9777 | 56.0467 | -66.7322 | -66.7108 | 0.018674 | -66.7498 | 56.052 | 56.1977 | 56.0819 | -66.8729 | -0.003989 | -0.062263 | -0.028216 | 0.073771 | 0.07776 | -0.2494 | -0.18041 | -0.14473 | -0.17508 | 0.017455 | -0.021629 | 0.1231 | -0.029374 | -0.14522 | 122.8931 | 122.7059 | 122.7749 | 66.7662 | -122.9593 | 122.7802 | 122.9259 | 122.8101 | 66.7469 | -123.1
165.6406 | 123.143 | -66.7511 | 56.2637 | -0.0045023 | -0.002547 | 0.0015427 | 0.052491 | -0.0017927 | 0.059907 | -0.0070964 | 0.00017519 | -0.00016665 | 0.06409 | 0.0068546 | 0.06582 | -66.761 | 0.033457 | -66.6636 | 56.1603 | 55.964 | 56.0513 | -66.7322 | -66.7016 | 0.023253 | -66.7544 | 56.0612 | 56.1886 | 56.0865 | -66.8729 | 0.0189 | -0.10346 | -0.009905 | 0.087503 | 0.068603 | -0.29976 | -0.21245 | -0.12184 | -0.20254 | 0.049501 | -0.003319 | 0.11852 | -0.075152 | -0.17726 | 122.9114 | 122.7151 | 122.8024 | 66.7846 | -122.9959 | 122.8123 | 122.9397 | 122.8376 | 66.7744 | -123.1367
166.6406 | 123.2574 | -66.7191 | 56.2317 | 0.01076 | -0.0023334 | 0.0013291 | 0.052705 | -0.0013653 | 0.060334 | -0.0070964 | -0.00046581 | 4.695e-05 | 0.063663 | 0.0068546 | 0.066034 | -66.7564 | 0.033457 | -66.6636 | 56.1557 | 55.9686 | 56.0467 | -66.7414 | -66.7108 | 0.027831 | -66.7498 | 56.0566 | 56.1977 | 56.0911 | -66.8821 | -0.022301 | -0.075996 | -0.037371 | 0.055459 | 0.07776 | -0.26314 | -0.18499 | -0.16304 | -0.17508 | 0.0083 | -0.030784 | 0.13226 | -0.033951 | -0.14064 | 122.8747 | 122.6876 | 122.7658 | 66.7525 | -122.973 | 122.7757 | 122.9168 | 122.8101 | 66.7469 | -123.1138
167.6406 | 123.262 | -66.7099 | 56.2271 | 0.01076 | -0.0029744 | 0.0013291 | 0.052491 | -0.0017927 | 0.060334 | -0.0070964 | -0.00046581 | 4.695e-05 | 0.063663 | 0.007282 | 0.06582 | -66.761 | 0.028878 | -66.659 | 56.1603 | 55.9731 | 56.0513 | -66.723 | -66.7153 | 0.018674 | -66.7498 | 56.052 | 56.2023 | 56.0819 | -66.8684 | -0.013141 | -0.066841 | -0.051104 | 0.050883 | 0.064024 | -0.25398 | -0.17583 | -0.15846 | -0.17508 | -0.005434 | -0.039939 | 0.11852 | -0.024795 | -0.14522 | 122.8702 | 122.683 | 122.7612 | 66.7388 | -122.9502 | 122.7619 | 122.9122 | 122.7918 | 66.7286 | -123.0955
168.6406 | 123.3032 | -66.7099 | 56.2363 | -0.012133 | -0.002547 | 0.0013291 | 0.052705 | -0.0015791 | 0.059907 | 0.00053414 | 0.00017519 | -0.00038025 | 0.06409 | 0.0070684 | 0.066034 | -66.761 | 0.038035 | -66.6682 | 56.1557 | 55.9731 | 56.0467 | -66.7276 | -66.7108 | 0.023253 | -66.7498 | 56.0475 | 56.1932 | 56.0865 | -66.8729 | -0.01772 | -0.080574 | -0.051104 | 0.041726 | 0.059446 | -0.26313 | -0.18956 | -0.16304 | -0.18881 | -0.000855 | -0.039939 | 0.1231 | -0.043108 | -0.14979 | 122.8656 | 122.683 | 122.7566 | 66.7479 | -122.9639 | 122.7574 | 122.9031 | 122.7964 | 66.7332 | -123.1092
169.6406 | 123.175 | -66.7328 | 56.282 | -0.012133 | -0.003188 | 0.0015427 | 0.052491 | -0.0017927 | 0.059693 | 0.00053414 | -0.00025221 | 4.695e-05 | 0.063877 | 0.0068546 | 0.066247 | -66.7564 | 0.028878 | -66.6544 | 56.1603 | 55.9731 | 56.0513 | -66.7459 | -66.7153 | 0.023253 | -66.7453 | 56.0566 | 56.1977 | 56.0911 | -66.8729 | -0.013147 | -0.12177 | -0.023638 | 0.078349 | 0.091496 | -0.30891 | -0.23076 | -0.14015 | -0.22543 | 0.017454 | -0.012472 | 0.12768 | -0.084305 | -0.19099 | 122.8931 | 122.7059 | 122.7841 | 66.7617 | -123.028 | 122.7894 | 122.9305 | 122.8238 | 66.756 | -123.155
170.6406 | 123.2162 | -66.6916 | 56.2317 | -0.0045023 | -0.0029744 | 0.0015427 | 0.052491 | -0.0015791 | 0.059693 | -0.0070964 | -0.00025221 | -0.00016665 | 0.06409 | 0.006641 | 0.066034 | -66.761 | 0.038035 | -66.6636 | 56.1603 | 55.9731 | 56.0467 | -66.7322 | -66.7153 | 0.027831 | -66.7498 | 56.0566 | 56.1977 | 56.0727 | -66.8729 | -0.04061 | -0.071418 | -0.069415 | 0.027993 | 0.068603 | -0.25856 | -0.18499 | -0.18135 | -0.17508 | -0.023745 | -0.05825 | 0.1231 | -0.033951 | -0.15895 | 122.8519 | 122.6647 | 122.7383 | 66.7296 | -122.9639 | 122.7482 | 122.8893 | 122.7643 | 66.7194 | -123.1046
171.6406 | 123.1613 | -66.7603 | 56.2592 | -0.012133 | -0.0029744 | 0.0013291 | 0.052278 | -0.0017927 | 0.059907 | -0.014727 | 0.00017519 | 4.695e-05 | 0.06409 | 0.0070684 | 0.066034 | -66.7564 | 0.038035 | -66.6636 | 56.1648 | 55.9731 | 56.0421 | -66.723 | -66.7199 | 0.027831 | -66.7544 | 56.0658 | 56.1932 | 56.0727 | -66.8729 | 0.037213 | -0.094306 | 0.003828 | 0.096658 | 0.059445 | -0.28602 | -0.21703 | -0.11268 | -0.19339 | 0.040342 | 0.005836 | 0.11852 | -0.065996 | -0.18642 | 122.9251 | 122.7334 | 122.8024 | 66.7983 | -122.9822 | 122.826 | 122.9534 | 122.833 | 66.7881 | -123.1321
172.6406 | 123.23 | -66.7145 | 56.2592 | -0.0045023 | -0.0029744 | 0.0011155 | 0.052919 | -0.0013653 | 0.06012 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.06409 | 0.0068546 | 0.066034 | -66.7518 | 0.0243 | -66.659 | 56.1603 | 55.9731 | 56.033 | -66.7368 | -66.7108 | 0.023253 | -66.759 | 56.052 | 56.1977 | 56.0865 | -66.8729 | -0.0223 | -0.098884 | -0.037369 | 0.055461 | 0.077761 | -0.28602 | -0.22619 | -0.15846 | -0.20712 | 0.003723 | -0.044518 | 0.11394 | -0.061417 | -0.17268 | 122.8747 | 122.6876 | 122.7474 | 66.7388 | -122.9959 | 122.7665 | 122.9122 | 122.801 | 66.7377 | -123.1321
173.6406 | 123.1842 | -66.7557 | 56.2546 | -0.012133 | -0.0029744 | 0.0011155 | 0.052705 | -0.0017927 | 0.059907 | 0.00053414 | -3.8406e-05 | 0.00026075 | 0.06409 | 0.0070684 | 0.06582 | -66.761 | 0.033457 | -66.659 | 56.1603 | 55.9731 | 56.0513 | -66.7322 | -66.7108 | 0.018674 | -66.7453 | 56.052 | 56.1932 | 56.0865 | -66.8729 | 0.023477 | -0.094307 | -0.005328 | 0.096659 | 0.073182 | -0.28145 | -0.2033 | -0.11726 | -0.20255 | 0.044921 | 0.010416 | 0.12768 | -0.061419 | -0.1681 | 122.9159 | 122.7288 | 122.807 | 66.7891 | -122.9868 | 122.8077 | 122.9488 | 122.8422 | 66.7743 | -123.1275
174.6562 | 123.2758 | -66.687 | 56.218 | -0.0045023 | -0.0027606 | 0.0011155 | 0.052278 | -0.0013653 | 0.059907 | 0.0081646 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.006641 | 0.066034 | -66.7564 | 0.028878 | -66.659 | 56.1694 | 55.9731 | 56.0513 | -66.7322 | -66.7153 | 0.023253 | -66.7453 | 56.052 | 56.1977 | 56.0819 | -66.8729 | -0.045187 | -0.048529 | -0.069414 | 0.027995 | 0.073182 | -0.24482 | -0.16668 | -0.18592 | -0.16592 | -0.028322 | -0.058248 | 0.12768 | -0.020219 | -0.13606 | 122.8564 | 122.6601 | 122.7383 | 66.7159 | -122.9502 | 122.739 | 122.8847 | 122.7689 | 66.7103 | -123.0909
175.6406 | 123.1476 | -66.7603 | 56.2637 | -0.0045023 | -0.003188 | 0.0015427 | 0.052491 | -0.0017927 | 0.06012 | 0.00053414 | -0.00046581 | -0.00038025 | 0.06409 | 0.0068546 | 0.066034 | -66.7518 | 0.033457 | -66.659 | 56.1603 | 55.9777 | 56.0467 | -66.7368 | -66.7199 | 0.027831 | -66.7498 | 56.0612 | 56.1977 | 56.0773 | -66.8729 | 0.023476 | -0.10346 | 0.008407 | 0.10124 | 0.077761 | -0.28602 | -0.21703 | -0.11268 | -0.20254 | 0.040342 | 0.010415 | 0.1231 | -0.065995 | -0.18642 | 122.9205 | 122.738 | 122.807 | 66.7937 | -123.0005 | 122.8214 | 122.958 | 122.8376 | 66.7881 | -123.1367
176.6406 | 123.2666 | -66.7145 | 56.2408 | -0.012133 | -0.0029744 | 0.0013291 | 0.052705 | -0.0015791 | 0.06012 | -0.0070964 | 0.00017519 | -0.00016665 | 0.064304 | 0.007282 | 0.06582 | -66.7564 | 0.028878 | -66.6544 | 56.1648 | 55.9823 | 56.0421 | -66.7459 | -66.7153 | 0.027831 | -66.7453 | 56.0566 | 56.1977 | 56.0773 | -66.8729 | -0.031457 | -0.075996 | -0.041948 | 0.060039 | 0.091496 | -0.25856 | -0.19872 | -0.15846 | -0.18423 | -0.000856 | -0.030782 | 0.12768 | -0.043107 | -0.16353 | 122.8793 | 122.6968 | 122.7566 | 66.7434 | -122.9868 | 122.7711 | 122.9122 | 122.7918 | 66.7423 | -123.1138
177.6406 | 123.1796 | -66.7236 | 56.2729 | -0.0045023 | -0.0029744 | 0.0015427 | 0.052064 | -0.0017927 | 0.06012 | 0.0081646 | -3.8406e-05 | 4.695e-05 | 0.06409 | 0.0070684 | 0.066034 | -66.7564 | 0.033457 | -66.6682 | 56.1694 | 55.9686 | 56.0513 | -66.7276 | -66.7199 | 0.027831 | -66.7407 | 56.0612 | 56.2023 | 56.0819 | -66.8729 | -0.003987 | -0.10346 | -0.032793 | 0.055459 | 0.059446 | -0.30433 | -0.22161 | -0.1493 | -0.2117 | 0.003721 | -0.017048 | 0.13226 | -0.070571 | -0.19099 | 122.8931 | 122.6922 | 122.7749 | 66.7571 | -123.0005 | 122.7848 | 122.926 | 122.8055 | 66.7515 | -123.1458
178.6406 | 123.2574 | -66.7099 | 56.2271 | -0.0045023 | -0.003188 | 0.0015427 | 0.052705 | -0.0013653 | 0.059907 | 0.0081646 | -0.00025221 | -0.00016665 | 0.064304 | 0.007282 | 0.065606 | -66.7564 | 0.033457 | -66.659 | 56.1694 | 55.9686 | 56.0421 | -66.7185 | -66.7108 | 0.027831 | -66.759 | 56.0612 | 56.1886 | 56.0727 | -66.8775 | -0.008562 | -0.057684 | -0.046526 | 0.050883 | 0.059445 | -0.25856 | -0.18499 | -0.16761 | -0.16592 | -0.000855 | -0.049096 | 0.11852 | -0.038531 | -0.15437 | 122.8793 | 122.6785 | 122.752 | 66.7434 | -122.9456 | 122.7711 | 122.8985 | 122.7826 | 66.7377 | -123.1046
179.6406 | 123.2208 | -66.7007 | 56.2683 | -0.0045023 | -0.003188 | 0.0013291 | 0.052705 | -0.0015791 | 0.06012 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.063877 | 0.007282 | 0.06582 | -66.7518 | 0.038035 | -66.6636 | 56.1603 | 55.9777 | 56.0467 | -66.7368 | -66.7108 | 0.023253 | -66.7544 | 56.0566 | 56.1977 | 56.0819 | -66.8729 | -0.036033 | -0.10804 | -0.051102 | 0.037149 | 0.073182 | -0.2906 | -0.22161 | -0.17219 | -0.2117 | -0.01001 | -0.053673 | 0.11852 | -0.070573 | -0.18641 | 122.861 | 122.6785 | 122.7474 | 66.7388 | -123.0051 | 122.7574 | 122.8985 | 122.7826 | 66.724 | -123.1412
180.6406 | 123.2391 | -66.6962 | 56.2408 | -0.0045023 | -0.003188 | 0.0013291 | 0.052705 | -0.0017927 | 0.06012 | 0.0081646 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.007282 | 0.066034 | -66.7564 | 0.033457 | -66.6682 | 56.1648 | 55.964 | 56.0513 | -66.7368 | -66.7199 | 0.023253 | -66.759 | 56.0566 | 56.1977 | 56.0773 | -66.8729 | -0.040611 | -0.075996 | -0.060259 | 0.027993 | 0.068604 | -0.27687 | -0.18956 | -0.17677 | -0.18423 | -0.023745 | -0.062829 | 0.11394 | -0.043107 | -0.16353 | 122.861 | 122.6601 | 122.7474 | 66.7296 | -122.9776 | 122.7528 | 122.8939 | 122.7735 | 66.7194 | -123.1138
181.6406 | 123.1613 | -66.7419 | 56.25 | 0.0031287 | -0.0029744 | 0.0013291 | 0.052705 | -0.0015791 | 0.06012 | -0.014727 | 0.00017519 | 0.00026075 | 0.064304 | 0.0074956 | 0.066034 | -66.7564 | 0.033457 | -66.6636 | 56.1603 | 55.9777 | 56.0421 | -66.7276 | -66.7108 | 0.027831 | -66.7498 | 56.0566 | 56.2069 | 56.0773 | -66.8684 | 0.014323 | -0.089729 | -0.014483 | 0.078347 | 0.064024 | -0.27229 | -0.20788 | -0.12641 | -0.19339 | 0.031188 | -0.007896 | 0.11852 | -0.043105 | -0.17268 | 122.9022 | 122.7197 | 122.7841 | 66.7754 | -122.9776 | 122.7986 | 122.9488 | 122.8193 | 66.7698 | -123.1184
182.6406 | 123.2849 | -66.7099 | 56.2134 | 0.0031287 | -0.0034016 | 0.0013291 | 0.052491 | -0.0015791 | 0.059907 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.063877 | 0.007282 | 0.065606 | -66.7656 | 0.033457 | -66.659 | 56.1648 | 55.9686 | 56.0467 | -66.7276 | -66.7108 | 0.018674 | -66.7453 | 56.0566 | 56.2023 | 56.0727 | -66.8684 | -0.01772 | -0.04853 | -0.055683 | 0.050883 | 0.068603 | -0.24483 | -0.16668 | -0.15846 | -0.15677 | -0.000855 | -0.03536 | 0.1231 | -0.011062 | -0.14064 | 122.8747 | 122.6785 | 122.7566 | 66.7434 | -122.941 | 122.7665 | 122.9122 | 122.7826 | 66.7286 | -123.0817
183.6406 | 123.2254 | -66.7145 | 56.2637 | 0.0031287 | -0.003188 | 0.0011155 | 0.052491 | -0.0015791 | 0.059693 | 0.0081646 | -3.8406e-05 | 4.695e-05 | 0.063877 | 0.007282 | 0.065606 | -66.7518 | 0.033457 | -66.659 | 56.1603 | 55.9731 | 56.0513 | -66.7459 | -66.7108 | 0.027831 | -66.7544 | 56.052 | 56.1932 | 56.0911 | -66.8775 | -0.031457 | -0.10346 | -0.037369 | 0.055461 | 0.086918 | -0.2906 | -0.21245 | -0.16304 | -0.2117 | 0.003723 | -0.03994 | 0.1231 | -0.070574 | -0.17268 | 122.8747 | 122.6876 | 122.7658 | 66.7479 | -123.0097 | 122.7665 | 122.9076 | 122.8055 | 66.7423 | -123.1412
184.6406 | 123.2941 | -66.6916 | 56.2592 | -0.0045023 | -0.0034016 | 0.0011155 | 0.052491 | -0.0015791 | 0.06012 | 0.0081646 | 0.00038879 | -0.00016665 | 0.063877 | 0.007282 | 0.065606 | -66.7564 | 0.042614 | -66.6636 | 56.1648 | 55.9686 | 56.0467 | -66.7322 | -66.7199 | 0.018674 | -66.7544 | 56.052 | 56.1932 | 56.0819 | -66.8729 | -0.04061 | -0.094306 | -0.064837 | 0.027993 | 0.068603 | -0.2906 | -0.21245 | -0.18135 | -0.20712 | -0.028323 | -0.062829 | 0.11852 | -0.065996 | -0.17726 | 122.8564 | 122.6601 | 122.7383 | 66.7342 | -122.9914 | 122.7436 | 122.8847 | 122.7735 | 66.7103 | -123.1321
185.6406 | 123.143 | -66.7328 | 56.2683 | -0.0045023 | -0.0034016 | 0.0013291 | 0.052278 | -0.0020063 | 0.059907 | 0.00053414 | 0.00017519 | -0.00016665 | 0.06409 | 0.007282 | 0.06582 | -66.7564 | 0.028878 | -66.659 | 56.1603 | 55.964 | 56.0421 | -66.7368 | -66.7108 | 0.027831 | -66.7544 | 56.0566 | 56.1932 | 56.0819 | -66.8821 | -0.00399 | -0.10804 | -0.023638 | 0.073771 | 0.077761 | -0.30434 | -0.22619 | -0.14931 | -0.2117 | 0.022033 | -0.02163 | 0.12768 | -0.075152 | -0.18641 | 122.8931 | 122.6968 | 122.7749 | 66.7617 | -123.0051 | 122.7894 | 122.9259 | 122.8147 | 66.7606 | -123.1504
186.6406 | 123.2529 | -66.7282 | 56.2225 | -0.0045023 | -0.003188 | 0.0013291 | 0.052278 | -0.0020063 | 0.059907 | 0.0081646 | -3.8406e-05 | 0.00026075 | 0.064304 | 0.0070684 | 0.066034 | -66.7564 | 0.038035 | -66.6636 | 56.1603 | 55.9686 | 56.0467 | -66.723 | -66.7108 | 0.027831 | -66.7544 | 56.0566 | 56.1977 | 56.0819 | -66.8775 | 0.005169 | -0.062263 | -0.028216 | 0.064614 | 0.059445 | -0.25398 | -0.17583 | -0.1493 | -0.16592 | 0.017455 | -0.026208 | 0.1231 | -0.024796 | -0.14064 | 122.8885 | 122.6968 | 122.7749 | 66.7662 | -122.9456 | 122.7848 | 122.9259 | 122.8101 | 66.756 | -123.1
187.6406 | 123.143 | -66.7511 | 56.2637 | -0.012133 | -0.003188 | 0.00090168 | 0.052491 | -0.0020063 | 0.060334 | 0.0081646 | -0.00025221 | -0.00016665 | 0.063663 | 0.0070684 | 0.06582 | -66.7564 | 0.038035 | -66.659 | 56.1603 | 55.9777 | 56.0467 | -66.7185 | -66.7153 | 0.027831 | -66.7544 | 56.0658 | 56.1932 | 56.0911 | -66.8775 | 0.032637 | -0.10346 | -0.005327 | 0.092082 | 0.059445 | -0.28602 | -0.21703 | -0.12642 | -0.19796 | 0.035765 | -0.003319 | 0.1231 | -0.070574 | -0.17268 | 122.9114 | 122.7288 | 122.7978 | 66.7891 | -122.9822 | 122.8169 | 122.9443 | 122.8422 | 66.7789 | -123.1412
188.6406 | 123.2483 | -66.687 | 56.2408 | -0.0045023 | -0.0034016 | 0.0011155 | 0.052278 | -0.0017927 | 0.059907 | -0.014727 | 0.00017519 | -0.00016665 | 0.06409 | 0.0077094 | 0.06582 | -66.7518 | 0.033457 | -66.6682 | 56.1557 | 55.9686 | 56.0513 | -66.7276 | -66.7108 | 0.018674 | -66.7498 | 56.0566 | 56.1932 | 56.0819 | -66.8867 | -0.040608 | -0.085152 | -0.064835 | 0.018838 | 0.059446 | -0.27229 | -0.18956 | -0.19966 | -0.18423 | -0.023743 | -0.062827 | 0.13683 | -0.047686 | -0.15895 | 122.8427 | 122.6556 | 122.7383 | 66.7205 | -122.9685 | 122.7436 | 122.8802 | 122.7689 | 66.7057 | -123.1275
189.6406 | 123.1979 | -66.7236 | 56.2271 | -0.0045023 | -0.003188 | 0.0013291 | 0.052705 | -0.0015791 | 0.059907 | 0.00053414 | 0.00038879 | -0.00038025 | 0.063877 | 0.0074956 | 0.06582 | -66.7473 | 0.038035 | -66.6682 | 56.1557 | 55.9686 | 56.0513 | -66.7459 | -66.7108 | 0.023253 | -66.7544 | 56.052 | 56.1932 | 56.0773 | -66.8775 | -0.022302 | -0.071419 | -0.023636 | 0.055459 | 0.077761 | -0.25856 | -0.17583 | -0.15388 | -0.17508 | 0.012878 | -0.030785 | 0.1231 | -0.033953 | -0.14979 | 122.8793 | 122.6922 | 122.7749 | 66.7617 | -122.973 | 122.7757 | 122.9168 | 122.801 | 66.7469 | -123.1046
190.6406 | 123.1567 | -66.7465 | 56.2592 | 0.0031287 | -0.0029744 | 0.0011155 | 0.052491 | -0.0017927 | 0.059907 | -0.0070964 | 0.00038879 | -0.00016665 | 0.063877 | 0.007282 | 0.065179 | -66.7518 | 0.042614 | -66.6682 | 56.1694 | 55.9731 | 56.0467 | -66.7322 | -66.7108 | 0.027831 | -66.7544 | 56.0566 | 56.1932 | 56.0865 | -66.8729 | 0.014322 | -0.089727 | -0.005326 | 0.078347 | 0.064025 | -0.28602 | -0.21245 | -0.12641 | -0.20254 | 0.035766 | -0.007897 | 0.11852 | -0.065996 | -0.17268 | 122.9159 | 122.7197 | 122.7932 | 66.7891 | -122.9914 | 122.8031 | 122.9397 | 122.833 | 66.7744 | -123.1321
191.6406 | 123.1842 | -66.7236 | 56.2637 | -0.0045023 | -0.0034016 | 0.0013291 | 0.052705 | -0.0017927 | 0.06012 | -0.0070964 | -3.8406e-05 | 4.695e-05 | 0.063877 | 0.007282 | 0.065606 | -66.7518 | 0.038035 | -66.6636 | 56.1648 | 55.9777 | 56.0467 | -66.7459 | -66.7199 | 0.03241 | -66.7498 | 56.0566 | 56.184 | 56.0956 | -66.8684 | -0.022302 | -0.098884 | -0.028214 | 0.060037 | 0.082339 | -0.28602 | -0.21703 | -0.14472 | -0.20712 | 0.003721 | -0.026206 | 0.11852 | -0.079731 | -0.1681 | 122.8885 | 122.7013 | 122.7703 | 66.7617 | -123.0097 | 122.7802 | 122.9076 | 122.8193 | 66.756 | -123.1321
192.6406 | 123.1201 | -66.7511 | 56.2729 | -0.0045023 | -0.0034016 | 0.0011155 | 0.052491 | -0.0017927 | 0.060334 | 0.0081646 | 0.00017519 | 4.695e-05 | 0.06409 | 0.0074956 | 0.065606 | -66.7518 | 0.033457 | -66.6636 | 56.1603 | 55.9823 | 56.0421 | -66.7276 | -66.7108 | 0.018674 | -66.7498 | 56.0566 | 56.1932 | 56.0865 | -66.8729 | 0.023479 | -0.11262 | -0.000748 | 0.087503 | 0.064024 | -0.2906 | -0.23076 | -0.12184 | -0.21628 | 0.040344 | 0.00126 | 0.1231 | -0.079729 | -0.18641 | 122.9114 | 122.7334 | 122.7932 | 66.7846 | -123.0005 | 122.8077 | 122.9443 | 122.8376 | 66.7698 | -123.1458
193.6406 | 123.175 | -66.7099 | 56.2683 | 0.01076 | -0.003188 | 0.0011155 | 0.052278 | -0.0015791 | 0.06012 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.063663 | 0.0070684 | 0.06582 | -66.7518 | 0.038035 | -66.659 | 56.1648 | 55.9823 | 56.0467 | -66.7368 | -66.7062 | 0.023253 | -66.7498 | 56.0566 | 56.1977 | 56.0819 | -66.8775 | -0.026878 | -0.10346 | -0.041947 | 0.050883 | 0.077761 | -0.28602 | -0.22161 | -0.16761 | -0.2117 | 0.003724 | -0.039939 | 0.12768 | -0.070573 | -0.18641 | 122.8747 | 122.6922 | 122.7566 | 66.7479 | -123.0051 | 122.7665 | 122.9076 | 122.7918 | 66.7332 | -123.1458
194.6406 | 123.2391 | -66.6962 | 56.2408 | 0.0031287 | -0.0027606 | 0.0013291 | 0.052491 | -0.0015791 | 0.059907 | 0.00053414 | 0.00017519 | 4.695e-05 | 0.063877 | 0.007282 | 0.066034 | -66.7518 | 0.038035 | -66.6636 | 56.1648 | 55.9731 | 56.0467 | -66.7322 | -66.7108 | 0.023253 | -66.7498 | 56.0566 | 56.1932 | 56.0819 | -66.8775 | -0.036032 | -0.075996 | -0.05568 | 0.032571 | 0.068603 | -0.26771 | -0.19414 | -0.18135 | -0.18423 | -0.014588 | -0.053672 | 0.12768 | -0.047686 | -0.15895 | 122.861 | 122.6693 | 122.7429 | 66.7342 | -122.973 | 122.7528 | 122.8893 | 122.7781 | 66.7194 | -123.1184
195.6406 | 123.2071 | -66.6962 | 56.2683 | 0.0031287 | -0.003188 | 0.0011155 | 0.052491 | -0.0017927 | 0.06012 | 0.0081646 | -3.8406e-05 | -0.00038025 | 0.06409 | 0.0070684 | 0.065393 | -66.7473 | 0.038035 | -66.659 | 56.1603 | 55.9777 | 56.0467 | -66.7276 | -66.7153 | 0.027831 | -66.7453 | 56.0566 | 56.1886 | 56.0819 | -66.8684 | -0.031453 | -0.10804 | -0.051102 | 0.03715 | 0.068603 | -0.2906 | -0.22161 | -0.17219 | -0.2117 | -0.019167 | -0.049093 | 0.1231 | -0.07973 | -0.18641 | 122.8564 | 122.6739 | 122.7429 | 66.7342 | -122.9959 | 122.7528 | 122.8847 | 122.7781 | 66.724 | -123.1367
196.6406 | 123.1522 | -66.7511 | 56.2592 | -0.0045023 | -0.003188 | 0.0015427 | 0.052491 | -0.0017927 | 0.059693 | -0.0070964 | -3.8406e-05 | -0.00016665 | 0.063877 | 0.0070684 | 0.06582 | -66.7564 | 0.033457 | -66.6636 | 56.1557 | 55.9731 | 56.0467 | -66.7459 | -66.7062 | 0.03241 | -66.7498 | 56.052 | 56.1932 | 56.0819 | -66.8821 | 0.005164 | -0.10346 | -0.005327 | 0.087503 | 0.082339 | -0.28602 | -0.21245 | -0.13099 | -0.20712 | 0.044923 | 0.00126 | 0.13226 | -0.065996 | -0.17726 | 122.9068 | 122.7242 | 122.7978 | 66.7846 | -123.0051 | 122.8031 | 122.9443 | 122.833 | 66.7835 | -123.1412
197.6406 | 123.1934 | -66.7099 | 56.2683 | 0.0031287 | -0.003188 | 0.0013291 | 0.052491 | -0.0017927 | 0.059907 | 0.00053414 | 0.00038879 | -0.00016665 | 0.064304 | 0.0074956 | 0.065606 | -66.7518 | 0.028878 | -66.659 | 56.1648 | 55.9594 | 56.0421 | -66.7368 | -66.7062 | 0.027831 | -66.7453 | 56.0566 | 56.1977 | 56.0956 | -66.8684 | -0.026878 | -0.10346 | -0.041947 | 0.050883 | 0.077761 | -0.30891 | -0.22619 | -0.15846 | -0.2117 | 0.003724 | -0.03536 | 0.1231 | -0.070573 | -0.17268 | 122.8747 | 122.6693 | 122.752 | 66.7388 | -123.0051 | 122.7665 | 122.9076 | 122.8055 | 66.7377 | -123.1367
198.6406 | 123.1522 | -66.7282 | 56.2546 | -0.0045023 | -0.003188 | 0.0011155 | 0.052491 | -0.0015791 | 0.060334 | -0.0070964 | -3.8406e-05 | -0.00016665 | 0.064518 | 0.0070684 | 0.06582 | -66.7473 | 0.038035 | -66.659 | 56.1648 | 55.9686 | 56.0559 | -66.723 | -66.7153 | 0.03241 | -66.759 | 56.0566 | 56.1977 | 56.0682 | -66.8684 | 0.005169 | -0.089729 | -0.019059 | 0.069193 | 0.064024 | -0.28602 | -0.19872 | -0.14015 | -0.19797 | 0.012876 | -0.030786 | 0.10936 | -0.05684 | -0.18642 | 122.8931 | 122.6968 | 122.7841 | 66.7662 | -122.9776 | 122.7848 | 122.9259 | 122.7964 | 66.7606 | -123.1229
199.6406 | 123.1476 | -66.7511 | 56.2683 | 0.0031287 | -0.003188 | 0.0017565 | 0.052064 | -0.0020063 | 0.06012 | -0.014727 | 0.00017519 | -0.00016665 | 0.063877 | 0.007282 | 0.06582 | -66.7518 | 0.038035 | -66.6544 | 56.1648 | 55.964 | 56.0467 | -66.7322 | -66.7108 | 0.018674 | -66.7361 | 56.052 | 56.2023 | 56.0819 | -66.8684 | 0.0189 | -0.10346 | -0.000748 | 0.09666 | 0.07776 | -0.30434 | -0.22161 | -0.11726 | -0.21628 | 0.040344 | 0.014996 | 0.13226 | -0.065994 | -0.18641 | 122.9159 | 122.7151 | 122.7978 | 66.7891 | -123.0005 | 122.8031 | 122.9534 | 122.833 | 66.7698 | -123.1367
200.6406 | 123.1842 | -66.7053 | 56.2729 | 0.0031287 | -0.0036154 | 0.0013291 | 0.052705 | -0.0017927 | 0.059907 | 0.0081646 | 0.00017519 | 4.695e-05 | 0.063663 | 0.007282 | 0.06582 | -66.7518 | 0.038035 | -66.6499 | 56.1603 | 55.9731 | 56.0513 | -66.7276 | -66.7062 | 0.027831 | -66.7407 | 56.0475 | 56.1932 | 56.0819 | -66.8821 | -0.022298 | -0.11262 | -0.046525 | 0.055461 | 0.077759 | -0.29976 | -0.22161 | -0.17677 | -0.22543 | -0.000854 | -0.035359 | 0.14141 | -0.079729 | -0.19099 | 122.8656 | 122.6785 | 122.7566 | 66.7434 | -123.0005 | 122.7528 | 122.8985 | 122.7872 | 66.7332 | -123.155
201.6406 | 123.2071 | -66.7053 | 56.2683 | 0.0031287 | -0.003188 | 0.0013291 | 0.052705 | -0.0013653 | 0.059907 | 0.0081646 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.0074956 | 0.06582 | -66.7473 | 0.033457 | -66.6544 | 56.1648 | 55.964 | 56.0421 | -66.7368 | -66.7108 | 0.023253 | -66.7498 | 56.0612 | 56.1932 | 56.0727 | -66.8684 | -0.031456 | -0.10346 | -0.041947 | 0.050883 | 0.082339 | -0.30434 | -0.22619 | -0.16304 | -0.20712 | -0.005433 | -0.044517 | 0.11852 | -0.075152 | -0.19557 | 122.8702 | 122.6693 | 122.7474 | 66.7388 | -123.0051 | 122.7665 | 122.8985 | 122.7781 | 66.7286 | -123.1367
202.6406 | 123.1842 | -66.7099 | 56.2637 | 0.0031287 | -0.003188 | 0.0013291 | 0.052278 | -0.0020063 | 0.06012 | -0.0070964 | -3.8406e-05 | -0.00038025 | 0.06409 | 0.007282 | 0.06582 | -66.7473 | 0.033457 | -66.659 | 56.1603 | 55.9869 | 56.0513 | -66.723 | -66.7108 | 0.023253 | -66.7498 | 56.0612 | 56.1932 | 56.0819 | -66.8821 | -0.013141 | -0.10346 | -0.037369 | 0.050883 | 0.064024 | -0.27686 | -0.21245 | -0.17219 | -0.20254 | -0.000855 | -0.039939 | 0.13226 | -0.070574 | -0.18184 | 122.8702 | 122.6968 | 122.7612 | 66.7434 | -122.9868 | 122.7711 | 122.9031 | 122.7918 | 66.7332 | -123.1458
203.6406 | 123.1659 | -66.7328 | 56.3049 | 0.018391 | -0.0029744 | 0.0013291 | 0.052278 | -0.0017927 | 0.06012 | -0.0070964 | -0.00025221 | -0.00038025 | 0.063663 | 0.007282 | 0.06582 | -66.7564 | 0.033457 | -66.6636 | 56.1557 | 55.9686 | 56.0467 | -66.7368 | -66.7108 | 0.027831 | -66.7498 | 56.0566 | 56.1932 | 56.0727 | -66.8729 | -0.00399 | -0.14924 | -0.023638 | 0.069192 | 0.073182 | -0.33638 | -0.25823 | -0.14015 | -0.24832 | 0.022033 | -0.017051 | 0.1231 | -0.11177 | -0.23219 | 122.8885 | 122.7013 | 122.7795 | 66.7662 | -123.0417 | 122.7894 | 122.9259 | 122.8055 | 66.7606 | -123.1779
204.6406 | 123.262 | -66.687 | 56.1905 | -0.012133 | -0.003188 | 0.0015427 | 0.052491 | -0.0015791 | 0.060334 | 0.00053414 | 0.00017519 | -0.00016665 | 0.063663 | 0.0074956 | 0.066034 | -66.7473 | 0.033457 | -66.6544 | 56.1603 | 55.9777 | 56.0513 | -66.7368 | -66.7062 | 0.023253 | -66.7453 | 56.0566 | 56.1932 | 56.0819 | -66.8729 | -0.049766 | -0.03022 | -0.060257 | 0.032573 | 0.082339 | -0.21278 | -0.13921 | -0.18592 | -0.13388 | -0.019164 | -0.058248 | 0.12768 | 0.002668 | -0.1086 | 122.8473 | 122.6647 | 122.7383 | 66.7205 | -122.9273 | 122.7436 | 122.8802 | 122.7689 | 66.7103 | -123.0634
205.6406 | 123.2758 | -66.655 | 56.2592 | -0.0045023 | -0.003188 | 0.0013291 | 0.052491 | -0.0015791 | 0.059907 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.064304 | 0.0074956 | 0.065393 | -66.7473 | 0.038035 | -66.6544 | 56.1694 | 55.9686 | 56.0513 | -66.723 | -66.7062 | 0.018674 | -66.7453 | 56.0566 | 56.1886 | 56.0819 | -66.8729 | -0.068073 | -0.089727 | -0.092301 | 0.000529 | 0.068602 | -0.2906 | -0.20787 | -0.21797 | -0.20254 | -0.051208 | -0.090292 | 0.12768 | -0.070574 | -0.17726 | 122.8244 | 122.6235 | 122.7062 | 66.693 | -122.9822 | 122.7116 | 122.8435 | 122.7369 | 66.6736 | -123.1321
206.6406 | 123.1888 | -66.6962 | 56.2729 | -0.0045023 | -0.003188 | 0.0011155 | 0.052278 | -0.0017927 | 0.06012 | -0.0070964 | -3.8406e-05 | -0.00016665 | 0.063877 | 0.007282 | 0.065393 | -66.7518 | 0.033457 | -66.659 | 56.1648 | 55.9731 | 56.0559 | -66.7322 | -66.7016 | 0.027831 | -66.7453 | 56.0566 | 56.1886 | 56.0682 | -66.8775 | -0.036032 | -0.10804 | -0.05568 | 0.03715 | 0.073182 | -0.29976 | -0.21703 | -0.18135 | -0.21628 | -0.005431 | -0.049093 | 0.13226 | -0.084307 | -0.20473 | 122.861 | 122.6693 | 122.752 | 66.7296 | -123.0051 | 122.7528 | 122.8847 | 122.7643 | 66.724 | -123.1504
207.6406 | 123.2437 | -66.6916 | 56.2683 | 0.0031287 | -0.0036154 | 0.00068808 | 0.052705 | -0.0015791 | 0.06012 | 0.00053414 | -0.00046581 | -0.00038025 | 0.064304 | 0.0074956 | 0.06582 | -66.7518 | 0.019721 | -66.6544 | 56.1694 | 55.9686 | 56.0467 | -66.7276 | -66.7199 | 0.018674 | -66.7498 | 56.0566 | 56.1977 | 56.0773 | -66.8775 | -0.036031 | -0.098883 | -0.060258 | 0.03715 | 0.073181 | -0.29976 | -0.22161 | -0.18593 | -0.2117 | -0.028323 | -0.05825 | 0.12768 | -0.070573 | -0.19099 | 122.861 | 122.6601 | 122.7383 | 66.7113 | -122.9959 | 122.7482 | 122.8893 | 122.7689 | 66.7103 | -123.1458
208.6406 | 123.1979 | -66.7007 | 56.2958 | 0.0031287 | -0.003188 | 0.0011155 | 0.052491 | -0.0015791 | 0.060334 | 0.00053414 | -3.8406e-05 | 0.00026075 | 0.063877 | 0.0074956 | 0.06582 | -66.7564 | 0.033457 | -66.6499 | 56.1603 | 55.9777 | 56.0513 | -66.7414 | -66.7062 | 0.03241 | -66.7498 | 56.0612 | 56.1932 | 56.0819 | -66.8821 | -0.040611 | -0.1355 | -0.055681 | 0.050884 | 0.091495 | -0.31806 | -0.24449 | -0.18135 | -0.23459 | -0.005431 | -0.049094 | 0.13226 | -0.10262 | -0.21388 | 122.861 | 122.6785 | 122.752 | 66.7342 | -123.0371 | 122.7619 | 122.8939 | 122.7826 | 66.7332 | -123.1779
209.6406 | 123.1293 | -66.7099 | 56.2912 | 0.01076 | -0.0027606 | 0.0011155 | 0.052278 | -0.0020063 | 0.06012 | -0.0070964 | 0.00038879 | -0.00038025 | 0.06409 | 0.007282 | 0.066034 | -66.7473 | 0.038035 | -66.6544 | 56.1648 | 55.9731 | 56.0559 | -66.7276 | -66.7062 | 0.023253 | -66.7453 | 56.0612 | 56.1932 | 56.0773 | -66.8775 | -0.01772 | -0.12635 | -0.037369 | 0.055461 | 0.073181 | -0.31807 | -0.23534 | -0.16761 | -0.23001 | 0.003724 | -0.03536 | 0.13226 | -0.09804 | -0.21388 | 122.8747 | 122.683 | 122.7658 | 66.7479 | -123.0188 | 122.7711 | 122.9031 | 122.7872 | 66.7332 | -123.1687
210.6406 | 123.1201 | -66.7465 | 56.282 | 0.0031287 | -0.0034016 | 0.0013291 | 0.052278 | -0.0017927 | 0.06012 | 0.015795 | -3.8406e-05 | 0.00026075 | 0.064304 | 0.007923 | 0.066034 | -66.7564 | 0.038035 | -66.6544 | 56.1603 | 55.9777 | 56.0513 | -66.7276 | -66.7062 | 0.018674 | -66.7498 | 56.0566 | 56.1886 | 56.0819 | -66.8821 | 0.018901 | -0.12177 | -0.009905 | 0.092082 | 0.073181 | -0.30433 | -0.23076 | -0.13557 | -0.22543 | 0.040345 | -0.003318 | 0.13226 | -0.093462 | -0.20015 | 122.9068 | 122.7242 | 122.7978 | 66.7846 | -123.0097 | 122.8031 | 122.9351 | 122.8284 | 66.7652 | -123.1641
211.6406 | 123.2437 | -66.6916 | 56.2683 | 0.01076 | -0.0034016 | 0.0013291 | 0.052705 | -0.0020063 | 0.059907 | 0.0081646 | -0.00025221 | -0.00038025 | 0.06409 | 0.0074956 | 0.06582 | -66.7473 | 0.033457 | -66.6636 | 56.1557 | 55.964 | 56.0513 | -66.7414 | -66.7153 | 0.018674 | -66.7498 | 56.0612 | 56.1977 | 56.0819 | -66.8775 | -0.049767 | -0.11262 | -0.05568 | 0.027993 | 0.07776 | -0.30434 | -0.21703 | -0.18593 | -0.20712 | -0.023745 | -0.05825 | 0.12768 | -0.070573 | -0.18641 | 122.8473 | 122.6556 | 122.7429 | 66.725 | -123.0097 | 122.7528 | 122.8893 | 122.7735 | 66.7103 | -123.1458
212.6406 | 123.1293 | -66.6916 | 56.2866 | 0.01076 | -0.0034016 | 0.0011155 | 0.052278 | -0.0020063 | 0.059907 | 0.0081646 | -0.00046581 | 4.695e-05 | 0.063663 | 0.0077094 | 0.065606 | -66.7518 | 0.038035 | -66.6544 | 56.1511 | 55.9731 | 56.0559 | -66.7368 | -66.7062 | 0.018674 | -66.7407 | 56.0566 | 56.1932 | 56.0911 | -66.8775 | -0.045189 | -0.13551 | -0.060258 | 0.03715 | 0.082339 | -0.31349 | -0.23076 | -0.18593 | -0.23001 | -0.014587 | -0.049092 | 0.13683 | -0.093462 | -0.19557 | 122.8427 | 122.6647 | 122.7474 | 66.7296 | -123.0234 | 122.7482 | 122.8847 | 122.7826 | 66.7103 | -123.1641
213.6406 | 123.2483 | -66.7007 | 56.2637 | 0.01076 | -0.003188 | 0.0013291 | 0.052491 | -0.0017927 | 0.060334 | -0.0070964 | -3.8406e-05 | -0.00016665 | 0.063877 | 0.0077094 | 0.06582 | -66.7518 | 0.042614 | -66.6544 | 56.1557 | 55.9686 | 56.0559 | -66.7185 | -66.7016 | 0.023253 | -66.7498 | 56.0703 | 56.1886 | 56.0727 | -66.8729 | -0.017717 | -0.10804 | -0.051102 | 0.046306 | 0.064023 | -0.29518 | -0.20787 | -0.17219 | -0.19339 | -0.000853 | -0.049094 | 0.1231 | -0.075152 | -0.191 | 122.8564 | 122.6693 | 122.7566 | 66.7434 | -122.9822 | 122.7711 | 122.8893 | 122.7735 | 66.724 | -123.1367
214.6406 | 123.1476 | -66.7374 | 56.2866 | -0.0045023 | -0.0034016 | 0.0013291 | 0.052705 | -0.0020063 | 0.059693 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.064304 | 0.0077094 | 0.065606 | -66.7518 | 0.038035 | -66.6544 | 56.1648 | 55.9731 | 56.0467 | -66.7459 | -66.7062 | 0.018674 | -66.7407 | 56.052 | 56.1932 | 56.0819 | -66.8684 | -0.008569 | -0.12177 | -0.014481 | 0.082927 | 0.091496 | -0.31349 | -0.23992 | -0.13099 | -0.23459 | 0.03119 | -0.003315 | 0.12768 | -0.093462 | -0.20472 | 122.9022 | 122.7105 | 122.7841 | 66.7754 | -123.0326 | 122.7894 | 122.9305 | 122.8193 | 66.756 | -123.155
215.6406 | 123.2117 | -66.6962 | 56.2683 | -0.0045023 | -0.003188 | 0.0011155 | 0.052919 | -0.0020063 | 0.060334 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.064304 | 0.0077094 | 0.065606 | -66.7518 | 0.038035 | -66.6544 | 56.1603 | 55.9686 | 56.0604 | -66.7368 | -66.7062 | 0.023253 | -66.7498 | 56.0566 | 56.1977 | 56.059 | -66.8684 | -0.040611 | -0.10804 | -0.05568 | 0.041728 | 0.082339 | -0.29976 | -0.20787 | -0.17219 | -0.2117 | -0.010009 | -0.053672 | 0.11852 | -0.070573 | -0.20931 | 122.8564 | 122.6647 | 122.7566 | 66.7342 | -123.0051 | 122.7528 | 122.8939 | 122.7552 | 66.7194 | -123.1367
216.6406 | 123.2712 | -66.6824 | 56.2912 | -0.012133 | -0.0036154 | 0.0013291 | 0.052491 | -0.0020063 | 0.06012 | -0.014727 | 0.00017519 | 4.695e-05 | 0.06409 | 0.007923 | 0.065606 | -66.7473 | 0.033457 | -66.6636 | 56.1511 | 55.9823 | 56.0513 | -66.7414 | -66.7153 | 0.023253 | -66.7544 | 56.052 | 56.1932 | 56.0727 | -66.8729 | -0.058922 | -0.14008 | -0.064835 | 0.018838 | 0.07776 | -0.30891 | -0.23992 | -0.1905 | -0.23917 | -0.0329 | -0.071984 | 0.11852 | -0.09804 | -0.21846 | 122.8335 | 122.6647 | 122.7337 | 66.7159 | -123.0326 | 122.7345 | 122.8756 | 122.7552 | 66.7057 | -123.1641
217.6406 | 123.2391 | -66.6733 | 56.2408 | -0.0045023 | -0.0036154 | 0.0013291 | 0.052491 | -0.0015791 | 0.059693 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.06409 | 0.007923 | 0.06582 | -66.7427 | 0.033457 | -66.6544 | 56.1557 | 55.9823 | 56.0513 | -66.7414 | -66.7062 | 0.018674 | -66.7498 | 56.052 | 56.1932 | 56.0773 | -66.8775 | -0.068077 | -0.085152 | -0.069412 | 0.01884 | 0.086917 | -0.25856 | -0.18956 | -0.20424 | -0.18881 | -0.032897 | -0.07656 | 0.12768 | -0.047686 | -0.16353 | 122.829 | 122.6556 | 122.7246 | 66.7067 | -122.9822 | 122.7253 | 122.8664 | 122.7506 | 66.692 | -123.1184
218.6406 | 123.262 | -66.6779 | 56.25 | 0.01076 | -0.0034016 | 0.00090168 | 0.052491 | -0.0020063 | 0.060334 | 0.0081646 | -3.8406e-05 | -0.00016665 | 0.064304 | 0.0074956 | 0.066034 | -66.7564 | 0.038035 | -66.6544 | 56.1557 | 55.9731 | 56.0467 | -66.7322 | -66.7062 | 0.018674 | -66.7453 | 56.0566 | 56.1977 | 56.0819 | -66.8775 | -0.054343 | -0.094307 | -0.07857 | 0.023417 | 0.07776 | -0.27687 | -0.2033 | -0.19966 | -0.19339 | -0.02832 | -0.067404 | 0.13226 | -0.052262 | -0.1681 | 122.8335 | 122.651 | 122.7246 | 66.7159 | -122.9822 | 122.7345 | 122.8756 | 122.7598 | 66.6965 | -123.1275
219.6406 | 123.1796 | -66.7007 | 56.2683 | -0.0045023 | -0.0036154 | 0.0015427 | 0.052491 | -0.0017927 | 0.060334 | -0.0070964 | -3.8406e-05 | 4.695e-05 | 0.064304 | 0.0077094 | 0.06582 | -66.7473 | 0.038035 | -66.659 | 56.1557 | 55.9731 | 56.0467 | -66.7414 | -66.7108 | 0.014095 | -66.7453 | 56.0612 | 56.1932 | 56.0773 | -66.8729 | -0.040611 | -0.11262 | -0.046524 | 0.041728 | 0.082339 | -0.29518 | -0.22161 | -0.17219 | -0.20712 | -0.01001 | -0.044515 | 0.12768 | -0.075152 | -0.19099 | 122.8564 | 122.6739 | 122.7474 | 66.7388 | -123.0097 | 122.7619 | 122.8939 | 122.7781 | 66.7148 | -123.1412
220.6406 | 123.2208 | -66.7007 | 56.2729 | 0.0031287 | -0.003188 | 0.0017565 | 0.052491 | -0.0017927 | 0.059907 | 0.0081646 | -3.8406e-05 | -0.00016665 | 0.063877 | 0.0074956 | 0.06582 | -66.7518 | 0.038035 | -66.6544 | 56.1557 | 55.9731 | 56.0559 | -66.7414 | -66.7016 | 0.018674 | -66.7453 | 56.0612 | 56.1932 | 56.0819 | -66.8729 | -0.040611 | -0.1172 | -0.051102 | 0.046306 | 0.086917 | -0.29976 | -0.21703 | -0.17219 | -0.2117 | -0.000853 | -0.044515 | 0.12768 | -0.079729 | -0.19099 | 122.8564 | 122.6739 | 122.7566 | 66.7388 | -123.0142 | 122.7619 | 122.8939 | 122.7826 | 66.7194 | -123.1458
221.6406 | 123.2712 | -66.7236 | 56.2042 | -0.0045023 | -0.0036154 | 0.0013291 | 0.052064 | -0.0020063 | 0.06012 | -0.0070964 | -3.8406e-05 | -0.00016665 | 0.063877 | 0.0077094 | 0.06582 | -66.7518 | 0.033457 | -66.659 | 56.1557 | 55.9686 | 56.0467 | -66.7322 | -66.7062 | 0.023253 | -66.7453 | 56.0612 | 56.2023 | 56.0727 | -66.8821 | -0.008566 | -0.048531 | -0.028214 | 0.064616 | 0.073182 | -0.23567 | -0.15752 | -0.15846 | -0.14303 | 0.017457 | -0.021627 | 0.13683 | -0.001907 | -0.13149 | 122.8793 | 122.6922 | 122.7703 | 66.7571 | -122.9364 | 122.7848 | 122.926 | 122.7964 | 66.7469 | -123.0863
222.6406 | 123.262 | -66.6824 | 56.2592 | -0.012133 | -0.0034016 | 0.0013291 | 0.052491 | -0.0020063 | 0.059907 | 0.00053414 | -3.8406e-05 | -0.00038025 | 0.06409 | 0.007923 | 0.066034 | -66.7427 | 0.033457 | -66.6544 | 56.1557 | 55.9777 | 56.0559 | -66.723 | -66.7108 | 0.023253 | -66.7498 | 56.0612 | 56.1886 | 56.0682 | -66.8775 | -0.040607 | -0.10346 | -0.060257 | 0.027995 | 0.068602 | -0.28144 | -0.20329 | -0.19508 | -0.19796 | -0.028321 | -0.067405 | 0.12768 | -0.070574 | -0.191 | 122.8381 | 122.6601 | 122.7383 | 66.7159 | -122.9822 | 122.7436 | 122.871 | 122.7506 | 66.7057 | -123.1367
223.6406 | 123.2574 | -66.7007 | 56.2134 | -0.012133 | -0.0036154 | 0.0013291 | 0.052064 | -0.0015791 | 0.06012 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.064304 | 0.0077094 | 0.065606 | -66.7518 | 0.038035 | -66.6544 | 56.1603 | 55.9731 | 56.0559 | -66.7414 | -66.7199 | 0.03241 | -66.7498 | 56.0612 | 56.1932 | 56.0727 | -66.8684 | -0.040611 | -0.053108 | -0.051102 | 0.046306 | 0.086917 | -0.24025 | -0.15752 | -0.16761 | -0.15219 | -0.019167 | -0.049094 | 0.11852 | -0.02022 | -0.14064 | 122.861 | 122.6739 | 122.7566 | 66.7388 | -122.9547 | 122.7619 | 122.8939 | 122.7735 | 66.7332 | -123.0817
224.6406 | 123.1659 | -66.7282 | 56.25 | -0.0045023 | -0.003829 | 0.0011155 | 0.052705 | -0.0017927 | 0.06012 | 0.00053414 | 0.00017519 | -0.00016665 | 0.064304 | 0.0077094 | 0.06582 | -66.7427 | 0.028878 | -66.6544 | 56.1603 | 55.9686 | 56.0467 | -66.7322 | -66.7062 | 0.03241 | -66.7498 | 56.052 | 56.1886 | 56.0819 | -66.8684 | -0.003989 | -0.089729 | -0.014481 | 0.073771 | 0.07776 | -0.28145 | -0.2033 | -0.14015 | -0.19797 | 0.022034 | -0.021629 | 0.11852 | -0.061419 | -0.1681 | 122.8885 | 122.6968 | 122.7749 | 66.7571 | -122.9822 | 122.7802 | 122.9168 | 122.8101 | 66.7606 | -123.1184
225.6406 | 123.1888 | -66.7282 | 56.2546 | -0.012133 | -0.003829 | 0.0013291 | 0.052705 | -0.0020063 | 0.059907 | 0.0081646 | -3.8406e-05 | 4.695e-05 | 0.064304 | 0.007923 | 0.066034 | -66.7518 | 0.042614 | -66.6544 | 56.1648 | 55.9777 | 56.0559 | -66.7459 | -66.7062 | 0.023253 | -66.7453 | 56.0612 | 56.1932 | 56.0773 | -66.8775 | -0.017725 | -0.089729 | -0.023637 | 0.073771 | 0.091496 | -0.27687 | -0.19872 | -0.1493 | -0.19339 | 0.022034 | -0.01705 | 0.13226 | -0.061419 | -0.17726 | 122.8931 | 122.7059 | 122.7841 | 66.7708 | -123.0005 | 122.7894 | 122.9214 | 122.8055 | 66.7515 | -123.1321
226.6406 | 123.2391 | -66.6962 | 56.25 | -0.0045023 | -0.0036154 | 0.0011155 | 0.052919 | -0.0017927 | 0.059907 | 0.0081646 | -3.8406e-05 | -0.00038025 | 0.063877 | 0.007923 | 0.06582 | -66.7427 | 0.033457 | -66.659 | 56.1557 | 55.9777 | 56.0513 | -66.7414 | -66.7016 | 0.018674 | -66.7453 | 56.0612 | 56.1977 | 56.0819 | -66.8775 | -0.045189 | -0.094307 | -0.046524 | 0.03715 | 0.082339 | -0.27229 | -0.19872 | -0.18135 | -0.18881 | -0.005431 | -0.049093 | 0.13226 | -0.052262 | -0.1681 | 122.8519 | 122.6739 | 122.7474 | 66.7296 | -122.9914 | 122.7574 | 122.8939 | 122.7781 | 66.7148 | -123.1275
227.6406 | 123.2208 | -66.7053 | 56.2271 | -0.0045023 | -0.0034016 | 0.0013291 | 0.052491 | -0.0020063 | 0.06012 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.063877 | 0.0077094 | 0.066034 | -66.7518 | 0.038035 | -66.6544 | 56.1557 | 55.9731 | 56.0467 | -66.7368 | -66.7062 | 0.018674 | -66.7407 | 56.052 | 56.1932 | 56.0727 | -66.8775 | -0.031456 | -0.071419 | -0.046525 | 0.050883 | 0.082339 | -0.25398 | -0.18041 | -0.17219 | -0.17508 | -0.000854 | -0.035359 | 0.13683 | -0.033953 | -0.15437 | 122.861 | 122.6785 | 122.752 | 66.7434 | -122.9639 | 122.7574 | 122.8985 | 122.7781 | 66.724 | -123.1046
228.6406 | 123.2712 | -66.6916 | 56.25 | -0.012133 | -0.0036154 | 0.0013291 | 0.052705 | -0.0017927 | 0.060548 | 0.0081646 | -3.8406e-05 | -0.00016665 | 0.063449 | 0.0077094 | 0.06582 | -66.7518 | 0.033457 | -66.6636 | 56.1557 | 55.9731 | 56.0467 | -66.723 | -66.7062 | 0.027831 | -66.7498 | 56.0612 | 56.1932 | 56.0682 | -66.8821 | -0.031452 | -0.094307 | -0.060258 | 0.027993 | 0.059445 | -0.27687 | -0.2033 | -0.19051 | -0.18881 | -0.014587 | -0.05825 | 0.13226 | -0.056841 | -0.18184 | 122.8473 | 122.6647 | 122.7383 | 66.725 | -122.973 | 122.7528 | 122.8847 | 122.7597 | 66.7194 | -123.1321
229.6406 | 123.2117 | -66.7191 | 56.2408 | 0.01076 | -0.0036154 | 0.0013291 | 0.052705 | -0.0020063 | 0.06012 | -0.0070964 | -3.8406e-05 | -0.00016665 | 0.064304 | 0.007923 | 0.065606 | -66.7518 | 0.028878 | -66.6544 | 56.1557 | 55.964 | 56.0513 | -66.7276 | -66.7016 | 0.014095 | -66.7407 | 56.052 | 56.1977 | 56.0819 | -66.8729 | -0.008565 | -0.085152 | -0.032792 | 0.064616 | 0.073181 | -0.27687 | -0.18956 | -0.15388 | -0.18881 | 0.017457 | -0.021626 | 0.13226 | -0.043107 | -0.15895 | 122.8747 | 122.683 | 122.7703 | 66.7479 | -122.9685 | 122.7711 | 122.9168 | 122.801 | 66.7331 | -123.1138
230.6406 | 123.1979 | -66.6962 | 56.2775 | 0.0031287 | -0.0036154 | 0.0015427 | 0.052705 | -0.0017927 | 0.06012 | 0.00053414 | 0.00017519 | 4.695e-05 | 0.063877 | 0.0074956 | 0.066034 | -66.7473 | 0.033457 | -66.6544 | 56.1557 | 55.9777 | 56.0467 | -66.723 | -66.7062 | 0.014095 | -66.7498 | 56.052 | 56.1932 | 56.0727 | -66.8729 | -0.026874 | -0.12177 | -0.051102 | 0.041728 | 0.068602 | -0.29975 | -0.23076 | -0.17677 | -0.22543 | -0.010009 | -0.053672 | 0.1231 | -0.084307 | -0.20473 | 122.8519 | 122.6739 | 122.7429 | 66.7296 | -123.0005 | 122.7482 | 122.8893 | 122.7689 | 66.7103 | -123.1504
231.6406 | 123.111 | -66.7328 | 56.2592 | -0.0045023 | -0.003829 | 0.0011155 | 0.052064 | -0.0022199 | 0.059907 | -0.014727 | 0.00017519 | 4.695e-05 | 0.06409 | 0.0077094 | 0.065606 | -66.7427 | 0.028878 | -66.6453 | 56.1557 | 55.9686 | 56.0513 | -66.723 | -66.7062 | 0.023253 | -66.7361 | 56.0658 | 56.1932 | 56.0773 | -66.8775 | 0.009747 | -0.10346 | -0.009903 | 0.087505 | 0.077758 | -0.2906 | -0.20787 | -0.14473 | -0.19339 | 0.026612 | -0.003315 | 0.14141 | -0.065996 | -0.18184 | 122.8885 | 122.7013 | 122.7841 | 66.7617 | -122.9822 | 122.7986 | 122.9259 | 122.8101 | 66.756 | -123.1367
232.6406 | 123.2346 | -66.7099 | 56.2637 | 0.01076 | -0.0034016 | 0.0011155 | 0.052919 | -0.0020063 | 0.059907 | 0.00053414 | -0.00025221 | -0.00016665 | 0.064304 | 0.0077094 | 0.065606 | -66.7518 | 0.033457 | -66.659 | 56.1511 | 55.9777 | 56.0604 | -66.7368 | -66.7153 | 0.023253 | -66.7498 | 56.052 | 56.2023 | 56.0819 | -66.8775 | -0.026878 | -0.11262 | -0.041947 | 0.050883 | 0.077761 | -0.28602 | -0.20329 | -0.16761 | -0.2117 | -0.005434 | -0.039939 | 0.12768 | -0.061416 | -0.18184 | 122.861 | 122.6876 | 122.7703 | 66.7434 | -123.0005 | 122.7619 | 122.9122 | 122.7918 | 66.7332 | -123.1412
233.6406 | 123.1705 | -66.7099 | 56.2363 | -0.012133 | -0.0036154 | 0.0011155 | 0.052705 | -0.0015791 | 0.059693 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.06409 | 0.0074956 | 0.066034 | -66.7427 | 0.033457 | -66.6453 | 56.1603 | 55.9686 | 56.0559 | -66.7368 | -66.7016 | 0.023253 | -66.7407 | 56.0566 | 56.1932 | 56.0727 | -66.8821 | -0.026878 | -0.075996 | -0.032791 | 0.064617 | 0.091495 | -0.26771 | -0.18041 | -0.17219 | -0.17965 | 0.008302 | -0.030781 | 0.14141 | -0.043108 | -0.16353 | 122.8702 | 122.6785 | 122.7658 | 66.7434 | -122.973 | 122.7665 | 122.9031 | 122.7826 | 66.7332 | -123.1184
234.6406 | 123.0148 | -66.7145 | 56.3095 | -0.0045023 | -0.0036154 | 0.0013291 | 0.052491 | -0.0017927 | 0.06012 | 0.0081646 | 0.00017519 | 4.695e-05 | 0.063663 | 0.007923 | 0.06582 | -66.7473 | 0.038035 | -66.6544 | 56.1603 | 55.9777 | 56.0513 | -66.7414 | -66.7153 | 0.027831 | -66.7453 | 56.0475 | 56.1932 | 56.0865 | -66.8775 | -0.026878 | -0.14924 | -0.032791 | 0.060039 | 0.086917 | -0.3318 | -0.25823 | -0.16304 | -0.26205 | -0.000856 | -0.030782 | 0.13226 | -0.11635 | -0.22303 | 122.8747 | 122.6922 | 122.7658 | 66.7525 | -123.0509 | 122.7619 | 122.9076 | 122.801 | 66.7423 | -123.187
235.6406 | 123.1659 | -66.7419 | 56.2317 | -0.0045023 | -0.003829 | 0.0013291 | 0.053132 | -0.0022199 | 0.059907 | -0.0070964 | -3.8406e-05 | 0.00026075 | 0.063877 | 0.0081366 | 0.06582 | -66.7473 | 0.028878 | -66.659 | 56.1511 | 55.9731 | 56.0559 | -66.7276 | -66.7062 | 0.018674 | -66.7407 | 56.052 | 56.1932 | 56.0865 | -66.8775 | 0.014323 | -0.080575 | -0.005326 | 0.082926 | 0.068603 | -0.25856 | -0.17583 | -0.13557 | -0.17966 | 0.035767 | 0.001262 | 0.13683 | -0.03853 | -0.14522 | 122.8931 | 122.7151 | 122.7978 | 66.7708 | -122.9593 | 122.794 | 122.9351 | 122.8284 | 66.7606 | -123.1092
236.6406 | 123.2162 | -66.6916 | 56.2363 | 0.0031287 | -0.0034016 | 0.0015427 | 0.053132 | -0.0020063 | 0.059907 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.063877 | 0.007923 | 0.06582 | -66.7427 | 0.033457 | -66.659 | 56.1557 | 55.964 | 56.0513 | -66.7276 | -66.7062 | 0.023253 | -66.7407 | 56.0566 | 56.1932 | 56.0773 | -66.8775 | -0.036031 | -0.080574 | -0.051102 | 0.032572 | 0.068603 | -0.27229 | -0.18499 | -0.18593 | -0.17965 | -0.014587 | -0.049092 | 0.13683 | -0.043108 | -0.15895 | 122.8473 | 122.6556 | 122.7429 | 66.725 | -122.9639 | 122.7482 | 122.8847 | 122.7689 | 66.7148 | -123.1138
237.6406 | 123.1293 | -66.7465 | 56.2546 | -0.0045023 | -0.003829 | 0.0013291 | 0.052705 | -0.0020063 | 0.059693 | -0.0070964 | 0.00038879 | -0.00016665 | 0.063877 | 0.0077094 | 0.06582 | -66.7473 | 0.042614 | -66.6544 | 56.1511 | 55.9777 | 56.0559 | -66.7322 | -66.7062 | 0.018674 | -66.7407 | 56.052 | 56.1886 | 56.0773 | -66.8775 | 0.014322 | -0.10346 | -0.000748 | 0.092082 | 0.07776 | -0.27687 | -0.19872 | -0.13099 | -0.20255 | 0.040345 | 0.00584 | 0.13683 | -0.065997 | -0.17726 | 122.8976 | 122.7242 | 122.8024 | 66.7891 | -122.9868 | 122.7986 | 122.9351 | 122.8238 | 66.7652 | -123.1321
238.6406 | 123.1796 | -66.7007 | 56.2546 | -0.019764 | -0.0040428 | 0.0013291 | 0.053132 | -0.0015791 | 0.059907 | -0.0070964 | 0.00017519 | -0.00016665 | 0.063663 | 0.0081366 | 0.06582 | -66.7473 | 0.033457 | -66.6453 | 56.1557 | 55.9731 | 56.0467 | -66.7185 | -66.7062 | 0.018674 | -66.7544 | 56.0566 | 56.1886 | 56.0773 | -66.8729 | -0.017717 | -0.098885 | -0.046524 | 0.055462 | 0.073179 | -0.28145 | -0.20788 | -0.17219 | -0.19797 | -0.005431 | -0.053673 | 0.11852 | -0.065997 | -0.17726 | 122.8564 | 122.6739 | 122.7474 | 66.7342 | -122.973 | 122.7574 | 122.8893 | 122.7781 | 66.7194 | -123.1275
239.6406 | 123.2483 | -66.7099 | 56.2363 | -0.0045023 | -0.0040428 | 0.0015427 | 0.052919 | -0.0022199 | 0.059907 | -0.0070964 | 0.00017519 | 4.695e-05 | 0.063877 | 0.0081366 | 0.065606 | -66.7518 | 0.038035 | -66.6544 | 56.1603 | 55.9777 | 56.0421 | -66.7322 | -66.7062 | 0.023253 | -66.7453 | 56.052 | 56.1977 | 56.0773 | -66.8729 | -0.022299 | -0.075996 | -0.041947 | 0.055461 | 0.07776 | -0.25856 | -0.19414 | -0.16304 | -0.18423 | 0.003724 | -0.03536 | 0.12768 | -0.038529 | -0.15895 | 122.8702 | 122.6876 | 122.752 | 66.7479 | -122.9685 | 122.7619 | 122.9076 | 122.7872 | 66.7332 | -123.1092
240.6406 | 123.1705 | -66.7099 | 56.25 | 0.0031287 | -0.0034016 | 0.0013291 | 0.052705 | -0.0020063 | 0.06012 | -0.0070964 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.0081366 | 0.065393 | -66.7473 | 0.033457 | -66.6499 | 56.1557 | 55.9686 | 56.0513 | -66.723 | -66.7108 | 0.023253 | -66.7453 | 56.0566 | 56.1886 | 56.0819 | -66.8729 | -0.013141 | -0.094307 | -0.037369 | 0.060039 | 0.07318 | -0.28145 | -0.19872 | -0.16304 | -0.19339 | -0.000855 | -0.03536 | 0.12768 | -0.061419 | -0.1681 | 122.8656 | 122.6785 | 122.7612 | 66.7434 | -122.973 | 122.7665 | 122.8985 | 122.7918 | 66.7332 | -123.1229
241.6406 | 123.1201 | -66.7603 | 56.2592 | -0.012133 | -0.003829 | 0.0013291 | 0.052705 | -0.0020063 | 0.059907 | -0.0070964 | -3.8406e-05 | -0.00059405 | 0.064304 | 0.007923 | 0.066247 | -66.7518 | 0.033457 | -66.659 | 56.1511 | 55.9731 | 56.0559 | -66.7322 | -66.7108 | 0.018674 | -66.7407 | 56.0566 | 56.1932 | 56.0682 | -66.8729 | 0.028055 | -0.10804 | 0.008407 | 0.10124 | 0.073182 | -0.28602 | -0.20329 | -0.11268 | -0.20254 | 0.049499 | 0.019573 | 0.13226 | -0.065996 | -0.191 | 122.9114 | 122.7334 | 122.8161 | 66.7937 | -122.9914 | 122.8169 | 122.9534 | 122.8284 | 66.7789 | -123.1321
242.6406 | 123.2437 | -66.7053 | 56.2454 | -0.0045023 | -0.0040428 | 0.0011155 | 0.052705 | -0.0017927 | 0.059907 | 0.00053414 | -0.00025221 | 4.695e-05 | 0.063877 | 0.0081366 | 0.065606 | -66.7564 | 0.033457 | -66.659 | 56.1557 | 55.9731 | 56.065 | -66.7368 | -66.7062 | 0.018674 | -66.7407 | 56.0612 | 56.1977 | 56.0727 | -66.8729 | -0.031456 | -0.089729 | -0.051104 | 0.046305 | 0.077761 | -0.27229 | -0.18041 | -0.16761 | -0.18423 | -0.000854 | -0.035359 | 0.13226 | -0.047684 | -0.17268 | 122.861 | 122.6785 | 122.7703 | 66.7388 | -122.9822 | 122.7665 | 122.9031 | 122.7781 | 66.724 | -123.1184
243.6406 | 123.0652 | -66.7511 | 56.2271 | -0.012133 | -0.003829 | 0.0011155 | 0.052705 | -0.0020063 | 0.059907 | 0.00053414 | -3.8406e-05 | -0.00038025 | 0.06409 | 0.0077094 | 0.06582 | -66.7473 | 0.038035 | -66.659 | 56.1557 | 55.9731 | 56.0513 | -66.7368 | -66.7108 | 0.036989 | -66.7453 | 56.0612 | 56.1932 | 56.0819 | -66.8729 | 0.014321 | -0.071419 | 0.00383 | 0.092082 | 0.077761 | -0.25398 | -0.17583 | -0.12184 | -0.16592 | 0.040344 | 0.005839 | 0.12768 | -0.033953 | -0.14522 | 122.9068 | 122.7242 | 122.8024 | 66.7891 | -122.9639 | 122.8123 | 122.9443 | 122.833 | 66.7881 | -123.1
244.6406 | 123.1842 | -66.7145 | 56.2958 | -0.012133 | -0.0040428 | 0.0013291 | 0.052491 | -0.0022199 | 0.06012 | -0.014727 | 0.00038879 | -0.00038025 | 0.064304 | 0.0083504 | 0.065606 | -66.7381 | 0.028878 | -66.659 | 56.1603 | 55.9731 | 56.0513 | -66.7414 | -66.7153 | 0.03241 | -66.7498 | 56.052 | 56.1886 | 56.0727 | -66.8775 | -0.026878 | -0.1355 | -0.023634 | 0.055461 | 0.082339 | -0.32264 | -0.24449 | -0.16304 | -0.24374 | -0.000856 | -0.035361 | 0.12768 | -0.10719 | -0.22304 | 122.8747 | 122.6876 | 122.7658 | 66.7434 | -123.0371 | 122.7665 | 122.9031 | 122.7872 | 66.7469 | -123.1733
245.6406 | 123.1567 | -66.7374 | 56.2408 | -0.0045023 | -0.003829 | 0.0013291 | 0.052705 | -0.0017927 | 0.060334 | 0.0081646 | -3.8406e-05 | -0.00038025 | 0.064304 | 0.007923 | 0.065606 | -66.7427 | 0.033457 | -66.6636 | 56.1603 | 55.9731 | 56.0559 | -66.7276 | -66.7016 | 0.014095 | -66.7453 | 56.0566 | 56.1932 | 56.0682 | -66.8821 | 0.009746 | -0.080574 | -0.005325 | 0.07377 | 0.064024 | -0.26771 | -0.18498 | -0.14473 | -0.18423 | 0.035768 | -0.007894 | 0.13683 | -0.047686 | -0.17269 | 122.8976 | 122.7105 | 122.7932 | 66.7708 | -122.9685 | 122.794 | 122.9305 | 122.8055 | 66.7515 | -123.1229
246.6406 | 123.1659 | -66.6687 | 56.2225 | -0.0045023 | -0.0040428 | 0.0013291 | 0.052705 | -0.0017927 | 0.06012 | 0.00053414 | -0.00025221 | -0.00016665 | 0.063663 | 0.007923 | 0.06582 | -66.7518 | 0.028878 | -66.6544 | 56.1603 | 55.9731 | 56.0559 | -66.7276 | -66.7016 | 0.023253 | -66.7453 | 56.0612 | 56.1886 | 56.0773 | -66.8775 | -0.058919 | -0.062263 | -0.083146 | 0.014262 | 0.073181 | -0.2494 | -0.16667 | -0.20881 | -0.16134 | -0.032897 | -0.076559 | 0.13226 | -0.033953 | -0.14522 | 122.829 | 122.6418 | 122.7246 | 66.6976 | -122.9502 | 122.7299 | 122.8573 | 122.746 | 66.692 | -123.1
247.6406 | 123.143 | -66.7557 | 56.2317 | -0.0045023 | -0.0040428 | 0.0015427 | 0.052278 | -0.0020063 | 0.06012 | 0.0081646 | -0.00025221 | -0.00016665 | 0.064518 | 0.007923 | 0.06582 | -66.7427 | 0.042614 | -66.6636 | 56.1557 | 55.964 | 56.0604 | -66.7322 | -66.7062 | 0.023253 | -66.7498 | 56.0566 | 56.1932 | 56.0727 | -66.8775 | 0.023477 | -0.075996 | 0.012985 | 0.09208 | 0.068603 | -0.26771 | -0.17125 | -0.12184 | -0.17508 | 0.0495 | 0.005837 | 0.12768 | -0.03853 | -0.15895 | 122.9114 | 122.7197 | 122.8161 | 66.7983 | -122.9639 | 122.8123 | 122.9488 | 122.8284 | 66.7789 | -123.1092
248.6406 | 123.1842 | -66.6962 | 56.2454 | -0.0045023 | -0.0040428 | 0.0017565 | 0.052491 | -0.0020063 | 0.060334 | -0.0070964 | -0.00046581 | -0.00059405 | 0.064304 | 0.007923 | 0.06582 | -66.7427 | 0.028878 | -66.659 | 56.1603 | 55.964 | 56.0559 | -66.7276 | -66.7108 | 0.023253 | -66.7407 | 56.0566 | 56.1932 | 56.0727 | -66.8821 | -0.031453 | -0.085151 | -0.046524 | 0.03715 | 0.068603 | -0.28145 | -0.18956 | -0.18593 | -0.18881 | -0.014588 | -0.044514 | 0.14141 | -0.052263 | -0.17268 | 122.8564 | 122.6601 | 122.752 | 66.725 | -122.973 | 122.7528 | 122.8893 | 122.7689 | 66.7194 | -123.1275
249.6406 | 123.2895 | -66.7053 | 56.218 | -0.0045023 | -0.00447 | 0.0015427 | 0.052705 | -0.0026473 | 0.060548 | 0.00053414 | -0.00046581 | -0.00080765 | 0.06409 | 0.0077094 | 0.065393 | -66.7427 | 0.033457 | -66.659 | 56.1648 | 55.9594 | 56.0513 | -66.7139 | -66.7108 | 0.027831 | -66.7453 | 56.0475 | 56.1977 | 56.0498 | -66.8729 | -0.008561 | -0.053108 | -0.037369 | 0.046305 | 0.054866 | -0.25856 | -0.16668 | -0.16761 | -0.1705 | -0.005433 | -0.039938 | 0.12768 | -0.020219 | -0.16811 | 122.8702 | 122.6647 | 122.7566 | 66.7388 | -122.9318 | 122.7528 | 122.9031 | 122.7552 | 66.7332 | -123.0909
250.6406 | 123.23 | -66.7053 | 56.2683 | 0.0031287 | -0.00447 | 0.0015427 | 0.052705 | -0.0022199 | 0.060334 | -0.0070964 | -0.00046581 | -0.00059405 | 0.06409 | 0.0074956 | 0.06582 | -66.7473 | 0.0243 | -66.659 | 56.1603 | 55.9411 | 56.0467 | -66.7322 | -66.7062 | 0.036989 | -66.7498 | 56.052 | 56.1932 | 56.027 | -66.8775 | -0.026877 | -0.10804 | -0.041947 | 0.046305 | 0.073182 | -0.32723 | -0.22161 | -0.17219 | -0.21628 | -0.000854 | -0.044517 | 0.12768 | -0.075152 | -0.24136 | 122.8656 | 122.6464 | 122.752 | 66.7296 | -123.0005 | 122.7574 | 122.8985 | 122.7323 | 66.7423 | -123.1458
251.6406 | 123.1522 | -66.7282 | 56.2775 | -0.0045023 | -0.0040428 | 0.0015427 | 0.052705 | -0.0017927 | 0.06012 | 0.0081646 | 0.00017519 | 0.00026075 | 0.063877 | 0.0083504 | 0.06582 | -66.7427 | 0.042614 | -66.6544 | 56.1603 | 55.9365 | 56.0513 | -66.7322 | -66.7062 | 0.027831 | -66.7453 | 56.0612 | 56.1977 | 55.9812 | -66.8729 | -0.003989 | -0.11719 | -0.014481 | 0.073771 | 0.07776 | -0.34096 | -0.22618 | -0.14473 | -0.21628 | 0.022034 | -0.01705 | 0.12768 | -0.079728 | -0.2963 | 122.8885 | 122.6647 | 122.7795 | 66.7708 | -123.0097 | 122.7894 | 122.9259 | 122.7094 | 66.756 | -123.1504
252.6406 | 123.2162 | -66.7145 | 56.2271 | 0.0031287 | -0.0046838 | 0.0013291 | 0.052491 | -0.0020063 | 0.06012 | 0.00053414 | -3.8406e-05 | -0.00038025 | 0.064518 | 0.0077094 | 0.065393 | -66.7381 | 0.033457 | -66.6499 | 56.1557 | 55.9273 | 56.0467 | -66.7368 | -66.7016 | 0.023253 | -66.7361 | 56.052 | 56.1932 | 55.972 | -66.8775 | -0.0223 | -0.071419 | -0.023634 | 0.064617 | 0.086917 | -0.29977 | -0.18041 | -0.16304 | -0.17508 | 0.01288 | -0.021625 | 0.14141 | -0.033953 | -0.2551 | 122.8702 | 122.6418 | 122.7612 | 66.7479 | -122.9639 | 122.7665 | 122.9076 | 122.6865 | 66.7377 | -123.1046
253.6406 | 123.1705 | -66.7282 | 56.2775 | -0.0045023 | -0.0042564 | 0.0015427 | 0.052491 | -0.0024337 | 0.060761 | 0.00053414 | -0.00025221 | 4.695e-05 | 0.064518 | 0.0081366 | 0.06582 | -66.7518 | 0.051771 | -66.6728 | 56.1877 | 55.9914 | 56.0925 | -66.7734 | -66.7245 | 0.041567 | -66.7453 | 56.0566 | 56.1932 | 55.9216 | -66.8775 | -0.045199 | -0.089725 | -0.023637 | 0.055458 | 0.10066 | -0.28602 | -0.18498 | -0.1493 | -0.22085 | 0.003719 | -0.01705 | 0.13226 | -0.084307 | -0.35582 | 122.916 | 122.7197 | 122.8207 | 66.78 | -123.0509 | 122.7848 | 122.9214 | 122.6499 | 66.7698 | -123.155
254.6406 | 123.1293 | -66.7236 | 56.2866 | -0.012133 | -0.0042564 | 0.0013291 | 0.052705 | -0.0020063 | 0.060761 | 0.0081646 | -0.00025221 | 4.695e-05 | 0.06409 | 0.0077094 | 0.06582 | -66.7427 | 0.047193 | -66.6682 | 56.1877 | 55.9686 | 56.0925 | -66.8009 | -66.7153 | 0.036989 | -66.7407 | 56.0566 | 56.1886 | 56.0315 | -66.8729 | -0.077249 | -0.09888 | -0.019058 | 0.055459 | 0.13271 | -0.31807 | -0.19413 | -0.1493 | -0.23001 | 0.008299 | -0.017048 | 0.13226 | -0.09804 | -0.25509 | 122.9114 | 122.6922 | 122.8161 | 66.7708 | -123.0875 | 122.7802 | 122.9122 | 122.7552 | 66.7606 | -123.1596
255.6406 | 123.1018 | -66.7557 | 56.2592 | -0.0045023 | -0.003829 | 0.0015427 | 0.052705 | -0.0022199 | 0.060548 | 0.00053414 | -0.00046581 | -0.00038025 | 0.063877 | 0.0081366 | 0.06582 | -66.7473 | 0.051771 | -66.6636 | 56.1877 | 55.9686 | 56.0925 | -66.8055 | -66.7153 | 0.03241 | -66.7407 | 56.052 | 56.1932 | 56.1643 | -66.8775 | -0.049785 | -0.071414 | 0.008407 | 0.09208 | 0.14186 | -0.2906 | -0.16667 | -0.12184 | -0.20712 | 0.040342 | 0.014995 | 0.13683 | -0.065996 | -0.094844 | 122.9434 | 122.7242 | 122.8482 | 66.8074 | -123.0646 | 122.8077 | 122.9488 | 122.92 | 66.7881 | -123.1367
256.6406 | 123.1979 | -66.7191 | 56.25 | 0.0031287 | -0.0042564 | 0.0015427 | 0.052705 | -0.0022199 | 0.060334 | 0.0081646 | -3.8406e-05 | -0.00059405 | 0.064518 | 0.0081366 | 0.06582 | -66.7427 | 0.047193 | -66.6728 | 56.1969 | 55.996 | 56.0925 | -66.8055 | -66.7153 | 0.036989 | -66.7453 | 56.052 | 56.1932 | 56.1872 | -66.8729 | -0.086406 | -0.053102 | -0.023636 | 0.046303 | 0.13271 | -0.25397 | -0.15751 | -0.15388 | -0.19797 | 0.003721 | -0.026205 | 0.12768 | -0.056841 | -0.062796 | 122.916 | 122.7151 | 122.8115 | 66.7662 | -123.0555 | 122.7711 | 122.9122 | 122.9063 | 66.756 | -123.1229
257.6406 | 123.1155 | -66.7328 | 56.2592 | -0.012133 | -0.00447 | 0.0013291 | 0.052491 | -0.0024337 | 0.060761 | 0.0081646 | -0.00025221 | -0.00016665 | 0.064304 | 0.007923 | 0.065393 | -66.7427 | 0.047193 | -66.6728 | 56.1923 | 56.0052 | 56.0925 | -66.8009 | -66.7199 | 0.050725 | -66.7407 | 56.0566 | 56.1886 | 56.1918 | -66.8775 | -0.068094 | -0.066835 | -0.009903 | 0.060036 | 0.12813 | -0.25397 | -0.16667 | -0.14473 | -0.20254 | 0.012876 | -0.007893 | 0.13683 | -0.070574 | -0.067373 | 122.9251 | 122.738 | 122.8253 | 66.78 | -123.06 | 122.7894 | 122.9214 | 122.9246 | 66.7835 | -123.1367
258.6406 | 123.2437 | -66.7282 | 56.2546 | -0.0045023 | -0.00447 | 0.0013291 | 0.052919 | -0.0020063 | 0.060548 | -0.0070964 | -0.00025221 | -0.00038025 | 0.064304 | 0.0083504 | 0.065393 | -66.7473 | 0.047193 | -66.6819 | 56.1877 | 56.0281 | 56.0833 | -66.8009 | -66.7199 | 0.03241 | -66.7361 | 56.0566 | 56.1977 | 56.1918 | -66.8775 | -0.072672 | -0.066837 | -0.019059 | 0.046301 | 0.11897 | -0.2265 | -0.17125 | -0.1493 | -0.19797 | 0.008298 | -0.007893 | 0.14141 | -0.05684 | -0.062796 | 122.916 | 122.7563 | 122.8115 | 66.7754 | -123.0555 | 122.7848 | 122.9259 | 122.92 | 66.7606 | -123.1321
259.6406 | 123.2071 | -66.6824 | 56.2088 | -0.0045023 | -0.0042564 | 0.0013291 | 0.052919 | -0.0020063 | 0.060548 | 0.0081646 | -0.00046581 | -0.00016665 | 0.064518 | 0.0081366 | 0.065393 | -66.7473 | 0.047193 | -66.6682 | 56.1877 | 55.9869 | 56.0925 | -66.8009 | -66.7245 | 0.03241 | -66.7361 | 56.0566 | 56.1932 | 56.2055 | -66.8821 | -0.11845 | -0.02106 | -0.064835 | 0.01426 | 0.13271 | -0.22193 | -0.11631 | -0.19966 | -0.15219 | -0.042057 | -0.053669 | 0.14599 | -0.015642 | -0.003283 | 122.8702 | 122.6693 | 122.7749 | 66.7296 | -123.0097 | 122.739 | 122.8756 | 122.888 | 66.7148 | -123.0909
260.6406 | 123.2346 | -66.7099 | 56.2317 | 0.0031287 | -0.0042564 | 0.0013291 | 0.052705 | -0.0020063 | 0.060548 | 0.00053414 | -0.00046581 | -0.00016665 | 0.063877 | 0.0083504 | 0.065606 | -66.7427 | 0.047193 | -66.6682 | 56.1877 | 55.964 | 56.0879 | -66.7917 | -66.7108 | 0.036989 | -66.7453 | 56.0566 | 56.1932 | 56.2101 | -66.8729 | -0.081825 | -0.043948 | -0.032791 | 0.041726 | 0.12355 | -0.26771 | -0.14378 | -0.16304 | -0.17508 | -0.000855 | -0.03536 | 0.12768 | -0.03853 | -0.021592 | 122.8976 | 122.6739 | 122.7978 | 66.7571 | -123.0234 | 122.7665 | 122.9031 | 122.92 | 66.7469 | -123.1046
261.6406 | 123.1064 | -66.7465 | 56.2592 | -0.0045023 | -0.0040428 | 0.0013291 | 0.052705 | -0.0020063 | 0.059907 | 0.00053414 | 0.00017519 | -0.00016665 | 0.063877 | 0.0081366 | 0.065393 | -66.7381 | 0.042614 | -66.659 | 56.1832 | 55.9502 | 56.0925 | -66.7917 | -66.7108 | 0.036989 | -66.7453 | 56.0566 | 56.1932 | 56.2055 | -66.8821 | -0.045204 | -0.075992 | 0.008409 | 0.087504 | 0.13271 | -0.30892 | -0.16667 | -0.13557 | -0.20254 | 0.035766 | 0.001261 | 0.13683 | -0.065996 | -0.053637 | 122.9297 | 122.6968 | 122.839 | 66.7891 | -123.0509 | 122.8031 | 122.9397 | 122.952 | 66.7835 | -123.1412
262.6406 | 123.2025 | -66.7053 | 56.2729 | 0.0031287 | -0.0034016 | 0.0013291 | 0.052705 | -0.0020063 | 0.06012 | 0.0081646 | 0.00017519 | -0.00016665 | 0.063877 | 0.0083504 | 0.065606 | -66.7473 | 0.042614 | -66.6636 | 56.174 | 55.9502 | 56.0788 | -66.7871 | -66.7062 | 0.041567 | -66.7453 | 56.0566 | 56.2023 | 56.2009 | -66.8775 | -0.081824 | -0.098882 | -0.041947 | 0.041726 | 0.12355 | -0.32265 | -0.19414 | -0.17219 | -0.21628 | -0.000854 | -0.039938 | 0.13226 | -0.070571 | -0.071949 | 122.8793 | 122.6556 | 122.7841 | 66.7479 | -123.06 | 122.7619 | 122.9076 | 122.9063 | 66.7469 | -123.1504
263.6406 | 123.262 | -66.655 | 56.2775 | -0.0045023 | -0.003829 | 0.0013291 | 0.052919 | -0.0015791 | 0.059907 | 0.0081646 | -0.00046581 | 0.00026075 | 0.063877 | 0.0083504 | 0.065606 | -66.7427 | 0.042614 | -66.6544 | 56.174 | 55.9548 | 56.0833 | -66.7871 | -66.7062 | 0.03241 | -66.7407 | 56.0566 | 56.1932 | 56.2009 | -66.8729 | -0.13218 | -0.10346 | -0.087723 | 0.000529 | 0.13271 | -0.32265 | -0.19413 | -0.21797 | -0.22085 | -0.051208 | -0.085713 | 0.13226 | -0.084307 | -0.076527 | 122.829 | 122.6098 | 122.7383 | 66.6976 | -123.0646 | 122.7116 | 122.8481 | 122.8559 | 66.6874 | -123.1504
264.6406 | 123.262 | -66.655 | 56.2683 | 0.0031287 | -0.003829 | 0.0013291 | 0.052705 | -0.0015791 | 0.06012 | 0.0081646 | 0.00017519 | 4.695e-05 | 0.063877 | 0.0083504 | 0.065393 | -66.7473 | 0.047193 | -66.6636 | 56.1786 | 55.9548 | 56.0833 | -66.7917 | -66.7153 | 0.03241 | -66.7407 | 56.0566 | 56.1977 | 56.2147 | -66.8775 | -0.13676 | -0.089727 | -0.092301 | -0.008628 | 0.12813 | -0.31349 | -0.18498 | -0.22255 | -0.2117 | -0.060366 | -0.085713 | 0.13683 | -0.070573 | -0.053636 | 122.8336 | 122.6098 | 122.7383 | 66.7022 | -123.06 | 122.7116 | 122.8527 | 122.8696 | 66.6874 | -123.1458
265.6406 | 123.0743 | -66.7328 | 56.2683 | -0.012133 | -0.00447 | 0.0015427 | 0.052491 | -0.0020063 | 0.060334 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.0083504 | 0.065393 | -66.7427 | 0.05635 | -66.6636 | 56.1877 | 55.964 | 56.0925 | -66.7963 | -66.7199 | 0.036989 | -66.7407 | 56.0566 | 56.1977 | 56.2147 | -66.8775 | -0.063516 | -0.08057 | -0.009903 | 0.069192 | 0.13271 | -0.30434 | -0.17582 | -0.14473 | -0.2117 | 0.012876 | -0.007893 | 0.13683 | -0.070573 | -0.053636 | 122.9205 | 122.6968 | 122.8253 | 66.7891 | -123.0646 | 122.7894 | 122.9305 | 122.9475 | 66.7698 | -123.1458
266.6406 | 123.2437 | -66.6962 | 56.218 | -0.012133 | -0.00447 | 0.0013291 | 0.052705 | -0.0020063 | 0.060334 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.06409 | 0.0081366 | 0.065179 | -66.7473 | 0.047193 | -66.6636 | 56.1969 | 56.0143 | 56.0971 | -66.7963 | -66.7108 | 0.03241 | -66.7407 | 56.052 | 56.1977 | 56.2009 | -66.8729 | -0.10014 | -0.021059 | -0.051102 | 0.032571 | 0.13271 | -0.20361 | -0.12089 | -0.17677 | -0.16592 | -0.014588 | -0.044514 | 0.13226 | -0.020219 | -0.017018 | 122.8931 | 122.7105 | 122.7932 | 66.7434 | -123.0143 | 122.7482 | 122.8939 | 122.8971 | 66.7286 | -123.0909
267.6406 | 123.1338 | -66.7236 | 56.282 | 0.0031287 | -0.0046838 | 0.0015427 | 0.052278 | -0.0024337 | 0.060975 | 0.015795 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.0081366 | 0.065606 | -66.7381 | 0.051771 | -66.6682 | 56.1969 | 56.0601 | 56.0925 | -66.8055 | -66.7199 | 0.03241 | -66.7407 | 56.052 | 56.1977 | 56.0865 | -66.8821 | -0.081828 | -0.085145 | -0.014479 | 0.055459 | 0.13729 | -0.22191 | -0.18955 | -0.15846 | -0.23001 | 0.003721 | -0.017048 | 0.14141 | -0.084305 | -0.19557 | 122.9205 | 122.7838 | 122.8161 | 66.7754 | -123.0875 | 122.7757 | 122.9214 | 122.8101 | 66.756 | -123.1641
268.6406 | 123.1567 | -66.7236 | 56.282 | 0.0031287 | -0.0048974 | 0.0015427 | 0.052491 | -0.0020063 | 0.060761 | 0.0081646 | -0.00046581 | -0.00059405 | 0.064518 | 0.0081366 | 0.065606 | -66.7381 | 0.047193 | -66.6728 | 56.1877 | 56.0464 | 56.0971 | -66.81 | -66.7245 | 0.03241 | -66.7453 | 56.0658 | 56.2023 | 56.0086 | -66.8729 | -0.086407 | -0.094302 | -0.014479 | 0.050881 | 0.13729 | -0.23565 | -0.18498 | -0.1493 | -0.21627 | -0.000858 | -0.021627 | 0.12768 | -0.079726 | -0.27341 | 122.9114 | 122.77 | 122.8207 | 66.7708 | -123.0921 | 122.7894 | 122.926 | 122.7323 | 66.756 | -123.155
269.6406 | 123.2162 | -66.6916 | 56.2042 | -0.012133 | -0.0046838 | 0.0017565 | 0.052705 | -0.0022199 | 0.060761 | 0.00053414 | -0.00067941 | -0.00059405 | 0.064304 | 0.0081366 | 0.065606 | -66.7473 | 0.047193 | -66.6728 | 56.1832 | 56.0418 | 56.1062 | -66.8009 | -66.7291 | 0.03241 | -66.7453 | 56.0566 | 56.1977 | 55.9629 | -66.8821 | -0.10929 | -0.021061 | -0.05568 | 0.018837 | 0.12813 | -0.16241 | -0.097999 | -0.19051 | -0.14761 | -0.037481 | -0.053671 | 0.13683 | -0.006486 | -0.24137 | 122.8748 | 122.7334 | 122.7978 | 66.7388 | -123.0051 | 122.7482 | 122.8893 | 122.6544 | 66.724 | -123.0863
270.6406 | 123.2483 | -66.7145 | 56.2317 | -0.012133 | -0.00447 | 0.0015427 | 0.052278 | -0.0024337 | 0.060548 | 0.00053414 | -0.00025221 | -0.00080765 | 0.063877 | 0.0081366 | 0.065393 | -66.7473 | 0.042614 | -66.6682 | 56.1969 | 55.9686 | 56.0971 | -66.7734 | -66.7291 | 0.036989 | -66.7453 | 56.0566 | 56.1977 | 55.9674 | -66.8821 | -0.058931 | -0.034791 | -0.032791 | 0.046304 | 0.10524 | -0.26314 | -0.13462 | -0.16762 | -0.17508 | -0.014592 | -0.030782 | 0.13683 | -0.033951 | -0.26426 | 122.9114 | 122.683 | 122.8115 | 66.7571 | -123.0051 | 122.7711 | 122.9122 | 122.6819 | 66.7515 | -123.1138
271.6406 | 123.0881 | -66.7419 | 56.2637 | -0.012133 | -0.0048974 | 0.0015427 | 0.052278 | -0.0024337 | 0.061189 | -0.0070964 | -0.00067941 | -0.00038025 | 0.064304 | 0.0081366 | 0.065606 | -66.7427 | 0.033457 | -66.6773 | 56.1603 | 55.9273 | 56.0513 | -66.7459 | -66.7199 | 0.03241 | -66.7407 | 56.0566 | 56.1932 | 55.9491 | -66.8775 | -0.003992 | -0.10346 | -0.000748 | 0.064612 | 0.068604 | -0.33639 | -0.21245 | -0.13557 | -0.20712 | 0.022031 | 0.001262 | 0.13683 | -0.070574 | -0.31462 | 122.9022 | 122.6693 | 122.7932 | 66.7754 | -123.0097 | 122.7986 | 122.9351 | 122.6911 | 66.7744 | -123.1412
272.6406 | 123.143 | -66.7465 | 56.2454 | -0.0045023 | -0.0048974 | 0.0015427 | 0.052491 | -0.0028609 | 0.060975 | 0.00053414 | -0.00046581 | -0.00038025 | 0.064518 | 0.0083504 | 0.065393 | -66.7427 | 0.033457 | -66.6544 | 56.1603 | 55.9273 | 56.0559 | -66.7414 | -66.7108 | 0.027831 | -66.7453 | 56.0566 | 56.1977 | 55.9766 | -66.8821 | 0.005165 | -0.085151 | 0.00383 | 0.092082 | 0.086917 | -0.31808 | -0.18956 | -0.13557 | -0.18881 | 0.035766 | 0.001261 | 0.13683 | -0.047684 | -0.26883 | 122.9068 | 122.6739 | 122.8024 | 66.78 | -122.9868 | 122.8031 | 122.9443 | 122.7231 | 66.7744 | -123.1275
273.6406 | 123.2071 | -66.6916 | 56.2225 | -0.0045023 | -0.0040428 | 0.0013291 | 0.052278 | -0.0024337 | 0.059907 | 0.00053414 | 0.00017519 | 0.00026075 | 0.063877 | 0.008564 | 0.065393 | -66.7427 | 0.033457 | -66.6499 | 56.1557 | 55.9319 | 56.0559 | -66.7414 | -66.7016 | 0.023253 | -66.7407 | 56.052 | 56.1977 | 55.9903 | -66.8775 | -0.049767 | -0.066841 | -0.051102 | 0.041728 | 0.091495 | -0.29061 | -0.16667 | -0.18593 | -0.1705 | -0.010009 | -0.049092 | 0.13683 | -0.024796 | -0.23221 | 122.8473 | 122.6235 | 122.7474 | 66.725 | -122.9639 | 122.7436 | 122.8893 | 122.6819 | 66.7148 | -123.1
274.6406 | 123.1934 | -66.7191 | 56.2546 | -0.019764 | -0.0042564 | 0.0015427 | 0.052705 | -0.0020063 | 0.059693 | -0.0070964 | -0.00025221 | 0.00026075 | 0.063877 | 0.008564 | 0.065606 | -66.7427 | 0.033457 | -66.6544 | 56.1603 | 55.9273 | 56.0513 | -66.7322 | -66.7016 | 0.018674 | -66.7407 | 56.0566 | 56.1977 | 55.9629 | -66.8775 | -0.013144 | -0.094307 | -0.023636 | 0.064616 | 0.07776 | -0.32724 | -0.2033 | -0.15846 | -0.19797 | 0.017457 | -0.021626 | 0.13683 | -0.05684 | -0.29173 | 122.8793 | 122.6464 | 122.7703 | 66.7525 | -122.9868 | 122.7757 | 122.9168 | 122.6819 | 66.7377 | -123.1321
275.6406 | 123.1522 | -66.7053 | 56.2592 | -0.012133 | -0.0040428 | 0.0015427 | 0.052064 | -0.0017927 | 0.059907 | -0.0070964 | -0.00025221 | -0.00016665 | 0.063877 | 0.0081366 | 0.065606 | -66.7381 | 0.033457 | -66.6544 | 56.1557 | 55.9365 | 56.0559 | -66.7505 | -66.7062 | 0.023253 | -66.7407 | 56.0566 | 56.2023 | 55.9857 | -66.8729 | -0.045192 | -0.10346 | -0.03279 | 0.050883 | 0.096075 | -0.32265 | -0.20329 | -0.16761 | -0.20254 | -0.000854 | -0.035359 | 0.13226 | -0.056838 | -0.27341 | 122.861 | 122.6418 | 122.7612 | 66.7388 | -123.0097 | 122.7619 | 122.9076 | 122.6911 | 66.7286 | -123.1321
276.6406 | 123.1384 | -66.7282 | 56.2225 | -0.019764 | -0.003829 | 0.0013291 | 0.052278 | -0.0017927 | 0.059693 | -0.0070964 | -3.8406e-05 | 4.695e-05 | 0.063877 | 0.0081366 | 0.065606 | -66.7427 | 0.033457 | -66.6499 | 56.1511 | 55.9319 | 56.0559 | -66.7322 | -66.697 | 0.018674 | -66.7453 | 56.0612 | 56.1932 | 55.9629 | -66.8821 | -0.003989 | -0.07142 | -0.014481 | 0.078349 | 0.082338 | -0.29061 | -0.16667 | -0.15388 | -0.16134 | 0.031191 | -0.01705 | 0.13683 | -0.029375 | -0.25968 | 122.8793 | 122.6601 | 122.7841 | 66.7617 | -122.9547 | 122.7894 | 122.9214 | 122.6911 | 66.7469 | -123.1046
277.6406 | 123.1842 | -66.7282 | 56.2546 | 0.0031287 | -0.00447 | 0.0015427 | 0.052491 | -0.0020063 | 0.059693 | -0.0070964 | 0.00017519 | -0.00016665 | 0.063663 | 0.008564 | 0.065606 | -66.7381 | 0.038035 | -66.6499 | 56.1557 | 55.9319 | 56.0604 | -66.7414 | -66.7153 | 0.027831 | -66.7498 | 56.0566 | 56.1977 | 55.9674 | -66.8775 | -0.013146 | -0.098885 | -0.009902 | 0.078349 | 0.091495 | -0.32266 | -0.19414 | -0.1493 | -0.19797 | 0.012876 | -0.021629 | 0.12768 | -0.05684 | -0.28715 | 122.8839 | 122.6601 | 122.7886 | 66.7662 | -122.9959 | 122.7848 | 122.9259 | 122.6956 | 66.756 | -123.1321
278.6406 | 123.1979 | -66.6916 | 56.2271 | -0.0045023 | -0.0040428 | 0.0013291 | 0.052278 | -0.0015791 | 0.06012 | -0.014727 | 0.00017519 | 4.695e-05 | 0.063663 | 0.0083504 | 0.065393 | -66.7381 | 0.028878 | -66.6499 | 56.1603 | 55.9319 | 56.0513 | -66.723 | -66.7108 | 0.023253 | -66.7453 | 56.0566 | 56.1977 | 55.9629 | -66.8729 | -0.031452 | -0.066841 | -0.046523 | 0.041728 | 0.07318 | -0.29519 | -0.17583 | -0.18135 | -0.1705 | -0.019166 | -0.053671 | 0.12768 | -0.029374 | -0.26426 | 122.8519 | 122.6235 | 122.7429 | 66.7205 | -122.9502 | 122.7482 | 122.8893 | 122.6544 | 66.7148 | -123.1
279.6406 | 123.2574 | -66.6916 | 56.2271 | -0.0045023 | -0.0042564 | 0.0011155 | 0.052491 | -0.0017927 | 0.059907 | -0.0070964 | -0.00025221 | 4.695e-05 | 0.063877 | 0.0081366 | 0.065393 | -66.7381 | 0.033457 | -66.6544 | 56.1557 | 55.9365 | 56.0513 | -66.7322 | -66.7016 | 0.023253 | -66.7361 | 56.0612 | 56.1977 | 55.9629 | -66.8821 | -0.04061 | -0.071419 | -0.046523 | 0.03715 | 0.07776 | -0.29061 | -0.17583 | -0.19051 | -0.16592 | -0.010009 | -0.044514 | 0.14599 | -0.029374 | -0.26426 | 122.8473 | 122.6281 | 122.7429 | 66.725 | -122.9593 | 122.7528 | 122.8893 | 122.6544 | 66.7148 | -123.1092
280.6406 | 123.23 | -66.6916 | 56.2317 | -0.012133 | -0.0042564 | 0.0015427 | 0.052491 | -0.0017927 | 0.059693 | 0.00053414 | 0.00017519 | 0.00026075 | 0.063877 | 0.008564 | 0.065393 | -66.7381 | 0.028878 | -66.6544 | 56.1511 | 55.9411 | 56.0604 | -66.7139 | -66.7016 | 0.023253 | -66.7361 | 56.0612 | 56.2023 | 55.9812 | -66.8729 | -0.022294 | -0.080575 | -0.046523 | 0.03715 | 0.059444 | -0.29061 | -0.17125 | -0.18135 | -0.1705 | -0.010009 | -0.044514 | 0.13683 | -0.029372 | -0.25052 | 122.8427 | 122.6327 | 122.752 | 66.7205 | -122.9456 | 122.7528 | 122.8939 | 122.6728 | 66.7148 | -123.1046
281.6406 | 123.175 | -66.7282 | 56.2683 | -0.0045023 | -0.0042564 | 0.0017565 | 0.052278 | -0.0022199 | 0.059693 | -0.0070964 | -0.00025221 | -0.00016665 | 0.063877 | 0.008564 | 0.065606 | -66.7381 | 0.033457 | -66.6499 | 56.1557 | 55.9319 | 56.065 | -66.7322 | -66.7016 | 0.027831 | -66.7453 | 56.0566 | 56.1932 | 56.027 | -66.8775 | -0.003989 | -0.11262 | -0.009902 | 0.078349 | 0.082338 | -0.33639 | -0.20329 | -0.1493 | -0.2117 | 0.026612 | -0.01705 | 0.13226 | -0.075152 | -0.24136 | 122.8839 | 122.6601 | 122.7932 | 66.7617 | -123.0005 | 122.7848 | 122.9214 | 122.7552 | 66.756 | -123.1458
282.6406 | 123.0927 | -66.7557 | 56.2683 | -0.0045023 | -0.0040428 | 0.0013291 | 0.052278 | -0.0020063 | 0.059693 | 0.00053414 | -0.00025221 | 4.695e-05 | 0.064304 | 0.008564 | 0.065606 | -66.7381 | 0.038035 | -66.6544 | 56.1557 | 55.9457 | 56.0559 | -66.7368 | -66.7016 | 0.027831 | -66.7361 | 56.0566 | 56.1932 | 56.0086 | -66.8729 | 0.018898 | -0.11262 | 0.017564 | 0.10124 | 0.082339 | -0.32265 | -0.21245 | -0.11726 | -0.2117 | 0.054078 | 0.019573 | 0.13683 | -0.075152 | -0.25967 | 122.9114 | 122.7013 | 122.8115 | 66.7937 | -123.0051 | 122.8123 | 122.9488 | 122.7643 | 66.7835 | -123.1412
283.6406 | 123.1201 | -66.7465 | 56.2408 | 0.0031287 | -0.0040428 | 0.0017565 | 0.052278 | -0.0022199 | 0.059907 | -0.014727 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.0083504 | 0.065606 | -66.7381 | 0.033457 | -66.6453 | 56.1557 | 55.9457 | 56.0604 | -66.7368 | -66.697 | 0.027831 | -66.7361 | 56.0566 | 56.1932 | 56.0224 | -66.8775 | 0.009743 | -0.085152 | 0.008409 | 0.10124 | 0.091495 | -0.29519 | -0.18041 | -0.13099 | -0.18423 | 0.049502 | 0.010418 | 0.14141 | -0.047686 | -0.21847 | 122.9022 | 122.6922 | 122.807 | 66.78 | -122.9776 | 122.8031 | 122.9397 | 122.7689 | 66.7744 | -123.1184
284.6406 | 123.2071 | -66.6916 | 56.1951 | -0.0045023 | -0.00447 | 0.0013291 | 0.052705 | -0.0015791 | 0.059907 | 0.00053414 | -0.00025221 | 4.695e-05 | 0.06409 | 0.008564 | 0.065606 | -66.7427 | 0.033457 | -66.6499 | 56.1557 | 55.9411 | 56.0513 | -66.7185 | -66.7062 | 0.018674 | -66.7498 | 56.052 | 56.2023 | 56.027 | -66.8821 | -0.026873 | -0.039375 | -0.051102 | 0.041728 | 0.068601 | -0.25399 | -0.14379 | -0.19051 | -0.14303 | -0.014587 | -0.05825 | 0.13226 | 0.007249 | -0.16812 | 122.8473 | 122.6327 | 122.7429 | 66.725 | -122.9135 | 122.7436 | 122.8939 | 122.7185 | 66.7103 | -123.0772
285.6406 | 123.1796 | -66.7053 | 56.2683 | 0.0031287 | -0.0042564 | 0.00090168 | 0.052064 | -0.0020063 | 0.06012 | 0.0081646 | -0.00025221 | 4.695e-05 | 0.064304 | 0.007923 | 0.065393 | -66.7381 | 0.038035 | -66.6499 | 56.1603 | 55.9411 | 56.0559 | -66.7322 | -66.7062 | 0.03241 | -66.7315 | 56.0612 | 56.1932 | 56.0544 | -66.8775 | -0.026877 | -0.10804 | -0.03279 | 0.055461 | 0.082338 | -0.32723 | -0.21245 | -0.17219 | -0.20712 | -0.000854 | -0.026202 | 0.14599 | -0.075152 | -0.21389 | 122.8656 | 122.6464 | 122.7612 | 66.7434 | -123.0005 | 122.7665 | 122.8985 | 122.7597 | 66.7377 | -123.1458
286.6406 | 123.1522 | -66.7419 | 56.2683 | 0.0031287 | -0.0042564 | 0.0015427 | 0.052491 | -0.0020063 | 0.060334 | -0.0070964 | -0.00025221 | -0.00038025 | 0.064304 | 0.008564 | 0.065606 | -66.7427 | 0.042614 | -66.6544 | 56.1603 | 55.9502 | 56.065 | -66.7276 | -66.7108 | 0.023253 | -66.7361 | 56.0475 | 56.2023 | 56.0453 | -66.8821 | 0.014323 | -0.10804 | -0.000748 | 0.087504 | 0.073181 | -0.31807 | -0.20329 | -0.14015 | -0.22086 | 0.031188 | 0.00584 | 0.14599 | -0.065994 | -0.22304 | 122.9022 | 122.6922 | 122.807 | 66.7846 | -122.9959 | 122.7894 | 122.9443 | 122.7872 | 66.7652 | -123.1504
287.6406 | 123.1842 | -66.7145 | 56.2546 | 0.0031287 | -0.00447 | 0.0013291 | 0.052491 | -0.0020063 | 0.06012 | 0.00053414 | -0.00046581 | -0.00016665 | 0.06409 | 0.008564 | 0.065606 | -66.7335 | 0.028878 | -66.6636 | 56.1603 | 55.9365 | 56.065 | -66.7368 | -66.7108 | 0.027831 | -66.7407 | 56.0566 | 56.1932 | 56.0498 | -66.8775 | -0.0223 | -0.094307 | -0.019056 | 0.050882 | 0.073182 | -0.31808 | -0.18956 | -0.16304 | -0.19797 | 0.003723 | -0.026203 | 0.13683 | -0.061419 | -0.20473 | 122.8747 | 122.651 | 122.7795 | 66.7434 | -122.9914 | 122.7711 | 122.9076 | 122.7643 | 66.7423 | -123.1321
288.6406 | 123.1247 | -66.7282 | 56.2637 | -0.0045023 | -0.00447 | 0.0015427 | 0.052278 | -0.0022199 | 0.06012 | 0.015795 | -3.8406e-05 | -0.00038025 | 0.063877 | 0.0081366 | 0.065393 | -66.7381 | 0.028878 | -66.6544 | 56.1603 | 55.9411 | 56.065 | -66.7414 | -66.7108 | 0.018674 | -66.7453 | 56.0566 | 56.1977 | 56.059 | -66.8867 | -0.013146 | -0.10346 | -0.009902 | 0.073771 | 0.086917 | -0.32265 | -0.19872 | -0.15846 | -0.20712 | 0.017455 | -0.01705 | 0.14141 | -0.065995 | -0.20473 | 122.8885 | 122.6693 | 122.7932 | 66.7571 | -123.0051 | 122.7848 | 122.9259 | 122.7872 | 66.7469 | -123.1504
289.6406 | 123.1293 | -66.7419 | 56.2546 | -0.0045023 | -0.0048974 | 0.0017565 | 0.052278 | -0.0022199 | 0.060334 | 0.00053414 | -0.00025221 | -0.00016665 | 0.064731 | 0.0081366 | 0.065393 | -66.7427 | 0.033457 | -66.659 | 56.1648 | 55.9502 | 56.0559 | -66.7414 | -66.7016 | 0.023253 | -66.7361 | 56.0566 | 56.2023 | 56.0544 | -66.8821 | 0.000587 | -0.089729 | -0.000748 | 0.082926 | 0.082339 | -0.30434 | -0.19872 | -0.14015 | -0.19797 | 0.040345 | 0.00584 | 0.14599 | -0.052261 | -0.20015 | 122.9068 | 122.6922 | 122.7978 | 66.7754 | -122.9959 | 122.7986 | 122.9443 | 122.7964 | 66.7652 | -123.1367
290.6406 | 123.143 | -66.7557 | 56.2729 | -0.0045023 | -0.0042564 | 0.0013291 | 0.052278 | -0.0024337 | 0.060548 | -0.0070964 | -0.00067941 | -0.00016665 | 0.064304 | 0.0083504 | 0.06582 | -66.7427 | 0.042614 | -66.6544 | 56.1648 | 55.9502 | 56.0604 | -66.7322 | -66.7016 | 0.027831 | -66.7315 | 56.0566 | 56.1886 | 56.0315 | -66.8775 | 0.023477 | -0.10804 | 0.012985 | 0.10124 | 0.07776 | -0.32265 | -0.21245 | -0.12184 | -0.21628 | 0.054078 | 0.024152 | 0.14599 | -0.084307 | -0.24136 | 122.9205 | 122.7059 | 122.8161 | 66.7983 | -123.0051 | 122.8123 | 122.9443 | 122.7872 | 66.7835 | -123.1504
291.6406 | 123.1201 | -66.7236 | 56.3004 | -0.0045023 | -0.0046838 | 0.0017565 | 0.052491 | -0.0024337 | 0.060334 | 0.0081646 | -0.00046581 | 4.695e-05 | 0.06409 | 0.008564 | 0.065606 | -66.7381 | 0.038035 | -66.6636 | 56.1603 | 55.9548 | 56.065 | -66.7368 | -66.7153 | 0.023253 | -66.7407 | 56.0566 | 56.1932 | 56.0453 | -66.8729 | -0.013145 | -0.14008 | -0.014479 | 0.060037 | 0.073182 | -0.34554 | -0.23534 | -0.1493 | -0.24374 | 0.008299 | -0.017048 | 0.13226 | -0.10719 | -0.25509 | 122.8839 | 122.6784 | 122.7887 | 66.7617 | -123.0371 | 122.7802 | 122.9168 | 122.7689 | 66.7469 | -123.1733
292.6406 | 123.1155 | -66.7191 | 56.2408 | -0.019764 | -0.00447 | 0.0013291 | 0.052064 | -0.0024337 | 0.060334 | 0.00053414 | -0.00046581 | -0.00038025 | 0.06409 | 0.008564 | 0.065606 | -66.7427 | 0.033457 | -66.6636 | 56.1648 | 55.9411 | 56.0559 | -66.7368 | -66.7153 | 0.03241 | -66.7315 | 56.0658 | 56.1977 | 56.0498 | -66.8775 | -0.017723 | -0.075996 | -0.023636 | 0.055459 | 0.073182 | -0.29977 | -0.18498 | -0.15846 | -0.17508 | 0.003721 | -0.012469 | 0.14599 | -0.043107 | -0.191 | 122.8839 | 122.6601 | 122.7749 | 66.7525 | -122.9776 | 122.7848 | 122.9168 | 122.7689 | 66.7515 | -123.1184
293.6406 | 123.1201 | -66.7282 | 56.2729 | 0.0031287 | -0.00447 | 0.0015427 | 0.052278 | -0.0017927 | 0.059907 | -0.0070964 | -3.8406e-05 | -0.00038025 | 0.063877 | 0.0083504 | 0.065606 | -66.7473 | 0.033457 | -66.6544 | 56.1648 | 55.9548 | 56.0559 | -66.7322 | -66.697 | 0.027831 | -66.7269 | 56.052 | 56.1977 | 56.0361 | -66.8821 | -0.003989 | -0.10804 | -0.019059 | 0.073771 | 0.07776 | -0.31807 | -0.21703 | -0.15388 | -0.22086 | 0.031191 | 0.001265 | 0.15515 | -0.07515 | -0.23678 | 122.8931 | 122.683 | 122.7841 | 66.7617 | -123.0051 | 122.7802 | 122.9259 | 122.7643 | 66.756 | -123.155
294.6406 | 123.1796 | -66.7282 | 56.2637 | -0.0045023 | -0.0048974 | 0.0017565 | 0.052278 | -0.0022199 | 0.059907 | 0.00053414 | -0.00067941 | 4.695e-05 | 0.064304 | 0.008564 | 0.065179 | -66.7381 | 0.047193 | -66.659 | 56.1603 | 55.9502 | 56.0604 | -66.723 | -66.7062 | 0.027831 | -66.7407 | 56.0475 | 56.1977 | 56.0315 | -66.8775 | 0.005169 | -0.10346 | -0.009902 | 0.069193 | 0.064024 | -0.3135 | -0.20329 | -0.1493 | -0.21628 | 0.022034 | -0.012471 | 0.13683 | -0.065995 | -0.2322 | 122.8885 | 122.6784 | 122.7886 | 66.7754 | -122.9868 | 122.7757 | 122.9259 | 122.7597 | 66.756 | -123.1412
295.6406 | 123.1705 | -66.7099 | 56.2866 | 0.0031287 | -0.0042564 | 0.0011155 | 0.052064 | -0.0022199 | 0.059907 | -0.0070964 | -3.8406e-05 | -0.00038025 | 0.064304 | 0.0083504 | 0.065606 | -66.7427 | 0.038035 | -66.6544 | 56.1511 | 55.9502 | 56.0604 | -66.7276 | -66.7062 | 0.027831 | -66.7361 | 56.052 | 56.1932 | 56.0361 | -66.8775 | -0.01772 | -0.13551 | -0.032791 | 0.055461 | 0.073181 | -0.33638 | -0.22618 | -0.16761 | -0.23459 | 0.003724 | -0.026203 | 0.14141 | -0.093462 | -0.25051 | 122.861 | 122.6601 | 122.7703 | 66.7479 | -123.0142 | 122.7619 | 122.9031 | 122.746 | 66.7377 | -123.1641
296.6406 | 123.111 | -66.7282 | 56.2866 | -0.0045023 | -0.0042564 | 0.0013291 | 0.052278 | -0.0020063 | 0.059907 | -0.0070964 | -3.8406e-05 | -0.00038025 | 0.064304 | 0.008564 | 0.065606 | -66.7381 | 0.042614 | -66.6544 | 56.1511 | 55.9365 | 56.065 | -66.7414 | -66.7062 | 0.023253 | -66.7361 | 56.0612 | 56.2023 | 56.0315 | -66.8775 | -0.013146 | -0.13551 | -0.009902 | 0.073771 | 0.086917 | -0.35012 | -0.2216 | -0.1493 | -0.22543 | 0.022034 | -0.007893 | 0.14141 | -0.084304 | -0.25509 | 122.8793 | 122.6647 | 122.7932 | 66.7708 | -123.028 | 122.7894 | 122.9305 | 122.7597 | 66.7515 | -123.1641
297.6406 | 123.1476 | -66.7099 | 56.2683 | -0.019764 | -0.00447 | 0.0015427 | 0.052278 | -0.0022199 | 0.060334 | 0.0081646 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.008564 | 0.065393 | -66.7427 | 0.047193 | -66.6453 | 56.1603 | 55.9411 | 56.0604 | -66.7185 | -66.7016 | 0.023253 | -66.7453 | 56.0566 | 56.2023 | 56.0315 | -66.8821 | -0.008562 | -0.10804 | -0.032791 | 0.064617 | 0.073179 | -0.32723 | -0.20787 | -0.17219 | -0.2117 | 0.008302 | -0.03536 | 0.13683 | -0.065994 | -0.23678 | 122.8702 | 122.651 | 122.7703 | 66.7571 | -122.9868 | 122.7665 | 122.9122 | 122.7414 | 66.7332 | -123.1504
298.6406 | 123.1476 | -66.7191 | 56.2729 | -0.0045023 | -0.0046838 | 0.0013291 | 0.052064 | -0.0022199 | 0.059907 | 0.00053414 | -0.00046581 | 4.695e-05 | 0.064518 | 0.0087778 | 0.065393 | -66.7335 | 0.033457 | -66.659 | 56.1557 | 55.9457 | 56.0604 | -66.7414 | -66.7016 | 0.027831 | -66.7361 | 56.0566 | 56.1977 | 56.0041 | -66.8821 | -0.022301 | -0.1172 | -0.014479 | 0.060038 | 0.082339 | -0.32723 | -0.21245 | -0.16304 | -0.21628 | 0.017457 | -0.017048 | 0.14599 | -0.07515 | -0.26883 | 122.8747 | 122.6647 | 122.7795 | 66.7525 | -123.0142 | 122.7757 | 122.9168 | 122.7231 | 66.7469 | -123.155
299.6406 | 123.1522 | -66.7236 | 56.2866 | -0.0045023 | -0.00447 | 0.0013291 | 0.052491 | -0.0017927 | 0.059907 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.064518 | 0.0087778 | 0.065606 | -66.7473 | 0.038035 | -66.659 | 56.1603 | 55.9502 | 56.0604 | -66.7414 | -66.7016 | 0.03241 | -66.7407 | 56.0566 | 56.2023 | 56.0178 | -66.8821 | -0.017723 | -0.12635 | -0.023636 | 0.064616 | 0.082339 | -0.33638 | -0.22618 | -0.15846 | -0.23001 | 0.022035 | -0.017048 | 0.14141 | -0.084304 | -0.26883 | 122.8839 | 122.6739 | 122.7841 | 66.7617 | -123.028 | 122.7802 | 122.926 | 122.7414 | 66.756 | -123.1687
300.6406 | 123.111 | -66.7099 | 56.3095 | -0.0045023 | -0.0048974 | 0.0013291 | 0.052278 | -0.0020063 | 0.06012 | 0.00053414 | -0.00025221 | -0.00038025 | 0.063877 | 0.008564 | 0.065606 | -66.7427 | 0.042614 | -66.6544 | 56.1557 | 55.9502 | 56.065 | -66.7047 | -66.7016 | 0.023253 | -66.7407 | 56.0612 | 56.2023 | 56.0315 | -66.8821 | 0.005175 | -0.15382 | -0.032791 | 0.055461 | 0.050286 | -0.35927 | -0.24449 | -0.17219 | -0.24832 | 0.008302 | -0.030781 | 0.14141 | -0.10719 | -0.27798 | 122.8656 | 122.6601 | 122.7749 | 66.7525 | -123.0142 | 122.7711 | 122.9122 | 122.7414 | 66.7332 | -123.1916
301.6406 | 123.2254 | -66.7007 | 56.2454 | -0.012133 | -0.0046838 | 0.0015427 | 0.052491 | -0.0022199 | 0.06012 | 0.0081646 | -0.0011066 | -0.00038025 | 0.064304 | 0.008564 | 0.065179 | -66.7335 | 0.033457 | -66.6544 | 56.1557 | 55.9411 | 56.0604 | -66.7322 | -66.7062 | 0.027831 | -66.7453 | 56.0475 | 56.2023 | 56.0407 | -66.8867 | -0.031454 | -0.089729 | -0.032789 | 0.046306 | 0.07776 | -0.30434 | -0.18498 | -0.18593 | -0.19797 | -0.005431 | -0.044515 | 0.14141 | -0.043105 | -0.20473 | 122.8564 | 122.6418 | 122.7612 | 66.7342 | -122.9776 | 122.7482 | 122.9031 | 122.7414 | 66.7286 | -123.1321
302.6406 | 123.1796 | -66.7282 | 56.3049 | 0.0031287 | -0.0048974 | 0.0011155 | 0.052278 | -0.0024337 | 0.060334 | 0.0081646 | -0.00046581 | -0.00059405 | 0.063877 | 0.0083504 | 0.065606 | -66.7381 | 0.033457 | -66.659 | 56.1603 | 55.9502 | 56.0604 | -66.7368 | -66.7062 | 0.023253 | -66.7361 | 56.052 | 56.2069 | 56.0361 | -66.8775 | -0.008568 | -0.14466 | -0.009902 | 0.069193 | 0.077761 | -0.35469 | -0.24449 | -0.1493 | -0.2529 | 0.022034 | -0.007893 | 0.14141 | -0.098037 | -0.26882 | 122.8885 | 122.6784 | 122.7886 | 66.7617 | -123.0417 | 122.7802 | 122.9351 | 122.7643 | 66.7515 | -123.1824
303.6406 | 123.2712 | -66.6595 | 56.2225 | 0.0031287 | -0.0046838 | 0.0011155 | 0.052491 | -0.0022199 | 0.06012 | 0.0081646 | -0.00046581 | 4.695e-05 | 0.06409 | 0.008564 | 0.065393 | -66.7381 | 0.038035 | -66.6544 | 56.1603 | 55.9457 | 56.0513 | -66.7368 | -66.7108 | 0.027831 | -66.7453 | 56.052 | 56.184 | 56.0498 | -66.8867 | -0.077232 | -0.062263 | -0.078566 | 0.005107 | 0.082339 | -0.27688 | -0.17125 | -0.22713 | -0.1705 | -0.051209 | -0.085714 | 0.14141 | -0.038532 | -0.17269 | 122.8198 | 122.6052 | 122.7108 | 66.6976 | -122.9593 | 122.7116 | 122.8435 | 122.7094 | 66.6874 | -123.1092
304.6406 | 123.1201 | -66.7191 | 56.2958 | 0.01076 | -0.0048974 | 0.0015427 | 0.052278 | -0.0022199 | 0.060334 | -0.0070964 | -0.00046581 | -0.00038025 | 0.06409 | 0.008564 | 0.064966 | -66.7427 | 0.038035 | -66.659 | 56.1648 | 55.9548 | 56.0559 | -66.7368 | -66.7062 | 0.03241 | -66.7315 | 56.0566 | 56.1932 | 56.0407 | -66.8821 | -0.017723 | -0.13093 | -0.023636 | 0.060038 | 0.077761 | -0.34096 | -0.23992 | -0.16304 | -0.23916 | 0.012879 | -0.012469 | 0.15057 | -0.10262 | -0.25509 | 122.8839 | 122.6739 | 122.7749 | 66.7571 | -123.0326 | 122.7757 | 122.9122 | 122.7597 | 66.7515 | -123.1779
305.6406 | 123.2254 | -66.6687 | 56.25 | 0.0031287 | -0.005111 | 0.0015427 | 0.052705 | -0.0024337 | 0.06012 | 0.00053414 | -0.00046581 | -0.00038025 | 0.064304 | 0.0087778 | 0.065606 | -66.7427 | 0.038035 | -66.6636 | 56.1557 | 55.9457 | 56.0513 | -66.7185 | -66.7108 | 0.023253 | -66.7453 | 56.0566 | 56.1932 | 56.0407 | -66.8821 | -0.049761 | -0.094307 | -0.07399 | 0.005105 | 0.054866 | -0.30434 | -0.19872 | -0.21339 | -0.19339 | -0.042054 | -0.076559 | 0.13683 | -0.056841 | -0.20931 | 122.8244 | 122.6144 | 122.72 | 66.7067 | -122.9685 | 122.7253 | 122.8619 | 122.7094 | 66.692 | -123.1321
306.6406 | 123.2254 | -66.6641 | 56.2546 | -0.012133 | -0.0046838 | 0.0019701 | 0.052064 | -0.0022199 | 0.060334 | 0.015795 | -0.00025221 | -0.00038025 | 0.06409 | 0.0087778 | 0.065179 | -66.7381 | 0.038035 | -66.6544 | 56.1603 | 55.9502 | 56.0559 | -66.723 | -66.7016 | 0.027831 | -66.7315 | 56.0566 | 56.1932 | 56.0407 | -66.8821 | -0.058917 | -0.094307 | -0.073988 | 0.009685 | 0.068602 | -0.30434 | -0.19872 | -0.21797 | -0.19797 | -0.037474 | -0.0674 | 0.15057 | -0.061419 | -0.21389 | 122.8244 | 122.6144 | 122.72 | 66.7022 | -122.9776 | 122.7207 | 122.8573 | 122.7048 | 66.692 | -123.1367
307.6406 | 123.2071 | -66.7191 | 56.218 | 0.0031287 | -0.0048974 | 0.0017565 | 0.052491 | -0.0024337 | 0.060334 | 0.00053414 | -3.8406e-05 | -0.00059405 | 0.06409 | 0.008564 | 0.064966 | -66.7381 | 0.042614 | -66.659 | 56.1603 | 55.9457 | 56.0559 | -66.7276 | -66.7016 | 0.023253 | -66.7407 | 56.0566 | 56.1977 | 56.0544 | -66.8821 | -0.008565 | -0.057686 | -0.019057 | 0.060038 | 0.068603 | -0.2723 | -0.1621 | -0.16304 | -0.16134 | 0.017457 | -0.021626 | 0.14141 | -0.020219 | -0.16353 | 122.8793 | 122.6647 | 122.7749 | 66.7617 | -122.9456 | 122.7757 | 122.9168 | 122.7735 | 66.7423 | -123.1001
308.6406 | 123.2071 | -66.6779 | 56.2912 | -0.0045023 | -0.0046838 | 0.0015427 | 0.052278 | -0.0026473 | 0.06012 | 0.0081646 | -3.8406e-05 | -0.00059405 | 0.064518 | 0.0089914 | 0.065179 | -66.7381 | 0.033457 | -66.6636 | 56.1603 | 55.9502 | 56.0559 | -66.7368 | -66.7108 | 0.027831 | -66.7361 | 56.052 | 56.1932 | 56.0453 | -66.8821 | -0.058922 | -0.13093 | -0.060256 | 0.01426 | 0.073182 | -0.34096 | -0.23534 | -0.20424 | -0.23917 | -0.032899 | -0.058247 | 0.14599 | -0.09804 | -0.24593 | 122.8381 | 122.6281 | 122.7337 | 66.7113 | -123.028 | 122.7299 | 122.871 | 122.7231 | 66.7057 | -123.1733
309.6406 | 123.2025 | -66.7053 | 56.2546 | -0.0045023 | -0.0046838 | 0.0015427 | 0.052705 | -0.0022199 | 0.060548 | 0.00053414 | -0.00046581 | -0.00059405 | 0.064304 | 0.008564 | 0.065179 | -66.7335 | 0.028878 | -66.6544 | 56.1557 | 55.9457 | 56.0559 | -66.7414 | -66.7108 | 0.018674 | -66.7407 | 56.0566 | 56.1932 | 56.0498 | -66.8913 | -0.036034 | -0.098885 | -0.028212 | 0.050883 | 0.086917 | -0.30892 | -0.19872 | -0.18593 | -0.19797 | -0.005433 | -0.035359 | 0.15057 | -0.061419 | -0.20473 | 122.861 | 122.651 | 122.7612 | 66.7342 | -122.9959 | 122.7619 | 122.8985 | 122.7552 | 66.724 | -123.1458
310.6406 | 123.2071 | -66.6779 | 56.2317 | 0.0031287 | -0.0048974 | 0.0017565 | 0.052491 | -0.0024337 | 0.060334 | -0.014727 | -0.00046581 | -0.00038025 | 0.064304 | 0.0087778 | 0.064966 | -66.7335 | 0.033457 | -66.6636 | 56.1603 | 55.9457 | 56.0559 | -66.7322 | -66.7108 | 0.027831 | -66.7361 | 56.0566 | 56.2023 | 56.027 | -66.8821 | -0.054343 | -0.071418 | -0.055678 | 0.01426 | 0.068603 | -0.28603 | -0.17583 | -0.20424 | -0.17508 | -0.032899 | -0.058247 | 0.14599 | -0.029372 | -0.20474 | 122.8381 | 122.6235 | 122.7337 | 66.7113 | -122.9639 | 122.7345 | 122.8802 | 122.7048 | 66.7057 | -123.1138
311.6406 | 123.262 | -66.687 | 56.2363 | -0.0045023 | -0.005111 | 0.0017565 | 0.052491 | -0.0022199 | 0.059693 | -0.0070964 | -0.00025221 | -0.00038025 | 0.064304 | 0.0089914 | 0.065606 | -66.7381 | 0.038035 | -66.6544 | 56.1511 | 55.9411 | 56.0604 | -66.7322 | -66.7016 | 0.018674 | -66.7361 | 56.0566 | 56.1932 | 56.0361 | -66.8867 | -0.045187 | -0.085153 | -0.0511 | 0.032573 | 0.07776 | -0.29519 | -0.17583 | -0.19966 | -0.17965 | -0.014586 | -0.049091 | 0.15057 | -0.043108 | -0.20016 | 122.8381 | 122.6281 | 122.7475 | 66.725 | -122.9685 | 122.7436 | 122.8802 | 122.7231 | 66.7057 | -123.1229
312.6406 | 123.1934 | -66.6641 | 56.2637 | 0.0031287 | -0.0053248 | 0.0013291 | 0.052278 | -0.0022199 | 0.060334 | 0.00053414 | -0.00025221 | -0.00038025 | 0.064304 | 0.0087778 | 0.065179 | -66.7244 | 0.038035 | -66.659 | 56.1603 | 55.9594 | 56.0604 | -66.7368 | -66.7108 | 0.027831 | -66.7361 | 56.052 | 56.1977 | 56.0498 | -66.8821 | -0.072654 | -0.10346 | -0.060253 | 0.005107 | 0.077761 | -0.30434 | -0.20329 | -0.21797 | -0.2117 | -0.046631 | -0.071979 | 0.14599 | -0.065995 | -0.21389 | 122.8244 | 122.6235 | 122.7246 | 66.7022 | -123.0005 | 122.7162 | 122.8619 | 122.714 | 66.692 | -123.1458
313.6406 | 123.1934 | -66.7007 | 56.2317 | 0.0031287 | -0.005111 | 0.0013291 | 0.052491 | -0.0020063 | 0.060334 | 0.0081646 | -0.00025221 | -0.00016665 | 0.06409 | 0.0089914 | 0.065606 | -66.7381 | 0.038035 | -66.6544 | 56.1694 | 55.9502 | 56.0604 | -66.7322 | -66.7016 | 0.018674 | -66.7361 | 56.0475 | 56.1977 | 56.0361 | -66.8821 | -0.031454 | -0.062261 | -0.037367 | 0.046306 | 0.07776 | -0.28145 | -0.17125 | -0.18135 | -0.18423 | -0.000853 | -0.035358 | 0.14599 | -0.033951 | -0.19558 | 122.8702 | 122.651 | 122.7612 | 66.7388 | -122.9639 | 122.7482 | 122.8985 | 122.7369 | 66.7194 | -123.1138
314.6406 | 123.1522 | -66.7145 | 56.337 | 0.01076 | -0.005111 | 0.0011155 | 0.052278 | -0.0024337 | 0.06012 | 0.0081646 | -0.00046581 | -0.00038025 | 0.064518 | 0.0087778 | 0.065393 | -66.7381 | 0.0243 | -66.6544 | 56.1648 | 55.9502 | 56.0604 | -66.7322 | -66.7062 | 0.023253 | -66.7453 | 56.052 | 56.1932 | 56.0361 | -66.8821 | -0.017721 | -0.17213 | -0.023634 | 0.060039 | 0.07776 | -0.38674 | -0.27654 | -0.16762 | -0.28494 | 0.008302 | -0.030782 | 0.13683 | -0.14382 | -0.30087 | 122.8793 | 122.6647 | 122.7749 | 66.7388 | -123.0692 | 122.7665 | 122.9076 | 122.7506 | 66.7377 | -123.2191
315.6406 | 123.2025 | -66.7053 | 56.1996 | -0.012133 | -0.0053248 | 0.0015427 | 0.052278 | -0.0024337 | 0.06012 | -0.0070964 | -0.00046581 | -0.00038025 | 0.06409 | 0.0087778 | 0.065179 | -66.7381 | 0.038035 | -66.6544 | 56.1557 | 55.9457 | 56.0559 | -66.7459 | -66.7062 | 0.014095 | -66.7315 | 56.0612 | 56.1886 | 56.0224 | -66.8821 | -0.040613 | -0.043953 | -0.03279 | 0.050883 | 0.091496 | -0.25399 | -0.14379 | -0.17677 | -0.13846 | -0.000854 | -0.026202 | 0.15057 | -0.011065 | -0.17727 | 122.861 | 122.651 | 122.7612 | 66.7434 | -122.9456 | 122.7665 | 122.8939 | 122.7277 | 66.7194 | -123.0817
316.6406 | 123.2529 | -66.6779 | 56.2454 | -0.0045023 | -0.0048974 | 0.0011155 | 0.052491 | -0.0026473 | 0.060334 | 0.0081646 | -0.00025221 | -0.00038025 | 0.064731 | 0.0089914 | 0.065393 | -66.7427 | 0.028878 | -66.6453 | 56.1511 | 55.9457 | 56.0604 | -66.7093 | -66.7062 | 0.023253 | -66.7407 | 56.0658 | 56.1932 | 56.0361 | -66.8913 | -0.031448 | -0.094308 | -0.064835 | 0.032573 | 0.064021 | -0.29976 | -0.18498 | -0.2134 | -0.17965 | -0.02832 | -0.062825 | 0.15057 | -0.052263 | -0.20931 | 122.829 | 122.6235 | 122.7383 | 66.7067 | -122.9547 | 122.7436 | 122.871 | 122.714 | 66.7011 | -123.1367
317.6406 | 123.3124 | -66.7282 | 56.1768 | -0.0045023 | -0.005111 | 0.0019701 | 0.052278 | -0.0022199 | 0.060334 | -0.0070964 | -0.00067941 | -0.00059405 | 0.064304 | 0.0089914 | 0.065393 | -66.729 | 0.038035 | -66.6544 | 56.1603 | 55.9502 | 56.0559 | -66.7276 | -66.7062 | 0.018674 | -66.7407 | 56.0475 | 56.1977 | 56.0453 | -66.8821 | 0.00059 | -0.016487 | -0.000746 | 0.073771 | 0.073181 | -0.22652 | -0.1209 | -0.15388 | -0.1293 | 0.022034 | -0.012471 | 0.14141 | 0.02098 | -0.13149 | 122.8885 | 122.6784 | 122.7841 | 66.7662 | -122.9044 | 122.7757 | 122.9259 | 122.7735 | 66.7469 | -123.0589
318.6406 | 123.1659 | -66.7236 | 56.2454 | 0.0031287 | -0.0048974 | 0.0013291 | 0.052491 | -0.0022199 | 0.059907 | 0.015795 | -0.00025221 | -0.00038025 | 0.064304 | 0.009205 | 0.06582 | -66.7427 | 0.038035 | -66.6544 | 56.1648 | 55.9502 | 56.065 | -66.723 | -66.7016 | 0.023253 | -66.7361 | 56.0475 | 56.2023 | 56.0453 | -66.8821 | 0.000592 | -0.080573 | -0.019058 | 0.069194 | 0.068602 | -0.29518 | -0.18041 | -0.15846 | -0.19797 | 0.022035 | -0.01247 | 0.14599 | -0.043105 | -0.20015 | 122.8885 | 122.6739 | 122.7887 | 66.7617 | -122.9685 | 122.7711 | 122.926 | 122.7689 | 66.7469 | -123.1275
319.6406 | 123.2529 | -66.7007 | 56.2546 | 0.0031287 | -0.005111 | 0.0015427 | 0.052491 | -0.0022199 | 0.06012 | 0.00053414 | -3.8406e-05 | -0.00059405 | 0.064304 | 0.0087778 | 0.064966 | -66.7335 | 0.047193 | -66.6544 | 56.1648 | 55.9502 | 56.0604 | -66.7185 | -66.7108 | 0.023253 | -66.7315 | 56.052 | 56.1932 | 56.0453 | -66.8821 | -0.017717 | -0.089729 | -0.032789 | 0.046306 | 0.064023 | -0.30434 | -0.19414 | -0.18135 | -0.20255 | -0.01001 | -0.030779 | 0.15057 | -0.061419 | -0.20931 | 122.8656 | 122.651 | 122.7612 | 66.7479 | -122.973 | 122.7528 | 122.8939 | 122.746 | 66.724 | -123.1367
320.6406 | 123.2117 | -66.7145 | 56.2546 | -0.0045023 | -0.0055384 | 0.0015427 | 0.052705 | -0.0022199 | 0.06012 | 0.015795 | -0.00025221 | -0.00059405 | 0.06409 | 0.0087778 | 0.065393 | -66.7335 | 0.033457 | -66.659 | 56.1557 | 55.9457 | 56.0559 | -66.7139 | -66.7108 | 0.027831 | -66.7407 | 56.052 | 56.1932 | 56.0361 | -66.8821 | 0.000595 | -0.098885 | -0.019056 | 0.055461 | 0.054866 | -0.30892 | -0.19872 | -0.16762 | -0.20255 | 0.003723 | -0.026203 | 0.14141 | -0.061419 | -0.21847 | 122.8702 | 122.6601 | 122.7703 | 66.7479 | -122.9685 | 122.7665 | 122.9076 | 122.7506 | 66.7423 | -123.1367
321.6406 | 123.2162 | -66.7053 | 56.2271 | -0.0045023 | -0.0053248 | 0.0017565 | 0.052278 | -0.0026473 | 0.060334 | -0.022357 | -0.00025221 | 4.695e-05 | 0.06409 | 0.0087778 | 0.065393 | -66.7427 | 0.038035 | -66.6544 | 56.1603 | 55.9502 | 56.0604 | -66.7276 | -66.7108 | 0.023253 | -66.7407 | 56.0612 | 56.2023 | 56.0498 | -66.8729 | -0.022298 | -0.066841 | -0.037369 | 0.050883 | 0.073181 | -0.27687 | -0.16667 | -0.16761 | -0.16592 | -0.005433 | -0.035359 | 0.13226 | -0.024795 | -0.17727 | 122.8656 | 122.6556 | 122.7658 | 66.7434 | -122.9547 | 122.7665 | 122.9076 | 122.7552 | 66.7286 | -123.1
322.6406 | 123.1796 | -66.7053 | 56.2408 | 0.0031287 | -0.005111 | 0.0015427 | 0.052705 | -0.0026473 | 0.060334 | 0.0081646 | -0.00046581 | -0.00038025 | 0.06409 | 0.008564 | 0.065393 | -66.7335 | 0.033457 | -66.659 | 56.1603 | 55.9457 | 56.0513 | -66.7368 | -66.7153 | 0.018674 | -66.7407 | 56.0566 | 56.1932 | 56.0453 | -66.8775 | -0.031456 | -0.080574 | -0.028212 | 0.046305 | 0.077761 | -0.29519 | -0.18956 | -0.17219 | -0.18423 | -0.010012 | -0.035359 | 0.13683 | -0.047686 | -0.19558 | 122.8656 | 122.651 | 122.7566 | 66.7388 | -122.9776 | 122.7619 | 122.8985 | 122.7506 | 66.724 | -123.1184
323.6406 | 123.0789 | -66.7282 | 56.2866 | -0.0045023 | -0.0053248 | 0.0013291 | 0.052705 | -0.0020063 | 0.06012 | 0.00053414 | -0.00067941 | -0.00059405 | 0.06409 | 0.0089914 | 0.065179 | -66.7335 | 0.042614 | -66.6499 | 56.1648 | 55.9548 | 56.0467 | -66.7414 | -66.7108 | 0.027831 | -66.7407 | 56.0566 | 56.1977 | 56.059 | -66.8729 | -0.013146 | -0.12177 | -0.005324 | 0.078349 | 0.091495 | -0.3318 | -0.23992 | -0.14473 | -0.23001 | 0.017455 | -0.012471 | 0.13226 | -0.088883 | -0.22762 | 122.8931 | 122.683 | 122.7749 | 66.7708 | -123.028 | 122.7848 | 122.9259 | 122.7872 | 66.756 | -123.1596
324.6406 | 123.2437 | -66.6779 | 56.25 | -0.0045023 | -0.0048974 | 0.0015427 | 0.052491 | -0.0020063 | 0.060334 | 0.00053414 | -0.00025221 | -0.00038025 | 0.064518 | 0.0089914 | 0.065606 | -66.729 | 0.038035 | -66.659 | 56.1557 | 55.9548 | 56.0559 | -66.723 | -66.7016 | 0.023253 | -66.7361 | 56.0612 | 56.2023 | 56.0407 | -66.8821 | -0.045185 | -0.094307 | -0.0511 | 0.018839 | 0.064024 | -0.29518 | -0.19414 | -0.20424 | -0.18881 | -0.023742 | -0.058247 | 0.14599 | -0.047683 | -0.20931 | 122.8335 | 122.6327 | 122.7337 | 66.7159 | -122.973 | 122.739 | 122.8802 | 122.7185 | 66.7011 | -123.1321
325.6406 | 123.1247 | -66.7236 | 56.2546 | -0.012133 | -0.005111 | 0.0015427 | 0.052491 | -0.0024337 | 0.060548 | -0.0070964 | -3.8406e-05 | -0.00059405 | 0.064304 | 0.0087778 | 0.065393 | -66.7381 | 0.033457 | -66.6636 | 56.1603 | 55.964 | 56.0604 | -66.7139 | -66.7062 | 0.018674 | -66.7407 | 56.052 | 56.1977 | 56.0498 | -66.8867 | 0.00975 | -0.094307 | -0.014479 | 0.060037 | 0.050287 | -0.2906 | -0.19414 | -0.16304 | -0.20255 | 0.017457 | -0.017048 | 0.14599 | -0.05684 | -0.20473 | 122.8839 | 122.6876 | 122.7841 | 66.7571 | -122.9685 | 122.7757 | 122.9214 | 122.7735 | 66.7423 | -123.1413
326.6406 | 123.2437 | -66.6824 | 56.2408 | -0.0045023 | -0.0048974 | 0.0011155 | 0.052278 | -0.0022199 | 0.060548 | 0.00053414 | -0.00025221 | 4.695e-05 | 0.064304 | 0.0089914 | 0.065606 | -66.7335 | 0.033457 | -66.659 | 56.1557 | 55.9594 | 56.0513 | -66.7322 | -66.7062 | 0.023253 | -66.7315 | 56.0566 | 56.1932 | 56.059 | -66.8913 | -0.049765 | -0.085152 | -0.0511 | 0.023417 | 0.073182 | -0.28145 | -0.18956 | -0.20882 | -0.18423 | -0.023742 | -0.04909 | 0.15973 | -0.047686 | -0.18184 | 122.8381 | 122.6418 | 122.7337 | 66.7159 | -122.973 | 122.739 | 122.8756 | 122.7414 | 66.7057 | -123.1321
327.6406 | 123.1338 | -66.7465 | 56.2866 | 0.0031287 | -0.005111 | 0.0013291 | 0.052491 | -0.0022199 | 0.060334 | 0.0081646 | -3.8406e-05 | -0.00038025 | 0.06409 | 0.0087778 | 0.065606 | -66.7335 | 0.033457 | -66.659 | 56.1557 | 55.964 | 56.0513 | -66.7322 | -66.7062 | 0.027831 | -66.7361 | 56.0566 | 56.1932 | 56.0544 | -66.8867 | 0.014322 | -0.13093 | 0.012987 | 0.087504 | 0.073182 | -0.32265 | -0.23534 | -0.14015 | -0.23001 | 0.040345 | 0.010418 | 0.15057 | -0.093462 | -0.2322 | 122.9022 | 122.7105 | 122.7978 | 66.78 | -123.0188 | 122.8031 | 122.9397 | 122.8009 | 66.7744 | -123.1733
328.6406 | 123.2391 | -66.687 | 56.2134 | -0.012133 | -0.0048974 | 0.0015427 | 0.052491 | -0.0020063 | 0.060334 | 0.00053414 | -0.00025221 | -0.00059405 | 0.06409 | 0.0087778 | 0.065393 | -66.7381 | 0.033457 | -66.6544 | 56.1557 | 55.9594 | 56.0559 | -66.7368 | -66.7062 | 0.018674 | -66.7361 | 56.052 | 56.2023 | 56.0498 | -66.8867 | -0.049766 | -0.057686 | -0.0511 | 0.032573 | 0.082339 | -0.25398 | -0.15752 | -0.19966 | -0.16135 | -0.019164 | -0.049091 | 0.15057 | -0.011062 | -0.16353 | 122.8427 | 122.6464 | 122.7429 | 66.7205 | -122.9502 | 122.739 | 122.8893 | 122.7369 | 66.7057 | -123.1001
329.6406 | 123.2071 | -66.7191 | 56.2225 | -0.012133 | -0.0048974 | 0.0015427 | 0.052491 | -0.0024337 | 0.060334 | 0.0081646 | -0.00025221 | 4.695e-05 | 0.064518 | 0.0089914 | 0.064966 | -66.7381 | 0.038035 | -66.6544 | 56.1557 | 55.964 | 56.0604 | -66.7322 | -66.7108 | 0.027831 | -66.7361 | 56.052 | 56.2023 | 56.0498 | -66.8821 | -0.013144 | -0.066841 | -0.019057 | 0.064616 | 0.07776 | -0.25856 | -0.1621 | -0.16304 | -0.1705 | 0.0083 | -0.017048 | 0.14599 | -0.020217 | -0.17269 | 122.8747 | 122.683 | 122.7795 | 66.7571 | -122.9547 | 122.7711 | 122.9214 | 122.7689 | 66.7469 | -123.1046
330.6406 | 123.2346 | -66.7145 | 56.2317 | -0.0045023 | -0.0046838 | 0.0013291 | 0.052919 | -0.0024337 | 0.060548 | 0.00053414 | -0.00046581 | -0.00038025 | 0.064304 | 0.0087778 | 0.065179 | -66.7381 | 0.033457 | -66.6544 | 56.1603 | 55.9548 | 56.0559 | -66.7368 | -66.697 | 0.023253 | -66.7315 | 56.0566 | 56.1932 | 56.0498 | -66.8821 | -0.0223 | -0.071418 | -0.023634 | 0.060039 | 0.082339 | -0.27687 | -0.17583 | -0.16762 | -0.17508 | 0.017459 | -0.017046 | 0.15057 | -0.03853 | -0.18184 | 122.8747 | 122.6693 | 122.7703 | 66.7479 | -122.9685 | 122.7711 | 122.9076 | 122.7643 | 66.7377 | -123.1138
331.6406 | 123.1201 | -66.7282 | 56.2683 | 0.0031287 | -0.0053248 | 0.0015427 | 0.052278 | -0.0024337 | 0.060334 | 0.00053414 | -0.00046581 | 4.695e-05 | 0.064304 | 0.0087778 | 0.065393 | -66.7381 | 0.038035 | -66.659 | 56.1557 | 55.9594 | 56.0604 | -66.7368 | -66.7016 | 0.027831 | -66.7361 | 56.052 | 56.1886 | 56.0682 | -66.8821 | -0.008568 | -0.11262 | -0.009902 | 0.069193 | 0.077761 | -0.30891 | -0.20787 | -0.15388 | -0.21628 | 0.026612 | -0.007893 | 0.14599 | -0.07973 | -0.20015 | 122.8839 | 122.6876 | 122.7886 | 66.7662 | -123.0051 | 122.7802 | 122.9168 | 122.7964 | 66.756 | -123.1504
332.6406 | 123.2117 | -66.7191 | 56.1996 | -0.0045023 | -0.005111 | 0.0013291 | 0.052278 | -0.0024337 | 0.06012 | 0.00053414 | -0.00046581 | -0.00038025 | 0.064304 | 0.0089914 | 0.065606 | -66.7381 | 0.038035 | -66.659 | 56.1511 | 55.9594 | 56.065 | -66.723 | -66.7016 | 0.023253 | -66.7361 | 56.052 | 56.1886 | 56.0544 | -66.8867 | -0.003986 | -0.048532 | -0.019057 | 0.060038 | 0.064024 | -0.24025 | -0.13463 | -0.16762 | -0.14761 | 0.017457 | -0.017048 | 0.15057 | -0.011065 | -0.14522 | 122.8702 | 122.6785 | 122.7841 | 66.7571 | -122.9227 | 122.7711 | 122.9076 | 122.7735 | 66.7423 | -123.0863
333.6406 | 123.1338 | -66.7465 | 56.2637 | 0.0031287 | -0.005111 | 0.0015427 | 0.052278 | -0.0024337 | 0.06012 | 0.00053414 | -0.00046581 | -0.00038025 | 0.06409 | 0.0087778 | 0.065393 | -66.7335 | 0.042614 | -66.659 | 56.1603 | 55.9686 | 56.065 | -66.7322 | -66.7016 | 0.023253 | -66.7361 | 56.052 | 56.1932 | 56.0636 | -66.8729 | 0.014322 | -0.10346 | 0.012987 | 0.087504 | 0.073182 | -0.29518 | -0.19872 | -0.12641 | -0.2117 | 0.044923 | 0.010418 | 0.13683 | -0.070574 | -0.20015 | 122.9068 | 122.7151 | 122.8115 | 66.7891 | -122.9959 | 122.7986 | 122.9397 | 122.8101 | 66.7698 | -123.1367
334.6406 | 123.2346 | -66.7053 | 56.1996 | 0.0031287 | -0.0053248 | 0.0015427 | 0.052705 | -0.0024337 | 0.060334 | -0.0070964 | -0.00046581 | -0.00016665 | 0.064731 | 0.009205 | 0.065606 | -66.729 | 0.038035 | -66.659 | 56.1603 | 55.964 | 56.0559 | -66.7185 | -66.7062 | 0.027831 | -66.7361 | 56.0566 | 56.1932 | 56.0453 | -66.8821 | -0.01314 | -0.039375 | -0.023634 | 0.046305 | 0.059445 | -0.23567 | -0.14379 | -0.17677 | -0.14303 | -0.000854 | -0.030781 | 0.14599 | -0.006487 | -0.15438 | 122.8656 | 122.6693 | 122.7612 | 66.7434 | -122.9181 | 122.7619 | 122.8985 | 122.7506 | 66.7332 | -123.0817
335.6406 | 123.1338 | -66.7282 | 56.2866 | 0.0031287 | -0.0048974 | 0.0013291 | 0.052278 | -0.0020063 | 0.06012 | 0.00053414 | -0.00067941 | -0.00059405 | 0.064304 | 0.0089914 | 0.065606 | -66.7381 | 0.042614 | -66.6499 | 56.1648 | 55.9686 | 56.065 | -66.7185 | -66.7062 | 0.027831 | -66.7361 | 56.052 | 56.1932 | 56.059 | -66.8867 | 0.009748 | -0.12177 | -0.009902 | 0.078349 | 0.068601 | -0.31807 | -0.2216 | -0.15846 | -0.23459 | 0.022034 | -0.007893 | 0.15057 | -0.093462 | -0.22762 | 122.8931 | 122.6968 | 122.7932 | 66.7708 | -123.0051 | 122.7802 | 122.9214 | 122.7872 | 66.756 | -123.1733
336.6406 | 123.2529 | -66.7419 | 56.2454 | 0.0031287 | -0.0048974 | 0.0015427 | 0.052064 | -0.0022199 | 0.060334 | 0.00053414 | -0.00046581 | -0.00038025 | 0.064518 | 0.0087778 | 0.065179 | -66.729 | 0.038035 | -66.659 | 56.1557 | 55.9777 | 56.0604 | -66.7322 | -66.7062 | 0.027831 | -66.7361 | 56.0612 | 56.1977 | 56.0544 | -66.8867 | 0.009744 | -0.089729 | 0.012987 | 0.082926 | 0.073182 | -0.26771 | -0.18498 | -0.14473 | -0.18423 | 0.035767 | 0.00584 | 0.15057 | -0.047684 | -0.191 | 122.8976 | 122.7197 | 122.8024 | 66.78 | -122.9776 | 122.8031 | 122.9397 | 122.7964 | 66.7698 | -123.1321
337.6406 | 123.1613 | -66.7328 | 56.2775 | -0.012133 | -0.0053248 | 0.0015427 | 0.052278 | -0.0024337 | 0.059907 | -0.0070964 | -0.00046581 | -0.00016665 | 0.064304 | 0.009205 | 0.065393 | -66.7381 | 0.033457 | -66.6544 | 56.1648 | 55.9686 | 56.0604 | -66.7322 | -66.7062 | 0.027831 | -66.7315 | 56.0566 | 56.1977 | 56.0544 | -66.8821 | 0.000589 | -0.11262 | -0.005324 | 0.078349 | 0.07776 | -0.30891 | -0.21703 | -0.14931 | -0.22085 | 0.026612 | 0.001264 | 0.15057 | -0.079728 | -0.22304 | 122.8976 | 122.7013 | 122.7932 | 66.7662 | -123.0097 | 122.7894 | 122.9305 | 122.7872 | 66.7606 | -123.1596
338.6406 | 123.2117 | -66.7145 | 56.1905 | -0.0045023 | -0.005111 | 0.0017565 | 0.052278 | -0.0022199 | 0.060548 | 0.00053414 | -3.8406e-05 | -0.00059405 | 0.06409 | 0.0089914 | 0.065179 | -66.729 | 0.042614 | -66.6544 | 56.1511 | 55.964 | 56.0604 | -66.7322 | -66.7016 | 0.023253 | -66.7315 | 56.052 | 56.1977 | 56.059 | -66.8821 | -0.017721 | -0.039377 | -0.014478 | 0.060039 | 0.07776 | -0.22652 | -0.13005 | -0.16762 | -0.13846 | 0.01288 | -0.017046 | 0.15057 | 0.007247 | -0.13149 | 122.8656 | 122.6785 | 122.7749 | 66.7571 | -122.9227 | 122.7665 | 122.9122 | 122.7735 | 66.7377 | -123.0726
339.6406 | 123.0972 | -66.7557 | 56.2546 | -0.012133 | -0.0053248 | 0.0013291 | 0.052491 | -0.0022199 | 0.06012 | -0.0070964 | -0.00025221 | -0.00059405 | 0.064304 | 0.0089914 | 0.064966 | -66.7335 | 0.042614 | -66.6636 | 56.1648 | 55.964 | 56.0559 | -66.7276 | -66.7062 | 0.027831 | -66.7315 | 56.052 | 56.1977 | 56.0682 | -66.8821 | 0.028056 | -0.089729 | 0.022142 | 0.09208 | 0.064024 | -0.2906 | -0.19872 | -0.12642 | -0.20255 | 0.0495 | 0.024152 | 0.15057 | -0.05684 | -0.18642 | 122.9205 | 122.7197 | 122.8115 | 66.7983 | -122.9822 | 122.8077 | 122.9534 | 122.8238 | 66.7835 | -123.1367
340.6406 | 123.1338 | -66.7236 | 56.2592 | 0.0031287 | -0.0053248 | 0.0015427 | 0.052491 | -0.0024337 | 0.060334 | 0.00053414 | -0.00046581 | -0.00038025 | 0.064304 | 0.0089914 | 0.065606 | -66.7427 | 0.028878 | -66.6544 | 56.1603 | 55.9594 | 56.0604 | -66.7414 | -66.7016 | 0.027831 | -66.7315 | 56.0566 | 56.2023 | 56.0498 | -66.8867 | -0.017723 | -0.098884 | -0.019058 | 0.069194 | 0.086917 | -0.29976 | -0.19872 | -0.16304 | -0.20254 | 0.022035 | -0.007891 | 0.15515 | -0.056838 | -0.20931 | 122.8839 | 122.683 | 122.7841 | 66.7525 | -123.0005 | 122.7802 | 122.926 | 122.7735 | 66.7515 | -123.1458
341.6406 | 123.1293 | -66.7236 | 56.2363 | 0.0031287 | -0.0053248 | 0.0011155 | 0.052491 | -0.0022199 | 0.060548 | 0.015795 | -0.00067941 | -0.00016665 | 0.064304 | 0.0089914 | 0.065393 | -66.7335 | 0.038035 | -66.6544 | 56.1557 | 55.9594 | 56.065 | -66.723 | -66.7016 | 0.036989 | -66.7361 | 56.0566 | 56.1977 | 56.059 | -66.8867 | 0.000592 | -0.080574 | -0.009901 | 0.069194 | 0.068602 | -0.27687 | -0.17125 | -0.16304 | -0.17965 | 0.022035 | -0.01247 | 0.15057 | -0.038529 | -0.17726 | 122.8793 | 122.683 | 122.7887 | 66.7617 | -122.9593 | 122.7802 | 122.9214 | 122.7826 | 66.7606 | -123.1229
342.6406 | 123.2254 | -66.6962 | 56.2363 | -0.0045023 | -0.0053248 | 0.0015427 | 0.052491 | -0.0024337 | 0.060334 | 0.00053414 | -0.00067941 | -0.00016665 | 0.064304 | 0.009205 | 0.065179 | -66.7427 | 0.033457 | -66.6544 | 56.1603 | 55.9594 | 56.065 | -66.7276 | -66.7108 | 0.027831 | -66.7361 | 56.052 | 56.1977 | 56.0498 | -66.8775 | -0.031453 | -0.075996 | -0.046524 | 0.041728 | 0.073181 | -0.27687 | -0.17125 | -0.18135 | -0.18423 | -0.014588 | -0.039936 | 0.14141 | -0.038529 | -0.18642 | 122.8564 | 122.6556 | 122.7612 | 66.7296 | -122.9639 | 122.7482 | 122.8939 | 122.746 | 66.724 | -123.1138
343.6406 | 123.143 | -66.7053 | 56.2683 | -0.0045023 | -0.005111 | 0.0017565 | 0.052278 | -0.0026473 | 0.060548 | 0.0081646 | -0.00046581 | -0.00016665 | 0.064518 | 0.0089914 | 0.065393 | -66.7335 | 0.042614 | -66.659 | 56.1648 | 55.9594 | 56.065 | -66.723 | -66.7062 | 0.023253 | -66.7315 | 56.0475 | 56.1932 | 56.059 | -66.8867 | -0.017719 | -0.10346 | -0.028212 | 0.046305 | 0.064024 | -0.30891 | -0.20329 | -0.18135 | -0.22086 | -0.000854 | -0.026202 | 0.15515 | -0.075152 | -0.20931 | 122.8702 | 122.6647 | 122.7703 | 66.7479 | -122.9914 | 122.7528 | 122.8985 | 122.7643 | 66.7286 | -123.155
344.6406 | 123.2758 | -66.7007 | 56.1676 | 0.0031287 | -0.0055384 | 0.0015427 | 0.052705 | -0.0024337 | 0.060334 | 0.0081646 | -0.00025221 | -0.00038025 | 0.06409 | 0.009205 | 0.065393 | -66.7381 | 0.038035 | -66.659 | 56.1603 | 55.9548 | 56.0604 | -66.7368 | -66.7062 | 0.018674 | -66.7361 | 56.0566 | 56.2069 | 56.0544 | -66.8821 | -0.036033 | -0.007332 | -0.037367 | 0.041728 | 0.077761 | -0.21279 | -0.10716 | -0.18135 | -0.11099 | -0.005431 | -0.035358 | 0.14599 | 0.039292 | -0.11318 | 122.861 | 122.6556 | 122.7612 | 66.7388 | -122.9044 | 122.7574 | 122.9076 | 122.7552 | 66.7194 | -123.0497
345.6406 | 123.1247 | -66.7419 | 56.2546 | -0.012133 | -0.0053248 | 0.0011155 | 0.052064 | -0.0026473 | 0.060761 | -0.0070964 | -0.00067941 | -0.00038025 | 0.064518 | 0.0094188 | 0.065179 | -66.7381 | 0.033457 | -66.6636 | 56.1648 | 55.9548 | 56.0604 | -66.7322 | -66.7062 | 0.023253 | -66.7315 | 56.0475 | 56.2023 | 56.0636 | -66.8821 | 0.009744 | -0.089729 | 0.003831 | 0.078347 | 0.068603 | -0.29976 | -0.19414 | -0.14015 | -0.20712 | 0.035767 | 0.010419 | 0.15057 | -0.052261 | -0.191 | 122.9068 | 122.6968 | 122.8024 | 66.7754 | -122.9868 | 122.7894 | 122.9443 | 122.8055 | 66.7652 | -123.1367
346.6406 | 123.1659 | -66.7191 | 56.2363 | -0.0045023 | -0.0053248 | 0.0017565 | 0.052705 | -0.0026473 | 0.060334 | -0.0070964 | -0.00025221 | 4.695e-05 | 0.064304 | 0.0087778 | 0.065393 | -66.7335 | 0.033457 | -66.659 | 56.1557 | 55.964 | 56.0604 | -66.7322 | -66.7016 | 0.023253 | -66.7269 | 56.0566 | 56.2023 | 56.0498 | -66.8867 | -0.013144 | -0.080574 | -0.014479 | 0.060038 | 0.073182 | -0.27229 | -0.17583 | -0.16762 | -0.17965 | 0.017457 | -0.00789 | 0.15973 | -0.03395 | -0.18642 | 122.8747 | 122.683 | 122.7795 | 66.7525 | -122.9685 | 122.7757 | 122.9214 | 122.7689 | 66.7423 | -123.1229
347.6406 | 123.2254 | -66.7099 | 56.2866 | -0.012133 | -0.0053248 | 0.0015427 | 0.052705 | -0.0024337 | 0.060761 | 0.0081646 | -0.00067941 | -0.00059405 | 0.064304 | 0.0094188 | 0.065393 | -66.729 | 0.038035 | -66.6544 | 56.1603 | 55.9594 | 56.0696 | -66.7459 | -66.7062 | 0.023253 | -66.7315 | 56.0566 | 56.1977 | 56.0636 | -66.8821 | -0.036035 | -0.12635 | -0.019056 | 0.055461 | 0.091496 | -0.32722 | -0.21702 | -0.17219 | -0.23001 | 0.003724 | -0.021624 | 0.15057 | -0.088883 | -0.22304 | 122.8702 | 122.6693 | 122.7795 | 66.7479 | -123.0326 | 122.7665 | 122.9076 | 122.7735 | 66.7332 | -123.1687
348.6406 | 123.0881 | -66.7557 | 56.2134 | -0.0045023 | -0.005111 | 0.0017565 | 0.052064 | -0.0026473 | 0.060761 | -0.0070964 | -0.00046581 | -0.00016665 | 0.06409 | 0.0089914 | 0.065393 | -66.7244 | 0.042614 | -66.659 | 56.1603 | 55.964 | 56.0696 | -66.7368 | -66.7016 | 0.018674 | -66.7361 | 56.0566 | 56.1932 | 56.059 | -66.8821 | 0.018898 | -0.053108 | 0.031299 | 0.096659 | 0.077761 | -0.2494 | -0.14378 | -0.12642 | -0.15677 | 0.054078 | 0.019573 | 0.14599 | -0.02022 | -0.15438 | 122.9159 | 122.7197 | 122.8253 | 66.7983 | -122.9502 | 122.8123 | 122.9488 | 122.8147 | 66.7743 | -123.0955
349.6406 | 123.1384 | -66.7511 | 56.2408 | -0.0045023 | -0.0055384 | 0.0015427 | 0.052705 | -0.0024337 | 0.060334 | -0.0070964 | -0.00025221 | -0.00038025 | 0.064304 | 0.009205 | 0.065393 | -66.7381 | 0.038035 | -66.6544 | 56.1603 | 55.9594 | 56.065 | -66.7368 | -66.7062 | 0.03241 | -66.7315 | 56.0612 | 56.1932 | 56.0453 | -66.8775 | 0.014321 | -0.080574 | 0.012987 | 0.09666 | 0.082339 | -0.28145 | -0.17583 | -0.12642 | -0.17965 | 0.044923 | 0.019575 | 0.14599 | -0.047686 | -0.19558 | 122.9114 | 122.7105 | 122.8161 | 66.7891 | -122.9776 | 122.8123 | 122.9443 | 122.7964 | 66.7835 | -123.1184
350.6406 | 123.1842 | -66.7328 | 56.2271 | 0.0031287 | -0.005111 | 0.0017565 | 0.052278 | -0.0026473 | 0.060548 | 0.00053414 | -0.00067941 | -0.00016665 | 0.064304 | 0.0087778 | 0.065606 | -66.729 | 0.038035 | -66.6544 | 56.1648 | 55.9548 | 56.0696 | -66.7368 | -66.7016 | 0.027831 | -66.7315 | 56.0566 | 56.1886 | 56.0544 | -66.8821 | -0.00399 | -0.062263 | 0.003832 | 0.078349 | 0.082339 | -0.27229 | -0.15752 | -0.14931 | -0.1705 | 0.03119 | 0.001264 | 0.15057 | -0.038531 | -0.17269 | 122.8976 | 122.6876 | 122.8024 | 66.7708 | -122.9639 | 122.7894 | 122.9214 | 122.7872 | 66.7606 | -123.1092
351.6406 | 123.175 | -66.7191 | 56.2546 | -0.0045023 | -0.0055384 | 0.0015427 | 0.052278 | -0.0024337 | 0.060548 | 0.00053414 | -0.00067941 | -0.00059405 | 0.06409 | 0.009205 | 0.065179 | -66.7335 | 0.033457 | -66.659 | 56.1694 | 55.9594 | 56.0559 | -66.7322 | -66.7108 | 0.023253 | -66.7269 | 56.0612 | 56.1932 | 56.059 | -66.8821 | -0.013144 | -0.08515 | -0.014479 | 0.060038 | 0.073182 | -0.29518 | -0.19872 | -0.16304 | -0.19339 | 0.0083 | -0.00789 | 0.15515 | -0.061419 | -0.19558 | 122.8885 | 122.6785 | 122.7749 | 66.7525 | -122.9868 | 122.7802 | 122.9122 | 122.7781 | 66.7423 | -123.1367
352.6406 | 123.2208 | -66.7236 | 56.218 | -0.012133 | -0.0055384 | 0.0019701 | 0.052491 | -0.0024337 | 0.060548 | -0.0070964 | -0.00046581 | -0.00059405 | 0.06409 | 0.0094188 | 0.065393 | -66.7381 | 0.042614 | -66.659 | 56.1648 | 55.9594 | 56.0559 | -66.7276 | -66.7016 | 0.03241 | -66.7361 | 56.0566 | 56.2023 | 56.0498 | -66.8821 | -0.003987 | -0.053108 | -0.014479 | 0.064616 | 0.068603 | -0.25856 | -0.1621 | -0.15846 | -0.16134 | 0.022035 | -0.01247 | 0.14599 | -0.01564 | -0.16811 | 122.8885 | 122.683 | 122.7795 | 66.7662 | -122.9456 | 122.7802 | 122.926 | 122.7735 | 66.756 | -123.1001
353.6406 | 123.1522 | -66.7191 | 56.2546 | -0.019764 | -0.0055384 | 0.0013291 | 0.052705 | -0.0024337 | 0.060334 | 0.0081646 | -0.00089301 | -0.00038025 | 0.064518 | 0.009205 | 0.065179 | -66.729 | 0.038035 | -66.6544 | 56.1648 | 55.9594 | 56.0604 | -66.7414 | -66.7016 | 0.027831 | -66.7269 | 56.0612 | 56.1977 | 56.0544 | -66.8775 | -0.022301 | -0.089729 | -0.009901 | 0.064616 | 0.086917 | -0.29518 | -0.19414 | -0.15846 | -0.19339 | 0.017457 | -0.00789 | 0.15057 | -0.05684 | -0.20015 | 122.8839 | 122.6785 | 122.7795 | 66.7571 | -122.9959 | 122.7802 | 122.9168 | 122.7735 | 66.7469 | -123.1321
354.6406 | 123.1384 | -66.7328 | 56.2363 | 0.01076 | -0.0055384 | 0.0013291 | 0.052064 | -0.0022199 | 0.060548 | -0.0070964 | -0.00025221 | -0.00059405 | 0.064304 | 0.0094188 | 0.064966 | -66.7381 | 0.042614 | -66.659 | 56.1603 | 55.9502 | 56.065 | -66.7322 | -66.697 | 0.023253 | -66.7361 | 56.0566 | 56.2023 | 56.059 | -66.8821 | 0.000589 | -0.075996 | -0.005324 | 0.073771 | 0.073182 | -0.28603 | -0.17125 | -0.14931 | -0.17965 | 0.035769 | -0.003315 | 0.14599 | -0.03395 | -0.17726 | 122.8931 | 122.683 | 122.7978 | 66.7754 | -122.9685 | 122.7894 | 122.9351 | 122.7918 | 66.756 | -123.1184
355.6406 | 123.1384 | -66.7007 | 56.2729 | 0.01076 | -0.0055384 | 0.0015427 | 0.052491 | -0.0026473 | 0.060548 | 0.0081646 | -0.00046581 | -0.00059405 | 0.06409 | 0.0089914 | 0.065179 | -66.7244 | 0.038035 | -66.6544 | 56.1694 | 55.964 | 56.065 | -66.7276 | -66.7108 | 0.027831 | -66.7315 | 56.052 | 56.1977 | 56.0544 | -66.8913 | -0.026875 | -0.10346 | -0.023632 | 0.046306 | 0.073181 | -0.30891 | -0.20787 | -0.19051 | -0.22086 | -0.01001 | -0.030779 | 0.15973 | -0.07515 | -0.21846 | 122.8702 | 122.6647 | 122.7658 | 66.7388 | -123.0005 | 122.7528 | 122.8985 | 122.7552 | 66.7286 | -123.1641
356.6406 | 123.1934 | -66.6962 | 56.282 | -0.0045023 | -0.0053248 | 0.0015427 | 0.052491 | -0.0024337 | 0.060548 | 0.015795 | -0.00067941 | -0.00059405 | 0.064518 | 0.0094188 | 0.065393 | -66.729 | 0.042614 | -66.659 | 56.1603 | 55.964 | 56.065 | -66.723 | -66.7016 | 0.018674 | -66.7361 | 56.052 | 56.1932 | 56.0498 | -66.8821 | -0.026874 | -0.12177 | -0.032789 | 0.03715 | 0.064024 | -0.31807 | -0.21703 | -0.18593 | -0.23001 | -0.005431 | -0.039936 | 0.14599 | -0.088884 | -0.2322 | 122.8564 | 122.6601 | 122.7612 | 66.7388 | -123.0051 | 122.7482 | 122.8893 | 122.746 | 66.7148 | -123.1641
357.6406 | 123.1384 | -66.7053 | 56.2729 | 0.0031287 | -0.0053248 | 0.0013291 | 0.052705 | -0.0024337 | 0.060761 | 0.00053414 | -0.00046581 | -0.00038025 | 0.064304 | 0.009205 | 0.065393 | -66.7335 | 0.047193 | -66.659 | 56.1603 | 55.964 | 56.065 | -66.7414 | -66.7062 | 0.023253 | -66.7315 | 56.052 | 56.1932 | 56.0498 | -66.8867 | -0.036034 | -0.11262 | -0.028212 | 0.046305 | 0.082339 | -0.30891 | -0.20787 | -0.18135 | -0.22086 | -0.000854 | -0.026202 | 0.15515 | -0.079729 | -0.22304 | 122.8656 | 122.6693 | 122.7703 | 66.7525 | -123.0142 | 122.7574 | 122.8985 | 122.7552 | 66.7286 | -123.1596
358.6406 | 123.1155 | -66.7099 | 56.2546 | -0.019764 | -0.0055384 | 0.0015427 | 0.052491 | -0.0026473 | 0.060761 | 0.00053414 | -0.00046581 | -0.00038025 | 0.06409 | 0.0094188 | 0.065606 | -66.729 | 0.038035 | -66.6544 | 56.1603 | 55.964 | 56.0604 | -66.7139 | -66.7062 | 0.018674 | -66.7315 | 56.052 | 56.1932 | 56.0498 | -66.8867 | -0.003983 | -0.094307 | -0.019056 | 0.055461 | 0.059444 | -0.2906 | -0.19414 | -0.17677 | -0.20255 | 0.003724 | -0.021624 | 0.15515 | -0.061419 | -0.20473 | 122.8702 | 122.6739 | 122.7703 | 66.7479 | -122.9685 | 122.7619 | 122.9031 | 122.7597 | 66.7286 | -123.1413
359.6406 | 123.0972 | -66.7557 | 56.2729 | 0.0031287 | -0.0053248 | 0.0015427 | 0.052278 | -0.0022199 | 0.060334 | 0.0081646 | -0.00025221 | -0.00038025 | 0.064304 | 0.0089914 | 0.06582 | -66.729 | 0.038035 | -66.6544 | 56.1603 | 55.964 | 56.065 | -66.7185 | -66.7108 | 0.03241 | -66.7315 | 56.0566 | 56.1932 | 56.0544 | -66.8821 | 0.037214 | -0.11262 | 0.02672 | 0.10124 | 0.064023 | -0.30891 | -0.20787 | -0.12642 | -0.21628 | 0.044921 | 0.024152 | 0.15057 | -0.079729 | -0.21846 | 122.9159 | 122.7197 | 122.8207 | 66.7937 | -122.9914 | 122.8123 | 122.9488 | 122.8101 | 66.7881 | -123.155
360.6406 | 123.1064 | -66.7648 | 56.25 | -0.0045023 | -0.0055384 | 0.0015427 | 0.052491 | -0.0024337 | 0.060548 | -0.0070964 | -0.00046581 | -0.00038025 | 0.064304 | 0.0096324 | 0.065393 | -66.7335 | 0.033457 | -66.6544 | 56.1557 | 55.9594 | 56.065 | -66.7368 | -66.7062 | 0.023253 | -66.7315 | 56.0612 | 56.1932 | 56.0636 | -66.8821 | 0.028054 | -0.094307 | 0.031298 | 0.11039 | 0.082339 | -0.2906 | -0.18498 | -0.11726 | -0.18881 | 0.058656 | 0.033308 | 0.15057 | -0.056841 | -0.18642 | 122.9205 | 122.7242 | 122.8298 | 66.7983 | -122.9868 | 122.826 | 122.958 | 122.8284 | 66.7881 | -123.1321
361.6406 | 123.0972 | -66.7099 | 56.2775 | -0.012133 | -0.0053248 | 0.0015427 | 0.052278 | -0.0024337 | 0.060334 | 0.00053414 | -0.00046581 | -0.00016665 | 0.06409 | 0.0094188 | 0.065393 | -66.7335 | 0.042614 | -66.6544 | 56.1603 | 55.964 | 56.0696 | -66.7322 | -66.7153 | 0.023253 | -66.7315 | 56.0612 | 56.1932 | 56.0773 | -66.8867 | -0.022299 | -0.11719 | -0.023634 | 0.055461 | 0.07776 | -0.31349 | -0.20787 | -0.17677 | -0.21628 | -0.005434 | -0.021624 | 0.15515 | -0.084307 | -0.20015 | 122.8702 | 122.6739 | 122.7795 | 66.7525 | -123.0097 | 122.7711 | 122.9031 | 122.7872 | 66.7332 | -123.1641
362.6406 | 123.1247 | -66.7145 | 56.2683 | -0.0045023 | -0.0055384 | 0.0015427 | 0.052491 | -0.0026473 | 0.06012 | 0.00053414 | -0.00025221 | -0.00038025 | 0.06409 | 0.0096324 | 0.064966 | -66.7198 | 0.038035 | -66.659 | 56.1557 | 55.9686 | 56.0696 | -66.7093 | -66.7062 | 0.027831 | -66.7224 | 56.0566 | 56.1977 | 56.0544 | -66.8913 | 0.005174 | -0.11262 | -0.005321 | 0.055461 | 0.050287 | -0.29976 | -0.19871 | -0.17677 | -0.2117 | 0.008302 | -0.007889 | 0.16888 | -0.070573 | -0.21389 | 122.8702 | 122.683 | 122.7841 | 66.7525 | -122.9776 | 122.7711 | 122.9122 | 122.7689 | 66.7423 | -123.1596
363.6406 | 123.2071 | -66.6779 | 56.2546 | 0.0031287 | -0.0053248 | 0.0013291 | 0.052705 | -0.0028609 | 0.06012 | 0.00053414 | -0.00067941 | -0.00038025 | 0.064304 | 0.0089914 | 0.065179 | -66.7335 | 0.033457 | -66.659 | 56.1603 | 55.9731 | 56.0604 | -66.7276 | -66.7016 | 0.023253 | -66.7361 | 56.0612 | 56.1932 | 56.0636 | -66.8913 | -0.049764 | -0.094307 | -0.055678 | 0.018839 | 0.068603 | -0.28145 | -0.19414 | -0.2134 | -0.19339 | -0.023742 | -0.058247 | 0.15515 | -0.061419 | -0.191 | 122.8381 | 122.651 | 122.7383 | 66.7113 | -122.9822 | 122.739 | 122.871 | 122.7414 | 66.7011 | -123.1458
364.6406 | 123.2346 | -66.6916 | 56.2225 | 0.01076 | -0.0055384 | 0.0017565 | 0.052491 | -0.0022199 | 0.060334 | -0.0070964 | -0.00046581 | -0.00080765 | 0.064304 | 0.0096324 | 0.064752 | -66.7198 | 0.038035 | -66.6544 | 56.1557 | 55.9686 | 56.0559 | -66.7368 | -66.7062 | 0.018674 | -66.7361 | 56.0612 | 56.1977 | 56.0682 | -66.8821 | -0.045189 | -0.066841 | -0.02821 | 0.03715 | 0.082339 | -0.25398 | -0.16667 | -0.19051 | -0.16134 | -0.014587 | -0.044514 | 0.14599 | -0.024796 | -0.15437 | 122.8473 | 122.6601 | 122.7474 | 66.7296 | -122.9593 | 122.7528 | 122.8893 | 122.7597 | 66.7103 | -123.1046
365.6406 | 123.1338 | -66.6962 | 56.2912 | -0.012133 | -0.0053248 | 0.0017565 | 0.052491 | -0.0024337 | 0.06012 | 0.0081646 | -0.00046581 | -0.00059405 | 0.06409 | 0.009846 | 0.065606 | -66.729 | 0.042614 | -66.6544 | 56.1648 | 55.9686 | 56.0604 | -66.7368 | -66.7016 | 0.023253 | -66.7269 | 56.0566 | 56.1932 | 56.059 | -66.8867 | -0.040611 | -0.12635 | -0.032789 | 0.041728 | 0.082339 | -0.32265 | -0.23076 | -0.19051 | -0.23459 | -0.005431 | -0.030778 | 0.15973 | -0.09804 | -0.2322 | 122.861 | 122.6647 | 122.7566 | 66.7388 | -123.028 | 122.7528 | 122.8893 | 122.7552 | 66.7194 | -123.1779
366.6406 | 123.1567 | -66.7099 | 56.2729 | 0.0031287 | -0.0055384 | 0.0017565 | 0.052491 | -0.0026473 | 0.06012 | 0.00053414 | -0.00067941 | -0.00016665 | 0.063877 | 0.0094188 | 0.065393 | -66.7335 | 0.038035 | -66.659 | 56.1648 | 55.964 | 56.065 | -66.7322 | -66.7062 | 0.018674 | -66.7269 | 56.0566 | 56.1932 | 56.0682 | -66.8867 | -0.022299 | -0.10804 | -0.023634 | 0.050883 | 0.073182 | -0.30891 | -0.20787 | -0.17677 | -0.21628 | 0.003724 | -0.017045 | 0.15973 | -0.079729 | -0.20473 | 122.8747 | 122.6739 | 122.7749 | 66.7479 | -123.0051 | 122.7665 | 122.9031 | 122.7781 | 66.7286 | -123.1596
367.6406 | 123.2025 | -66.6641 | 56.2454 | -0.0045023 | -0.0053248 | 0.0015427 | 0.052919 | -0.0024337 | 0.060334 | 0.0081646 | -0.00046581 | -0.00038025 | 0.06409 | 0.009846 | 0.065393 | -66.7335 | 0.033457 | -66.6544 | 56.1557 | 55.964 | 56.065 | -66.723 | -66.7016 | 0.018674 | -66.7269 | 56.0566 | 56.2023 | 56.0636 | -66.8867 | -0.058917 | -0.089729 | -0.06941 | 0.009685 | 0.068602 | -0.28145 | -0.18041 | -0.22255 | -0.18881 | -0.037474 | -0.062821 | 0.15973 | -0.043105 | -0.18184 | 122.8198 | 122.6281 | 122.7291 | 66.6976 | -122.9685 | 122.7207 | 122.8664 | 122.7277 | 66.6828 | -123.1321
368.6406 | 123.1796 | -66.7007 | 56.2775 | -0.0045023 | -0.005752 | 0.0017565 | 0.052278 | -0.0022199 | 0.06012 | -0.0070964 | -0.00046581 | -0.00038025 | 0.063877 | 0.0094188 | 0.065179 | -66.7381 | 0.033457 | -66.6544 | 56.1648 | 55.9686 | 56.065 | -66.723 | -66.697 | 0.027831 | -66.7315 | 56.0612 | 56.1977 | 56.0636 | -66.8775 | -0.022296 | -0.11262 | -0.037367 | 0.046306 | 0.068602 | -0.30891 | -0.21245 | -0.17677 | -0.21628 | 0.003726 | -0.030779 | 0.14599 | -0.079728 | -0.21388 | 122.8656 | 122.6693 | 122.7658 | 66.7342 | -123.0005 | 122.7619 | 122.8985 | 122.7643 | 66.7286 | -123.155
369.6406 | 123.1476 | -66.7282 | 56.2592 | -0.0045023 | -0.0055384 | 0.0013291 | 0.052278 | -0.0022199 | 0.060334 | -0.0070964 | -0.00046581 | -0.00016665 | 0.06409 | 0.0096324 | 0.064966 | -66.7244 | 0.047193 | -66.6544 | 56.1648 | 55.9686 | 56.065 | -66.7368 | -66.7016 | 0.027831 | -66.7315 | 56.052 | 56.1977 | 56.0453 | -66.8867 | -0.008568 | -0.094306 | 0.003833 | 0.073771 | 0.082339 | -0.2906 | -0.19414 | -0.15846 | -0.20712 | 0.026612 | -0.003314 | 0.15515 | -0.061417 | -0.21389 | 122.8931 | 122.6968 | 122.7932 | 66.7754 | -122.9959 | 122.7802 | 122.9259 | 122.7735 | 66.756 | -123.1458
370.6406 | 123.143 | -66.7145 | 56.3004 | -0.012133 | -0.0055384 | 0.0015427 | 0.052491 | -0.0024337 | 0.060334 | 0.00053414 | -0.00067941 | -0.00038025 | 0.063877 | 0.009205 | 0.065393 | -66.7244 | 0.033457 | -66.6499 | 56.1511 | 55.9686 | 56.0696 | -66.7276 | -66.7016 | 0.023253 | -66.7315 | 56.0566 | 56.1977 | 56.0682 | -66.8821 | -0.013142 | -0.14924 | -0.009899 | 0.064617 | 0.077759 | -0.3318 | -0.23076 | -0.16762 | -0.24374 | 0.01288 | -0.017046 | 0.15057 | -0.10262 | -0.23219 | 122.8656 | 122.683 | 122.7841 | 66.7479 | -123.028 | 122.7711 | 122.9122 | 122.7826 | 66.7377 | -123.1824
371.6406 | 123.1979 | -66.6458 | 56.2363 | 0.01076 | -0.0053248 | 0.0013291 | 0.052491 | -0.0024337 | 0.060334 | 0.0081646 | -0.00046581 | -0.00059405 | 0.063877 | 0.0094188 | 0.065179 | -66.729 | 0.033457 | -66.659 | 56.1511 | 55.9731 | 56.065 | -66.7322 | -66.7016 | 0.023253 | -66.7315 | 56.0612 | 56.1932 | 56.0498 | -66.8867 | -0.086386 | -0.085153 | -0.083143 | -0.013204 | 0.073182 | -0.26313 | -0.17125 | -0.24086 | -0.17508 | -0.055785 | -0.085711 | 0.15515 | -0.043108 | -0.18642 | 122.7969 | 122.6189 | 122.7108 | 66.6793 | -122.9685 | 122.707 | 122.839 | 122.6957 | 66.6691 | -123.1229
372.6406 | 123.143 | -66.6962 | 56.2637 | -0.0045023 | -0.0059658 | 0.0013291 | 0.052278 | -0.0026473 | 0.059907 | 0.00053414 | -0.00025221 | -0.00016665 | 0.06409 | 0.009846 | 0.065179 | -66.7335 | 0.033457 | -66.6544 | 56.1694 | 55.9686 | 56.065 | -66.7368 | -66.7016 | 0.023253 | -66.7269 | 56.0566 | 56.1977 | 56.0682 | -66.8775 | -0.040611 | -0.094305 | -0.037367 | 0.041728 | 0.082339 | -0.29518 | -0.19872 | -0.18135 | -0.20712 | -0.005431 | -0.030778 | 0.15057 | -0.065995 | -0.19557 | 122.8656 | 122.6647 | 122.7612 | 66.7296 | -123.0005 | 122.7528 | 122.8939 | 122.7643 | 66.7194 | -123.1412
373.6406 | 123.2254 | -66.7007 | 56.2408 | 0.01076 | -0.0055384 | 0.0013291 | 0.052491 | -0.0026473 | 0.059907 | 0.0081646 | -0.00025221 | 4.695e-05 | 0.064518 | 0.0096324 | 0.065393 | -66.7381 | 0.033457 | -66.6499 | 56.1603 | 55.964 | 56.065 | -66.723 | -66.7016 | 0.023253 | -66.7315 | 56.0612 | 56.2069 | 56.0727 | -66.8821 | -0.022296 | -0.080574 | -0.037367 | 0.050884 | 0.07318 | -0.27687 | -0.17583 | -0.18135 | -0.17965 | -0.000853 | -0.030779 | 0.15057 | -0.03395 | -0.16811 | 122.861 | 122.6647 | 122.7658 | 66.7342 | -122.9639 | 122.7619 | 122.9076 | 122.7735 | 66.724 | -123.1229
374.6406 | 123.1979 | -66.687 | 56.2088 | -0.0045023 | -0.005752 | 0.0015427 | 0.052278 | -0.0022199 | 0.06012 | -0.0070964 | -0.00025221 | -0.00016665 | 0.064304 | 0.0094188 | 0.065179 | -66.7244 | 0.038035 | -66.6499 | 56.1603 | 55.964 | 56.065 | -66.723 | -66.7016 | 0.023253 | -66.7361 | 56.0566 | 56.1977 | 56.0682 | -66.8821 | -0.036029 | -0.04853 | -0.037365 | 0.037151 | 0.07318 | -0.24483 | -0.14378 | -0.19508 | -0.15219 | -0.014586 | -0.049091 | 0.14599 | -0.011063 | -0.14064 | 122.8473 | 122.651 | 122.752 | 66.725 | -122.9318 | 122.7436 | 122.8847 | 122.7552 | 66.7103 | -123.0909
375.6406 | 123.2025 | -66.6595 | 56.2592 | 0.0031287 | -0.0059658 | 0.0015427 | 0.053132 | -0.0026473 | 0.06012 | -0.0070964 | -0.00046581 | -0.00016665 | 0.06409 | 0.009205 | 0.065179 | -66.7244 | 0.042614 | -66.659 | 56.1557 | 55.964 | 56.0604 | -66.7276 | -66.697 | 0.018674 | -66.7361 | 56.0566 | 56.1977 | 56.0773 | -66.8867 | -0.068074 | -0.10346 | -0.064831 | 0.000529 | 0.068603 | -0.29518 | -0.19872 | -0.22713 | -0.20254 | -0.037473 | -0.076557 | 0.15057 | -0.061417 | -0.18184 | 122.8152 | 122.6235 | 122.72 | 66.7022 | -122.9868 | 122.7162 | 122.8573 | 122.7369 | 66.6782 | -123.1458
376.6406 | 123.1247 | -66.7099 | 56.2958 | 0.0031287 | -0.0053248 | 0.00090168 | 0.052491 | -0.0028609 | 0.060548 | 0.00053414 | -0.00089301 | -0.00038025 | 0.064304 | 0.0096324 | 0.065179 | -66.7244 | 0.038035 | -66.659 | 56.1603 | 55.9777 | 56.0696 | -66.7368 | -66.697 | 0.018674 | -66.7269 | 56.0658 | 56.2023 | 56.0727 | -66.8821 | -0.026878 | -0.1355 | -0.014477 | 0.050883 | 0.077761 | -0.31806 | -0.22618 | -0.17219 | -0.23001 | 0.012881 | -0.017045 | 0.15515 | -0.093459 | -0.22304 | 122.8702 | 122.6876 | 122.7795 | 66.7479 | -123.0326 | 122.7757 | 122.9122 | 122.7826 | 66.7286 | -123.1779
377.6406 | 123.2071 | -66.6962 | 56.25 | 0.01076 | -0.005752 | 0.0013291 | 0.052705 | -0.0024337 | 0.060334 | 0.0081646 | -0.00025221 | -0.00016665 | 0.06409 | 0.009846 | 0.065393 | -66.7244 | 0.033457 | -66.6453 | 56.1648 | 55.9731 | 56.0696 | -66.7322 | -66.7062 | 0.023253 | -66.7315 | 56.0566 | 56.2069 | 56.0682 | -66.8821 | -0.036032 | -0.085151 | -0.02821 | 0.050884 | 0.086916 | -0.27687 | -0.1804 | -0.18593 | -0.19339 | -0.010009 | -0.035357 | 0.15057 | -0.043105 | -0.18184 | 122.861 | 122.6693 | 122.7658 | 66.7296 | -122.9822 | 122.7528 | 122.9031 | 122.7643 | 66.7194 | -123.1321
378.6406 | 123.2529 | -66.655 | 56.2454 | -0.0045023 | -0.005752 | 0.0013291 | 0.052278 | -0.0028609 | 0.06012 | -0.0070964 | -0.00046581 | -0.00038025 | 0.064304 | 0.0096324 | 0.065179 | -66.729 | 0.033457 | -66.6499 | 56.1511 | 55.9777 | 56.0604 | -66.7276 | -66.697 | 0.018674 | -66.7269 | 56.0566 | 56.2161 | 56.0682 | -66.8821 | -0.072652 | -0.094308 | -0.073988 | 0.005107 | 0.077759 | -0.26771 | -0.18498 | -0.22713 | -0.18881 | -0.042051 | -0.071977 | 0.15515 | -0.02937 | -0.17726 | 122.8061 | 122.6327 | 122.7154 | 66.6884 | -122.973 | 122.7116 | 122.871 | 122.7231 | 66.6736 | -123.1275
379.6406 | 123.1796 | -66.7648 | 56.2775 | -0.012133 | -0.005752 | 0.0015427 | 0.052491 | -0.0022199 | 0.06012 | 0.0081646 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.009846 | 0.065179 | -66.7244 | 0.038035 | -66.659 | 56.1648 | 55.964 | 56.065 | -66.7368 | -66.7016 | 0.018674 | -66.7269 | 56.0566 | 56.2115 | 56.0727 | -66.8775 | 0.028054 | -0.11262 | 0.040455 | 0.10581 | 0.077761 | -0.31349 | -0.21245 | -0.11268 | -0.22085 | 0.063234 | 0.037887 | 0.15057 | -0.065992 | -0.20473 | 122.9297 | 122.7288 | 122.8298 | 66.8029 | -123.0142 | 122.8214 | 122.9763 | 122.8376 | 66.7835 | -123.155
380.6406 | 123.1476 | -66.6412 | 56.25 | 0.0031287 | -0.0059658 | 0.0017565 | 0.052491 | -0.0028609 | 0.059907 | 0.00053414 | -0.00046581 | -0.00038025 | 0.064304 | 0.009846 | 0.064966 | -66.7335 | 0.038035 | -66.6544 | 56.1603 | 55.9686 | 56.0696 | -66.7322 | -66.6924 | 0.023253 | -66.7315 | 56.0612 | 56.2069 | 56.0682 | -66.8867 | -0.090964 | -0.089729 | -0.092299 | -0.013204 | 0.07776 | -0.28145 | -0.1804 | -0.24544 | -0.18881 | -0.051205 | -0.090289 | 0.15515 | -0.043105 | -0.18184 | 122.8015 | 122.6098 | 122.7108 | 66.6793 | -122.9822 | 122.7024 | 122.8481 | 122.7094 | 66.6645 | -123.1367
381.6406 | 123.1705 | -66.6687 | 56.2637 | 0.0031287 | -0.005752 | 0.0015427 | 0.052278 | -0.0024337 | 0.06012 | 0.00053414 | -0.00046581 | 4.695e-05 | 0.064304 | 0.0094188 | 0.064966 | -66.7244 | 0.038035 | -66.6499 | 56.1557 | 55.9686 | 56.0696 | -66.7368 | -66.6924 | 0.023253 | -66.7269 | 56.0566 | 56.2069 | 56.0544 | -66.8867 | -0.068077 | -0.10804 | -0.055676 | 0.01884 | 0.086917 | -0.29518 | -0.19414 | -0.21797 | -0.20712 | -0.023739 | -0.058244 | 0.15973 | -0.056838 | -0.20931 | 122.8244 | 122.6373 | 122.7383 | 66.7067 | -123.0005 | 122.7253 | 122.8756 | 122.7231 | 66.692 | -123.1504
382.6406 | 123.2529 | -66.6779 | 56.25 | 0.0031287 | -0.0055384 | 0.0013291 | 0.052705 | -0.0026473 | 0.059907 | 0.00053414 | -0.00025221 | -0.00016665 | 0.063877 | 0.0096324 | 0.065606 | -66.7244 | 0.033457 | -66.6499 | 56.1603 | 55.9686 | 56.0696 | -66.723 | -66.697 | 0.023253 | -66.7315 | 56.0566 | 56.2115 | 56.0819 | -66.8867 | -0.045185 | -0.089729 | -0.046521 | 0.027995 | 0.07318 | -0.28145 | -0.1804 | -0.20882 | -0.19339 | -0.019163 | -0.053668 | 0.15515 | -0.038526 | -0.1681 | 122.8381 | 122.6464 | 122.7475 | 66.7113 | -122.973 | 122.7345 | 122.8893 | 122.7598 | 66.7011 | -123.1367
383.6406 | 123.1613 | -66.6779 | 56.2317 | -0.0045023 | -0.005752 | 0.0013291 | 0.052705 | -0.0026473 | 0.06012 | 0.0081646 | -0.00025221 | -0.00038025 | 0.064518 | 0.009846 | 0.065179 | -66.729 | 0.033457 | -66.6544 | 56.1511 | 55.964 | 56.0742 | -66.7368 | -66.6924 | 0.014095 | -66.7178 | 56.0566 | 56.2069 | 56.0682 | -66.8867 | -0.058922 | -0.080575 | -0.0511 | 0.023417 | 0.082339 | -0.26771 | -0.15752 | -0.20882 | -0.17508 | -0.014584 | -0.039932 | 0.16889 | -0.024794 | -0.16353 | 122.829 | 122.6418 | 122.752 | 66.7113 | -122.9685 | 122.7345 | 122.8848 | 122.746 | 66.692 | -123.1184
384.6562 | 123.1201 | -66.7053 | 56.282 | -0.0045023 | -0.005752 | 0.0013291 | 0.052278 | -0.0028609 | 0.060334 | -0.014727 | -0.00025221 | -0.00038025 | 0.06409 | 0.009846 | 0.064966 | -66.729 | 0.033457 | -66.6544 | 56.1603 | 55.9731 | 56.0742 | -66.7322 | -66.7016 | 0.023253 | -66.7269 | 56.0612 | 56.2023 | 56.059 | -66.8821 | -0.026877 | -0.12177 | -0.023634 | 0.050883 | 0.07776 | -0.30891 | -0.20787 | -0.17677 | -0.22085 | 0.003724 | -0.021623 | 0.15515 | -0.079726 | -0.22304 | 122.8656 | 122.6785 | 122.7795 | 66.7388 | -123.0142 | 122.7665 | 122.9076 | 122.7643 | 66.7286 | -123.1641
385.6406 | 123.23 | -66.6824 | 56.2271 | -0.0045023 | -0.0061794 | 0.0013291 | 0.052491 | -0.0024337 | 0.060334 | 0.0081646 | -3.8406e-05 | -0.00038025 | 0.06409 | 0.0096324 | 0.065179 | -66.7244 | 0.033457 | -66.6544 | 56.1557 | 55.9731 | 56.0696 | -66.7185 | -66.6924 | 0.018674 | -66.7224 | 56.0566 | 56.2069 | 56.0682 | -66.8821 | -0.036028 | -0.071419 | -0.041943 | 0.027995 | 0.064023 | -0.25398 | -0.15752 | -0.19966 | -0.1705 | -0.010006 | -0.039933 | 0.15973 | -0.020217 | -0.15895 | 122.8381 | 122.6556 | 122.752 | 66.7159 | -122.9456 | 122.739 | 122.8893 | 122.7506 | 66.7011 | -123.1092
386.6406 | 123.2483 | -66.6641 | 56.218 | 0.01076 | -0.0059658 | 0.0017565 | 0.052705 | -0.0024337 | 0.060334 | -0.0070964 | -0.00089301 | -0.00038025 | 0.06409 | 0.0094188 | 0.065179 | -66.729 | 0.033457 | -66.6453 | 56.1694 | 55.9731 | 56.0742 | -66.7276 | -66.697 | 0.023253 | -66.7269 | 56.0658 | 56.2069 | 56.059 | -66.8821 | -0.063496 | -0.048529 | -0.064832 | 0.018841 | 0.082337 | -0.24482 | -0.14378 | -0.21797 | -0.15219 | -0.032895 | -0.062821 | 0.15515 | -0.011062 | -0.15895 | 122.8336 | 122.6373 | 122.7383 | 66.6976 | -122.9456 | 122.7299 | 122.871 | 122.7231 | 66.6874 | -123.1001
387.6406 | 123.1613 | -66.6733 | 56.25 | -0.0045023 | -0.005752 | 0.0015427 | 0.052705 | -0.0024337 | 0.06012 | -0.0070964 | -0.00046581 | -0.00038025 | 0.06409 | 0.0096324 | 0.064966 | -66.7152 | 0.038035 | -66.6544 | 56.1694 | 55.9777 | 56.0742 | -66.723 | -66.697 | 0.018674 | -66.7269 | 56.0658 | 56.2069 | 56.059 | -66.8867 | -0.049762 | -0.080572 | -0.041941 | 0.01884 | 0.068602 | -0.27229 | -0.17583 | -0.21339 | -0.18423 | -0.02374 | -0.053666 | 0.15973 | -0.043105 | -0.191 | 122.8427 | 122.651 | 122.7475 | 66.7113 | -122.973 | 122.739 | 122.8802 | 122.7323 | 66.692 | -123.1367
388.6406 | 123.1567 | -66.6687 | 56.2637 | 0.0031287 | -0.005752 | 0.0013291 | 0.052919 | -0.0024337 | 0.059693 | 0.00053414 | -0.00046581 | -0.00016665 | 0.06409 | 0.0094188 | 0.065393 | -66.729 | 0.033457 | -66.6499 | 56.1648 | 55.9823 | 56.0696 | -66.7276 | -66.6833 | 0.018674 | -66.7269 | 56.0566 | 56.2115 | 56.0773 | -66.8775 | -0.058919 | -0.098884 | -0.060255 | 0.01884 | 0.077759 | -0.28144 | -0.19414 | -0.20881 | -0.20712 | -0.014582 | -0.058244 | 0.15057 | -0.052259 | -0.18642 | 122.8336 | 122.651 | 122.7383 | 66.7022 | -122.9914 | 122.7253 | 122.8802 | 122.746 | 66.6874 | -123.1412
389.6406 | 123.1659 | -66.6779 | 56.3004 | -0.0045023 | -0.0061794 | 0.0017565 | 0.052278 | -0.0026473 | 0.06012 | -0.0070964 | -0.00046581 | -0.00038025 | 0.064304 | 0.0094188 | 0.065179 | -66.7244 | 0.038035 | -66.6499 | 56.174 | 55.9777 | 56.0833 | -66.7276 | -66.6924 | 0.03241 | -66.7224 | 56.0658 | 56.2069 | 56.0727 | -66.8729 | -0.049764 | -0.12635 | -0.046521 | 0.027995 | 0.077759 | -0.32264 | -0.21702 | -0.19508 | -0.23458 | -0.014584 | -0.044511 | 0.15057 | -0.093459 | -0.22762 | 122.8519 | 122.6556 | 122.7612 | 66.7159 | -123.028 | 122.7436 | 122.8848 | 122.7506 | 66.7103 | -123.1733
390.6406 | 123.2483 | -66.6733 | 56.2454 | -0.012133 | -0.005752 | 0.0017565 | 0.052705 | -0.0024337 | 0.060334 | 0.0081646 | -0.00067941 | -0.00038025 | 0.06409 | 0.0096324 | 0.065179 | -66.7106 | 0.033457 | -66.6453 | 56.1694 | 55.9731 | 56.0742 | -66.7322 | -66.6879 | 0.018674 | -66.7178 | 56.0612 | 56.2023 | 56.0544 | -66.8729 | -0.05892 | -0.075994 | -0.037363 | 0.027996 | 0.086916 | -0.27229 | -0.17125 | -0.19966 | -0.18423 | -0.014582 | -0.044509 | 0.15515 | -0.043105 | -0.191 | 122.8427 | 122.6464 | 122.7475 | 66.7067 | -122.9776 | 122.7345 | 122.8756 | 122.7277 | 66.692 | -123.1184
391.6406 | 123.2162 | -66.687 | 56.2546 | -0.0045023 | -0.005752 | 0.0015427 | 0.052705 | -0.0026473 | 0.060334 | 0.0081646 | -0.00025221 | -0.00016665 | 0.06409 | 0.010273 | 0.064752 | -66.7152 | 0.0243 | -66.6499 | 56.1694 | 55.9823 | 56.0788 | -66.7047 | -66.6924 | 0.023253 | -66.7269 | 56.0658 | 56.2023 | 56.0727 | -66.8775 | -0.017713 | -0.08515 | -0.028208 | 0.037151 | 0.054864 | -0.27229 | -0.17583 | -0.1905 | -0.18881 | -0.005428 | -0.039933 | 0.15057 | -0.052261 | -0.18184 | 122.8564 | 122.6693 | 122.7658 | 66.7113 | -122.9593 | 122.7528 | 122.8893 | 122.7597 | 66.7103 | -123.1321
392.6406 | 123.2483 | -66.6595 | 56.2454 | 0.0031287 | -0.005752 | 0.0013291 | 0.052705 | -0.0024337 | 0.060334 | 0.0081646 | -0.00067941 | -0.00016665 | 0.063877 | 0.009846 | 0.065393 | -66.7106 | 0.033457 | -66.6407 | 56.1648 | 55.9823 | 56.0833 | -66.7185 | -66.697 | 0.027831 | -66.7269 | 56.0612 | 56.2023 | 56.0682 | -66.8821 | -0.058916 | -0.080573 | -0.051096 | 0.018842 | 0.077758 | -0.26313 | -0.16209 | -0.22255 | -0.18423 | -0.037473 | -0.067399 | 0.15515 | -0.043105 | -0.17726 | 122.8244 | 122.6418 | 122.7429 | 66.693 | -122.9639 | 122.7207 | 122.8619 | 122.7277 | 66.6874 | -123.1275
393.6406 | 123.2071 | -66.6824 | 56.2271 | -0.019764 | -0.0059658 | 0.0015427 | 0.052491 | -0.0024337 | 0.06012 | -0.0070964 | -0.00025221 | -0.00059405 | 0.064304 | 0.0096324 | 0.065179 | -66.7152 | 0.028878 | -66.6407 | 56.1557 | 55.9777 | 56.0742 | -66.7139 | -66.6833 | 0.023253 | -66.7224 | 56.0658 | 56.2069 | 56.0636 | -66.8775 | -0.031449 | -0.071419 | -0.032786 | 0.04173 | 0.073179 | -0.2494 | -0.15294 | -0.19508 | -0.16134 | -0.000849 | -0.039933 | 0.15515 | -0.020217 | -0.16353 | 122.8381 | 122.6601 | 122.7566 | 66.7113 | -122.941 | 122.7482 | 122.8893 | 122.746 | 66.7057 | -123.1046
394.6406 | 123.2254 | -66.6595 | 56.2912 | -0.012133 | -0.0059658 | 0.0017565 | 0.052064 | -0.0022199 | 0.060548 | 0.00053414 | -0.00025221 | -0.00016665 | 0.063877 | 0.0096324 | 0.064966 | -66.7152 | 0.033457 | -66.6499 | 56.1694 | 55.9823 | 56.0833 | -66.723 | -66.6924 | 0.018674 | -66.7269 | 56.0612 | 56.2115 | 56.0727 | -66.8867 | -0.063495 | -0.12177 | -0.055674 | 0.009685 | 0.07318 | -0.30891 | -0.20787 | -0.22713 | -0.23001 | -0.032894 | -0.067399 | 0.15973 | -0.079725 | -0.21846 | 122.829 | 122.6418 | 122.7429 | 66.693 | -123.0142 | 122.7207 | 122.871 | 122.7323 | 66.6782 | -123.1779
395.6406 | 123.1888 | -66.687 | 56.2592 | 0.0031287 | -0.0059658 | 0.0013291 | 0.052491 | -0.0024337 | 0.060334 | 0.00053414 | -0.00025221 | -0.00016665 | 0.06409 | 0.01006 | 0.064966 | -66.7106 | 0.0243 | -66.6407 | 56.174 | 55.9777 | 56.0742 | -66.7093 | -66.6924 | 0.027831 | -66.7178 | 56.0703 | 56.2206 | 56.0773 | -66.8775 | -0.022292 | -0.085149 | -0.02363 | 0.046308 | 0.0686 | -0.28144 | -0.18498 | -0.1905 | -0.18881 | -0.005428 | -0.030776 | 0.15973 | -0.038524 | -0.18184 | 122.861 | 122.6647 | 122.7612 | 66.7113 | -122.9685 | 122.7574 | 122.9076 | 122.7643 | 66.7148 | -123.1367
396.6406 | 123.262 | -66.655 | 56.2592 | -0.0045023 | -0.0059658 | 0.0015427 | 0.053132 | -0.0028609 | 0.060548 | 0.0081646 | -0.00067941 | 4.695e-05 | 0.064304 | 0.009846 | 0.064966 | -66.7198 | 0.028878 | -66.6361 | 56.1648 | 55.9869 | 56.0742 | -66.723 | -66.6833 | 0.014095 | -66.7178 | 56.0795 | 56.2206 | 56.0636 | -66.8775 | -0.068073 | -0.094306 | -0.064831 | 0.018842 | 0.086915 | -0.27229 | -0.18498 | -0.22255 | -0.17965 | -0.028315 | -0.06282 | 0.15973 | -0.038524 | -0.19557 | 122.8198 | 122.6418 | 122.7291 | 66.6838 | -122.9822 | 122.7345 | 122.8756 | 122.7185 | 66.6691 | -123.1367
397.6406 | 123.2529 | -66.6687 | 56.2454 | 0.0031287 | -0.0059658 | 0.0017565 | 0.052064 | -0.0026473 | 0.06012 | 0.00053414 | -0.00046581 | -0.00016665 | 0.064304 | 0.0096324 | 0.065393 | -66.7106 | 0.028878 | -66.6407 | 56.174 | 55.9869 | 56.0833 | -66.7139 | -66.6787 | 0.03241 | -66.7224 | 56.0658 | 56.2206 | 56.0773 | -66.8729 | -0.045182 | -0.071416 | -0.041941 | 0.027997 | 0.073179 | -0.25855 | -0.16209 | -0.20423 | -0.17965 | -0.010003 | -0.053666 | 0.15057 | -0.024791 | -0.1681 | 122.8427 | 122.6556 | 122.752 | 66.6976 | -122.9593 | 122.7345 | 122.8893 | 122.746 | 66.7011 | -123.1184
398.6406 | 123.2025 | -66.6779 | 56.2683 | 0.01076 | -0.005752 | 0.0011155 | 0.052278 | -0.0024337 | 0.060334 | -0.0070964 | -0.00025221 | 4.695e-05 | 0.064518 | 0.009846 | 0.064966 | -66.7106 | 0.028878 | -66.6407 | 56.1786 | 55.9777 | 56.0788 | -66.7047 | -66.6833 | 0.023253 | -66.7269 | 56.0703 | 56.2206 | 56.0819 | -66.8821 | -0.026869 | -0.089727 | -0.032786 | 0.037152 | 0.064021 | -0.2906 | -0.18956 | -0.20424 | -0.19796 | -0.005427 | -0.049089 | 0.15515 | -0.04768 | -0.18641 | 122.8564 | 122.6556 | 122.7566 | 66.7067 | -122.973 | 122.7482 | 122.8985 | 122.7598 | 66.7011 | -123.1504
399.6406 | 123.2117 | -66.6687 | 56.2729 | 0.0031287 | -0.0061794 | 0.0015427 | 0.052491 | -0.0024337 | 0.059907 | 0.00053414 | -0.00046581 | -0.00016665 | 0.06409 | 0.01006 | 0.065606 | -66.7061 | 0.028878 | -66.6407 | 56.174 | 55.9869 | 56.0879 | -66.7185 | -66.6833 | 0.023253 | -66.7178 | 56.0703 | 56.2161 | 56.0727 | -66.8775 | -0.049761 | -0.098882 | -0.037363 | 0.027997 | 0.077758 | -0.28602 | -0.18498 | -0.20881 | -0.20254 | -0.014582 | -0.049087 | 0.15973 | -0.056836 | -0.20015 | 122.8427 | 122.6556 | 122.7566 | 66.6976 | -122.9914 | 122.739 | 122.8848 | 122.7414 | 66.692 | -123.1504
400.6406 | 123.2437 | -66.6412 | 56.2729 | 0.01076 | -0.0059658 | 0.0013291 | 0.053132 | -0.0022199 | 0.059907 | 0.0081646 | -0.00025221 | -0.00059405 | 0.063877 | 0.01006 | 0.065179 | -66.7106 | 0.0243 | -66.6361 | 56.1648 | 55.9823 | 56.0879 | -66.7185 | -66.6879 | 0.027831 | -66.7178 | 56.0612 | 56.2161 | 56.0682 | -66.8684 | -0.077227 | -0.10804 | -0.069407 | 0.005109 | 0.082336 | -0.2906 | -0.18498 | -0.22712 | -0.2117 | -0.046626 | -0.076553 | 0.15057 | -0.056836 | -0.20473 | 122.8061 | 122.6235 | 122.7291 | 66.6655 | -122.9914 | 122.7024 | 122.8573 | 122.7094 | 66.6691 | -123.1412
401.6406 | 123.23 | -66.6595 | 56.2592 | -0.019764 | -0.0061794 | 0.0017565 | 0.052491 | -0.0022199 | 0.06012 | -0.0070964 | -0.00046581 | -0.00038025 | 0.063877 | 0.01006 | 0.065179 | -66.7015 | 0.0243 | -66.6361 | 56.174 | 55.9869 | 56.0833 | -66.723 | -66.6833 | 0.018674 | -66.7178 | 56.0795 | 56.2252 | 56.0773 | -66.8592 | -0.063495 | -0.085149 | -0.041939 | 0.02342 | 0.086915 | -0.27229 | -0.17582 | -0.19965 | -0.17965 | -0.023737 | -0.058242 | 0.14141 | -0.033945 | -0.18184 | 122.8336 | 122.6464 | 122.7429 | 66.6838 | -122.9822 | 122.7391 | 122.8848 | 122.7369 | 66.6782 | -123.1184
402.6406 | 123.1934 | -66.6641 | 56.2637 | 0.01076 | -0.0055384 | 0.0017565 | 0.052491 | -0.0026473 | 0.06012 | 0.015795 | -0.00025221 | -0.00038025 | 0.06409 | 0.009846 | 0.065179 | -66.7061 | 0.033457 | -66.6315 | 56.174 | 55.9914 | 56.0879 | -66.7185 | -66.6741 | 0.023253 | -66.6995 | 56.0703 | 56.2206 | 56.0819 | -66.8775 | -0.054338 | -0.089727 | -0.04194 | 0.032576 | 0.086914 | -0.27229 | -0.17582 | -0.21339 | -0.19339 | -0.010001 | -0.035349 | 0.17804 | -0.043102 | -0.18184 | 122.8381 | 122.6556 | 122.752 | 66.6976 | -122.9822 | 122.7345 | 122.8848 | 122.746 | 66.6874 | -123.1412
403.6406 | 123.1979 | -66.6733 | 56.2729 | 0.0031287 | -0.0059658 | 0.0017565 | 0.052705 | -0.0026473 | 0.06012 | 0.00053414 | -3.8406e-05 | 4.695e-05 | 0.063877 | 0.0096324 | 0.065393 | -66.6969 | 0.033457 | -66.6361 | 56.174 | 55.9914 | 56.0833 | -66.7139 | -66.6833 | 0.023253 | -66.7086 | 56.0749 | 56.2161 | 56.0819 | -66.8638 | -0.040604 | -0.098882 | -0.023628 | 0.037153 | 0.077757 | -0.28144 | -0.18956 | -0.1905 | -0.19796 | -0.010004 | -0.035351 | 0.15515 | -0.056836 | -0.19099 | 122.8473 | 122.6647 | 122.7566 | 66.7067 | -122.9868 | 122.7482 | 122.8893 | 122.7552 | 66.6965 | -123.1367
404.6406 | 123.2437 | -66.6412 | 56.2546 | 0.0031287 | -0.0059658 | 0.0015427 | 0.052705 | -0.0026473 | 0.059907 | 0.0081646 | -0.00025221 | -0.00016665 | 0.063877 | 0.0096324 | 0.065179 | -66.7015 | 0.028878 | -66.6315 | 56.1786 | 55.9823 | 56.0833 | -66.7047 | -66.6787 | 0.023253 | -66.7086 | 56.0749 | 56.2252 | 56.0911 | -66.8729 | -0.06349 | -0.075994 | -0.06025 | 0.009687 | 0.073177 | -0.27229 | -0.17125 | -0.2317 | -0.17965 | -0.037469 | -0.067395 | 0.16431 | -0.029368 | -0.16352 | 122.8198 | 122.6235 | 122.7246 | 66.6701 | -122.9593 | 122.7162 | 122.8664 | 122.7323 | 66.6645 | -123.1275
405.6406 | 123.262 | -66.6916 | 56.2363 | -0.0045023 | -0.0059658 | 0.0011155 | 0.052491 | -0.0026473 | 0.060334 | 0.0081646 | -0.00046581 | -0.00038025 | 0.06409 | 0.01006 | 0.064966 | -66.6969 | 0.019721 | -66.6361 | 56.1786 | 55.9914 | 56.0833 | -66.7093 | -66.6833 | 0.018674 | -66.7041 | 56.0795 | 56.2206 | 56.0773 | -66.8638 | -0.017715 | -0.057683 | -0.005318 | 0.055463 | 0.073178 | -0.24482 | -0.15293 | -0.17219 | -0.15676 | 0.008306 | -0.012463 | 0.15973 | -0.015636 | -0.15895 | 122.8702 | 122.683 | 122.7749 | 66.7113 | -122.9456 | 122.7711 | 122.9122 | 122.7689 | 66.7103 | -123.1
406.6406 | 123.1796 | -66.6779 | 56.2683 | -0.012133 | -0.0059658 | 0.0015427 | 0.052705 | -0.0024337 | 0.059693 | 0.00053414 | -0.00046581 | -0.00059405 | 0.064304 | 0.01006 | 0.065179 | -66.6923 | 0.0243 | -66.6315 | 56.1877 | 55.9914 | 56.0879 | -66.7001 | -66.6741 | 0.014095 | -66.7041 | 56.0841 | 56.2252 | 56.0773 | -66.8638 | -0.02229 | -0.08057 | -0.014472 | 0.046308 | 0.068598 | -0.27686 | -0.1804 | -0.18592 | -0.18423 | 0.003731 | -0.026196 | 0.15973 | -0.043101 | -0.19099 | 122.8656 | 122.6693 | 122.7658 | 66.7022 | -122.9685 | 122.7619 | 122.9031 | 122.7552 | 66.692 | -123.1321
407.6406 | 123.2208 | -66.6641 | 56.25 | -0.012133 | -0.0059658 | 0.0015427 | 0.052919 | -0.0022199 | 0.060334 | 0.00053414 | -0.00046581 | -0.00059405 | 0.064304 | 0.01006 | 0.065179 | -66.7015 | 0.0243 | -66.627 | 56.1923 | 55.9914 | 56.1016 | -66.7047 | -66.6741 | 0.014095 | -66.7132 | 56.0795 | 56.2252 | 56.0911 | -66.8684 | -0.040601 | -0.05768 | -0.037361 | 0.037154 | 0.077755 | -0.25855 | -0.14835 | -0.20423 | -0.1705 | -0.010001 | -0.049085 | 0.15515 | -0.02479 | -0.15895 | 122.8564 | 122.6556 | 122.7658 | 66.6884 | -122.9547 | 122.7436 | 122.8893 | 122.7552 | 66.6782 | -123.1184
408.6406 | 123.2162 | -66.6733 | 56.2637 | -0.0045023 | -0.0059658 | 0.0015427 | 0.052705 | -0.0024337 | 0.060334 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.0096324 | 0.065393 | -66.6923 | 0.015142 | -66.6315 | 56.174 | 56.0006 | 56.0925 | -66.6956 | -66.6741 | 0.018674 | -66.7086 | 56.0795 | 56.2298 | 56.0865 | -66.8684 | -0.022288 | -0.089727 | -0.019049 | 0.041731 | 0.064019 | -0.26313 | -0.17124 | -0.19508 | -0.18423 | -0.000846 | -0.035351 | 0.15973 | -0.033945 | -0.17726 | 122.8473 | 122.6739 | 122.7658 | 66.6884 | -122.9593 | 122.7528 | 122.9031 | 122.7598 | 66.692 | -123.1321
409.6406 | 123.2208 | -66.6321 | 56.2637 | -0.0045023 | -0.0061794 | 0.0015427 | 0.052705 | -0.0022199 | 0.060334 | 0.00053414 | -0.00046581 | -0.00038025 | 0.06409 | 0.009846 | 0.065393 | -66.6923 | 0.015142 | -66.6315 | 56.1832 | 55.996 | 56.0879 | -66.6956 | -66.6741 | 0.023253 | -66.6995 | 56.0795 | 56.2389 | 56.0911 | -66.8638 | -0.063487 | -0.08057 | -0.060248 | 0.000532 | 0.064019 | -0.26771 | -0.17582 | -0.2317 | -0.18423 | -0.042045 | -0.067393 | 0.16431 | -0.024788 | -0.17268 | 122.8152 | 122.6281 | 122.72 | 66.6472 | -122.9593 | 122.7116 | 122.871 | 122.7231 | 66.6553 | -123.1275
410.6406 | 123.1934 | -66.6504 | 56.2546 | 0.01076 | -0.0059658 | 0.0015427 | 0.052705 | -0.0026473 | 0.059907 | 0.00053414 | -0.00046581 | -0.00038025 | 0.06409 | 0.009846 | 0.065393 | -66.6877 | 0.015142 | -66.6178 | 56.1877 | 56.0006 | 56.0971 | -66.7001 | -66.6695 | 0.018674 | -66.6949 | 56.0841 | 56.2344 | 56.0773 | -66.8592 | -0.049755 | -0.066837 | -0.037359 | 0.032578 | 0.082333 | -0.25397 | -0.15751 | -0.20881 | -0.1705 | -0.019156 | -0.044503 | 0.16431 | -0.020211 | -0.17726 | 122.8381 | 122.651 | 122.7475 | 66.6655 | -122.9547 | 122.7345 | 122.8848 | 122.7277 | 66.6691 | -123.1138
411.6406 | 123.2208 | -66.6367 | 56.2637 | 0.0031287 | -0.0059658 | 0.0013291 | 0.052919 | -0.0024337 | 0.06012 | -0.0070964 | -0.00067941 | -0.00038025 | 0.06409 | 0.01006 | 0.064966 | -66.6877 | 0.0243 | -66.6178 | 56.1877 | 55.9914 | 56.1016 | -66.6956 | -66.6604 | 0.014095 | -66.7041 | 56.0932 | 56.2298 | 56.0911 | -66.8592 | -0.058909 | -0.075992 | -0.051092 | 0.018845 | 0.077754 | -0.27229 | -0.16209 | -0.22254 | -0.17049 | -0.023731 | -0.067394 | 0.15515 | -0.033945 | -0.17268 | 122.8244 | 122.6281 | 122.7383 | 66.661 | -122.9593 | 122.7299 | 122.8664 | 122.7277 | 66.6508 | -123.1229
412.6406 | 123.1888 | -66.6504 | 56.2912 | -0.012133 | -0.0061794 | 0.0015427 | 0.052705 | -0.0026473 | 0.06012 | 0.00053414 | -0.00046581 | -0.00016665 | 0.06409 | 0.01006 | 0.064966 | -66.6786 | 0.019721 | -66.6178 | 56.1923 | 55.9914 | 56.1062 | -66.691 | -66.6558 | 0.018674 | -66.6949 | 56.0887 | 56.2206 | 56.1002 | -66.8546 | -0.040597 | -0.098879 | -0.028202 | 0.032578 | 0.073175 | -0.29975 | -0.18497 | -0.20423 | -0.20254 | -0.005419 | -0.044503 | 0.15973 | -0.070568 | -0.19099 | 122.8427 | 122.6418 | 122.7566 | 66.6701 | -122.9822 | 122.7391 | 122.871 | 122.7506 | 66.6691 | -123.1458
413.6406 | 123.2391 | -66.6183 | 56.2408 | -0.0045023 | -0.0059658 | 0.0017565 | 0.052278 | -0.0022199 | 0.06012 | 0.00053414 | -0.00025221 | -0.00038025 | 0.063877 | 0.01006 | 0.064966 | -66.6832 | 0.019721 | -66.6132 | 56.1923 | 56.0098 | 56.1016 | -66.6956 | -66.6604 | 0.014095 | -66.6857 | 56.0887 | 56.2344 | 56.0956 | -66.8684 | -0.07722 | -0.048525 | -0.064825 | 0.005112 | 0.082332 | -0.23108 | -0.1392 | -0.25001 | -0.15218 | -0.042042 | -0.06739 | 0.18262 | -0.006478 | -0.14521 | 122.8107 | 122.6281 | 122.72 | 66.6381 | -122.9364 | 122.707 | 122.8527 | 122.714 | 66.6324 | -123.1092
414.6406 | 123.1979 | -66.6733 | 56.2866 | 0.0031287 | -0.0059658 | 0.0015427 | 0.052278 | -0.0028609 | 0.059907 | -0.0070964 | -0.00067941 | -0.00016665 | 0.06409 | 0.01006 | 0.065179 | -66.6786 | 0.019721 | -66.6178 | 56.1969 | 56.0052 | 56.1062 | -66.7001 | -66.6695 | 0.014095 | -66.6995 | 56.0932 | 56.2344 | 56.1002 | -66.85 | -0.026867 | -0.089723 | -0.005314 | 0.055466 | 0.082333 | -0.28144 | -0.1804 | -0.17676 | -0.19338 | 0.003732 | -0.026194 | 0.15057 | -0.052254 | -0.18641 | 122.8702 | 122.6785 | 122.7795 | 66.693 | -122.9868 | 122.7665 | 122.9076 | 122.7735 | 66.6874 | -123.1367
415.6406 | 123.23 | -66.6595 | 56.2454 | -0.012133 | -0.005752 | 0.0015427 | 0.052064 | -0.0024337 | 0.060334 | -0.0070964 | -0.00046581 | -0.00016665 | 0.063877 | 0.009846 | 0.065179 | -66.6694 | 0.015142 | -66.6087 | 56.2015 | 56.0098 | 56.1108 | -66.6773 | -66.6558 | 0.018674 | -66.6857 | 56.0932 | 56.2435 | 56.0865 | -66.85 | -0.017706 | -0.043946 | -0.00989 | 0.05089 | 0.068596 | -0.23566 | -0.13462 | -0.1905 | -0.15218 | 0.003736 | -0.026191 | 0.1643 | -0.001898 | -0.15895 | 122.861 | 122.6693 | 122.7703 | 66.6747 | -122.9227 | 122.7528 | 122.9031 | 122.746 | 66.6782 | -123.0955
416.6406 | 123.175 | -66.6367 | 56.2683 | -0.012133 | -0.0061794 | 0.0013291 | 0.052705 | -0.0024337 | 0.06012 | 0.00053414 | -0.00046581 | -0.00016665 | 0.063877 | 0.0096324 | 0.065179 | -66.674 | 0.019721 | -66.6178 | 56.2015 | 56.0052 | 56.1108 | -66.6864 | -66.6512 | 0.009516 | -66.6812 | 56.0887 | 56.2344 | 56.0956 | -66.85 | -0.049751 | -0.066835 | -0.037357 | 0.018845 | 0.068596 | -0.26313 | -0.15751 | -0.21338 | -0.17965 | -0.014574 | -0.0445 | 0.16888 | -0.033944 | -0.17268 | 122.8381 | 122.6418 | 122.7475 | 66.6564 | -122.9547 | 122.7253 | 122.871 | 122.7323 | 66.6462 | -123.1184
417.6406 | 123.2483 | -66.6412 | 56.2775 | -0.0045023 | -0.0059658 | 0.0013291 | 0.052491 | -0.0026473 | 0.06012 | -0.0070964 | -0.00025221 | -0.00016665 | 0.064304 | 0.010273 | 0.064966 | -66.6694 | 0.010564 | -66.6087 | 56.2015 | 56.0098 | 56.1108 | -66.691 | -66.6558 | 0.018674 | -66.6812 | 56.1024 | 56.2435 | 56.0956 | -66.8455 | -0.049753 | -0.07599 | -0.028201 | 0.032579 | 0.082332 | -0.2677 | -0.16666 | -0.20423 | -0.17507 | -0.014575 | -0.039923 | 0.16431 | -0.033942 | -0.18183 | 122.8427 | 122.651 | 122.752 | 66.6518 | -122.9685 | 122.7436 | 122.8848 | 122.7369 | 66.6599 | -123.1229
418.6406 | 123.175 | -66.6367 | 56.282 | -0.012133 | -0.0061794 | 0.0015427 | 0.052919 | -0.0024337 | 0.060548 | 0.0081646 | -0.00025221 | 0.00026075 | 0.06409 | 0.0096324 | 0.065179 | -66.6603 | 0.010564 | -66.6132 | 56.2015 | 56.0143 | 56.1154 | -66.6864 | -66.6558 | 0.018674 | -66.6903 | 56.1024 | 56.2527 | 56.1094 | -66.8455 | -0.049751 | -0.080567 | -0.023622 | 0.023423 | 0.073174 | -0.2677 | -0.16666 | -0.20881 | -0.17965 | -0.019152 | -0.053658 | 0.15515 | -0.029362 | -0.17268 | 122.8381 | 122.651 | 122.752 | 66.6472 | -122.9685 | 122.7391 | 122.8893 | 122.746 | 66.6553 | -123.1275
419.6406 | 123.1979 | -66.6275 | 56.2866 | -0.0045023 | -0.0063932 | 0.0015427 | 0.052491 | -0.0026473 | 0.06012 | 0.0081646 | -0.00046581 | -0.00038025 | 0.06409 | 0.01006 | 0.065179 | -66.6603 | 0.019721 | -66.6041 | 56.2061 | 56.0006 | 56.1154 | -66.6818 | -66.6512 | 0.009516 | -66.6812 | 56.0978 | 56.2435 | 56.1002 | -66.8409 | -0.054328 | -0.080566 | -0.032778 | 0.023424 | 0.077752 | -0.28601 | -0.17124 | -0.21338 | -0.1888 | -0.02373 | -0.053656 | 0.15973 | -0.043097 | -0.18641 | 122.8336 | 122.6281 | 122.7429 | 66.6472 | -122.9685 | 122.7253 | 122.871 | 122.7277 | 66.637 | -123.1275
420.6406 | 123.2529 | -66.6321 | 56.2775 | 0.01076 | -0.0063932 | 0.0013291 | 0.052278 | -0.0026473 | 0.059907 | 0.00053414 | -3.8406e-05 | -0.00059405 | 0.064304 | 0.01006 | 0.064966 | -66.6511 | 0.005985 | -66.5995 | 56.2061 | 56.0189 | 56.12 | -66.6818 | -66.6421 | 0.014095 | -66.6766 | 56.107 | 56.2527 | 56.1094 | -66.8409 | -0.04975 | -0.071411 | -0.019043 | 0.03258 | 0.08233 | -0.25854 | -0.15751 | -0.2088 | -0.17049 | -0.009994 | -0.044499 | 0.16431 | -0.024785 | -0.1681 | 122.8381 | 122.651 | 122.752 | 66.6381 | -122.9593 | 122.7391 | 122.8848 | 122.7414 | 66.6462 | -123.1184
421.6406 | 123.2391 | -66.6321 | 56.2637 | -0.0045023 | -0.0063932 | 0.0015427 | 0.052278 | -0.0026473 | 0.06012 | 0.00053414 | -0.00046581 | -0.00038025 | 0.063877 | 0.0096324 | 0.065179 | -66.6603 | -0.003172 | -66.5903 | 56.2152 | 56.0281 | 56.1291 | -66.6818 | -66.6467 | 0.014095 | -66.6766 | 56.1024 | 56.2481 | 56.1048 | -66.8409 | -0.04975 | -0.048521 | -0.0282 | 0.041737 | 0.091487 | -0.23565 | -0.13462 | -0.2088 | -0.16134 | -0.014573 | -0.044499 | 0.16431 | -0.01563 | -0.15894 | 122.8473 | 122.6602 | 122.7612 | 66.6289 | -122.9456 | 122.7345 | 122.8802 | 122.7369 | 66.6462 | -123.1046
422.6406 | 123.1979 | -66.6504 | 56.2866 | -0.0045023 | -0.0061794 | 0.0015427 | 0.052278 | -0.0026473 | 0.06012 | 0.00053414 | -0.00046581 | -0.00016665 | 0.06409 | 0.01006 | 0.065179 | -66.6511 | 0.001407 | -66.5949 | 56.2015 | 56.0143 | 56.12 | -66.6818 | -66.6375 | 0.009516 | -66.6766 | 56.1161 | 56.2573 | 56.1094 | -66.8363 | -0.031439 | -0.085145 | -0.000732 | 0.055469 | 0.086908 | -0.27228 | -0.16666 | -0.18591 | -0.17049 | 0.012895 | -0.026188 | 0.15973 | -0.029361 | -0.17725 | 122.8519 | 122.6647 | 122.7704 | 66.6518 | -122.9685 | 122.7665 | 122.9077 | 122.7598 | 66.6599 | -123.1229
423.6406 | 123.1842 | -66.655 | 56.3049 | 0.0031287 | -0.0061794 | 0.0011155 | 0.052064 | -0.0026473 | 0.059907 | 0.00053414 | -0.00025221 | -0.00016665 | 0.06409 | 0.009846 | 0.064752 | -66.6465 | -0.007751 | -66.5903 | 56.2244 | 56.0235 | 56.12 | -66.6635 | -66.6375 | 0.009516 | -66.6674 | 56.1161 | 56.2618 | 56.1277 | -66.8363 | -0.008547 | -0.080564 | 0.008423 | 0.064625 | 0.073172 | -0.28143 | -0.18497 | -0.18134 | -0.1888 | 0.017472 | -0.012454 | 0.16888 | -0.043094 | -0.17725 | 122.8793 | 122.6785 | 122.7749 | 66.6472 | -122.9684 | 122.7711 | 122.9168 | 122.7826 | 66.6645 | -123.1412
424.6406 | 123.23 | -66.655 | 56.2729 | 0.0031287 | -0.0063932 | 0.0011155 | 0.052278 | -0.0024337 | 0.06012 | 0.00053414 | -0.00025221 | -0.00016665 | 0.064304 | 0.010273 | 0.064752 | -66.6374 | -0.007751 | -66.5812 | 56.2198 | 56.0372 | 56.1291 | -66.6773 | -66.6375 | 0.014095 | -66.6674 | 56.1116 | 56.2618 | 56.1277 | -66.8226 | -0.022284 | -0.053098 | 0.01758 | 0.073781 | 0.096065 | -0.23565 | -0.14377 | -0.1676 | -0.16133 | 0.017472 | -0.012454 | 0.15515 | -0.01105 | -0.14521 | 122.8748 | 122.6922 | 122.7841 | 66.6472 | -122.9501 | 122.7665 | 122.9168 | 122.7826 | 66.6691 | -123.0955
425.6406 | 123.1064 | -66.655 | 56.3278 | -0.012133 | -0.0061794 | 0.0015427 | 0.05185 | -0.0026473 | 0.059907 | 0.0081646 | -0.00046581 | -0.00038025 | 0.06409 | 0.009846 | 0.065179 | -66.6374 | -0.012329 | -66.5858 | 56.2244 | 56.0235 | 56.1337 | -66.6635 | -66.6283 | 0.014095 | -66.6537 | 56.1253 | 56.2664 | 56.1231 | -66.818 | -0.008547 | -0.10345 | 0.01758 | 0.069203 | 0.07775 | -0.30432 | -0.19412 | -0.16302 | -0.20253 | 0.02663 | 0.001282 | 0.16431 | -0.061403 | -0.20472 | 122.8793 | 122.6785 | 122.7887 | 66.6426 | -122.9913 | 122.7803 | 122.9214 | 122.7781 | 66.6691 | -123.1458
426.6406 | 123.2483 | -66.6092 | 56.2912 | -0.012133 | -0.0061794 | 0.0017565 | 0.052064 | -0.0024337 | 0.059907 | -0.014727 | -0.00089301 | 4.695e-05 | 0.064304 | 0.010273 | 0.065179 | -66.6191 | -0.012329 | -66.5812 | 56.2244 | 56.0281 | 56.1291 | -66.6589 | -66.6329 | 0.000359 | -66.6583 | 56.1161 | 56.2664 | 56.1277 | -66.818 | -0.049744 | -0.066831 | -0.009882 | 0.028005 | 0.077749 | -0.26312 | -0.16208 | -0.2088 | -0.17507 | -0.023725 | -0.049073 | 0.15973 | -0.024782 | -0.16352 | 122.8336 | 122.6373 | 122.7383 | 66.5969 | -122.9501 | 122.7253 | 122.8756 | 122.7369 | 66.6096 | -123.1092
427.6406 | 123.1979 | -66.6367 | 56.3095 | -0.0045023 | -0.0059658 | 0.0013291 | 0.052491 | -0.0028609 | 0.06012 | 0.015795 | -0.00046581 | -0.00016665 | 0.064304 | 0.010273 | 0.064752 | -66.6145 | -0.016908 | -66.5812 | 56.2244 | 56.0464 | 56.1429 | -66.6635 | -66.6192 | 0.014095 | -66.6537 | 56.1299 | 56.271 | 56.1185 | -66.8088 | -0.026857 | -0.085141 | 0.022162 | 0.055471 | 0.082328 | -0.26311 | -0.16666 | -0.17218 | -0.17964 | 0.017477 | -0.017028 | 0.15515 | -0.038513 | -0.19098 | 122.861 | 122.6831 | 122.7795 | 66.6197 | -122.973 | 122.7665 | 122.9077 | 122.7552 | 66.6508 | -123.1183
428.6406 | 123.23 | -66.5955 | 56.3324 | 0.0031287 | -0.0061794 | 0.0017565 | 0.052491 | -0.0020063 | 0.06012 | 0.0081646 | -0.00046581 | -0.00059405 | 0.064304 | 0.010487 | 0.065179 | -66.6099 | -0.021486 | -66.5675 | 56.2289 | 56.0372 | 56.1429 | -66.6589 | -66.6146 | 0.000359 | -66.6491 | 56.1253 | 56.2756 | 56.1277 | -66.8088 | -0.063477 | -0.10345 | -0.014458 | 0.028007 | 0.091484 | -0.29516 | -0.18954 | -0.21337 | -0.20711 | -0.019143 | -0.053648 | 0.15973 | -0.056823 | -0.20472 | 122.8244 | 122.6327 | 122.7383 | 66.574 | -122.9913 | 122.7207 | 122.871 | 122.7231 | 66.5958 | -123.1412
429.6406 | 123.1705 | -66.6183 | 56.3141 | 0.0031287 | -0.0066068 | 0.0013291 | 0.052491 | -0.0026473 | 0.060334 | -0.0070964 | -0.00067941 | -0.00016665 | 0.063663 | 0.01006 | 0.064966 | -66.6099 | -0.021486 | -66.5766 | 56.2335 | 56.051 | 56.1429 | -66.6498 | -66.6146 | 0.000359 | -66.6445 | 56.1344 | 56.2756 | 56.146 | -66.8088 | -0.031431 | -0.080562 | 0.00843 | 0.041739 | 0.07317 | -0.26311 | -0.17123 | -0.19049 | -0.17964 | 0.003745 | -0.026182 | 0.1643 | -0.038513 | -0.16809 | 122.8519 | 122.6693 | 122.7612 | 66.5969 | -122.9639 | 122.7528 | 122.8939 | 122.7643 | 66.6187 | -123.1229
430.6406 | 123.2574 | -66.6092 | 56.2958 | -0.0045023 | -0.0063932 | 0.0015427 | 0.052278 | -0.0026473 | 0.059693 | 0.015795 | -0.00067941 | -0.00038025 | 0.064304 | 0.01006 | 0.065393 | -66.6099 | -0.030644 | -66.5675 | 56.2381 | 56.0556 | 56.1429 | -66.6498 | -66.6192 | -0.00422 | -66.6445 | 56.1436 | 56.2847 | 56.146 | -66.8043 | -0.040586 | -0.057672 | -0.000725 | 0.04174 | 0.082326 | -0.24022 | -0.15292 | -0.19506 | -0.15217 | -0.009989 | -0.035337 | 0.15972 | -0.011045 | -0.14978 | 122.8473 | 122.6647 | 122.752 | 66.5785 | -122.9456 | 122.7528 | 122.8939 | 122.7552 | 66.605 | -123.1
431.6406 | 123.0972 | -66.6504 | 56.3461 | -0.012133 | -0.0063932 | 0.0015427 | 0.05185 | -0.0024337 | 0.059693 | -0.0070964 | -0.00025221 | -0.00059405 | 0.064304 | 0.010273 | 0.065179 | -66.5962 | -0.030644 | -66.5583 | 56.2518 | 56.0601 | 56.1612 | -66.6452 | -66.6009 | 0.004938 | -66.6354 | 56.1482 | 56.2802 | 56.1506 | -66.8043 | 0.005192 | -0.094291 | 0.054209 | 0.092096 | 0.086904 | -0.286 | -0.18496 | -0.15386 | -0.19795 | 0.049525 | 0.01502 | 0.16888 | -0.065977 | -0.19555 | 122.9022 | 122.7105 | 122.8116 | 66.6197 | -122.9913 | 122.7986 | 122.9305 | 122.801 | 66.6553 | -123.1504
432.6406 | 123.23 | -66.5955 | 56.3324 | 0.0031287 | -0.0063932 | 0.0013291 | 0.052064 | -0.0026473 | 0.060334 | 0.00053414 | -0.00046581 | -0.00016665 | 0.06409 | 0.010487 | 0.065179 | -66.5962 | -0.035222 | -66.5491 | 56.2564 | 56.0693 | 56.1703 | -66.636 | -66.5963 | 0.004938 | -66.6308 | 56.1482 | 56.2939 | 56.1597 | -66.7951 | -0.040582 | -0.07598 | -0.000723 | 0.04632 | 0.086902 | -0.26311 | -0.16207 | -0.19964 | -0.18422 | -0.000828 | -0.035333 | 0.1643 | -0.038508 | -0.17267 | 122.8519 | 122.6647 | 122.7658 | 66.5602 | -122.9684 | 122.7436 | 122.8893 | 122.7552 | 66.6004 | -123.1275
433.6406 | 123.0927 | -66.6046 | 56.369 | -0.0045023 | -0.0068204 | 0.0015427 | 0.052278 | -0.0024337 | 0.060334 | 0.00053414 | -3.8406e-05 | -0.00016665 | 0.063877 | 0.010273 | 0.065179 | -66.587 | -0.044379 | -66.5537 | 56.2564 | 56.0739 | 56.1657 | -66.6315 | -66.6009 | -0.008798 | -66.6308 | 56.1528 | 56.2893 | 56.1552 | -66.7905 | -0.026848 | -0.1126 | 0.017588 | 0.050897 | 0.077745 | -0.29515 | -0.20327 | -0.1859 | -0.21626 | 0.003748 | -0.026178 | 0.15973 | -0.079709 | -0.21387 | 122.861 | 122.6785 | 122.7704 | 66.5602 | -123.0005 | 122.7574 | 122.8939 | 122.7598 | 66.5958 | -123.1595
434.6406 | 123.1842 | -66.5955 | 56.3324 | -0.012133 | -0.0061794 | 0.0015427 | 0.052064 | -0.0030747 | 0.059907 | 0.00053414 | -0.00046581 | -0.00038025 | 0.063877 | 0.010487 | 0.065393 | -66.5779 | -0.044379 | -66.5446 | 56.2656 | 56.0739 | 56.1703 | -66.636 | -66.5917 | -0.013377 | -66.6171 | 56.1619 | 56.303 | 56.1689 | -66.7859 | -0.040582 | -0.066823 | 0.01759 | 0.050899 | 0.091481 | -0.25853 | -0.16207 | -0.19048 | -0.17048 | 0.00375 | -0.021597 | 0.16888 | -0.029351 | -0.16351 | 122.861 | 122.6693 | 122.7658 | 66.5511 | -122.9684 | 122.7574 | 122.8985 | 122.7643 | 66.5821 | -123.1183
435.6406 | 123.1293 | -66.6183 | 56.3553 | -0.0045023 | -0.0061794 | 0.0013291 | 0.052064 | -0.0028609 | 0.060334 | -0.0070964 | -0.00046581 | -0.00038025 | 0.063877 | 0.01006 | 0.064966 | -66.5687 | -0.053537 | -66.5354 | 56.2656 | 56.0739 | 56.1841 | -66.6223 | -66.5871 | -0.008798 | -66.6125 | 56.1619 | 56.3076 | 56.1506 | -66.7859 | -0.003957 | -0.089712 | 0.049635 | 0.082943 | 0.0869 | -0.28142 | -0.17122 | -0.16759 | -0.19337 | 0.031217 | 0.005869 | 0.17346 | -0.047662 | -0.20471 | 122.8839 | 122.6922 | 122.8024 | 66.5648 | -122.9776 | 122.7803 | 122.926 | 122.7689 | 66.6095 | -123.1412
436.6406 | 123.2254 | -66.5863 | 56.3187 | -0.0045023 | -0.0061794 | 0.0015427 | 0.052278 | -0.0028609 | 0.06012 | -0.0070964 | -0.00089301 | -0.00016665 | 0.063877 | 0.010487 | 0.064966 | -66.5596 | -0.062694 | -66.5217 | 56.2702 | 56.0876 | 56.1886 | -66.604 | -66.578 | -0.00422 | -66.6125 | 56.1665 | 56.3122 | 56.1689 | -66.7814 | -0.017685 | -0.048513 | 0.026749 | 0.064635 | 0.08232 | -0.23106 | -0.13003 | -0.19506 | -0.15217 | 0.008332 | -0.026174 | 0.16888 | -0.006462 | -0.14978 | 122.8565 | 122.6739 | 122.7749 | 66.5236 | -122.9227 | 122.7528 | 122.8985 | 122.7552 | 66.5821 | -123.1
437.6406 | 123.2574 | -66.6367 | 56.369 | -0.012133 | -0.0061794 | 0.0013291 | 0.052278 | -0.0026473 | 0.06012 | -0.0070964 | -0.00089301 | -0.00059405 | 0.064304 | 0.01006 | 0.065179 | -66.555 | -0.081008 | -66.5217 | 56.2793 | 56.0968 | 56.1978 | -66.5994 | -66.5688 | -0.00422 | -66.5987 | 56.1711 | 56.3168 | 56.1735 | -66.7722 | 0.037248 | -0.08971 | 0.081681 | 0.11499 | 0.077741 | -0.27226 | -0.17122 | -0.13555 | -0.19795 | 0.067843 | 0.037917 | 0.17346 | -0.052237 | -0.19555 | 122.916 | 122.7334 | 122.8345 | 66.5556 | -122.9684 | 122.8077 | 122.9534 | 122.8101 | 66.6324 | -123.1412
438.6406 | 123.2071 | -66.5726 | 56.3553 | -0.012133 | -0.0063932 | 0.0013291 | 0.05185 | -0.0026473 | 0.059907 | -0.0070964 | -0.00067941 | -0.00038025 | 0.063877 | 0.010273 | 0.064966 | -66.5458 | -0.085587 | -66.5171 | 56.2793 | 56.1059 | 56.2024 | -66.6086 | -66.5642 | -0.008798 | -66.5987 | 56.1848 | 56.3214 | 56.1872 | -66.7676 | -0.035997 | -0.075977 | 0.026751 | 0.05548 | 0.091477 | -0.24936 | -0.15291 | -0.19505 | -0.17048 | 0.008335 | -0.02617 | 0.16888 | -0.033926 | -0.16808 | 122.8519 | 122.6785 | 122.7749 | 66.487 | -122.9639 | 122.7574 | 122.8939 | 122.7598 | 66.5638 | -123.1229
439.6406 | 123.111 | -66.5955 | 56.4056 | -0.0045023 | -0.0063932 | 0.0011155 | 0.052491 | -0.0024337 | 0.059907 | 0.00053414 | -0.00046581 | -0.00016665 | 0.063877 | 0.010273 | 0.065179 | -66.5367 | -0.081008 | -66.5125 | 56.2885 | 56.1105 | 56.2024 | -66.604 | -66.5505 | -0.013377 | -66.5896 | 56.1848 | 56.3259 | 56.1872 | -66.7585 | -0.00853 | -0.11717 | 0.058796 | 0.082946 | 0.091476 | -0.29514 | -0.20326 | -0.16301 | -0.22083 | 0.044959 | 0.005875 | 0.16888 | -0.079701 | -0.21844 | 122.8839 | 122.706 | 122.7978 | 66.5145 | -123.0096 | 122.7803 | 122.9214 | 122.7827 | 66.5821 | -123.1641
440.6406 | 123.1567 | -66.5909 | 56.3782 | -0.0045023 | -0.0061794 | 0.0017565 | 0.052064 | -0.0026473 | 0.060334 | 0.0081646 | -0.00067941 | -0.00080765 | 0.063663 | 0.010273 | 0.065393 | -66.5229 | -0.094744 | -66.4988 | 56.2976 | 56.1013 | 56.2115 | -66.5765 | -66.5459 | -0.013377 | -66.5896 | 56.194 | 56.3397 | 56.2147 | -66.7585 | 0.014366 | -0.080551 | 0.067953 | 0.092103 | 0.077737 | -0.27683 | -0.16664 | -0.16759 | -0.18421 | 0.04496 | 0.001297 | 0.16888 | -0.038499 | -0.1635 | 122.8885 | 122.6922 | 122.8024 | 66.4961 | -122.9547 | 122.7848 | 122.9306 | 122.8056 | 66.5775 | -123.1366
441.6406 | 123.0743 | -66.5771 | 56.4285 | 0.0031287 | -0.0061794 | 0.0017565 | 0.052064 | -0.0028609 | 0.06012 | 0.0081646 | -0.00046581 | -0.00038025 | 0.06409 | 0.01006 | 0.064752 | -66.5092 | -0.10848 | -66.4896 | 56.3068 | 56.1151 | 56.2161 | -66.5811 | -66.5413 | -0.017956 | -66.5713 | 56.2031 | 56.3397 | 56.2147 | -66.7356 | -0.003946 | -0.12175 | 0.067955 | 0.087527 | 0.091473 | -0.31345 | -0.21242 | -0.15842 | -0.2254 | 0.035805 | 0.005879 | 0.1643 | -0.088853 | -0.21385 | 122.8839 | 122.6922 | 122.7933 | 66.4687 | -123.0096 | 122.7803 | 122.9168 | 122.7918 | 66.5592 | -123.1641
442.6406 | 123.1018 | -66.5543 | 56.4011 | -0.012133 | -0.0063932 | 0.0015427 | 0.05185 | -0.0026473 | 0.059907 | 0.00053414 | -0.00046581 | -0.00038025 | 0.06409 | 0.010273 | 0.064966 | -66.4955 | -0.1039 | -66.4759 | 56.3114 | 56.1288 | 56.2344 | -66.5765 | -66.5276 | -0.022535 | -66.5621 | 56.2077 | 56.3534 | 56.2284 | -66.7356 | -0.022255 | -0.089704 | 0.058802 | 0.078374 | 0.10063 | -0.27225 | -0.16664 | -0.18131 | -0.19336 | 0.026653 | -0.007852 | 0.17346 | -0.047652 | -0.17265 | 122.8656 | 122.6831 | 122.7887 | 66.4504 | -122.9776 | 122.762 | 122.9077 | 122.7827 | 66.5317 | -123.1366
443.6406 | 123.1064 | -66.5314 | 56.4194 | -0.0045023 | -0.0070342 | 0.0015427 | 0.052278 | -0.0024337 | 0.06012 | 0.015795 | -0.00025221 | -0.00038025 | 0.06409 | 0.010273 | 0.065179 | -66.4771 | -0.12679 | -66.4713 | 56.3205 | 56.138 | 56.239 | -66.5674 | -66.5184 | -0.022535 | -66.5575 | 56.2214 | 56.3717 | 56.233 | -66.731 | -0.035985 | -0.098859 | 0.054228 | 0.060064 | 0.096049 | -0.2814 | -0.18037 | -0.19962 | -0.19794 | 0.012923 | -0.026161 | 0.17346 | -0.047648 | -0.18638 | 122.8519 | 122.6693 | 122.7704 | 66.4046 | -122.9867 | 122.7528 | 122.9031 | 122.7644 | 66.5088 | -123.1504
444.6406 | 123.1247 | -66.5543 | 56.4285 | -0.0045023 | -0.0061794 | 0.0017565 | 0.052278 | -0.0024337 | 0.06012 | 0.0081646 | -0.00046581 | -0.00038025 | 0.063877 | 0.010487 | 0.065393 | -66.468 | -0.14053 | -66.4576 | 56.3388 | 56.1609 | 56.2436 | -66.549 | -66.5139 | -0.027113 | -66.5438 | 56.2306 | 56.3763 | 56.2513 | -66.7127 | 0.005218 | -0.0897 | 0.086273 | 0.096687 | 0.091469 | -0.26766 | -0.18494 | -0.15842 | -0.19793 | 0.04039 | 0.010463 | 0.16888 | -0.052225 | -0.17722 | 122.8931 | 122.7151 | 122.7978 | 66.4137 | -122.9776 | 122.7849 | 122.9306 | 122.8056 | 66.5271 | -123.1412
445.6406 | 123.1476 | -66.5359 | 56.4514 | -0.0045023 | -0.0066068 | 0.0019701 | 0.052064 | -0.0026473 | 0.06012 | 0.00053414 | -0.00046581 | -0.00016665 | 0.063877 | 0.010273 | 0.065179 | -66.4543 | -0.14511 | -66.4484 | 56.348 | 56.1746 | 56.2573 | -66.5536 | -66.5001 | -0.036271 | -66.5255 | 56.2443 | 56.3855 | 56.2513 | -66.7035 | -0.017671 | -0.10343 | 0.081698 | 0.087533 | 0.1052 | -0.27681 | -0.1941 | -0.16757 | -0.20709 | 0.035816 | 0.010468 | 0.17804 | -0.065955 | -0.20011 | 122.8839 | 122.7106 | 122.7933 | 66.3908 | -123.005 | 122.7803 | 122.9214 | 122.7873 | 66.4997 | -123.1549
446.6406 | 123.1293 | -66.5451 | 56.4651 | 0.0031287 | -0.0061794 | 0.0017565 | 0.05185 | -0.0028609 | 0.060334 | 0.0081646 | -0.00046581 | -0.00038025 | 0.06409 | 0.010487 | 0.064966 | -66.4268 | -0.15884 | -66.4301 | 56.3617 | 56.1746 | 56.2756 | -66.5261 | -66.4772 | -0.036271 | -66.5072 | 56.2626 | 56.4084 | 56.265 | -66.6944 | 0.018958 | -0.10343 | 0.11832 | 0.115 | 0.096044 | -0.29054 | -0.18952 | -0.14926 | -0.2025 | 0.067864 | 0.037938 | 0.1872 | -0.056795 | -0.20011 | 122.9068 | 122.7197 | 122.8207 | 66.3863 | -122.9913 | 122.8077 | 122.9535 | 122.8101 | 66.5088 | -123.1595
447.6406 | 123.1613 | -66.4993 | 56.4743 | -0.012133 | -0.0066068 | 0.0015427 | 0.052278 | -0.0026473 | 0.060334 | 0.00053414 | -0.00067941 | 4.695e-05 | 0.064731 | 0.010487 | 0.065179 | -66.3947 | -0.168 | -66.4118 | 56.38 | 56.1883 | 56.2939 | -66.5078 | -66.4818 | -0.036271 | -66.498 | 56.2718 | 56.4221 | 56.2834 | -66.6715 | -0.008502 | -0.09427 | 0.1046 | 0.087539 | 0.096041 | -0.28596 | -0.18036 | -0.17214 | -0.2025 | 0.01751 | 0.001319 | 0.17346 | -0.052214 | -0.19095 | 122.8794 | 122.6877 | 122.7933 | 66.3313 | -122.9821 | 122.7711 | 122.9214 | 122.7827 | 66.4631 | -123.1458
448.6406 | 123.1155 | -66.4856 | 56.5018 | 0.0031287 | -0.0063932 | 0.0013291 | 0.05185 | -0.0026473 | 0.060334 | -0.0070964 | -0.00067941 | -0.00038025 | 0.063877 | 0.010273 | 0.065179 | -66.3764 | -0.1909 | -66.3981 | 56.3892 | 56.2112 | 56.3123 | -66.4849 | -66.4498 | -0.050007 | -66.4889 | 56.2855 | 56.445 | 56.3062 | -66.6532 | 0.000659 | -0.11258 | 0.10918 | 0.087541 | 0.086882 | -0.29053 | -0.18951 | -0.16756 | -0.21623 | 0.035827 | -0.003256 | 0.1643 | -0.056787 | -0.19552 | 122.8748 | 122.6968 | 122.7979 | 66.2947 | -122.9867 | 122.7711 | 122.9306 | 122.7918 | 66.4356 | -123.1549
449.6406 | 123.1201 | -66.4581 | 56.5384 | 0.0031287 | -0.0063932 | 0.0017565 | 0.052064 | -0.0028609 | 0.060548 | -0.0070964 | -0.00046581 | -0.00038025 | 0.064304 | 0.01006 | 0.064966 | -66.3444 | -0.20463 | -66.366 | 56.4167 | 56.2341 | 56.3352 | -66.4804 | -66.4315 | -0.054586 | -66.4568 | 56.313 | 56.4587 | 56.3383 | -66.6348 | -0.022228 | -0.12173 | 0.11376 | 0.092122 | 0.11435 | -0.30426 | -0.20324 | -0.17671 | -0.22538 | 0.026676 | 0.001329 | 0.17804 | -0.079673 | -0.20009 | 122.8748 | 122.6923 | 122.7933 | 66.2535 | -123.0187 | 122.7711 | 122.9168 | 122.7964 | 66.4035 | -123.1732
450.6406 | 123.1018 | -66.449 | 56.5659 | -0.0045023 | -0.0066068 | 0.0015427 | 0.052064 | -0.0028609 | 0.059907 | 0.00053414 | -0.00046581 | -0.00038025 | 0.06409 | 0.010273 | 0.064752 | -66.3123 | -0.22295 | -66.3431 | 56.4441 | 56.2616 | 56.358 | -66.462 | -66.404 | -0.054586 | -66.4293 | 56.3359 | 56.4816 | 56.3566 | -66.6119 | -0.013067 | -0.12173 | 0.13665 | 0.10586 | 0.11893 | -0.30425 | -0.20781 | -0.16297 | -0.22996 | 0.044994 | 0.019646 | 0.18261 | -0.084246 | -0.20925 | 122.8931 | 122.7106 | 122.807 | 66.226 | -123.0279 | 122.7849 | 122.9306 | 122.8056 | 66.3944 | -123.1778
451.6406 | 123.1338 | -66.3895 | 56.5842 | -0.012133 | -0.0063932 | 0.0013291 | 0.052064 | -0.0028609 | 0.059907 | 0.00053414 | -0.00046581 | -0.00059405 | 0.063877 | 0.010701 | 0.064966 | -66.2757 | -0.2321 | -66.3156 | 56.4716 | 56.2845 | 56.3764 | -66.4254 | -66.3811 | -0.059164 | -66.4064 | 56.3679 | 56.5182 | 56.3749 | -66.5845 | -0.035946 | -0.11257 | 0.11377 | 0.073819 | 0.10976 | -0.29967 | -0.20781 | -0.19501 | -0.21622 | 0.008377 | -0.016971 | 0.17803 | -0.065927 | -0.20924 | 122.8611 | 122.674 | 122.7658 | 66.1574 | -123.0096 | 122.7574 | 122.9077 | 122.7644 | 66.3303 | -123.1686
452.6406 | 123.0881 | -66.3757 | 56.6025 | -0.012133 | -0.0063932 | 0.0011155 | 0.052278 | -0.0028609 | 0.060334 | 0.0081646 | -0.00089301 | -0.00059405 | 0.063877 | 0.010487 | 0.065179 | -66.2208 | -0.255 | -66.2836 | 56.4991 | 56.312 | 56.413 | -66.3796 | -66.3261 | -0.068322 | -66.3652 | 56.4 | 56.5457 | 56.4161 | -66.5387 | -0.003889 | -0.10341 | 0.15498 | 0.092134 | 0.096023 | -0.2905 | -0.18949 | -0.16295 | -0.20248 | 0.049589 | 0.010505 | 0.17346 | -0.056766 | -0.18634 | 122.8748 | 122.6877 | 122.7887 | 66.1207 | -122.9821 | 122.7757 | 122.9214 | 122.7919 | 66.3074 | -123.1412
453.6406 | 123.1384 | -66.3345 | 56.6574 | -0.0045023 | -0.0063932 | 0.0015427 | 0.052278 | -0.0026473 | 0.059907 | 0.0081646 | -0.00025221 | -0.00016665 | 0.063877 | 0.010273 | 0.064752 | -66.1567 | -0.27331 | -66.2378 | 56.5403 | 56.3578 | 56.4588 | -66.3521 | -66.3033 | -0.082058 | -66.3332 | 56.4366 | 56.6052 | 56.4619 | -66.5066 | -0.017614 | -0.11713 | 0.17788 | 0.096718 | 0.11433 | -0.29965 | -0.19863 | -0.1721 | -0.22078 | 0.031284 | 0.001358 | 0.17346 | -0.052176 | -0.19549 | 122.8748 | 122.6923 | 122.7933 | 66.0612 | -123.0096 | 122.7712 | 122.9398 | 122.7965 | 66.2525 | -123.164
454.6406 | 123.1201 | -66.2704 | 56.6895 | -0.0045023 | -0.0066068 | 0.0011155 | 0.052064 | -0.0028609 | 0.059907 | 0.00053414 | -0.00046581 | -0.00016665 | 0.064304 | 0.010701 | 0.065179 | -66.088 | -0.27789 | -66.192 | 56.5906 | 56.4081 | 56.5046 | -66.3018 | -66.262 | -0.082058 | -66.2874 | 56.4778 | 56.6419 | 56.5031 | -66.4517 | -0.031333 | -0.098814 | 0.18247 | 0.078414 | 0.10975 | -0.28132 | -0.18489 | -0.18124 | -0.21162 | 0.008406 | -0.016942 | 0.1643 | -0.047591 | -0.18633 | 122.8611 | 122.6786 | 122.775 | 65.9926 | -122.9912 | 122.7483 | 122.9123 | 122.7736 | 66.1884 | -123.1411
455.6406 | 123.1613 | -66.2292 | 56.7444 | 0.0031287 | -0.0068204 | 0.0015427 | 0.052064 | -0.0024337 | 0.06012 | 0.00053414 | -0.00067941 | -0.00038025 | 0.06409 | 0.010487 | 0.065179 | -66.001 | -0.2962 | -66.1371 | 56.6456 | 56.4585 | 56.5549 | -66.2514 | -66.1934 | -0.095794 | -66.2279 | 56.5465 | 56.6922 | 56.5626 | -66.4013 | -0.022164 | -0.098805 | 0.22826 | 0.092155 | 0.11432 | -0.28589 | -0.18946 | -0.17207 | -0.19787 | 0.035887 | 0.001382 | 0.17345 | -0.052158 | -0.18174 | 122.8748 | 122.6877 | 122.7842 | 65.933 | -122.9958 | 122.7758 | 122.9215 | 122.7919 | 66.1335 | -123.1457
456.6406 | 123.143 | -66.188 | 56.7947 | 0.0031287 | -0.0066068 | 0.0015427 | 0.052278 | -0.0028609 | 0.06012 | 0.00053414 | -0.00025221 | -0.00038025 | 0.063663 | 0.010701 | 0.064966 | -65.9094 | -0.30994 | -66.0776 | 56.7051 | 56.5272 | 56.619 | -66.1736 | -66.143 | -0.10953 | -66.1683 | 56.5969 | 56.7517 | 56.6176 | -66.351 | 0.014479 | -0.08964 | 0.27863 | 0.11047 | 0.095994 | -0.26756 | -0.17571 | -0.1629 | -0.19787 | 0.045054 | 0.019706 | 0.18261 | -0.04299 | -0.17715 | 122.8931 | 122.7152 | 122.8071 | 65.8781 | -122.9683 | 122.7849 | 122.9398 | 122.8056 | 66.0785 | -123.1457
457.6406 | 123.1338 | -66.0553 | 56.9 | 0.0031287 | -0.0068204 | 0.0015427 | 0.05185 | -0.0022199 | 0.06012 | 0.00053414 | -0.00046581 | -0.00059405 | 0.063877 | 0.010487 | 0.064752 | -65.7904 | -0.32825 | -65.9997 | 56.7784 | 56.5867 | 56.6831 | -66.1232 | -66.0743 | -0.10037 | -66.0951 | 56.6701 | 56.8158 | 56.6954 | -66.2777 | -0.067904 | -0.12167 | 0.26491 | 0.055553 | 0.12346 | -0.31332 | -0.2169 | -0.22239 | -0.22989 | -0.019016 | -0.039785 | 0.18261 | -0.084175 | -0.2046 | 122.8337 | 122.642 | 122.7384 | 65.727 | -123.0232 | 122.7254 | 122.8711 | 122.7507 | 65.9549 | -123.1777
458.6406 | 123.1476 | -66.0278 | 56.9504 | -0.0045023 | -0.0068204 | 0.0017565 | 0.05185 | -0.0026473 | 0.06012 | 0.00053414 | -0.00046581 | -0.00059405 | 0.06409 | 0.010273 | 0.064966 | -65.6851 | -0.34199 | -65.9265 | 56.847 | 56.6691 | 56.7655 | -66.0362 | -66.0011 | -0.11869 | -66.031 | 56.7342 | 56.8937 | 56.755 | -66.2136 | -0.00837 | -0.10335 | 0.34275 | 0.10134 | 0.10971 | -0.28125 | -0.18483 | -0.18576 | -0.21615 | 0.026777 | -0.003149 | 0.18261 | -0.056692 | -0.19543 | 122.8749 | 122.697 | 122.7934 | 65.6858 | -122.9866 | 122.7621 | 122.9215 | 122.7828 | 65.9091 | -123.164
459.6406 | 123.0927 | -65.9271 | 57.0419 | 0.01076 | -0.0061794 | 0.0017565 | 0.052064 | -0.0026473 | 0.060548 | 0.00053414 | -0.00025221 | -0.00059405 | 0.063877 | 0.010914 | 0.064966 | -65.5523 | -0.3603 | -65.8395 | 56.934 | 56.7516 | 56.848 | -65.9538 | -65.9049 | -0.12327 | -65.9303 | 56.8258 | 56.9761 | 56.8465 | -66.122 | -0.026657 | -0.10791 | 0.37481 | 0.087619 | 0.11428 | -0.29038 | -0.19397 | -0.19489 | -0.21613 | 0.022222 | -0.003126 | 0.19176 | -0.065831 | -0.19541 | 122.8611 | 122.6787 | 122.7751 | 65.5668 | -122.9957 | 122.7529 | 122.9032 | 122.7736 | 65.8039 | -123.1639
460.6406 | 123.1522 | -65.8127 | 57.1289 | -0.0045023 | -0.0066068 | 0.0015427 | 0.052278 | -0.0026473 | 0.060334 | 0.015795 | -0.00025221 | -0.00016665 | 0.064304 | 0.010914 | 0.065179 | -65.3875 | -0.36946 | -65.7205 | 57.0439 | 56.8569 | 56.9578 | -65.8485 | -65.8042 | -0.137 | -65.8295 | 56.9265 | 57.0906 | 56.9564 | -66.0167 | -0.035783 | -0.085006 | 0.4252 | 0.092213 | 0.128 | -0.27204 | -0.17106 | -0.20401 | -0.20238 | 0.008513 | -0.016835 | 0.18718 | -0.038341 | -0.1725 | 122.8566 | 122.6695 | 122.7705 | 65.4432 | -122.9774 | 122.7392 | 122.9032 | 122.7691 | 65.6757 | -123.1456
461.6406 | 123.0972 | -65.6113 | 57.3807 | -0.0045023 | -0.0068204 | 0.0015427 | 0.052064 | -0.0026473 | 0.060334 | 0.015795 | -0.00089301 | -0.00038025 | 0.06409 | 0.010701 | 0.064966 | -65.0533 | -0.3832 | -65.4961 | 57.2545 | 57.0767 | 57.1685 | -65.6333 | -65.5844 | -0.15532 | -65.6189 | 57.1463 | 57.3058 | 57.1624 | -65.7969 | -0.02199 | -0.12617 | 0.558 | 0.11513 | 0.13712 | -0.30402 | -0.21222 | -0.18565 | -0.23438 | 0.026875 | -0.00763 | 0.17802 | -0.074916 | -0.21823 | 122.8658 | 122.6879 | 122.7797 | 65.2281 | -123.0139 | 122.7576 | 122.917 | 122.7737 | 65.456 | -123.1776
462.6406 | 123.143 | -65.3 | 57.6508 | -0.0045023 | -0.0063932 | 0.0015427 | 0.052278 | -0.0028609 | 0.060548 | 0.00053414 | -0.00046581 | -0.00016665 | 0.063877 | 0.010701 | 0.065179 | -64.6504 | -0.40609 | -65.226 | 57.5246 | 57.3422 | 57.4294 | -65.3631 | -65.3234 | -0.15532 | -65.3442 | 57.421 | 57.5713 | 57.428 | -65.5313 | -0.063112 | -0.12613 | 0.64962 | 0.073972 | 0.13708 | -0.30853 | -0.22132 | -0.23136 | -0.22975 | -0.023418 | -0.044187 | 0.18717 | -0.079438 | -0.22275 | 122.8246 | 122.6422 | 122.7294 | 64.8939 | -123.0139 | 122.721 | 122.8713 | 122.728 | 65.1447 | -123.1821
463.6406 | 123.1155 | -64.8102 | 58.2138 | -0.0045023 | -0.0066068 | 0.0013291 | 0.052278 | -0.0026473 | 0.060761 | 0.0081646 | -0.00067941 | -0.00038025 | 0.06409 | 0.010701 | 0.064752 | -63.8537 | -0.40151 | -64.7041 | 58.0328 | 57.8505 | 57.9468 | -64.8594 | -64.806 | -0.16448 | -64.8359 | 57.9384 | 58.0887 | 57.9454 | -65.0139 | -0.049237 | -0.18097 | 0.95645 | 0.10609 | 0.15533 | -0.36331 | -0.26698 | -0.20376 | -0.27543 | 0.004169 | -0.025757 | 0.178 | -0.1251 | -0.26842 | 122.843 | 122.6607 | 122.757 | 64.4087 | -123.0732 | 122.7486 | 122.8989 | 122.7556 | 64.6457 | -123.2277
464.6406 | 123.1705 | -64.5081 | 58.461 | -0.0045023 | -0.0072478 | 0.0017565 | 0.052064 | -0.0026473 | 0.060548 | 0.00053414 | -0.00046581 | 4.695e-05 | 0.063877 | 0.010701 | 0.064966 | -63.4234 | -0.41525 | -64.4111 | 58.3258 | 58.1481 | 58.2307 | -64.5709 | -64.5221 | -0.18279 | -64.5566 | 58.2085 | 58.3588 | 58.2293 | -64.7255 | -0.062889 | -0.13515 | 1.0847 | 0.096975 | 0.15986 | -0.31288 | -0.2303 | -0.21741 | -0.2525 | -0.014075 | -0.04858 | 0.16883 | -0.10216 | -0.23174 | 122.8339 | 122.6562 | 122.7388 | 64.0928 | -123.0319 | 122.7166 | 122.8669 | 122.7373 | 64.3253 | -123.1865
465.6406 | 123.0972 | -64.7186 | 58.2504 | -0.0045023 | -0.0068204 | 0.0015427 | 0.052278 | -0.0024337 | 0.060548 | -0.0070964 | -0.00046581 | -0.00016665 | 0.063877 | 0.010487 | 0.065179 | -63.5424 | -0.43814 | -64.4752 | 58.2434 | 58.0474 | 58.1529 | -64.6442 | -64.6137 | -0.19653 | -64.6482 | 58.1307 | 58.2856 | 58.1468 | -64.817 | 0.074419 | -0.00699 | 1.1762 | 0.24345 | 0.16903 | -0.20304 | -0.097567 | -0.09842 | -0.11976 | 0.10492 | 0.070417 | 0.16884 | 0.035154 | -0.10358 | 122.9621 | 122.766 | 122.8715 | 64.2805 | -122.8946 | 122.8493 | 123.0042 | 122.8655 | 64.5221 | -123.0675
466.6406 | 123.1659 | -64.3158 | 58.6533 | -0.0045023 | -0.0066068 | 0.0017565 | 0.052491 | -0.0026473 | 0.060548 | 0.00053414 | -0.00067941 | -0.00016665 | 0.063877 | 0.010914 | 0.065179 | -63.1258 | -0.43814 | -64.2005 | 58.5044 | 58.3175 | 58.4138 | -64.3832 | -64.339 | -0.2011 | -64.3735 | 58.3962 | 58.5603 | 58.4078 | -64.5423 | -0.067414 | -0.14885 | 1.19 | 0.11532 | 0.18273 | -0.33572 | -0.23942 | -0.22652 | -0.25704 | -0.023187 | -0.057692 | 0.16883 | -0.092962 | -0.24543 | 122.8202 | 122.6333 | 122.7296 | 63.8777 | -123.0365 | 122.712 | 122.8761 | 122.7236 | 64.1147 | -123.1956
467.6406 | 123.2162 | -63.858 | 59.1568 | -0.0045023 | -0.0070342 | 0.0015427 | 0.052278 | -0.0026473 | 0.060761 | -0.0070964 | -3.8406e-05 | 4.695e-05 | 0.063877 | 0.010701 | 0.064752 | -62.4665 | -0.4473 | -63.7655 | 58.921 | 58.7388 | 58.8305 | -63.9665 | -63.9223 | -0.21484 | -63.9568 | 58.8129 | 58.9724 | 58.8336 | -64.1348 | -0.1085 | -0.23576 | 1.3916 | 0.092488 | 0.20098 | -0.418 | -0.32631 | -0.27677 | -0.34393 | -0.064289 | -0.098794 | 0.17798 | -0.18443 | -0.32316 | 122.7791 | 122.5968 | 122.6885 | 63.4107 | -123.1233 | 122.6709 | 122.8304 | 122.6917 | 63.6432 | -123.2916
468.6406 | 123.1522 | -63.4827 | 59.5001 | -0.0045023 | -0.0063932 | 0.0015427 | 0.052278 | -0.0026473 | 0.060761 | 0.0081646 | -0.00067941 | -0.00016665 | 0.063877 | 0.010701 | 0.064966 | -61.8942 | -0.44272 | -63.381 | 59.2827 | 59.096 | 59.1922 | -63.6048 | -63.5606 | -0.22858 | -63.6043 | 59.17 | 59.3341 | 59.1999 | -63.7731 | -0.12213 | -0.21739 | 1.5885 | 0.1017 | 0.22382 | -0.40416 | -0.30792 | -0.29041 | -0.33013 | -0.077937 | -0.1216 | 0.16881 | -0.16604 | -0.3002 | 122.7654 | 122.5786 | 122.6749 | 63.0399 | -123.1049 | 122.6527 | 122.8167 | 122.6826 | 63.2541 | -123.2732
469.6406 | 123.0972 | -62.5122 | 60.4568 | 0.0031287 | -0.0066068 | 0.0017565 | 0.052278 | -0.0026473 | 0.061189 | -0.0070964 | -0.00046581 | 4.695e-05 | 0.06409 | 0.010701 | 0.065393 | -60.397 | -0.45188 | -62.4012 | 60.2488 | 60.0667 | 60.1491 | -62.6249 | -62.5991 | -0.23316 | -62.6382 | 60.1406 | 60.3002 | 60.1614 | -62.8069 | -0.1127 | -0.20808 | 2.1152 | 0.11099 | 0.22369 | -0.39016 | -0.30772 | -0.29474 | -0.31622 | -0.086867 | -0.12595 | 0.16879 | -0.15668 | -0.29542 | 122.761 | 122.5789 | 122.6613 | 62.0603 | -123.0818 | 122.6528 | 122.8124 | 122.6736 | 62.2791 | -123.2638
470.6406 | 123.143 | -62.2696 | 60.704 | -0.0045023 | -0.0070342 | 0.0017565 | 0.052491 | -0.0022199 | 0.06183 | -0.0070964 | -0.00067941 | -0.00059405 | 0.063877 | 0.010487 | 0.064752 | -59.6553 | -0.46103 | -61.9159 | 60.7158 | 60.5246 | 60.6207 | -62.1762 | -62.1412 | -0.24689 | -62.1711 | 60.6031 | 60.758 | 60.6239 | -62.3353 | 0.093423 | 0.011726 | 2.6142 | 0.35367 | 0.26025 | -0.17946 | -0.083314 | -0.065737 | -0.10098 | 0.12839 | 0.098463 | 0.1642 | 0.053985 | -0.080172 | 122.9854 | 122.7942 | 122.8903 | 61.8086 | -122.8802 | 122.8726 | 123.0276 | 122.8935 | 62.0227 | -123.0394
471.6406 | 123.1384 | -61.7523 | 61.2122 | 0.01076 | -0.0068204 | 0.0015427 | 0.052278 | -0.0028609 | 0.061616 | 0.0081646 | -0.00067941 | -0.00038025 | 0.063663 | 0.010914 | 0.064966 | -59.17 | -0.45645 | -61.5863 | 61.0042 | 60.8268 | 60.9138 | -61.8785 | -61.839 | -0.26063 | -61.8735 | 60.9007 | 61.0465 | 60.9169 | -62.0469 | -0.12622 | -0.20795 | 2.5823 | 0.16604 | 0.29226 | -0.38537 | -0.2984 | -0.29454 | -0.3115 | -0.086689 | -0.12119 | 0.17335 | -0.16568 | -0.29526 | 122.7565 | 122.5791 | 122.6661 | 61.2959 | -123.0907 | 122.653 | 122.7988 | 122.6692 | 61.4917 | -123.259
472.6406 | 123.1293 | -61.5509 | 61.409 | -0.0045023 | -0.0063932 | 0.0019701 | 0.052491 | -0.0022199 | 0.062043 | 0.00053414 | -0.00046581 | -0.00038025 | 0.063877 | 0.010701 | 0.064966 | -58.378 | -0.45188 | -61.101 | 61.4758 | 61.2893 | 61.3716 | -61.439 | -61.3903 | -0.27894 | -61.4202 | 61.3539 | 61.5089 | 61.3885 | -61.589 | 0.11194 | 0.066782 | 3.1729 | 0.44992 | 0.33798 | -0.11973 | -0.03738 | -0.038078 | -0.055066 | 0.16061 | 0.13068 | 0.16876 | 0.09992 | -0.020501 | 123.0267 | 122.8402 | 122.9225 | 61.099 | -122.848 | 122.9048 | 123.0598 | 122.9394 | 61.272 | -122.998
473.6406 | 123.1064 | -45.8038 | 77.2568 | -0.0045023 | -0.0063932 | 0.0021837 | 0.052705 | -0.0024337 | 0.066103 | 0.0081646 | -0.00025221 | -0.00016665 | 0.063877 | 0.010701 | 0.064538 | -34.8542 | -0.34199 | -45.9377 | 76.7676 | 76.5783 | 76.6 | -46.1408 | -46.1844 | -0.21484 | -46.1823 | 76.5774 | 76.7236 | 76.768 | -46.2408 | -0.33694 | -0.48918 | 10.9496 | -0.13389 | 0.20305 | -0.67848 | -0.65673 | -0.43695 | -0.67935 | -0.38057 | -0.37844 | 0.058512 | -0.53316 | -0.48875 | 122.5714 | 122.3821 | 122.4039 | 45.4618 | -123.3975 | 122.3813 | 122.5274 | 122.5719 | 45.589 | -123.4976
474.6406 | 123.1201 | -41.7618 | 81.2439 | 0.01076 | -0.0066068 | 0.0017565 | 0.052919 | -0.0022199 | 0.067599 | 0.0081646 | -3.8406e-05 | 0.00026075 | 0.063877 | 0.011342 | 0.064752 | -29.2732 | -0.2962 | -42.4124 | 80.3021 | 80.0857 | 80.1302 | -42.5463 | -42.6405 | -0.18279 | -42.6841 | 80.1532 | 80.3132 | 80.234 | -42.7105 | -0.78454 | -0.94179 | 12.4886 | -0.65066 | 0.13387 | -1.1581 | -1.1137 | -0.94874 | -1.0907 | -0.8787 | -0.92236 | 0.026378 | -0.93066 | -1.0099 | 122.0639 | 121.8475 | 121.8919 | 41.4656 | -123.7902 | 121.915 | 122.075 | 121.9958 | 41.579 | -123.9544
475.6406 | 123.1155 | -32.4326 | 90.596 | -0.0045023 | -0.0066068 | 0.0015427 | 0.052919 | -0.0026473 | 0.07059 | 0.015795 | -0.00046581 | -0.00038025 | 0.06409 | 0.010487 | 0.064752 | -13.3495 | -0.21837 | -32.3906 | 90.4524 | 90.2006 | 90.2626 | -32.4406 | -32.6131 | -0.13242 | -32.6705 | 90.2809 | 90.464 | 90.339 | -32.6096 | -0.008077 | -0.14361 | 19.083 | 0.041968 | 0.050045 | -0.39541 | -0.33341 | -0.17709 | -0.31515 | -0.18055 | -0.23795 | -0.060854 | -0.13201 | -0.25701 | 122.885 | 122.6332 | 122.6952 | 32.2142 | -123.0366 | 122.7134 | 122.8966 | 122.7716 | 32.3001 | -123.2057
476.6406 | 123.1476 | -31.9473 | 91.04 | -0.0045023 | -0.0066068 | 0.0021837 | 0.053132 | -0.0022199 | 0.070804 | 0.00053414 | -0.00046581 | -0.00016665 | 0.064518 | 0.010487 | 0.064752 | -12.3881 | -0.22295 | -31.9602 | 90.869 | 90.6356 | 90.693 | -32.0285 | -32.1964 | -0.14158 | -32.2584 | 90.7067 | 90.8944 | 90.7648 | -32.2021 | -0.081203 | -0.17101 | 19.5593 | -0.012902 | 0.068301 | -0.40445 | -0.34705 | -0.25481 | -0.33338 | -0.24911 | -0.31109 | -0.056285 | -0.14565 | -0.27523 | 122.8164 | 122.5829 | 122.6403 | 31.7244 | -123.0686 | 122.654 | 122.8417 | 122.7121 | 31.8057 | -123.2422
477.6406 | 123.0515 | -32.0663 | 90.9622 | -0.012133 | -0.0066068 | 0.0023975 | 0.052919 | -0.0028609 | 0.071017 | 0.0081646 | -3.8406e-05 | -0.00016665 | 0.06409 | 0.010914 | 0.064538 | -11.9943 | -0.22752 | -31.9236 | 90.9011 | 90.6539 | 90.7205 | -32.0148 | -32.169 | -0.15532 | -32.2355 | 90.7433 | 90.9219 | 90.7877 | -32.1747 | 0.051552 | -0.061141 | 20.072 | 0.14274 | 0.09119 | -0.30831 | -0.24176 | -0.10832 | -0.21893 | -0.10262 | -0.16918 | -0.060864 | -0.04036 | -0.17452 | 122.9674 | 122.7203 | 122.7868 | 31.8388 | -122.977 | 122.8096 | 122.9882 | 122.854 | 31.911 | -123.1369
478.6406 | 123.1384 | -31.6727 | 91.333 | 0.0031287 | -0.0066068 | 0.0021837 | 0.053132 | -0.0026473 | 0.071017 | 0.00053414 | -0.00046581 | 4.695e-05 | 0.064304 | 0.011128 | 0.064538 | -11.6647 | -0.22752 | -31.5573 | 91.2628 | 91.0202 | 91.073 | -31.6485 | -31.8118 | -0.15532 | -31.8784 | 91.1004 | 91.2836 | 91.1494 | -31.8084 | 0.024189 | -0.070237 | 20.008 | 0.11533 | 0.091138 | -0.31279 | -0.26 | -0.13569 | -0.23259 | -0.13916 | -0.20572 | -0.070031 | -0.049439 | -0.1836 | 122.9354 | 122.6929 | 122.7457 | 31.4451 | -122.9815 | 122.7731 | 122.9562 | 122.8221 | 31.5174 | -123.1414
479.6406 | 123.0927 | -31.5903 | 91.4154 | -0.0045023 | -0.0063932 | 0.0023975 | 0.053132 | -0.0028609 | 0.071445 | 0.0081646 | -3.8406e-05 | 4.695e-05 | 0.063877 | 0.010914 | 0.064752 | -11.1702 | -0.24584 | -31.4978 | 91.336 | 91.1026 | 91.16 | -31.676 | -31.7706 | -0.17821 | -31.796 | 91.1737 | 91.3568 | 91.2364 | -31.7305 | -0.085681 | -0.07938 | 20.4201 | 0.092448 | 0.17813 | -0.31276 | -0.2554 | -0.14024 | -0.24174 | -0.18035 | -0.2057 | -0.065453 | -0.058578 | -0.179 | 122.9263 | 122.6929 | 122.7503 | 31.3444 | -123.0914 | 122.7639 | 122.9471 | 122.8267 | 31.4121 | -123.1459
480.6406 | 123.2208 | -41.5192 | 81.3583 | -0.0045023 | -0.0068204 | 0.0023975 | 0.055269 | -0.0024337 | 0.073154 | 0.00053414 | -0.00025221 | -0.00016665 | 0.063877 | 0.010487 | 0.064538 | -11.7059 | -0.30536 | -34.8583 | 87.9251 | 87.5952 | 87.7581 | -35.1376 | -35.2871 | -0.22858 | -35.3536 | 87.6482 | 87.8771 | 87.6376 | -35.3249 | 6.3815 | 6.5668 | 29.8133 | 6.6609 | 0.27934 | 6.2368 | 6.3998 | 6.1943 | 6.2899 | 6.2321 | 6.1655 | -0.028739 | 6.5188 | 6.2793 | 129.4443 | 129.1144 | 129.2773 | 41.2138 | -116.496 | 129.1674 | 129.3963 | 129.1568 | 41.2906 | -116.6832
481.6406 | 123.1201 | -31.4896 | 91.5298 | 0.01076 | -0.0061794 | 0.0019701 | 0.053773 | -0.0022199 | 0.071445 | 0.0081646 | 0.00017519 | 0.00026075 | 0.06409 | 0.010914 | 0.064752 | -10.3873 | -0.30078 | -31.8916 | 90.8873 | 90.6676 | 90.7067 | -32.0377 | -32.1919 | -0.19653 | -32.2172 | 90.7341 | 90.9081 | 90.8289 | -32.1655 | -0.54812 | -0.6425 | 21.1022 | -0.40199 | 0.14613 | -0.8622 | -0.82312 | -0.67594 | -0.79571 | -0.7023 | -0.72765 | -0.051707 | -0.62172 | -0.70094 | 122.3769 | 122.1572 | 122.1963 | 31.1888 | -123.5675 | 122.2237 | 122.3977 | 122.3185 | 31.293 | -123.6953
482.6406 | 123.1247 | -73.7686 | 49.0448 | 0.0031287 | -0.0070342 | 0.0015427 | 0.076424 | -0.0020063 | 0.090247 | 0.015795 | -0.00046581 | -0.00038025 | 0.064304 | 0.010701 | 0.065393 | -9.8654 | -0.68996 | -62.9872 | 59.301 | 59.1097 | 59.2975 | -63.9207 | -63.7941 | -0.52619 | -63.8011 | 59.0967 | 59.3249 | 59.1541 | -63.9791 | 9.8479 | 10.2562 | 63.9032 | 10.7814 | 0.9335 | 10.0649 | 10.2527 | 9.7895 | 10.0519 | 9.9745 | 9.9675 | 0.17797 | 10.2801 | 10.1093 | 133.0697 | 132.8783 | 133.0661 | 73.0787 | -112.9655 | 132.8653 | 133.0935 | 132.9228 | 73.2424 | -113.0239
483.6406 | 123.0972 | -101.0605 | 21.9223 | -0.0045023 | -0.0074614 | 0.0011155 | 0.1057 | -0.0017927 | 0.11375 | 0.015795 | -0.00089301 | -0.00059405 | 0.063449 | 0.011128 | 0.065179 | -4.0829 | -1.1936 | -98.9725 | 22.5595 | 22.46 | 22.6 | -100.4972 | -100.1079 | -0.94285 | -100.1378 | 22.4093 | 22.5633 | 22.5574 | -100.5685 | 0.5633 | 0.63718 | 96.9776 | 2.088 | 1.5247 | 0.53768 | 0.67771 | 0.49203 | 0.48695 | 0.95262 | 0.92269 | 0.43066 | 0.64102 | 0.63507 | 123.62 | 123.5205 | 123.6605 | 99.8669 | -122.4195 | 123.4697 | 123.6238 | 123.6179 | 100.1176 | -122.4908
484.6406 | 123.1338 | -107.7713 | 15.2527 | -0.012133 | -0.0072478 | 0.0011155 | 0.11083 | -0.0013653 | 0.11781 | 0.023426 | -0.0011066 | -0.0010212 | 0.063663 | 0.010914 | 0.065179 | -3.8311 | -1.3768 | -105.5881 | 15.6507 | 15.5779 | 15.6909 | -107.3976 | -106.9393 | -1.0527 | -106.9875 | 15.5415 | 15.6679 | 15.6803 | -107.4733 | 0.37367 | 0.39801 | 103.9402 | 2.1832 | 1.8095 | 0.32517 | 0.43821 | 0.29799 | 0.28882 | 0.832 | 0.78376 | 0.48577 | 0.41526 | 0.42762 | 123.422 | 123.3492 | 123.4622 | 106.3945 | -122.6503 | 123.3128 | 123.4392 | 123.4516 | 106.7186 | -122.726
485.6406 | 123.1293 | -108.7372 | 14.3051 | -0.0045023 | -0.0076752 | 0.0011155 | 0.11211 | -0.0013653 | 0.11866 | 0.00053414 | -0.00067941 | -0.00059405 | 0.063236 | 0.011128 | 0.065606 | -3.6388 | -1.4958 | -106.6045 | 14.4237 | 14.369 | 14.4638 | -108.666 | -108.1435 | -1.0207 | -108.1917 | 14.3191 | 14.4455 | 14.4899 | -108.7187 | 0.071193 | 0.11857 | 105.0984 | 2.1327 | 2.0615 | 0.063909 | 0.15872 | 0.018436 | 0.013935 | 0.59368 | 0.54544 | 0.527 | 0.14035 | 0.18475 | 123.1609 | 123.1062 | 123.201 | 107.2414 | -122.9711 | 123.0562 | 123.1826 | 123.2271 | 107.7165 | -123.0239
486.6406 | 123.0927 | -110.8154 | 12.2269 | 0.0031287 | -0.0074614 | 0.0015427 | 0.11403 | -0.0011517 | 0.11973 | 0.0081646 | -0.0011066 | -0.00080765 | 0.063663 | 0.011128 | 0.065393 | -3.593 | -1.6286 | -108.4358 | 12.2123 | 12.2352 | 12.3302 | -110.7998 | -110.2634 | -1.094 | -110.3071 | 12.1809 | 12.3073 | 12.3379 | -110.8616 | 0.015662 | -0.014542 | 107.2224 | 2.3796 | 2.3639 | 0.008377 | 0.10334 | -0.046203 | -0.045976 | 0.55199 | 0.50832 | 0.55453 | 0.080386 | 0.11106 | 123.0278 | 123.0507 | 123.1456 | 109.1869 | -123.0266 | 122.9963 | 123.1227 | 123.1534 | 109.7215 | -123.0885
487.6406 | 123.0972 | -111.2549 | 11.8149 | 0.0031287 | -0.0074614 | 0.0015427 | 0.11531 | -0.00029708 | 0.12059 | 0.00053414 | -0.00089301 | -0.00038025 | 0.063449 | 0.010914 | 0.065606 | -3.4327 | -1.6652 | -108.1611 | 11.434 | 11.4568 | 11.5381 | -111.5873 | -111.0144 | -1.1352 | -111.0809 | 11.4025 | 11.5197 | 11.5641 | -111.6538 | -0.33246 | -0.38088 | 107.8221 | 3.0938 | 3.4262 | -0.35805 | -0.27677 | -0.39889 | -0.41233 | 0.24053 | 0.17398 | 0.57286 | -0.29514 | -0.25074 | 122.6889 | 122.7117 | 122.793 | 109.5897 | -123.4022 | 122.6574 | 122.7746 | 122.819 | 110.1197 | -123.4686
488.6406 | 123.0698 | -111.9644 | 11.087 | 0.01076 | -0.0078888 | 0.0011155 | 0.11745 | 0.0011987 | 0.12123 | 0.00053414 | -0.00089301 | -0.00059405 | 0.063236 | 0.010914 | 0.065393 | -2.6865 | -1.6057 | -106.3436 | 10.9624 | 10.976 | 11.0711 | -112.0636 | -111.4585 | -1.1809 | -111.5296 | 10.9218 | 11.0573 | 11.0925 | -112.1254 | -0.099135 | -0.12461 | 109.278 | 5.6209 | 5.72 | -0.11099 | -0.015946 | -0.16097 | -0.16523 | 0.50593 | 0.4348 | 0.59577 | -0.02974 | 0.005511 | 122.9268 | 122.9405 | 123.0355 | 110.3587 | -123.1506 | 122.8862 | 123.0217 | 123.057 | 110.7835 | -123.2124
489.6406 | 123.1979 | -112.4039 | 10.5331 | 0.0031287 | -0.0074614 | 0.0013291 | 0.11724 | 0.00013032 | 0.12144 | 0.00053414 | -0.0011066 | -0.0010212 | 0.063449 | 0.011128 | 0.06582 | -2.9245 | -1.4683 | -108.3122 | 10.4084 | 10.4266 | 10.5171 | -112.6039 | -111.985 | -1.2267 | -112.0562 | 10.3815 | 10.4941 | 10.5385 | -112.6794 | -0.2 | -0.1247 | 109.4793 | 4.0917 | 4.2917 | -0.10657 | -0.016063 | -0.27555 | -0.1516 | 0.41883 | 0.3477 | 0.62325 | -0.039014 | 0.005394 | 122.8123 | 122.8304 | 122.9209 | 110.9355 | -123.137 | 122.7854 | 122.898 | 122.9424 | 111.1771 | -123.2126
490.6406 | 123.111 | -113.0585 | 9.9838 | 0.0031287 | -0.0076752 | 0.0013291 | 0.11638 | -0.00072428 | 0.12166 | -0.014727 | -0.0011066 | -0.00059405 | 0.063449 | 0.011128 | 0.065179 | -2.8742 | -1.5324 | -110.2168 | 9.859 | 9.8863 | 9.9768 | -113.1625 | -112.4979 | -1.2908 | -112.569 | 9.8413 | 9.9447 | 10.0028 | -113.2197 | -0.10402 | -0.12479 | 110.1843 | 2.8417 | 2.9457 | -0.097569 | -0.007022 | -0.16125 | -0.14255 | 0.56062 | 0.48948 | 0.65074 | -0.039131 | 0.019014 | 122.9175 | 122.9447 | 123.0353 | 111.526 | -123.1463 | 122.8998 | 123.0032 | 123.0613 | 111.7676 | -123.2036
491.6406 | 123.2025 | -112.9486 | 10.0113 | -0.0045023 | -0.0074614 | 0.0013291 | 0.11702 | -0.00051068 | 0.12144 | 0.0081646 | -0.0011066 | -0.00059405 | 0.063236 | 0.011128 | 0.065393 | -2.9657 | -1.5507 | -109.7132 | 10.0605 | 9.9549 | 10.1783 | -112.8328 | -112.2506 | -1.3229 | -112.3401 | 10.0382 | 10.1645 | 10.1997 | -113.0228 | 0.1158 | 0.049192 | 109.9829 | 3.2354 | 3.1196 | -0.056351 | 0.16697 | -0.074227 | 0.026865 | 0.698 | 0.60855 | 0.68278 | 0.15318 | 0.18843 | 123.0091 | 122.9035 | 123.1269 | 111.3979 | -122.8441 | 122.9868 | 123.1131 | 123.1483 | 111.6257 | -123.0341
492.6406 | 123.111 | -112.294 | 10.7254 | 0.0031287 | -0.0074614 | 0.0013291 | 0.11638 | -8.3276e-05 | 0.12144 | 0.00053414 | -0.00089301 | -0.00059405 | 0.063449 | 0.011342 | 0.06582 | -2.7826 | -1.5416 | -108.8525 | 10.619 | 10.5136 | 10.7323 | -112.2788 | -111.6508 | -1.3366 | -111.7494 | 10.583 | 10.7139 | 10.7492 | -112.478 | 0.015245 | -0.10636 | 109.5114 | 3.4416 | 3.4263 | -0.21183 | 0.006871 | -0.18395 | -0.14241 | 0.64321 | 0.54461 | 0.72856 | -0.011502 | 0.023749 | 122.9131 | 122.8076 | 123.0263 | 110.7524 | -123.0042 | 122.877 | 123.0079 | 123.0432 | 110.9574 | -123.2034
493.6406 | 123.1888 | -112.0056 | 10.9039 | 0.01076 | -0.0074614 | 0.0011155 | 0.11681 | -0.00029708 | 0.12101 | 0.0081646 | -0.00067941 | -0.0010212 | 0.063663 | 0.011342 | 0.065606 | -2.7414 | -1.6652 | -108.1062 | 10.9853 | 10.8845 | 11.1031 | -111.8941 | -111.2067 | -1.3687 | -111.3373 | 10.963 | 11.0893 | 10.9186 | -112.0888 | 0.11148 | 0.081387 | 109.2642 | 3.8994 | 3.7879 | -0.019468 | 0.19921 | -0.083141 | 0.059082 | 0.79896 | 0.6683 | 0.75144 | 0.18542 | 0.014629 | 122.9909 | 122.8901 | 123.1088 | 110.3404 | -122.7981 | 122.9686 | 123.095 | 122.9242 | 110.6369 | -122.9927
494.6406 | 123.1293 | -112.7289 | 10.2356 | 0.0031287 | -0.0070342 | 0.0011155 | 0.11766 | 0.00034392 | 0.12166 | 0.00053414 | -0.00089301 | -0.00038025 | 0.063449 | 0.011128 | 0.065606 | -2.7094 | -1.7522 | -108.532 | 10.1933 | 10.0877 | 10.3019 | -112.7046 | -111.9621 | -1.4053 | -112.0836 | 10.148 | 10.2835 | 10.099 | -112.8946 | 0.024281 | -0.042339 | 110.0195 | 4.1969 | 4.1726 | -0.14787 | 0.066289 | -0.16575 | -0.087556 | 0.76674 | 0.64524 | 0.81098 | 0.047916 | -0.1366 | 122.9221 | 122.8166 | 123.0308 | 110.9767 | -122.9402 | 122.8769 | 123.0124 | 122.8279 | 111.3236 | -123.1302
495.6406 | 123.056 | -111.3876 | 11.6226 | 0.0031287 | -0.0072478 | 0.0013291 | 0.11681 | 0.00055772 | 0.12123 | -0.0070964 | -0.00089301 | -0.00059405 | 0.063663 | 0.011555 | 0.065606 | -2.7094 | -1.8621 | -106.751 | 11.5164 | 11.411 | 11.6205 | -111.3767 | -110.5702 | -1.4145 | -110.71 | 11.4941 | 11.6205 | 11.4405 | -111.553 | 0.010921 | -0.10621 | 108.6783 | 4.6366 | 4.6257 | -0.21158 | -0.002098 | -0.1654 | -0.1285 | 0.81742 | 0.6776 | 0.843 | -0.002156 | -0.1821 | 122.904 | 122.7987 | 123.0082 | 109.5255 | -122.9993 | 122.8818 | 123.0081 | 122.8282 | 109.9732 | -123.1757
496.6406 | 123.1888 | -112.4817 | 10.4736 | -0.0045023 | -0.0072478 | 0.0011155 | 0.11916 | 0.0011987 | 0.12208 | 0.0081646 | -0.00089301 | -0.00059405 | 0.063663 | 0.011342 | 0.065606 | -2.6819 | -1.9628 | -107.0715 | 10.4817 | 10.3762 | 10.5949 | -112.4024 | -111.5043 | -1.4511 | -111.6761 | 10.4502 | 10.5811 | 10.4103 | -112.6062 | 0.079297 | 0.008062 | 109.7998 | 5.4102 | 5.3309 | -0.097431 | 0.12128 | -0.12447 | -0.023412 | 0.97742 | 0.80555 | 0.93002 | 0.10749 | -0.063297 | 122.9634 | 122.8579 | 123.0766 | 110.5189 | -122.876 | 122.9319 | 123.0628 | 122.892 | 111.0306 | -123.0798
497.6406 | 123.2208 | -114.3814 | 8.5464 | 0.0031287 | -0.0074614 | 0.0017565 | 0.12066 | 0.0011987 | 0.12336 | 0.0081646 | -0.00089301 | -0.00059405 | 0.063663 | 0.011342 | 0.06582 | -2.7002 | -2.2009 | -108.4679 | 8.6046 | 8.4943 | 8.7177 | -114.2843 | -113.2488 | -1.5244 | -113.4939 | 8.573 | 8.6993 | 8.5194 | -114.4881 | 0.097079 | 0.058108 | 111.6812 | 5.9135 | 5.8165 | -0.052184 | 0.17124 | -0.10665 | 0.02659 | 1.1326 | 0.88752 | 0.99417 | 0.15287 | -0.027075 | 122.986 | 122.8757 | 123.0991 | 112.1805 | -122.8308 | 122.9544 | 123.0807 | 122.9008 | 112.8571 | -123.0345
498.6406 | 123.1659 | -116.1438 | 6.7886 | 0.018391 | -0.0078888 | 0.0011155 | 0.12258 | 0.0022669 | 0.12401 | 0.015795 | -0.0011066 | -0.00016665 | 0.063663 | 0.011342 | 0.066034 | -2.6865 | -2.3291 | -109.498 | 6.7915 | 6.6947 | 6.9137 | -116.1022 | -114.8788 | -1.5839 | -115.2246 | 6.7691 | 6.8816 | 6.72 | -116.283 | 0.041636 | 0.00288 | 113.4573 | 6.6458 | 6.6042 | -0.093888 | 0.12508 | -0.13915 | -0.019524 | 1.265 | 0.91916 | 1.0583 | 0.092975 | -0.068653 | 122.9353 | 122.8385 | 123.0575 | 113.8147 | -122.8908 | 122.9129 | 123.0254 | 122.8638 | 114.5599 | -123.0716
499.6406 | 123.1796 | -116.8762 | 6.0516 | 0.0031287 | -0.0083162 | 0.0013291 | 0.12472 | 0.0026943 | 0.12443 | 0.0081646 | -0.0011066 | -0.00080765 | 0.063449 | 0.011769 | 0.066247 | -2.6773 | -2.4527 | -109.3927 | 5.9949 | 5.8934 | 6.117 | -116.9081 | -115.5793 | -1.648 | -115.9618 | 5.9725 | 6.0941 | 5.9141 | -117.1026 | -0.031833 | -0.056761 | 114.1989 | 7.4835 | 7.5154 | -0.1582 | 0.065406 | -0.22634 | -0.079183 | 1.2969 | 0.91441 | 1.1407 | 0.042455 | -0.13749 | 122.8711 | 122.7697 | 122.9933 | 114.4235 | -122.9597 | 122.8487 | 122.9703 | 122.7904 | 115.2282 | -123.1542
500.6406 | 123.1338 | -117.1738 | 5.809 | -0.012133 | -0.0076752 | 0.0011155 | 0.12643 | 0.0050445 | 0.12529 | 0.0081646 | -0.00089301 | -0.00059405 | 0.063449 | 0.011555 | 0.066247 | -2.7185 | -2.5718 | -106.6457 | 5.537 | 5.431 | 5.6638 | -117.3659 | -115.6297 | -1.6709 | -116.3052 | 5.5146 | 5.6408 | 5.47 | -117.5604 | -0.19218 | -0.27199 | 114.4553 | 10.528 | 10.7202 | -0.37806 | -0.14526 | -0.38668 | -0.29442 | 1.5441 | 0.86855 | 1.2552 | -0.16821 | -0.339 | 122.7108 | 122.6047 | 122.8375 | 114.602 | -123.175 | 122.6884 | 122.8146 | 122.6438 | 115.5029 | -123.3695
501.6406 | 123.2071 | -117.0181 | 5.9097 | 0.01076 | -0.0078888 | 0.0011155 | 0.16232 | 0.045213 | 0.12486 | 0.00053414 | -0.00089301 | -0.00038025 | 0.063449 | 0.011555 | 0.066675 | -2.6956 | -1.5782 | -53.3912 | 5.8529 | 5.7606 | 5.9751 | -117.0454 | -114.8925 | -1.6754 | -115.8794 | 5.8351 | 5.9567 | 5.7859 | -117.2262 | -0.027294 | -0.056784 | 114.3225 | 63.627 | 63.6543 | -0.14908 | 0.065377 | -0.20806 | -0.074631 | 2.1256 | 1.1387 | 1.3468 | 0.047004 | -0.12378 | 122.8711 | 122.7788 | 122.9932 | 115.4399 | -122.9552 | 122.8532 | 122.9749 | 122.8041 | 115.3427 | -123.1359
502.6406 | 123.2071 | -115.7913 | 7.1411 | -0.0045023 | -0.0076752 | 0.0011155 | 0.17557 | 0.060597 | 0.12422 | 0.00053414 | -0.00067941 | -0.0010212 | 0.063449 | 0.012196 | 0.067102 | -2.5171 | -1.1845 | -31.1178 | 7.3913 | 7.2992 | 7.5181 | -115.4932 | -112.9283 | -1.6983 | -114.2036 | 7.3781 | 7.4997 | 7.3289 | -115.6877 | 0.29815 | 0.25017 | 113.2743 | 84.6735 | 84.3753 | 0.15805 | 0.37698 | 0.10361 | 0.23694 | 2.8631 | 1.5877 | 1.4841 | 0.35861 | 0.18782 | 123.1826 | 123.0905 | 123.3094 | 114.6069 | -122.6343 | 123.1694 | 123.291 | 123.1203 | 114.093 | -122.8288
503.6406 | 123.1155 | -118.1992 | 4.6921 | -0.012133 | -0.0076752 | 0.00068808 | 0.18668 | 0.069144 | 0.12593 | -0.0070964 | -0.0011066 | -0.00059405 | 0.063449 | 0.013051 | 0.067102 | -2.2698 | -1.1478 | -22.4649 | 4.7633 | 4.6663 | 4.8946 | -118.126 | -115.3779 | -1.7899 | -115.2567 | 4.7454 | 4.867 | 4.6917 | -118.3114 | 0.07311 | 0.071211 | 115.9293 | 95.7343 | 95.6612 | -0.025795 | 0.20248 | -0.11221 | 0.053338 | 2.8213 | 2.9425 | 3.0547 | 0.17495 | -0.000417 | 122.9624 | 122.8654 | 123.0937 | 117.0513 | -122.8181 | 122.9446 | 123.0662 | 122.8908 | 116.4092 | -123.0034
504.6406 | 123.1659 | -117.746 | 5.1773 | -0.0045023 | -0.0074614 | 0.0011155 | 0.19117 | 0.072349 | 0.12636 | 0.0081646 | -0.00089301 | -0.00080765 | 0.063449 | 0.016043 | 0.067102 | -2.0546 | -1.1661 | -18.5596 | 5.0517 | 4.9548 | 5.1647 | -117.8284 | -114.9978 | -1.8357 | -111.3465 | 5.0384 | 5.1601 | 4.9893 | -118.0275 | -0.082446 | -0.12558 | 115.6913 | 99.1864 | 99.2688 | -0.22255 | -0.012614 | -0.28151 | -0.13887 | 2.7481 | 6.3995 | 6.681 | -0.017251 | -0.18804 | 122.7977 | 122.7007 | 122.9107 | 116.5798 | -123.0057 | 122.7844 | 122.906 | 122.7352 | 115.9103 | -123.2048
505.6406 | 123.1338 | -118.7622 | 4.1977 | -0.0045023 | -0.0076752 | 0.0011155 | 0.19395 | 0.074058 | 0.12721 | 0.0081646 | -0.00067941 | -0.00059405 | 0.063663 | 0.014761 | 0.067102 | -1.7525 | -1.2073 | -16.7695 | 4.0994 | 4.0161 | 4.2352 | -118.7671 | -116.0189 | -1.8632 | -113.6954 | 4.0998 | 4.2123 | 4.0369 | -118.9753 | -0.00489 | -0.09827 | 117.0097 | 101.9927 | 101.9976 | -0.18162 | 0.037544 | -0.21309 | -0.097845 | 2.7433 | 5.0669 | 5.2799 | 0.014592 | -0.16077 | 122.8616 | 122.7783 | 122.9974 | 117.5549 | -122.9648 | 122.8621 | 122.9745 | 122.7991 | 116.899 | -123.173
506.6406 | 123.2162 | -118.8675 | 4.0421 | -0.012133 | -0.0078888 | 0.0011155 | 0.19545 | 0.075126 | 0.12721 | 0.0081646 | -0.00089301 | -0.00038025 | 0.063236 | 0.014547 | 0.068598 | -1.5007 | -1.1982 | -14.984 | 4.0216 | 3.9108 | 4.1345 | -118.8724 | -113.3174 | -2.0234 | -114.3867 | 3.9991 | 4.1207 | 3.9499 | -119.0623 | -0.004919 | -0.020463 | 117.3668 | 103.8835 | 103.8884 | -0.13129 | 0.092454 | -0.1948 | -0.042932 | 5.55 | 4.4808 | 4.6756 | 0.07866 | -0.092126 | 122.8891 | 122.7783 | 123.002 | 117.6693 | -122.9145 | 122.8666 | 122.9882 | 122.8174 | 116.8441 | -123.1043
507.6406 | 123.111 | -118.1442 | 4.8111 | 0.0031287 | -0.0078888 | 0.0013291 | 0.25378 | 0.07534 | 0.12721 | 0.0081646 | -0.0011066 | -0.00059405 | 0.063877 | 0.080999 | 0.066888 | -1.377 | -1.2211 | -13.6517 | 4.9006 | 4.8037 | 5.0273 | -117.9795 | -115.213 | -1.1535 | -26.0268 | 4.8965 | 5.009 | 4.8428 | -118.1465 | 0.1647 | 0.089544 | 116.7672 | 104.4925 | 104.3278 | -0.007445 | 0.21624 | -0.002305 | 0.08541 | 2.9312 | 92.1174 | 92.1197 | 0.19787 | 0.031659 | 123.0449 | 122.9479 | 123.1716 | 116.9231 | -122.7906 | 123.0407 | 123.1532 | 122.987 | 116.9908 | -122.9576
508.6406 | 123.175 | -119.1376 | 3.7903 | -0.0045023 | -0.0074614 | 0.0013291 | 0.24716 | 0.077049 | 0.12785 | -0.0070964 | -0.0013204 | -0.00038025 | 0.063663 | 0.071384 | 0.067102 | -1.2809 | -1.244 | -12.8093 | 3.724 | 3.6223 | 3.8506 | -119.17 | -116.1379 | -1.3595 | -40.5459 | 3.7198 | 3.8414 | 3.6661 | -119.337 | -0.032469 | -0.066288 | 117.8567 | 106.3283 | 106.3608 | -0.16799 | 0.060351 | -0.19945 | -0.07045 | 2.9996 | 78.5917 | 78.7911 | 0.051135 | -0.12423 | 122.8616 | 122.7599 | 122.9882 | 117.8936 | -122.9603 | 122.8574 | 122.979 | 122.8036 | 117.7781 | -123.1273
509.6406 | 123.1293 | -119.3436 | 3.5522 | 0.0031287 | -0.0081024 | 0.0011155 | 0.25271 | 0.07769 | 0.12828 | 0.0081646 | -0.0011066 | -0.00059405 | 0.063663 | 0.075657 | 0.067102 | -1.1252 | -1.2577 | -12.3286 | 3.3623 | 3.256 | 3.4798 | -119.5043 | -116.2616 | -1.2496 | -32.2676 | 3.3536 | 3.4797 | 3.2998 | -119.6896 | -0.16074 | -0.18994 | 118.2183 | 107.015 | 107.1757 | -0.29627 | -0.072479 | -0.34603 | -0.19869 | 3.082 | 87.076 | 87.422 | -0.072537 | -0.25248 | 122.7059 | 122.5995 | 122.8233 | 118.0859 | -123.0566 | 122.6971 | 122.8233 | 122.6433 | 118.0939 | -123.2418
510.6406 | 123.1659 | -119.5358 | 3.3737 | 0.0031287 | -0.0083162 | 0.0013291 | 0.26852 | 0.077904 | 0.12892 | 0.0081646 | -0.0011066 | -0.00038025 | 0.063449 | 0.091897 | 0.067529 | -1.0154 | -1.2989 | -12.0493 | 3.257 | 3.169 | 3.3928 | -119.5959 | -115.8037 | -1.0527 | -13.3483 | 3.2574 | 3.3836 | 3.2128 | -119.7812 | -0.060054 | -0.11672 | 118.5205 | 107.4865 | 107.5466 | -0.20474 | 0.019056 | -0.24534 | -0.11631 | 3.7321 | 106.1875 | 106.4328 | 0.00984 | -0.16095 | 122.7928 | 122.7048 | 122.9286 | 118.2369 | -122.9696 | 122.7932 | 122.9194 | 122.7486 | 118.4831 | -123.1549
511.6406 | 123.1384 | -119.6274 | 3.3005 | -0.0045023 | -0.0074614 | 0.00090168 | 0.26959 | 0.077904 | 0.12935 | -0.0070964 | -0.0011066 | -0.00016665 | 0.063663 | 0.092965 | 0.067743 | -0.98331 | -1.3676 | -12.3927 | 3.1517 | 3.0682 | 3.292 | -119.6966 | -115.8632 | -1.007 | -12.1808 | 3.1658 | 3.2828 | 3.0983 | -119.8865 | -0.069239 | -0.14878 | 118.6441 | 107.2347 | 107.304 | -0.23224 | -0.008431 | -0.2591 | -0.13464 | 3.7642 | 107.4466 | 107.7057 | -0.017647 | -0.20217 | 122.7791 | 122.6956 | 122.9194 | 118.2598 | -122.9971 | 122.7932 | 122.9102 | 122.7257 | 118.6204 | -123.187
512.6406 | 123.0652 | -119.696 | 3.1769 | 0.0031287 | -0.0076752 | 0.0015427 | 0.26959 | 0.077904 | 0.12999 | 0.00053414 | -0.0013204 | -0.00016665 | 0.06409 | 0.092965 | 0.067743 | -0.91463 | -1.4454 | -12.3102 | 3.0876 | 2.9904 | 3.2142 | -119.7699 | -115.8586 | -1.0527 | -12.7485 | 3.088 | 3.205 | 3.0388 | -119.9552 | -0.073837 | -0.089281 | 118.7814 | 107.3858 | 107.4596 | -0.18648 | 0.037328 | -0.25912 | -0.088879 | 3.8374 | 106.9475 | 107.2066 | 0.028112 | -0.13809 | 122.7836 | 122.6864 | 122.9103 | 118.2506 | -122.9468 | 122.784 | 122.901 | 122.7348 | 118.6433 | -123.132
513.6406 | 123.1018 | -119.7418 | 3.1403 | -0.0045023 | -0.0076752 | 0.00090168 | 0.27045 | 0.077904 | 0.12999 | 0.0081646 | -0.0011066 | -0.00016665 | 0.063877 | 0.092965 | 0.067957 | -0.92836 | -1.5141 | -12.5117 | 3.0143 | 2.9217 | 3.1455 | -119.8431 | -115.4053 | -1.0894 | -12.309 | 3.0239 | 3.1455 | 2.9655 | -120.0238 | -0.10132 | -0.12591 | 118.8135 | 107.2301 | 107.3314 | -0.21855 | 0.00527 | -0.28203 | -0.11636 | 4.3365 | 107.4328 | 107.7149 | 0.005212 | -0.17473 | 122.7562 | 122.6635 | 122.8873 | 118.2277 | -122.9834 | 122.7657 | 122.8873 | 122.7073 | 118.6524 | -123.1641
514.6406 | 123.1613 | -119.7556 | 3.1311 | 0.01076 | -0.0074614 | 0.0011155 | 0.27088 | 0.07769 | 0.13042 | 0.00053414 | -0.0013204 | -0.00016665 | 0.063877 | 0.093392 | 0.06817 | -0.91005 | -1.5645 | -12.5941 | 3.0006 | 2.9126 | 3.1318 | -119.8431 | -115.268 | -1.1077 | -11.8786 | 3.0056 | 3.118 | 2.9564 | -120.0376 | -0.08759 | -0.1305 | 118.8455 | 107.1615 | 107.249 | -0.21855 | 0.000689 | -0.28203 | -0.12552 | 4.4876 | 107.877 | 108.159 | -0.013105 | -0.17473 | 122.7562 | 122.6681 | 122.8873 | 118.1911 | -122.9742 | 122.7611 | 122.8736 | 122.7119 | 118.6479 | -123.1687
515.6406 | 123.1201 | -119.7876 | 3.1357 | 0.0031287 | -0.0076752 | 0.0013291 | 0.27301 | 0.077476 | 0.13106 | 0.00053414 | -0.00067941 | -0.00016665 | 0.063663 | 0.094033 | 0.069025 | -0.90547 | -1.6332 | -12.3789 | 2.9823 | 2.8851 | 3.1181 | -119.8615 | -113.9173 | -1.1168 | -11.0773 | 2.9873 | 3.118 | 2.9426 | -120.0467 | -0.073862 | -0.15339 | 118.8821 | 107.4087 | 107.4825 | -0.2506 | -0.017623 | -0.25914 | -0.14841 | 5.8703 | 108.7103 | 108.9694 | -0.017682 | -0.19305 | 122.7699 | 122.6727 | 122.9057 | 118.1544 | -122.9971 | 122.7749 | 122.9056 | 122.7302 | 118.6708 | -123.1824
516.6406 | 123.1476 | -119.9066 | 3.0029 | 0.01076 | -0.0078888 | 0.0013291 | 0.27258 | 0.077904 | 0.13127 | 0.015795 | -0.00089301 | -0.00038025 | 0.063663 | 0.09382 | 0.067957 | -0.80933 | -1.7201 | -12.356 | 2.8816 | 2.7843 | 3.0036 | -119.953 | -114.8742 | -1.1397 | -10.9766 | 2.8865 | 3.0081 | 2.8282 | -120.1566 | -0.046423 | -0.12136 | 119.0973 | 107.5506 | 107.597 | -0.21859 | 0.000663 | -0.25002 | -0.11638 | 5.0324 | 108.93 | 109.1801 | 0.005183 | -0.17476 | 122.7882 | 122.691 | 122.9102 | 118.1865 | -122.956 | 122.7932 | 122.9147 | 122.7348 | 118.7669 | -123.1596
517.6406 | 123.0972 | -119.9158 | 2.9663 | -0.0045023 | -0.0074614 | 0.0015427 | 0.27408 | 0.077476 | 0.13127 | 0.0081646 | -0.0011066 | -0.00038025 | 0.063877 | 0.094674 | 0.068811 | -0.69487 | -1.8163 | -11.8753 | 2.8404 | 2.7477 | 2.9715 | -119.9942 | -114.4667 | -1.1581 | -10.4775 | 2.8499 | 2.9623 | 2.7961 | -120.1887 | -0.078478 | -0.12594 | 119.2209 | 108.0405 | 108.1189 | -0.21859 | 0.005233 | -0.27291 | -0.11639 | 5.4491 | 109.4383 | 109.7112 | -0.003982 | -0.17019 | 122.7561 | 122.6635 | 122.8873 | 118.0995 | -122.9606 | 122.7657 | 122.8781 | 122.7119 | 118.7577 | -123.155
518.6406 | 123.1842 | -119.9432 | 2.9114 | 0.0031287 | -0.0074614 | 0.0013291 | 0.27365 | 0.077904 | 0.13191 | 0.00053414 | -0.00067941 | -0.00016665 | 0.063449 | 0.093392 | 0.069025 | -0.7727 | -1.885 | -11.9989 | 2.8175 | 2.7294 | 2.9441 | -120.0126 | -113.9447 | -1.1855 | -11.7321 | 2.8179 | 2.944 | 2.7778 | -120.2024 | -0.069328 | -0.093903 | 119.1705 | 107.9443 | 108.0136 | -0.18198 | 0.032694 | -0.25918 | -0.093507 | 5.9985 | 108.2112 | 108.4704 | 0.032635 | -0.13357 | 122.7607 | 122.6726 | 122.8873 | 118.0583 | -122.9239 | 122.7611 | 122.8872 | 122.721 | 118.7577 | -123.1138
519.6406 | 123.0789 | -119.9936 | 2.916 | -0.012133 | -0.0081024 | 0.0011155 | 0.27387 | 0.076408 | 0.13277 | 0.0081646 | -0.0013204 | -0.00038025 | 0.063877 | 0.09382 | 0.06988 | -0.74065 | -1.9949 | -13.8577 | 2.79 | 2.6973 | 2.9212 | -120.04 | -113.3266 | -1.2405 | -11.1323 | 2.7904 | 2.912 | 2.7412 | -120.2391 | -0.046447 | -0.12595 | 119.2529 | 106.1359 | 106.1823 | -0.21861 | 0.005223 | -0.24546 | -0.12556 | 6.667 | 108.8613 | 109.1068 | -0.003993 | -0.17478 | 122.7836 | 122.6909 | 122.9148 | 117.9987 | -122.956 | 122.784 | 122.9056 | 122.7348 | 118.7531 | -123.155
520.6406 | 123.1247 | -120.0165 | 2.8885 | 0.01076 | -0.0081024 | 0.0015427 | 0.27301 | 0.076194 | 0.13341 | 0.00053414 | -0.0013204 | -0.00016665 | 0.064304 | 0.094033 | 0.069666 | -0.59872 | -2.0864 | -14.4666 | 2.7671 | 2.6745 | 2.8891 | -120.0675 | -113.1847 | -1.2908 | -11.1689 | 2.7629 | 2.8891 | 2.7091 | -120.2574 | -0.051033 | -0.12138 | 119.4178 | 105.5499 | 105.6009 | -0.21404 | 0.000638 | -0.24089 | -0.12556 | 6.8318 | 108.8476 | 109.0885 | 0.00058 | -0.17936 | 122.7836 | 122.6909 | 122.9056 | 117.93 | -122.956 | 122.7794 | 122.9055 | 122.7256 | 118.7256 | -123.1459
521.6406 | 123.0743 | -119.9844 | 2.9343 | 0.01076 | -0.0078888 | 0.0015427 | 0.276 | 0.077263 | 0.13405 | 0.0081646 | -0.0011066 | 4.695e-05 | 0.063877 | 0.093606 | 0.070734 | -0.61246 | -2.2009 | -12.8825 | 2.7854 | 2.6973 | 2.912 | -120.0355 | -112.5253 | -1.213 | -11.1735 | 2.7858 | 2.9074 | 2.732 | -120.2391 | -0.051023 | -0.14884 | 119.372 | 107.1019 | 107.1529 | -0.23692 | -0.022244 | -0.25462 | -0.14844 | 7.4591 | 108.811 | 109.0656 | -0.026882 | -0.20225 | 122.7699 | 122.6818 | 122.8965 | 117.7835 | -122.9697 | 122.7703 | 122.8918 | 122.7165 | 118.7714 | -123.1733
522.6406 | 123.1155 | -119.8746 | 3.0075 | 0.01076 | -0.0078888 | 0.0011155 | 0.27771 | 0.077904 | 0.1349 | -0.0070964 | -0.00089301 | -0.00016665 | 0.06409 | 0.09382 | 0.071802 | -0.44763 | -2.2787 | -11.7883 | 2.7992 | 2.7111 | 2.9349 | -120.0171 | -110.5565 | -1.1947 | -10.9354 | 2.8087 | 2.9303 | 2.7503 | -120.2162 | -0.14257 | -0.20835 | 119.4269 | 108.0862 | 108.2288 | -0.29642 | -0.072593 | -0.34158 | -0.19879 | 9.3181 | 108.9392 | 109.2808 | -0.077231 | -0.25717 | 122.6737 | 122.5857 | 122.8095 | 117.5958 | -123.0247 | 122.6833 | 122.8048 | 122.6249 | 118.6799 | -123.2237
523.6406 | 123.0835 | -121.4859 | 1.3046 | 0.0031287 | -0.0078888 | 0.0013291 | 0.77132 | 0.077263 | 0.53873 | 0.0081646 | -0.00089301 | 4.695e-05 | 0.063877 | 0.092965 | 0.1265 | -0.31486 | -2.4069 | -12.0264 | 3.2524 | 3.1781 | 3.3241 | -119.4265 | -14.0373 | -1.0482 | -11.4436 | 3.2162 | 3.3469 | 3.341 | -119.7629 | 2.0594 | 1.9478 | 121.171 | 109.4595 | 107.4001 | 1.8735 | 2.0195 | 1.723 | 1.9116 | 107.4486 | 110.0423 | 108.3193 | 2.0423 | 2.0363 | 124.7383 | 124.664 | 124.81 | 119.079 | -120.7311 | 124.7021 | 124.8328 | 124.8269 | 120.4377 | -121.0675
524.6406 | 123.0927 | -111.3693 | 11.348 | -0.012133 | -0.0078888 | 0.0013291 | 0.016165 | -0.0028609 | 0.015892 | 0.015795 | -0.0013204 | 0.00047435 | 0.21023 | 0.087196 | 0.12393 | -0.021844 | -0.007751 | -0.026723 | 0.065863 | 0.023254 | 0.14655 | -0.09511 | -11.3038 | -0.96575 | -10.6149 | 11.6361 | 11.767 | 11.7839 | -111.26 | 111.2742 | -11.2821 | 111.3475 | 111.3426 | 0.068387 | -11.3247 | -11.2014 | 0.10933 | 0.28809 | 100.0655 | 100.7545 | 100.6451 | 0.41902 | 0.43595 | 111.4352 | 111.3926 | 111.5159 | 111.3616 | -11.4431 | 123.0054 | 123.1363 | 123.1532 | 110.4036 | -122.608
525.6406 | 123.0652 | -114.3311 | 8.519 | -0.0045023 | -0.0081024 | 0.0011155 | 0.01531 | -0.0026473 | 0.014397 | 0.0081646 | -0.0013204 | -0.00016665 | 0.21407 | 0.089546 | 0.12415 | -0.026423 | -0.003172 | -0.008409 | 0.065863 | 0.032411 | 0.13281 | -0.049321 | -10.6628 | -0.98406 | -10.7522 | 8.5273 | 8.6535 | 8.6796 | -114.4102 | 114.2817 | -8.4531 | 114.3046 | 114.3226 | 0.040912 | -8.4866 | -8.3862 | -0.079162 | 0.008271 | 103.6683 | 103.5788 | 103.658 | 0.13455 | 0.16064 | 114.3969 | 114.3635 | 114.4639 | 114.3279 | -8.5683 | 122.8583 | 122.9846 | 123.0107 | 113.347 | -122.9292
526.6406 | 123.0881 | -115.7135 | 7.132 | 0.01076 | -0.0078888 | 0.0013291 | 0.014669 | -0.0032883 | 0.014824 | 0.023426 | -0.00089301 | -0.00016665 | 0.22048 | 0.090615 | 0.12949 | -0.040158 | -0.003172 | -0.017566 | 0.029236 | 0.023254 | 0.13281 | -0.040163 | -10.5071 | -0.97949 | -10.7019 | 7.0896 | 7.2113 | 7.2419 | -115.8663 | 115.6733 | -7.1027 | 115.6733 | 115.6959 | 0.022597 | -7.1087 | -6.9991 | -0.15278 | -0.042352 | 105.2064 | 105.0116 | 105.1644 | 0.079312 | 0.10998 | 115.7427 | 115.7368 | 115.8463 | 115.7103 | -7.1721 | 122.8031 | 122.9248 | 122.9554 | 114.734 | -122.9982
527.6406 | 123.0515 | -120.8588 | 1.9821 | 0.0031287 | -0.0081024 | 0.0015427 | 0.014669 | -0.0028609 | 0.014397 | 0.023426 | -0.00089301 | -0.00016665 | 0.3226 | 0.092538 | 0.22371 | -0.026423 | -0.003172 | -0.003831 | 0.033814 | 0.023254 | 0.13281 | -0.026426 | -10.791 | -1.0207 | -11.6496 | 3.1521 | 3.324 | 3.254 | -119.6621 | 120.8323 | -1.9483 | 120.8323 | 120.8549 | 0.022595 | -1.9589 | -1.8493 | 1.1966 | 1.17 | 110.0678 | 109.2091 | 108.0125 | 1.3419 | 1.2719 | 120.8926 | 120.882 | 120.9916 | 120.8556 | -2.0085 | 124.0109 | 124.1828 | 124.1127 | 119.8381 | -121.6442
528.6406 | 123.1338 | -14.5889 | 108.0826 | -0.0045023 | -0.0076752 | 0.0013291 | 0.014669 | -0.0028609 | 0.01461 | 0.023426 | -3.8406e-05 | 0.0034656 | 0.13566 | 0.025017 | 0.13462 | -0.031001 | -0.003172 | -0.012988 | 0.024657 | 0.023254 | 0.12823 | -0.021847 | -4.0282 | -0.1599 | -2.5655 | 101.782 | 101.9929 | 102.0785 | -20.8055 | 14.5671 | -108.0579 | 14.5579 | 14.5759 | 0.008859 | -108.0593 | -107.9544 | -6.2165 | -6.3005 | 10.5607 | 12.0234 | 18.24 | -6.0897 | -6.004 | 14.6136 | 14.6122 | 14.7172 | 14.5858 | -108.1044 | 116.371 | 116.5818 | 116.6675 | 14.429 | -128.888
529.6406 | 123.0515 | -119.751 | 3.1082 | -0.0045023 | -0.0078888 | 0.0013291 | 0.014456 | -0.0028609 | 0.014183 | 0.0081646 | -0.0011066 | -0.00038025 | 0.26577 | 0.092538 | 0.17072 | -0.026423 | -0.003172 | -0.012988 | 0.024657 | 0.018675 | 0.12365 | -0.035584 | -10.8551 | -1.094 | -11.8465 | 3.761 | 3.933 | 3.84 | -119.1356 | 119.7154 | -3.0836 | 119.7246 | 119.738 | 0.022596 | -3.0895 | -2.9846 | 0.61542 | 0.65282 | 108.8959 | 107.9044 | 107.289 | 0.82478 | 0.73183 | 119.7756 | 119.7697 | 119.8746 | 119.7478 | -3.1438 | 123.512 | 123.684 | 123.591 | 118.657 | -122.2438
530.6406 | 123.1018 | -120.0806 | 2.8381 | 0.0031287 | -0.0081024 | 0.00068808 | 0.014669 | -0.0026473 | 0.014397 | 0.023426 | -0.0011066 | 4.695e-05 | 0.2459 | 0.093606 | 0.15107 | -0.021844 | 0.001407 | -0.012988 | 0.024657 | 0.027833 | 0.13739 | -0.035584 | -8.8221 | -1.1306 | -11.3795 | 2.6805 | 2.8067 | 2.8282 | -120.3077 | 120.045 | -2.8135 | 120.0587 | 120.0676 | 0.022596 | -2.8103 | -2.7007 | -0.22717 | -0.15762 | 111.2584 | 108.7011 | 108.9282 | -0.031481 | -0.009965 | 120.1052 | 120.1084 | 120.218 | 120.082 | -2.8737 | 122.7611 | 122.8872 | 122.9087 | 118.95 | -123.1459
531.6406 | 123.0835 | -120.4697 | 2.4399 | 0.0031287 | -0.0078888 | 0.00068808 | 0.014242 | -0.0024337 | 0.014397 | 0.015795 | -0.00089301 | 4.695e-05 | 0.24804 | 0.09382 | 0.15149 | -0.026423 | 0.010564 | -0.008409 | 0.024657 | 0.023254 | 0.13281 | -0.021847 | -8.085 | -1.0894 | -11.3246 | 2.1403 | 2.2572 | 2.2925 | -120.8618 | 120.4478 | -2.4152 | 120.4432 | 120.4613 | 0.013438 | -2.4166 | -2.3071 | -0.3921 | -0.29963 | 112.3847 | 109.1451 | 109.5372 | -0.18266 | -0.14741 | 120.4943 | 120.4929 | 120.6025 | 120.4802 | -2.4617 | 122.6099 | 122.7269 | 122.7621 | 119.3803 | -123.3017
532.6406 | 123.111 | -120.1813 | 2.6962 | 0.0031287 | -0.0081024 | 0.0011155 | 0.014456 | -0.0026473 | 0.014397 | 0.0081646 | -0.0011066 | -0.00016665 | 0.24847 | 0.09382 | 0.15256 | -0.031001 | -0.003172 | -0.008409 | 0.024657 | -0.013378 | 0.12365 | -0.031005 | -7.5538 | -1.0665 | -11.0453 | 2.4745 | 2.5915 | 2.6313 | -120.5184 | 120.1503 | -2.6716 | 120.1503 | 120.1729 | 0.022596 | -2.7096 | -2.5726 | -0.33709 | -0.22174 | 112.6274 | 109.136 | 109.4731 | -0.10477 | -0.064938 | 120.2059 | 120.1679 | 120.3049 | 120.1781 | -2.7272 | 122.6558 | 122.7727 | 122.8126 | 119.1148 | -123.2146
533.6406 | 123.0972 | -120.2133 | 2.6871 | 0.0031287 | -0.0078888 | 0.0011155 | 0.014456 | -0.0028609 | 0.014824 | 0.00053414 | -0.0013204 | -0.00016665 | 0.24825 | 0.09382 | 0.15214 | -0.031001 | 0.005985 | -0.012988 | 0.015501 | -0.013378 | 0.12823 | -0.031005 | -7.737 | -1.0711 | -10.8209 | 2.5569 | 2.6785 | 2.7045 | -120.4451 | 120.1823 | -2.6716 | 120.1823 | 120.2003 | 0.018017 | -2.7005 | -2.5588 | -0.23178 | -0.13018 | 112.4763 | 109.3924 | 109.6242 | -0.00862 | 0.017475 | 120.2288 | 120.1999 | 120.3415 | 120.2193 | -2.7181 | 122.7702 | 122.8918 | 122.9179 | 119.1423 | -123.1322
534.6406 | 122.9874 | -120.2911 | 2.6138 | 0.0031287 | -0.0078888 | 0.00090168 | 0.014669 | -0.0026473 | 0.01461 | 0.0081646 | -0.0011066 | -0.00038025 | 0.24868 | 0.09382 | 0.15235 | -0.021844 | 0.005985 | -0.012988 | 0.024657 | -0.017957 | 0.13281 | -0.026426 | -7.769 | -1.1168 | -10.8163 | 2.4699 | 2.5915 | 2.6267 | -120.5321 | 120.2647 | -2.5892 | 120.2693 | 120.2782 | 0.013438 | -2.6318 | -2.481 | -0.24096 | -0.14393 | 112.5221 | 109.4748 | 109.7158 | -0.022371 | 0.01288 | 120.3158 | 120.2732 | 120.4239 | 120.2971 | -2.6403 | 122.761 | 122.8826 | 122.9178 | 119.1743 | -123.1459
535.6406 | 123.0606 | -120.5795 | 2.3392 | -0.0045023 | -0.0081024 | 0.0011155 | 0.014456 | -0.0028609 | 0.015465 | 0.00053414 | -0.0011066 | 4.695e-05 | 0.25167 | 0.094461 | 0.15555 | -0.021844 | 0.010564 | -0.008409 | 0.015501 | -0.017957 | 0.12823 | -0.031005 | -7.7049 | -1.1809 | -10.711 | 2.241 | 2.3534 | 2.3886 | -120.7748 | 120.5485 | -2.3237 | 120.5577 | 120.5711 | 0.022596 | -2.3571 | -2.2109 | -0.19524 | -0.098193 | 112.8746 | 109.8685 | 110.0638 | 0.0142 | 0.049452 | 120.595 | 120.5616 | 120.7078 | 120.5901 | -2.3702 | 122.8205 | 122.9329 | 122.9682 | 119.3986 | -123.1139
536.6406 | 123.1064 | -120.5521 | 2.33 | 0.0031287 | -0.0081024 | 0.0013291 | 0.014456 | -0.0028609 | 0.015465 | -0.0070964 | -0.00089301 | 4.695e-05 | 0.24932 | 0.094247 | 0.1532 | -0.03558 | 0.005985 | -0.008409 | 0.029236 | -0.013378 | 0.12823 | -0.031005 | -7.6591 | -1.2222 | -10.6057 | 2.1311 | 2.2481 | 2.2833 | -120.8892 | 120.5211 | -2.3008 | 120.5165 | 120.5437 | 0.022596 | -2.3434 | -2.2018 | -0.33718 | -0.19892 | 112.8929 | 109.9464 | 110.2835 | -0.081952 | -0.046701 | 120.5813 | 120.5387 | 120.6803 | 120.558 | -2.361 | 122.6832 | 122.8001 | 122.8354 | 119.3299 | -123.2193
537.6406 | 123.0743 | -121.0373 | 1.8814 | -0.0045023 | -0.0081024 | 0.0011155 | 0.014242 | -0.0028609 | 0.015251 | -0.0070964 | -0.0011066 | -0.00038025 | 0.25018 | 0.094247 | 0.15385 | -0.021844 | -0.003172 | -0.008409 | 0.029236 | -0.017957 | 0.13281 | -0.031005 | -7.6774 | -1.3046 | -11.1918 | 1.7923 | 1.9092 | 1.9445 | -121.2327 | 121.0063 | -1.8522 | 121.0154 | 121.0289 | 0.022596 | -1.8994 | -1.7486 | -0.19536 | -0.089122 | 113.3598 | 109.8455 | 110.0409 | 0.027839 | 0.063091 | 121.0665 | 121.0193 | 121.1701 | 121.0341 | -1.9124 | 122.8296 | 122.9465 | 122.9818 | 119.7327 | -123.1141
538.6406 | 123.1293 | -121.2662 | 1.5793 | -0.0045023 | -0.0081024 | 0.0011155 | 0.014669 | -0.0028609 | 0.015251 | 0.00053414 | -0.0011066 | -0.00038025 | 0.25317 | 0.094461 | 0.15641 | -0.026423 | 0.001407 | -0.012988 | 0.024657 | -0.013378 | 0.11907 | -0.031005 | -7.6454 | -1.3778 | -10.9399 | 1.4764 | 1.5979 | 1.624 | -121.5486 | 121.2352 | -1.5546 | 121.2398 | 121.2532 | 0.018017 | -1.5927 | -1.4602 | -0.28242 | -0.10291 | 113.6208 | 110.3262 | 110.6086 | 0.018618 | 0.044712 | 121.2908 | 121.2528 | 121.3852 | 121.2676 | -1.6103 | 122.7425 | 122.8641 | 122.8902 | 119.8883 | -123.1279
539.6406 | 123.0789 | -121.5363 | 1.355 | 0.0031287 | -0.0081024 | 0.00068808 | 0.014456 | -0.0026473 | 0.015465 | 0.0081646 | -0.001534 | 4.695e-05 | 0.25424 | 0.094888 | 0.15662 | -0.021844 | 0.001407 | -0.003831 | 0.024657 | -0.017957 | 0.12823 | -0.026426 | -7.5676 | -1.4648 | -10.8529 | 1.2291 | 1.3507 | 1.3722 | -121.7958 | 121.5098 | -1.3303 | 121.5144 | 121.5324 | 0.022595 | -1.3729 | -1.2268 | -0.25959 | -0.12585 | 113.9687 | 110.6833 | 110.9429 | -0.004322 | 0.017194 | 121.5609 | 121.5183 | 121.6645 | 121.5377 | -1.3814 | 122.7654 | 122.8869 | 122.9084 | 120.0714 | -123.1508
540.6406 | 123.4451 | -121.6644 | 1.2222 | 0.0031287 | -0.0083162 | 0.0013291 | 0.014669 | -0.0030747 | 0.015465 | 0.0081646 | -0.00089301 | -0.00016665 | 0.25723 | 0.094888 | 0.16004 | -0.026423 | -0.003172 | -0.012988 | 0.020079 | -0.027115 | 0.13281 | -0.026426 | -7.7232 | -1.5427 | -11.0178 | 1.1605 | 1.2682 | 1.3035 | -121.8737 | 121.638 | -1.2022 | 121.638 | 121.6514 | 0.013438 | -1.2493 | -1.0894 | -0.20926 | -0.061775 | 113.9412 | 110.6466 | 110.8559 | 0.046015 | 0.081266 | 121.6845 | 121.6373 | 121.7972 | 121.6613 | -1.2487 | 122.8249 | 122.9327 | 122.9679 | 120.1218 | -123.0959
541.6406 | 123.1064 | -121.8338 | 1.0529 | -0.0045023 | -0.0081024 | 0.0011155 | 0.014883 | -0.0028609 | 0.015679 | -0.0070964 | -0.0011066 | 4.695e-05 | 0.25979 | 0.094247 | 0.16282 | -0.031001 | -0.003172 | -0.012988 | 0.029236 | -0.017957 | 0.12823 | -0.031005 | -7.6271 | -1.5747 | -11.8053 | 0.94984 | 1.0759 | 1.102 | -122.0706 | 121.8028 | -1.0236 | 121.8028 | 121.8208 | 0.018017 | -1.0708 | -0.92463 | -0.23678 | -0.10301 | 114.2067 | 110.0285 | 110.2653 | 0.023086 | 0.049181 | 121.863 | 121.8158 | 121.962 | 121.8306 | -1.0839 | 122.7836 | 122.9097 | 122.9358 | 120.2591 | -123.1234
542.6406 | 123.0652 | -121.907 | 1.0025 | 0.0031287 | -0.0081024 | 0.0011155 | 0.014456 | -0.0028609 | 0.015465 | 0.0081646 | -0.00067941 | -0.00016665 | 0.25808 | 0.094888 | 0.16111 | -0.03558 | 0.001407 | -0.008409 | 0.024657 | -0.013378 | 0.12365 | -0.031005 | -7.5264 | -1.6754 | -11.5306 | 0.86743 | 0.98437 | 0.81359 | -122.1759 | 121.876 | -0.97784 | 121.8715 | 121.8986 | 0.022596 | -1.0159 | -0.87885 | -0.26885 | -0.13507 | 114.3807 | 110.3764 | 110.6453 | -0.018132 | -0.18892 | 121.9317 | 121.8937 | 122.0307 | 121.9085 | -1.0335 | 122.7745 | 122.8914 | 122.7206 | 120.2316 | -123.1784
543.6406 | 123.024 | -122.0673 | 0.83313 | 0.01076 | -0.0081024 | 0.0013291 | 0.014242 | -0.0030747 | 0.015465 | 0.00053414 | -0.0013204 | 0.00026075 | 0.29141 | 0.094461 | 0.19572 | -0.026423 | -0.003172 | -0.017566 | 0.029236 | -0.013378 | 0.12823 | -0.003531 | -7.3844 | -1.7762 | -11.3978 | 0.96816 | 1.0805 | 0.90516 | -122.0019 | 122.0637 | -0.80389 | 122.0408 | 122.0497 | -0.014035 | -0.84651 | -0.7049 | 0.065365 | 0.13503 | 114.6829 | 110.6694 | 110.6041 | 0.24739 | 0.072027 | 122.0965 | 122.0539 | 122.1955 | 122.0641 | -0.83666 | 123.0354 | 123.1478 | 122.9724 | 120.2911 | -122.835
544.6406 | 123.1613 | -122.0535 | 0.82855 | 0.0031287 | -0.0078888 | 0.0011155 | 0.014242 | -0.0026473 | 0.015465 | 0.00053414 | -0.00089301 | -0.00016665 | 0.25723 | 0.094674 | 0.15961 | -0.031001 | 0.001407 | -0.003831 | 0.029236 | -0.022536 | 0.12365 | -0.021847 | -7.3112 | -1.8357 | -11.3062 | 0.69345 | 0.81496 | 0.64418 | -122.3453 | 122.0317 | -0.79932 | 122.0225 | 122.0497 | 0.018016 | -0.85109 | -0.7049 | -0.29178 | -0.1351 | 114.7424 | 110.7473 | 111.0391 | -0.01359 | -0.18438 | 122.0828 | 122.031 | 122.1772 | 122.0549 | -0.8504 | 122.747 | 122.8685 | 122.6977 | 120.2178 | -123.1739
545.6406 | 123.1155 | -122.0261 | 0.91095 | -0.012133 | -0.0085298 | 0.0013291 | 0.014883 | -0.0030747 | 0.015251 | 0.00053414 | -0.00067941 | -0.00016665 | 0.25808 | 0.094674 | 0.16047 | -0.031001 | 0.001407 | -0.008409 | 0.020079 | -0.022536 | 0.11907 | -0.026426 | -7.3569 | -1.9319 | -11.3612 | 0.73923 | 0.86075 | 0.67623 | -122.3087 | 121.9996 | -0.89087 | 121.9951 | 122.0177 | 0.018017 | -0.93349 | -0.79188 | -0.28261 | -0.17172 | 114.6691 | 110.6649 | 110.9475 | -0.050202 | -0.23472 | 122.0461 | 122.0035 | 122.1451 | 122.0275 | -0.93738 | 122.7653 | 122.8868 | 122.7023 | 120.0942 | -123.2196
546.6406 | 123.1476 | -122.0306 | 0.86975 | 0.0031287 | -0.0083162 | 0.0011155 | 0.014456 | -0.0028609 | 0.015465 | 0.0081646 | -0.0011066 | 0.00026075 | 0.26065 | 0.094888 | 0.16282 | -0.03558 | 0.001407 | -0.022144 | 0.024657 | -0.017957 | 0.12365 | -0.021847 | -7.2333 | -2.0234 | -11.2421 | 0.73465 | 0.85617 | 0.68538 | -122.3133 | 122.0088 | -0.84509 | 121.9951 | 122.0085 | -0.000297 | -0.88771 | -0.7461 | -0.28261 | -0.1351 | 114.7973 | 110.7885 | 111.0711 | -0.013582 | -0.18437 | 122.0553 | 122.0127 | 122.1543 | 122.032 | -0.8916 | 122.7653 | 122.8868 | 122.716 | 120.0072 | -123.183
547.6406 | 123.0972 | -122.0169 | 0.91095 | -0.0045023 | -0.0083162 | 0.0013291 | 0.014456 | -0.0030747 | 0.015038 | 0.00053414 | -0.00067941 | 4.695e-05 | 0.2615 | 0.094888 | 0.16453 | -0.031001 | -0.007751 | -0.022144 | 0.020079 | -0.022536 | 0.12365 | -0.026426 | -6.9128 | -2.1196 | -11.1964 | 0.73923 | 0.86533 | 0.68538 | -122.3087 | 121.9905 | -0.89087 | 121.9859 | 121.9948 | 0.004282 | -0.93349 | -0.7873 | -0.29177 | -0.17172 | 115.1041 | 110.8206 | 111.1123 | -0.045623 | -0.22557 | 122.037 | 121.9944 | 122.1406 | 122.0092 | -0.93738 | 122.7561 | 122.8822 | 122.7023 | 119.8973 | -123.2196
548.6406 | 123.1476 | -122.1497 | 0.75531 | -0.0045023 | -0.0078888 | 0.00068808 | 0.014242 | -0.0028609 | 0.015251 | 0.0081646 | -0.00089301 | 0.00026075 | 0.26812 | 0.095102 | 0.1703 | -0.026423 | 0.001407 | -0.017566 | 0.024657 | -0.017957 | 0.11449 | -0.017268 | -6.9174 | -2.202 | -10.9857 | 0.62477 | 0.75544 | 0.57092 | -122.4186 | 122.1324 | -0.73065 | 122.1232 | 122.1321 | -0.000298 | -0.77327 | -0.64082 | -0.26891 | -0.13054 | 115.2323 | 111.1639 | 111.4328 | 0.00013 | -0.18439 | 122.1743 | 122.1317 | 122.2642 | 122.1511 | -0.77258 | 122.7744 | 122.9051 | 122.7206 | 119.9477 | -123.1739
549.6406 | 123.0286 | -122.4426 | 0.50354 | -0.0045023 | -0.0074614 | 0.0011155 | 0.014883 | -0.0026473 | 0.015038 | -0.014727 | -0.00046581 | -0.00016665 | 0.25872 | 0.094888 | 0.16175 | -0.026423 | 0.001407 | -0.022144 | 0.024657 | -0.022536 | 0.12365 | -0.021847 | -7.0593 | -2.2615 | -11.0636 | 0.43247 | 0.56314 | 0.40609 | -122.6063 | 122.4208 | -0.47888 | 122.4162 | 122.4205 | -0.000297 | -0.52608 | -0.37989 | -0.16367 | -0.071066 | 115.3833 | 111.3791 | 111.5427 | 0.059599 | -0.097451 | 122.4673 | 122.4201 | 122.5663 | 122.444 | -0.52539 | 122.8751 | 123.0058 | 122.8487 | 120.1811 | -123.1098
550.6406 | 123.1476 | -122.3511 | 0.54474 | 0.01076 | -0.0083162 | 0.0011155 | 0.014242 | -0.0032883 | 0.015465 | 0.0081646 | -0.0013204 | -0.00016665 | 0.25979 | 0.095102 | 0.16303 | -0.031001 | 0.001407 | -0.022144 | 0.020079 | -0.022536 | 0.11907 | -0.031005 | -6.9998 | -2.3302 | -10.8529 | 0.40958 | 0.53567 | 0.35572 | -122.6384 | 122.3201 | -0.52466 | 122.3201 | 122.3289 | 0.008861 | -0.56727 | -0.42567 | -0.28728 | -0.13516 | 115.3513 | 111.4981 | 111.7854 | -0.009072 | -0.18901 | 122.3712 | 122.3285 | 122.4701 | 122.3525 | -0.57574 | 122.7607 | 122.8867 | 122.7068 | 120.0209 | -123.1831
551.6406 | 123.0652 | -122.3648 | 0.55847 | -0.0045023 | -0.0081024 | 0.0013291 | 0.014456 | -0.0026473 | 0.015038 | -0.0070964 | -0.0013204 | -0.00016665 | 0.26214 | 0.094888 | 0.16496 | -0.026423 | 0.005985 | -0.022144 | 0.015501 | -0.022536 | 0.12365 | -0.026426 | -6.9128 | -2.3714 | -10.8117 | 0.405 | 0.53567 | 0.35115 | -122.6384 | 122.3384 | -0.54297 | 122.3384 | 122.3427 | 0.004282 | -0.58101 | -0.43482 | -0.27354 | -0.15347 | 115.452 | 111.5531 | 111.8266 | -0.022805 | -0.20733 | 122.3803 | 122.3423 | 122.4885 | 122.3708 | -0.5849 | 122.7698 | 122.9005 | 122.716 | 119.9934 | -123.1968
552.6406 | 123.1522 | -122.3465 | 0.54932 | 0.0031287 | -0.0081024 | 0.0011155 | 0.014242 | -0.0024337 | 0.015251 | 0.00053414 | -0.00089301 | -0.00016665 | 0.26535 | 0.094888 | 0.16859 | -0.026423 | -0.003172 | -0.022144 | 0.024657 | -0.022536 | 0.12365 | -0.012689 | -6.8441 | -2.4813 | -10.9995 | 0.41416 | 0.52651 | 0.35115 | -122.6338 | 122.3338 | -0.52466 | 122.3201 | 122.3244 | -0.009455 | -0.57185 | -0.42566 | -0.28727 | -0.13516 | 115.5024 | 111.347 | 111.6343 | -0.022806 | -0.19817 | 122.3712 | 122.324 | 122.4701 | 122.3433 | -0.562 | 122.7607 | 122.873 | 122.6976 | 119.8652 | -123.1831
553.6406 | 123.0652 | -122.4152 | 0.50812 | 0.0031287 | -0.0081024 | 0.0011155 | 0.014669 | -0.0028609 | 0.015465 | 0.00053414 | -0.00067941 | 4.695e-05 | 0.29611 | 0.095315 | 0.197 | -0.026423 | 0.001407 | -0.022144 | 0.020079 | -0.027115 | 0.11907 | -0.017268 | -7.1784 | -2.5088 | -10.9399 | 0.43705 | 0.56314 | 0.58008 | -122.6017 | 122.3979 | -0.48804 | 122.3887 | 122.393 | -0.004876 | -0.53523 | -0.38904 | -0.18656 | -0.071066 | 115.2368 | 111.4752 | 111.6618 | 0.055021 | 0.071958 | 122.4352 | 122.388 | 122.5342 | 122.4166 | -0.52539 | 122.8522 | 122.9783 | 122.9952 | 119.9064 | -123.1098
554.6406 | 123.0789 | -122.4564 | 0.46692 | 0.0031287 | -0.0083162 | 0.0013291 | 0.014456 | -0.0026473 | 0.015465 | 0.00053414 | -0.0011066 | 0.00047435 | 0.2615 | 0.095315 | 0.16367 | -0.031001 | -0.003172 | -0.022144 | 0.015501 | -0.027115 | 0.12365 | -0.017268 | -6.4137 | -2.582 | -10.8942 | 0.32717 | 0.44867 | 0.47935 | -122.7253 | 122.4391 | -0.45142 | 122.4254 | 122.4342 | -0.004876 | -0.49403 | -0.34327 | -0.26899 | -0.13975 | 116.0426 | 111.5622 | 111.8312 | -0.018245 | 0.012428 | 122.4719 | 122.4292 | 122.58 | 122.4532 | -0.48419 | 122.7835 | 122.905 | 122.9357 | 119.8743 | -123.1923
555.6406 | 122.9828 | -120.8679 | 2.0737 | 0.0031287 | -0.0085298 | 0.0011155 | 0.014242 | -0.0028609 | 0.015251 | 0.015795 | -0.00089301 | 0.0017564 | 1.8404 | 0.083136 | 1.7466 | -0.03558 | -0.007751 | -0.022144 | 0.020079 | -0.017957 | 0.12365 | -0.00811 | -6.9494 | -2.3165 | -9.5709 | 15.1981 | 15.233 | 15.3644 | -107.3543 | 120.8598 | -2.0536 | 120.8323 | 120.8458 | -0.014034 | -2.0916 | -1.95 | 13.5137 | 13.1245 | 113.9185 | 111.297 | 97.7833 | 13.1593 | 13.2907 | 120.888 | 120.85 | 120.9916 | 120.8602 | -2.0818 | 136.066 | 136.1009 | 136.2323 | 118.5515 | -109.4279
556.6406 | 123.0972 | -61.4594 | 61.3724 | -0.012133 | -0.0083162 | 0.0013291 | 0.013815 | -0.0028609 | 0.015038 | -0.0070964 | -0.00089301 | -0.00038025 | 0.014738 | 0.01241 | 0.017962 | -0.031001 | -0.003172 | -0.026723 | 0.020079 | -0.022536 | 0.11907 | -0.00811 | -0.00811 | -0.040849 | -0.019721 | -0.029954 | 0.091543 | 0.12679 | -0.22367 | 61.4512 | -61.3523 | 61.4283 | 61.4326 | -0.018613 | -61.3949 | -61.2533 | 61.2357 | -61.4023 | 61.4512 | 61.4396 | 0.20395 | -61.2808 | -61.2456 | 61.4794 | 61.4368 | 61.5784 | 61.4562 | -61.3805 | 61.4294 | 61.5509 | 61.5861 | 61.4185 | -61.596
557.6406 | 123.0972 | -61.441 | 61.3815 | -0.0045023 | -0.0078888 | 0.00090168 | 0.014242 | -0.0030747 | 0.015465 | -0.0070964 | -0.0011066 | -0.00038025 | 0.014097 | 0.01241 | 0.017535 | -0.03558 | -0.003172 | -0.035879 | 0.024657 | -0.027115 | 0.11907 | -0.012689 | -0.00811 | -0.045428 | -0.015143 | -0.020797 | 0.082386 | 0.11306 | -0.20078 | 61.4284 | -61.3569 | 61.4055 | 61.4052 | -0.02319 | -61.4086 | -61.2625 | 61.2403 | -61.4023 | 61.4329 | 61.4259 | 0.18564 | -61.2991 | -61.2685 | 61.4657 | 61.4139 | 61.5601 | 61.4379 | -61.3942 | 61.4202 | 61.5234 | 61.5541 | 61.3956 | -61.5823
558.6406 | 123.0972 | -61.4456 | 61.4319 | -0.0045023 | -0.0083162 | 0.0011155 | 0.014242 | -0.0026473 | 0.015465 | 0.00053414 | -0.00089301 | -0.00038025 | 0.01431 | 0.012624 | 0.017321 | -0.031001 | -0.003172 | -0.026723 | 0.020079 | -0.017957 | 0.12365 | -0.00811 | -0.021846 | -0.031692 | -0.015143 | -0.034533 | 0.091543 | 0.12222 | -0.1962 | 61.4375 | -61.4118 | 61.4146 | 61.4189 | -0.018613 | -61.4498 | -61.3082 | 61.2494 | -61.4664 | 61.4238 | 61.4305 | 0.18106 | -61.3403 | -61.3097 | 61.4657 | 61.4277 | 61.5693 | 61.4424 | -61.44 | 61.4111 | 61.5372 | 61.5678 | 61.4139 | -61.6281
559.6406 | 123.1293 | -61.409 | 61.4273 | 0.0031287 | -0.0083162 | 0.0013291 | 0.014456 | -0.0028609 | 0.015251 | 0.0081646 | -0.00089301 | -0.00059405 | 0.014097 | 0.01241 | 0.017321 | -0.03558 | 0.001407 | -0.031301 | 0.015501 | -0.027115 | 0.12823 | -0.012689 | -0.026425 | -0.031692 | -0.015143 | -0.025376 | 0.082386 | 0.12222 | -0.19162 | 61.3963 | -61.4118 | 61.3734 | 61.3777 | -0.018612 | -61.4544 | -61.2991 | 61.2174 | -61.4527 | 61.3826 | 61.3939 | 0.17648 | -61.3449 | -61.3051 | 61.4245 | 61.3819 | 61.5372 | 61.4104 | -61.44 | 61.3836 | 61.4914 | 61.5312 | 61.3773 | -61.6189
560.6406 | 123.111 | -61.4365 | 61.4273 | -0.012133 | -0.0087436 | 0.00090168 | 0.014456 | -0.0030747 | 0.015251 | 0.00053414 | -0.00089301 | -0.00038025 | 0.01431 | 0.012624 | 0.017321 | -0.031001 | -0.012329 | -0.031301 | 0.015501 | -0.022536 | 0.12365 | -0.017268 | -0.026425 | -0.036271 | -0.010564 | -0.029954 | 0.077807 | 0.12679 | -0.18246 | 61.4192 | -61.4118 | 61.4055 | 61.4052 | -0.014033 | -61.4498 | -61.3037 | 61.254 | -61.4573 | 61.41 | 61.4259 | 0.1719 | -61.3495 | -61.3005 | 61.452 | 61.4139 | 61.5601 | 61.4241 | -61.4446 | 61.4065 | 61.5143 | 61.5633 | 61.4002 | -61.6098
561.6406 | 123.1567 | -61.4319 | 61.4365 | -0.0045023 | -0.0085298 | 0.00090168 | 0.014456 | -0.0028609 | 0.015251 | 0.0081646 | -0.00089301 | -0.00038025 | 0.01431 | 0.01241 | 0.017535 | -0.031001 | -0.007751 | -0.026723 | 0.024657 | -0.013378 | 0.12365 | -0.012689 | -0.021846 | -0.036271 | -0.015143 | -0.025376 | 0.086964 | 0.11306 | -0.17788 | 61.4192 | -61.4118 | 61.4009 | 61.4052 | -0.014034 | -61.4498 | -61.3128 | 61.254 | -61.4618 | 61.41 | 61.4167 | 0.16274 | -61.3495 | -61.3234 | 61.4565 | 61.4185 | 61.5555 | 61.4241 | -61.4492 | 61.4065 | 61.5188 | 61.5449 | 61.3956 | -61.6143
562.6406 | 123.1384 | -61.4227 | 61.4456 | -0.0045023 | -0.0085298 | 0.00090168 | 0.014028 | -0.0030747 | 0.015465 | 0.0081646 | -0.00089301 | -0.00080765 | 0.014097 | 0.012624 | 0.017321 | -0.03558 | -0.012329 | -0.031301 | 0.020079 | -0.022536 | 0.11907 | -0.017268 | -0.026425 | -0.027113 | -0.010564 | -0.034533 | 0.086964 | 0.12222 | -0.17788 | 61.4055 | -61.4255 | 61.3871 | 61.3914 | -0.014033 | -61.4682 | -61.3265 | 61.2448 | -61.4802 | 61.3963 | 61.4122 | 0.16732 | -61.3587 | -61.3234 | 61.4428 | 61.4002 | 61.5418 | 61.4104 | -61.4629 | 61.3882 | 61.5097 | 61.5449 | 61.3956 | -61.6235
563.6406 | 123.1659 | -61.4227 | 61.4273 | -0.0045023 | -0.0083162 | 0.0013291 | 0.014028 | -0.0030747 | 0.015251 | 0.00053414 | -0.00089301 | -0.00038025 | 0.014097 | 0.012838 | 0.017748 | -0.040158 | -0.007751 | -0.031301 | 0.024657 | -0.027115 | 0.12365 | -0.017268 | -0.021846 | -0.031692 | -0.015143 | -0.029954 | 0.082386 | 0.11306 | -0.16873 | 61.4055 | -61.4027 | 61.3826 | 61.3914 | -0.014033 | -61.4544 | -61.3037 | 61.254 | -61.4573 | 61.4009 | 61.4076 | 0.15358 | -61.3449 | -61.3142 | 61.4474 | 61.3956 | 61.5464 | 61.415 | -61.4446 | 61.3928 | 61.5051 | 61.5358 | 61.391 | -61.596
564.6406 | 123.143 | -61.4319 | 61.441 | 0.0031287 | -0.0081024 | 0.0015427 | 0.014242 | -0.0028609 | 0.015251 | -0.0070964 | -0.00067941 | -0.00059405 | 0.013883 | 0.012196 | 0.017321 | -0.03558 | -0.007751 | -0.022144 | 0.024657 | -0.017957 | 0.11449 | -0.017268 | -0.031003 | -0.027113 | -0.019721 | -0.029954 | 0.086964 | 0.11306 | -0.16873 | 61.4146 | -61.4164 | 61.3963 | 61.4097 | -0.004876 | -61.459 | -61.3265 | 61.2632 | -61.471 | 61.4009 | 61.4122 | 0.14901 | -61.3541 | -61.328 | 61.4565 | 61.4139 | 61.5464 | 61.4241 | -61.4583 | 61.4019 | 61.5188 | 61.5449 | 61.4048 | -61.6098
565.6406 | 122.9782 | -61.4273 | 61.441 | -0.0045023 | -0.0081024 | 0.0011155 | 0.014242 | -0.0030747 | 0.015465 | -0.022357 | -0.00089301 | -0.00059405 | 0.014097 | 0.01241 | 0.017107 | -0.031001 | -0.007751 | -0.031301 | 0.020079 | -0.022536 | 0.12365 | -0.021847 | -0.031003 | -0.027113 | -0.0243 | -0.034533 | 0.096121 | 0.12222 | -0.16873 | 61.4055 | -61.421 | 61.3963 | 61.396 | -0.009454 | -61.4636 | -61.3174 | 61.2586 | -61.4756 | 61.3963 | 61.403 | 0.14443 | -61.3449 | -61.3188 | 61.4474 | 61.4048 | 61.551 | 61.4196 | -61.4629 | 61.3928 | 61.5234 | 61.5495 | 61.4002 | -61.6098
566.6406 | 123.1522 | -61.4273 | 61.4685 | 0.0031287 | -0.0085298 | 0.0015427 | 0.014456 | -0.0028609 | 0.015038 | 0.00053414 | -0.00067941 | -0.00038025 | 0.013669 | 0.012624 | 0.017321 | -0.044736 | -0.012329 | -0.035879 | 0.015501 | -0.027115 | 0.12365 | -0.017268 | -0.026425 | -0.022535 | -0.0243 | -0.039111 | 0.096121 | 0.12222 | -0.16873 | 61.41 | -61.453 | 61.3826 | 61.3914 | -0.018611 | -61.4956 | -61.3449 | 61.2586 | -61.5076 | 61.4009 | 61.403 | 0.14443 | -61.3724 | -61.3463 | 61.4428 | 61.4002 | 61.551 | 61.415 | -61.4858 | 61.3882 | 61.5234 | 61.5495 | 61.4048 | -61.6372
567.6406 | 123.1567 | -61.4182 | 61.4456 | -0.0045023 | -0.0083162 | 0.0015427 | 0.014028 | -0.0028609 | 0.015038 | 0.00053414 | -0.00067941 | -0.00080765 | 0.014097 | 0.012624 | 0.017321 | -0.031001 | -0.016908 | -0.035879 | 0.015501 | -0.013378 | 0.12365 | -0.012689 | -0.031003 | -0.031692 | -0.015143 | -0.034533 | 0.091543 | 0.016908 | -0.16873 | 61.4055 | -61.4301 | 61.3872 | 61.3823 | -0.02319 | -61.459 | -61.322 | 61.2494 | -61.4802 | 61.3871 | 61.403 | 0.15358 | -61.3541 | -61.4287 | 61.4337 | 61.4048 | 61.5418 | 61.4012 | -61.4583 | 61.3836 | 61.5097 | 61.4351 | 61.3865 | -61.6143
568.6406 | 123.1613 | -61.409 | 61.4456 | 0.0031287 | -0.0081024 | 0.0013291 | 0.014456 | -0.0028609 | 0.015038 | 0.00053414 | -0.0011066 | -0.00059405 | 0.01431 | 0.012838 | 0.017107 | -0.040158 | -0.012329 | -0.035879 | 0.020079 | -0.022536 | 0.11907 | -0.021847 | -0.021846 | -0.031692 | -0.019721 | -0.034533 | 0.082386 | 0.016908 | -0.16415 | 61.3871 | -61.4255 | 61.3688 | 61.3731 | -0.014032 | -61.4682 | -61.3265 | 61.2448 | -61.4802 | 61.3872 | 61.3893 | 0.14443 | -61.3632 | -61.4287 | 61.4291 | 61.3865 | 61.5281 | 61.3967 | -61.4675 | 61.3745 | 61.4914 | 61.4259 | 61.3773 | -61.6098
569.6406 | 123.0148 | -61.4639 | 61.4456 | -0.012133 | -0.0083162 | 0.00068808 | 0.014028 | -0.0032883 | 0.015251 | 0.00053414 | -0.0011066 | -0.00059405 | 0.01431 | 0.012624 | 0.017535 | -0.03558 | -0.016908 | -0.026723 | 0.024657 | -0.017957 | 0.12365 | -0.012689 | -0.026425 | -0.027113 | -0.0243 | -0.029954 | 0.096121 | 0.021486 | -0.16873 | 61.4512 | -61.421 | 61.4283 | 61.4372 | -0.014034 | -61.4636 | -61.322 | 61.2952 | -61.4756 | 61.4375 | 61.4396 | 0.14443 | -61.3495 | -61.4241 | 61.4886 | 61.446 | 61.5876 | 61.447 | -61.4583 | 61.434 | 61.56 | 61.4854 | 61.4368 | -61.6143
570.6406 | 123.1659 | -61.4227 | 61.4639 | -0.0045023 | -0.0083162 | 0.00090168 | 0.014242 | -0.0030747 | 0.015038 | -0.0070964 | -0.00067941 | -0.00038025 | 0.014738 | 0.012838 | 0.017321 | -0.026423 | -0.012329 | -0.031301 | 0.015501 | -0.017957 | 0.11907 | -0.026426 | -0.031003 | -0.022535 | -0.0243 | -0.034533 | 0.091543 | 0.026065 | -0.16415 | 61.3963 | -61.4484 | 61.3963 | 61.3914 | -0.004875 | -61.4819 | -61.3449 | 61.2586 | -61.4985 | 61.3917 | 61.3984 | 0.13985 | -61.3724 | -61.4379 | 61.4382 | 61.4048 | 61.5418 | 61.4104 | -61.4904 | 61.3882 | 61.5143 | 61.4488 | 61.4002 | -61.6281
571.6406 | 122.9095 | -61.4639 | 61.4777 | -0.012133 | -0.0087436 | 0.0011155 | 0.013815 | -0.0028609 | 0.015465 | 0.00053414 | -0.0011066 | -0.00080765 | 0.01431 | 0.012838 | 0.017321 | -0.031001 | -0.016908 | -0.035879 | 0.015501 | -0.017957 | 0.12365 | -0.012689 | -0.035582 | -0.031692 | -0.028879 | -0.029954 | 0.096121 | 0.016908 | -0.16873 | 61.4512 | -61.4622 | 61.4329 | 61.428 | -0.02319 | -61.4956 | -61.354 | 61.2952 | -61.5076 | 61.4283 | 61.435 | 0.13985 | -61.3815 | -61.4608 | 61.4794 | 61.446 | 61.5876 | 61.447 | -61.4903 | 61.434 | 61.56 | 61.4808 | 61.4322 | -61.6464
572.6406 | 123.1979 | -61.4502 | 61.4456 | -0.0045023 | -0.0078888 | 0.0011155 | 0.014242 | -0.0028609 | 0.015251 | -0.0070964 | -0.00046581 | -0.00059405 | 0.014097 | 0.012838 | 0.017535 | -0.040158 | -0.016908 | -0.031301 | 0.020079 | -0.022536 | 0.11907 | -0.017268 | -0.035582 | -0.027113 | -0.028879 | -0.029954 | 0.086964 | 0.016908 | -0.16873 | 61.4329 | -61.4255 | 61.41 | 61.4189 | -0.014033 | -61.4682 | -61.3265 | 61.2815 | -61.4756 | 61.4146 | 61.4213 | 0.13985 | -61.3587 | -61.4287 | 61.4703 | 61.4277 | 61.5693 | 61.4333 | -61.4629 | 61.4202 | 61.5372 | 61.4671 | 61.4231 | -61.6143
573.6406 | 122.8912 | -61.4639 | 61.4868 | -0.0045023 | -0.0087436 | 0.0011155 | 0.013815 | -0.0028609 | 0.015465 | 0.0081646 | -0.00067941 | -0.00059405 | 0.01431 | 0.012838 | 0.017321 | -0.03558 | -0.012329 | -0.040457 | 0.024657 | -0.017957 | 0.12365 | -0.017268 | -0.035582 | -0.027113 | -0.0243 | -0.029954 | 0.091543 | 0.021486 | -0.15957 | 61.4467 | -61.4622 | 61.4283 | 61.4235 | -0.023189 | -61.5048 | -61.3632 | 61.3044 | -61.5168 | 61.4283 | 61.4396 | 0.13527 | -61.3953 | -61.4653 | 61.4886 | 61.446 | 61.5876 | 61.4516 | -61.5041 | 61.434 | 61.5555 | 61.4854 | 61.4368 | -61.6464
574.6406 | 123.1659 | -61.4273 | 61.4365 | -0.012133 | -0.0085298 | 0.0013291 | 0.014242 | -0.0026473 | 0.015251 | 0.00053414 | -0.0011066 | -0.00038025 | 0.01431 | 0.012838 | 0.017107 | -0.040158 | -0.016908 | -0.045036 | 0.015501 | -0.022536 | 0.11907 | -0.017268 | -0.035582 | -0.036271 | -0.033458 | -0.034533 | 0.091543 | 0.021486 | -0.16415 | 61.41 | -61.421 | 61.3871 | 61.3823 | -0.027768 | -61.459 | -61.3174 | 61.2632 | -61.471 | 61.3917 | 61.3938 | 0.13069 | -61.3449 | -61.415 | 61.4428 | 61.4048 | 61.5464 | 61.4104 | -61.4537 | 61.3928 | 61.5189 | 61.4488 | 61.391 | -61.6006
575.6406 | 122.6852 | -61.4822 | 61.5143 | -0.012133 | -0.0083162 | 0.0011155 | 0.014456 | -0.0030747 | 0.015251 | 0.00053414 | -0.00089301 | -0.00038025 | 0.01431 | 0.012624 | 0.017107 | -0.044736 | -0.021486 | -0.035879 | 0.020079 | -0.027115 | 0.12365 | -0.021847 | -0.035582 | -0.027113 | -0.0243 | -0.029954 | 0.086964 | 0.016908 | -0.16873 | 61.4604 | -61.4942 | 61.4375 | 61.4464 | -0.014032 | -61.5414 | -61.3906 | 61.3135 | -61.5442 | 61.4467 | 61.4579 | 0.14443 | -61.4273 | -61.4974 | 61.5023 | 61.4551 | 61.6059 | 61.4608 | -61.5361 | 61.4523 | 61.5692 | 61.4991 | 61.4551 | -61.683
576.6406 | 123.111 | -61.4456 | 61.4639 | -0.0045023 | -0.0089572 | 0.0011155 | 0.014242 | -0.0028609 | 0.015038 | 0.00053414 | -0.0013204 | -0.00059405 | 0.01431 | 0.01241 | 0.017535 | -0.044736 | -0.016908 | -0.045036 | 0.020079 | -0.022536 | 0.12365 | -0.021847 | -0.035582 | -0.031692 | -0.033458 | -0.034533 | 0.086964 | 0.026065 | -0.16873 | 61.4238 | -61.4438 | 61.4009 | 61.4006 | -0.023189 | -61.4865 | -61.3403 | 61.2769 | -61.4985 | 61.41 | 61.4122 | 0.13527 | -61.377 | -61.4379 | 61.4657 | 61.4231 | 61.5693 | 61.4287 | -61.4858 | 61.4111 | 61.5326 | 61.4717 | 61.4139 | -61.6327
577.6406 | 122.7905 | -61.4777 | 61.4822 | 0.0031287 | -0.0085298 | 0.0013291 | 0.014242 | -0.0030747 | 0.015465 | 0.00053414 | -0.00089301 | -0.00038025 | 0.01431 | 0.013051 | 0.017321 | -0.040158 | -0.021486 | -0.049614 | 0.020079 | -0.022536 | 0.12365 | -0.00811 | -0.031003 | -0.027113 | -0.0243 | -0.034533 | 0.086964 | 0.016908 | -0.15957 | 61.4696 | -61.4622 | 61.4375 | 61.428 | -0.041504 | -61.5048 | -61.3586 | 61.3181 | -61.5168 | 61.4467 | 61.4534 | 0.13527 | -61.3953 | -61.4653 | 61.4977 | 61.4551 | 61.6013 | 61.4562 | -61.4903 | 61.4431 | 61.5646 | 61.4946 | 61.4505 | -61.6418
578.6406 | 122.9279 | -61.4822 | 61.5051 | -0.012133 | -0.0085298 | 0.00090168 | 0.014028 | -0.0030747 | 0.015465 | -0.0070964 | -0.00089301 | -0.00059405 | 0.01431 | 0.012624 | 0.017107 | -0.03558 | -0.030644 | -0.045036 | 0.015501 | -0.013378 | 0.11907 | -0.021847 | -0.035582 | -0.022535 | -0.033458 | -0.034533 | 0.086964 | 0.026065 | -0.15499 | 61.4604 | -61.4896 | 61.4467 | 61.4372 | -0.023189 | -61.5185 | -61.3861 | 61.3272 | -61.5397 | 61.4467 | 61.4488 | 0.12153 | -61.4182 | -61.4791 | 61.4977 | 61.4689 | 61.6013 | 61.4516 | -61.527 | 61.4477 | 61.5692 | 61.5083 | 61.4597 | -61.6601
579.6406 | 122.612 | -61.4685 | 61.5005 | -0.012133 | -0.0085298 | 0.0013291 | 0.014028 | -0.0026473 | 0.015251 | 0.00053414 | -0.0011066 | -0.00080765 | 0.01431 | 0.012624 | 0.017535 | -0.03558 | -0.026065 | -0.045036 | 0.020079 | -0.027115 | 0.11907 | -0.021847 | -0.035582 | -0.022535 | -0.0243 | -0.034533 | 0.091543 | 0.012329 | -0.15957 | 61.4467 | -61.4805 | 61.4329 | 61.4235 | -0.023189 | -61.5277 | -61.3815 | 61.3089 | -61.5351 | 61.4329 | 61.4442 | 0.13527 | -61.409 | -61.4882 | 61.4886 | 61.4414 | 61.5876 | 61.4424 | -61.5224 | 61.434 | 61.56 | 61.4808 | 61.446 | -61.6601
580.6406 | 122.937 | -61.5051 | 61.4777 | -0.0045023 | -0.0085298 | 0.0011155 | 0.014028 | -0.0030747 | 0.015465 | 0.00053414 | -0.00089301 | -0.00059405 | 0.014097 | 0.012838 | 0.017321 | -0.03558 | -0.030644 | -0.05877 | 0.024657 | -0.017957 | 0.11907 | -0.017268 | -0.031003 | -0.022535 | -0.028879 | -0.034533 | 0.086964 | 0.021486 | -0.15041 | 61.4879 | -61.453 | 61.4695 | 61.4464 | -0.041502 | -61.4956 | -61.3586 | 61.3547 | -61.5122 | 61.4741 | 61.4762 | 0.12153 | -61.3907 | -61.4562 | 61.5298 | 61.4872 | 61.6242 | 61.4745 | -61.4949 | 61.4706 | 61.5921 | 61.5266 | 61.4826 | -61.6281
581.6406 | 122.6303 | -61.4502 | 61.5005 | -0.0045023 | -0.0087436 | 0.0011155 | 0.014028 | -0.0030747 | 0.015038 | 0.00053414 | -0.00089301 | -0.00059405 | 0.014097 | 0.012624 | 0.017321 | -0.040158 | -0.030644 | -0.049614 | 0.015501 | -0.017957 | 0.12365 | -0.012689 | -0.035582 | -0.031692 | -0.033458 | -0.04369 | 0.091543 | 0.026065 | -0.14583 | 61.4375 | -61.485 | 61.41 | 61.4006 | -0.036925 | -61.5185 | -61.3769 | 61.3044 | -61.5442 | 61.4146 | 61.4167 | 0.11237 | -61.409 | -61.4745 | 61.4657 | 61.4322 | 61.5738 | 61.4196 | -61.5132 | 61.4065 | 61.5417 | 61.4763 | 61.4185 | -61.6464
582.6406 | 122.7448 | -61.4731 | 61.5097 | 0.0031287 | -0.0085298 | 0.0011155 | 0.014028 | -0.0030747 | 0.015465 | -0.0070964 | -0.00089301 | -0.00038025 | 0.014951 | 0.012624 | 0.017535 | -0.040158 | -0.030644 | -0.049614 | 0.015501 | -0.017957 | 0.12365 | -0.017268 | -0.021846 | -0.031692 | -0.033458 | -0.04369 | 0.086964 | 0.012329 | -0.14583 | 61.4558 | -61.4942 | 61.4329 | 61.4235 | -0.032346 | -61.5277 | -61.3861 | 61.3272 | -61.5534 | 61.4512 | 61.4396 | 0.11237 | -61.4227 | -61.4974 | 61.4886 | 61.4551 | 61.5967 | 61.4424 | -61.527 | 61.4294 | 61.56 | 61.4854 | 61.4414 | -61.6555
583.6406 | 122.644 | -61.4594 | 61.5051 | 0.01076 | -0.0089572 | 0.00090168 | 0.014242 | -0.0030747 | 0.015251 | -0.0070964 | -0.0013204 | -0.00038025 | 0.014738 | 0.012624 | 0.017107 | -0.026423 | -0.035222 | -0.054192 | 0.024657 | -0.022536 | 0.11449 | -0.021847 | -0.035582 | -0.036271 | -0.038036 | -0.029954 | 0.082386 | 0.012329 | -0.1321 | 61.4375 | -61.4805 | 61.4329 | 61.4052 | -0.032345 | -61.5277 | -61.3906 | 61.3273 | -61.5351 | 61.4238 | 61.4213 | 0.094061 | -61.4227 | -61.4928 | 61.484 | 61.4368 | 61.5738 | 61.4241 | -61.527 | 61.4294 | 61.5417 | 61.4717 | 61.4231 | -61.6372
584.6406 | 122.818 | -61.4685 | 61.5189 | -0.019764 | -0.0087436 | 0.0011155 | 0.014456 | -0.0032883 | 0.015251 | 0.0081646 | -0.00089301 | -0.00038025 | 0.014951 | 0.012624 | 0.017107 | -0.040158 | -0.039801 | -0.054192 | 0.020079 | -0.022536 | 0.11907 | -0.021847 | -0.031003 | -0.036271 | -0.028879 | -0.029954 | 0.086964 | 0.026065 | -0.12752 | 61.4467 | -61.4988 | 61.4283 | 61.4143 | -0.032345 | -61.5414 | -61.3998 | 61.341 | -61.5488 | 61.4375 | 61.4396 | 0.098639 | -61.4319 | -61.4928 | 61.4886 | 61.446 | 61.5876 | 61.4287 | -61.5407 | 61.4386 | 61.5555 | 61.4946 | 61.4322 | -61.6464
585.6406 | 122.7081 | -61.4639 | 61.5417 | 0.0031287 | -0.0085298 | 0.0011155 | 0.014028 | -0.0026473 | 0.015465 | 0.0081646 | -0.00089301 | -0.00080765 | 0.014951 | 0.012838 | 0.016894 | -0.03558 | -0.035222 | -0.054192 | 0.020079 | -0.022536 | 0.12365 | -0.017268 | -0.031003 | -0.036271 | -0.0243 | -0.029954 | 0.086964 | 0.021486 | -0.13668 | 61.4467 | -61.5217 | 61.4283 | 61.4097 | -0.036924 | -61.5643 | -61.4181 | 61.3273 | -61.5717 | 61.4329 | 61.4396 | 0.11238 | -61.4548 | -61.5203 | 61.484 | 61.4414 | 61.5876 | 61.4287 | -61.559 | 61.434 | 61.5509 | 61.4854 | 61.4277 | -61.6784
586.6406 | 122.6761 | -61.4548 | 61.5097 | 0.0031287 | -0.0083162 | 0.0015427 | 0.014242 | -0.0028609 | 0.015251 | 0.00053414 | -0.0011066 | -0.00059405 | 0.015165 | 0.013051 | 0.017535 | -0.03558 | -0.039801 | -0.05877 | 0.029236 | -0.022536 | 0.11907 | -0.017268 | -0.040161 | -0.036271 | -0.028879 | -0.039111 | 0.082386 | 0.021486 | -0.14583 | 61.4375 | -61.4805 | 61.4192 | 61.396 | -0.041502 | -61.5322 | -61.3906 | 61.3089 | -61.5488 | 61.4146 | 61.4259 | 0.11695 | -61.4273 | -61.4882 | 61.484 | 61.4322 | 61.5738 | 61.415 | -61.527 | 61.4157 | 61.5372 | 61.4763 | 61.4185 | -61.6555
587.6406 | 122.7859 | -61.4594 | 61.528 | -0.0045023 | -0.0087436 | 0.0011155 | 0.014028 | -0.0032883 | 0.015038 | -0.0070964 | -0.00089301 | -0.00038025 | 0.014951 | 0.013051 | 0.017107 | -0.031001 | -0.048958 | -0.05877 | 0.020079 | -0.017957 | 0.12365 | -0.021847 | -0.035582 | -0.040849 | -0.028879 | -0.04369 | 0.086964 | 0.021486 | -0.14583 | 61.4375 | -61.5079 | 61.4283 | 61.4006 | -0.036923 | -61.546 | -61.4044 | 61.3135 | -61.5717 | 61.4238 | 61.4305 | 0.11695 | -61.4411 | -61.5065 | 61.4794 | 61.4414 | 61.583 | 61.4104 | -61.5499 | 61.4157 | 61.5463 | 61.4808 | 61.4185 | -61.6738
588.6406 | 122.6624 | -61.4822 | 61.4227 | 0.01076 | -0.0085298 | 0.0011155 | 0.013815 | -0.0032883 | 0.015038 | 0.0081646 | -0.0011066 | -0.00038025 | 0.014524 | 0.01241 | 0.016894 | -0.040158 | -0.044379 | -0.05877 | 0.024657 | -0.022536 | 0.12365 | -0.017268 | -0.040161 | -0.040849 | -0.033458 | -0.039111 | 0.086964 | 0.016908 | -0.14125 | 61.465 | -61.3981 | 61.4421 | 61.4235 | -0.041502 | -61.4453 | -61.2991 | 61.341 | -61.4618 | 61.4421 | 61.4488 | 0.1078 | -61.3358 | -61.4058 | 61.5069 | 61.4597 | 61.6059 | 61.4379 | -61.44 | 61.4431 | 61.5692 | 61.4991 | 61.4414 | -61.564
589.6406 | 122.9233 | -61.4822 | 61.5372 | -0.019764 | -0.0085298 | 0.0011155 | 0.014242 | -0.0028609 | 0.015251 | 0.00053414 | -0.0011066 | -0.00038025 | 0.014951 | 0.012624 | 0.017321 | -0.040158 | -0.044379 | -0.05877 | 0.033814 | -0.017957 | 0.11449 | -0.021847 | -0.035582 | -0.040849 | -0.033458 | -0.034533 | 0.091543 | 0.021486 | -0.1321 | 61.4604 | -61.5034 | 61.4421 | 61.4235 | -0.036923 | -61.5551 | -61.4227 | 61.3501 | -61.5717 | 61.4467 | 61.4488 | 0.098639 | -61.4456 | -61.5157 | 61.5161 | 61.4643 | 61.5967 | 61.4379 | -61.559 | 61.4477 | 61.5738 | 61.5037 | 61.4414 | -61.6693
590.6406 | 122.8088 | -61.4822 | 61.5189 | -0.012133 | -0.0087436 | 0.0013291 | 0.014028 | -0.0030747 | 0.015038 | 0.0081646 | -0.0011066 | -0.00080765 | 0.014951 | 0.013051 | 0.017321 | -0.03558 | -0.039801 | -0.05877 | 0.024657 | -0.022536 | 0.11907 | -0.012689 | -0.040161 | -0.040849 | -0.038036 | -0.034533 | 0.086964 | 0.026065 | -0.13668 | 61.4695 | -61.4942 | 61.4467 | 61.4235 | -0.046081 | -61.5414 | -61.3998 | 61.3456 | -61.5534 | 61.4421 | 61.4442 | 0.09864 | -61.4319 | -61.4928 | 61.5069 | 61.4597 | 61.6013 | 61.4424 | -61.5315 | 61.4477 | 61.5692 | 61.5083 | 61.4414 | -61.6555
591.6406 | 123.2529 | -61.4594 | 61.4777 | -0.012133 | -0.0085298 | 0.0017565 | 0.014028 | -0.0028609 | 0.015465 | -0.0070964 | -0.00089301 | -0.00080765 | 0.014524 | 0.012624 | 0.017321 | -0.040158 | -0.044379 | -0.049614 | 0.024657 | -0.022536 | 0.12365 | -0.012689 | -0.035582 | -0.045428 | -0.038036 | -0.025376 | 0.086964 | 0.021486 | -0.13668 | 61.4467 | -61.453 | 61.4192 | 61.4097 | -0.036925 | -61.5002 | -61.354 | 61.3227 | -61.503 | 61.4238 | 61.4213 | 0.09864 | -61.3907 | -61.4562 | 61.484 | 61.4368 | 61.583 | 61.415 | -61.4903 | 61.434 | 61.5463 | 61.4808 | 61.4139 | -61.6143
592.6406 | 122.8088 | -61.4914 | 61.5372 | -0.012133 | -0.0087436 | 0.0011155 | 0.014028 | -0.0028609 | 0.015251 | 0.015795 | -0.00067941 | -0.00038025 | 0.014524 | 0.012838 | 0.017748 | -0.026423 | -0.044379 | -0.063349 | 0.015501 | -0.027115 | 0.11907 | -0.021847 | -0.044739 | -0.050007 | -0.028879 | -0.034533 | 0.082386 | 0.016908 | -0.13668 | 61.4695 | -61.5217 | 61.465 | 61.428 | -0.041502 | -61.5643 | -61.4181 | 61.3547 | -61.5717 | 61.4467 | 61.4625 | 0.1078 | -61.4548 | -61.5203 | 61.5069 | 61.4643 | 61.6105 | 61.447 | -61.559 | 61.4569 | 61.5738 | 61.5083 | 61.4414 | -61.6738
593.6406 | 123.1476 | -61.4685 | 61.5143 | -0.0045023 | -0.0087436 | 0.0013291 | 0.014028 | -0.0030747 | 0.014824 | 0.00053414 | -0.00089301 | -0.00038025 | 0.014738 | 0.012838 | 0.017321 | -0.031001 | -0.044379 | -0.05877 | 0.020079 | -0.022536 | 0.12823 | -0.017268 | -0.035582 | -0.054586 | -0.033458 | -0.029954 | 0.086964 | 0.012329 | -0.1321 | 61.4512 | -61.4942 | 61.4375 | 61.4097 | -0.041502 | -61.5368 | -61.3861 | 61.3364 | -61.5442 | 61.4329 | 61.435 | 0.098639 | -61.4273 | -61.502 | 61.4886 | 61.446 | 61.5967 | 61.4241 | -61.5316 | 61.4386 | 61.5555 | 61.4808 | 61.4139 | -61.6464
594.6406 | 122.8867 | -61.4594 | 61.5143 | 0.01076 | -0.0085298 | 0.0013291 | 0.014028 | -0.0030747 | 0.015465 | 0.00053414 | -0.001534 | -0.00038025 | 0.014738 | 0.012624 | 0.017321 | -0.040158 | -0.039801 | -0.067927 | 0.020079 | -0.017957 | 0.11907 | -0.012689 | -0.044739 | -0.050007 | -0.033458 | -0.034533 | 0.091543 | 0.016908 | -0.1321 | 61.4467 | -61.4942 | 61.4192 | 61.3914 | -0.055238 | -61.5322 | -61.3952 | 61.3273 | -61.5488 | 61.4146 | 61.4259 | 0.098639 | -61.4227 | -61.4974 | 61.4794 | 61.4414 | 61.5784 | 61.4196 | -61.527 | 61.4248 | 61.5509 | 61.4763 | 61.4093 | -61.6464
595.6406 | 123.1796 | -61.4548 | 61.5097 | 0.0031287 | -0.0087436 | 0.00068808 | 0.014028 | -0.0026473 | 0.015038 | 0.015795 | -0.00067941 | -0.00059405 | 0.014738 | 0.012838 | 0.017321 | -0.040158 | -0.048958 | -0.063349 | 0.020079 | -0.027115 | 0.11907 | -0.017268 | -0.035582 | -0.050007 | -0.033458 | -0.034533 | 0.086964 | 0.016908 | -0.12294 | 61.4375 | -61.4896 | 61.4146 | 61.3914 | -0.046081 | -61.5368 | -61.3906 | 61.3318 | -61.5442 | 61.4192 | 61.4213 | 0.089481 | -61.4227 | -61.4928 | 61.4749 | 61.4277 | 61.5738 | 61.4058 | -61.527 | 61.4202 | 61.5417 | 61.4717 | 61.4048 | -61.6326
596.6406 | 123.1064 | -61.4822 | 61.5326 | -0.012133 | -0.0085298 | 0.00090168 | 0.014028 | -0.0035019 | 0.015251 | 0.015795 | -0.00067941 | -0.00038025 | 0.014738 | 0.013051 | 0.017535 | -0.03558 | -0.048958 | -0.063349 | 0.015501 | -0.022536 | 0.11907 | -0.017268 | -0.040161 | -0.054586 | -0.033458 | -0.039111 | 0.086964 | 0.016908 | -0.13668 | 61.465 | -61.5171 | 61.4467 | 61.4189 | -0.046081 | -61.5551 | -61.4135 | 61.3456 | -61.5717 | 61.4421 | 61.4488 | 0.10322 | -61.4456 | -61.5157 | 61.4977 | 61.4597 | 61.6013 | 61.4333 | -61.5499 | 61.4431 | 61.5692 | 61.4991 | 61.4277 | -61.6693
597.6406 | 123.2666 | -61.409 | 61.5143 | -0.0045023 | -0.0089572 | 0.0011155 | 0.014028 | -0.0030747 | 0.015251 | 0.015795 | -0.00089301 | -0.00038025 | 0.014524 | 0.013265 | 0.017321 | -0.040158 | -0.048958 | -0.072505 | 0.020079 | -0.013378 | 0.12365 | -0.017268 | -0.044739 | -0.050007 | -0.038036 | -0.025376 | 0.077807 | 0.021486 | -0.12752 | 61.3917 | -61.4942 | 61.3688 | 61.3365 | -0.055237 | -61.5277 | -61.3906 | 61.2815 | -61.5397 | 61.3643 | 61.371 | 0.089482 | -61.4365 | -61.4928 | 61.4291 | 61.3956 | 61.5326 | 61.36 | -61.5316 | 61.3836 | 61.4868 | 61.4305 | 61.359 | -61.6418
598.6406 | 123.1338 | -61.4868 | 61.5601 | -0.0045023 | -0.0091708 | 0.0013291 | 0.013815 | -0.0028609 | 0.015038 | -0.0070964 | -0.00089301 | -0.00038025 | 0.014951 | 0.012838 | 0.017107 | -0.03558 | -0.039801 | -0.063349 | 0.024657 | -0.017957 | 0.12365 | -0.026426 | -0.040161 | -0.045428 | -0.033458 | -0.034533 | 0.082386 | 0.021486 | -0.13668 | 61.4604 | -61.5354 | 61.4512 | 61.4235 | -0.036923 | -61.578 | -61.4364 | 61.3501 | -61.5946 | 61.4467 | 61.4534 | 0.10322 | -61.4777 | -61.5386 | 61.5115 | 61.4689 | 61.6105 | 61.447 | -61.5865 | 61.4523 | 61.5692 | 61.5083 | 61.4414 | -61.6967
599.6406 | 123.2666 | -61.4456 | 61.5005 | -0.0045023 | -0.0089572 | 0.0013291 | 0.013815 | -0.0028609 | 0.015038 | 0.00053414 | -0.00089301 | -0.00038025 | 0.014738 | 0.013051 | 0.017535 | -0.03558 | -0.039801 | -0.067927 | 0.020079 | -0.022536 | 0.12365 | -0.021847 | -0.058476 | -0.045428 | -0.033458 | -0.034533 | 0.082386 | 0.016908 | -0.1321 | 61.4238 | -61.4805 | 61.41 | 61.3777 | -0.04608 | -61.5231 | -61.3769 | 61.3135 | -61.5351 | 61.3871 | 61.4122 | 0.098639 | -61.4182 | -61.4836 | 61.4657 | 61.4231 | 61.5693 | 61.4058 | -61.5224 | 61.4111 | 61.528 | 61.4625 | 61.4002 | -61.6326
600.6406 | 123.2346 | -61.4502 | 61.5463 | 0.0031287 | -0.0089572 | 0.0013291 | 0.014028 | -0.0032883 | 0.015251 | 0.00053414 | -0.0011066 | -0.00059405 | 0.014524 | 0.012838 | 0.017321 | -0.03558 | -0.039801 | -0.072505 | 0.024657 | -0.022536 | 0.11907 | -0.012689 | -0.049318 | -0.050007 | -0.033458 | -0.039111 | 0.082386 | 0.021486 | -0.1321 | 61.4375 | -61.5217 | 61.4146 | 61.3777 | -0.059816 | -61.5689 | -61.4273 | 61.3181 | -61.5854 | 61.4009 | 61.4167 | 0.098639 | -61.4639 | -61.5248 | 61.4749 | 61.4277 | 61.5693 | 61.4104 | -61.559 | 61.4111 | 61.5326 | 61.4717 | 61.4002 | -61.6784
601.6406 | 122.7768 | -61.4868 | 61.5463 | -0.012133 | -0.0089572 | 0.0011155 | 0.014242 | -0.0028609 | 0.015251 | 0.00053414 | -0.00089301 | -0.00038025 | 0.014738 | 0.013051 | 0.017321 | -0.03558 | -0.039801 | -0.067927 | 0.015501 | -0.022536 | 0.12365 | -0.017268 | -0.044739 | -0.059164 | -0.033458 | -0.04369 | 0.082386 | 0.003172 | -0.12752 | 61.4695 | -61.5308 | 61.4512 | 61.4189 | -0.050659 | -61.5689 | -61.4227 | 61.3593 | -61.59 | 61.4421 | 61.4534 | 0.09406 | -61.4639 | -61.5432 | 61.5023 | 61.4643 | 61.6105 | 61.447 | -61.5636 | 61.4431 | 61.5692 | 61.49 | 61.4277 | -61.6738
602.6406 | 123.2391 | -61.4594 | 61.5097 | 0.0031287 | -0.0087436 | 0.0015427 | 0.014028 | -0.0030747 | 0.015251 | 0.0081646 | -0.0011066 | -0.00038025 | 0.014524 | 0.013051 | 0.017535 | -0.040158 | -0.044379 | -0.067927 | 0.020079 | -0.008799 | 0.11449 | -0.012689 | -0.044739 | -0.054586 | -0.038036 | -0.039111 | 0.077807 | 0.016908 | -0.12294 | 61.4467 | -61.4896 | 61.4192 | 61.3914 | -0.055238 | -61.5185 | -61.3952 | 61.3364 | -61.5488 | 61.4146 | 61.4213 | 0.084903 | -61.4319 | -61.4928 | 61.4794 | 61.4506 | 61.5738 | 61.415 | -61.5224 | 61.4202 | 61.5372 | 61.4763 | 61.4048 | -61.6326
603.6406 | 123.2666 | -61.441 | 61.528 | -0.012133 | -0.0089572 | 0.0015427 | 0.013601 | -0.0028609 | 0.015038 | -0.0070964 | -0.0011066 | -0.00038025 | 0.014951 | 0.013265 | 0.017321 | -0.040158 | -0.039801 | -0.072505 | 0.029236 | -0.022536 | 0.11907 | -0.012689 | -0.063054 | -0.059164 | -0.042615 | -0.029954 | 0.091543 | 0.021486 | -0.12294 | 61.4284 | -61.4988 | 61.4009 | 61.3685 | -0.059816 | -61.5506 | -61.4089 | 61.3181 | -61.558 | 61.378 | 61.3984 | 0.080324 | -61.4365 | -61.5065 | 61.4703 | 61.4185 | 61.5601 | 61.4012 | -61.5407 | 61.4111 | 61.5326 | 61.4625 | 61.3819 | -61.651
604.6406 | 123.2803 | -61.4273 | 61.5005 | 0.0031287 | -0.0089572 | 0.0011155 | 0.014242 | -0.0028609 | 0.015465 | -0.014727 | -0.00089301 | -0.00038025 | 0.014951 | 0.013051 | 0.017321 | -0.031001 | -0.030644 | -0.067927 | 0.015501 | -0.027115 | 0.12365 | -0.00811 | -0.058476 | -0.0729 | -0.042615 | -0.034533 | 0.077807 | 0.021486 | -0.13668 | 61.4192 | -61.485 | 61.3963 | 61.3594 | -0.059817 | -61.5277 | -61.3769 | 61.2906 | -61.5351 | 61.3688 | 61.3847 | 0.094061 | -61.4227 | -61.4791 | 61.4428 | 61.4002 | 61.551 | 61.3967 | -61.5087 | 61.3928 | 61.5051 | 61.4488 | 61.3544 | -61.6372
605.6406 | 123.2758 | -61.4273 | 61.5189 | 0.0031287 | -0.0093846 | 0.0015427 | 0.014242 | -0.0030747 | 0.015251 | 0.00053414 | -0.0011066 | -0.00059405 | 0.014524 | 0.013051 | 0.017321 | -0.031001 | -0.035222 | -0.067927 | 0.020079 | -0.017957 | 0.11907 | -0.017268 | -0.053897 | -0.059164 | -0.042615 | -0.029954 | 0.077807 | 0.016908 | -0.13668 | 61.41 | -61.4988 | 61.3963 | 61.3594 | -0.050659 | -61.5368 | -61.3998 | 61.2906 | -61.5488 | 61.3734 | 61.3847 | 0.094061 | -61.4411 | -61.502 | 61.4474 | 61.4093 | 61.5464 | 61.3921 | -61.5361 | 61.3974 | 61.5051 | 61.4442 | 61.3681 | -61.6555
606.6406 | 123.0835 | -61.4914 | 61.5463 | -0.0045023 | -0.0087436 | 0.0013291 | 0.014242 | -0.0030747 | 0.015465 | 0.00053414 | -0.0011066 | -0.00038025 | 0.014524 | 0.013051 | 0.017107 | -0.031001 | -0.039801 | -0.072505 | 0.020079 | -0.022536 | 0.12365 | -0.017268 | -0.058476 | -0.068322 | -0.051772 | -0.04369 | 0.086964 | 0.016908 | -0.12752 | 61.4741 | -61.5262 | 61.4604 | 61.4189 | -0.055237 | -61.5689 | -61.4227 | 61.3639 | -61.59 | 61.4329 | 61.4396 | 0.075746 | -61.4594 | -61.5294 | 61.5115 | 61.4689 | 61.615 | 61.4516 | -61.5636 | 61.4477 | 61.5784 | 61.5083 | 61.4231 | -61.6738
607.6406 | 123.2208 | -61.4685 | 61.528 | 0.01076 | -0.0091708 | 0.0011155 | 0.013601 | -0.0030747 | 0.015251 | 0.00053414 | -0.0011066 | -0.00059405 | 0.014951 | 0.013051 | 0.017535 | -0.026423 | -0.039801 | -0.072505 | 0.020079 | -0.017957 | 0.12365 | -0.021847 | -0.058476 | -0.068322 | -0.047194 | -0.039111 | 0.096121 | 0.016908 | -0.14125 | 61.4467 | -61.5079 | 61.4421 | 61.396 | -0.050658 | -61.546 | -61.4044 | 61.3273 | -61.5671 | 61.41 | 61.4213 | 0.094061 | -61.4319 | -61.5111 | 61.4886 | 61.4505 | 61.5922 | 61.4287 | -61.5499 | 61.4294 | 61.5646 | 61.4854 | 61.4002 | -61.6693
608.6406 | 123.2849 | -61.4182 | 61.5417 | -0.012133 | -0.0093846 | 0.00090168 | 0.013815 | -0.0032883 | 0.015038 | 0.00053414 | -0.00089301 | -0.00059405 | 0.014951 | 0.013051 | 0.017535 | -0.031001 | -0.035222 | -0.063349 | 0.029236 | -0.022536 | 0.11907 | -0.021847 | -0.053897 | -0.068322 | -0.042615 | -0.04369 | 0.086964 | 0.007751 | -0.14125 | 61.3963 | -61.5125 | 61.3872 | 61.3548 | -0.041502 | -61.5643 | -61.4227 | 61.2769 | -61.5854 | 61.3643 | 61.3755 | 0.09864 | -61.4548 | -61.534 | 61.4474 | 61.3956 | 61.5372 | 61.3829 | -61.5636 | 61.3745 | 61.5051 | 61.4259 | 61.3498 | -61.683
609.6406 | 123.2254 | -61.4273 | 61.5326 | -0.0045023 | -0.0089572 | 0.0013291 | 0.013815 | -0.0028609 | 0.015251 | -0.0070964 | -0.00089301 | -0.00016665 | 0.014524 | 0.013479 | 0.017748 | -0.026423 | -0.044379 | -0.05877 | 0.020079 | -0.017957 | 0.11907 | -0.00811 | -0.053897 | -0.063743 | -0.047194 | -0.039111 | 0.086964 | 0.016908 | -0.1321 | 61.4192 | -61.5125 | 61.4009 | 61.3685 | -0.05066 | -61.5506 | -61.4135 | 61.2952 | -61.5717 | 61.3734 | 61.3801 | 0.084903 | -61.4456 | -61.5157 | 61.4474 | 61.4093 | 61.5464 | 61.3829 | -61.5407 | 61.3882 | 61.5143 | 61.4442 | 61.3636 | -61.6647
610.6406 | 123.2941 | -61.4502 | 61.5372 | 0.01076 | -0.0089572 | 0.0011155 | 0.014028 | -0.0030747 | 0.015038 | 0.00053414 | -0.00089301 | -0.00038025 | 0.014524 | 0.013051 | 0.017748 | -0.031001 | -0.044379 | -0.067927 | 0.020079 | -0.013378 | 0.12823 | -0.012689 | -0.063054 | -0.068322 | -0.051772 | -0.034533 | 0.082386 | 0.012329 | -0.12752 | 61.4375 | -61.5171 | 61.4192 | 61.3823 | -0.055238 | -61.5505 | -61.4089 | 61.3227 | -61.5717 | 61.3871 | 61.3984 | 0.075746 | -61.4548 | -61.5248 | 61.4703 | 61.4368 | 61.5784 | 61.4058 | -61.5499 | 61.4157 | 61.5326 | 61.4625 | 61.3819 | -61.6647
611.6406 | 123.2254 | -61.4365 | 61.5417 | 0.0031287 | -0.0089572 | 0.0011155 | 0.014028 | -0.0030747 | 0.015038 | 0.00053414 | -0.0011066 | -0.00059405 | 0.014524 | 0.013051 | 0.017535 | -0.03558 | -0.048958 | -0.077084 | 0.024657 | -0.022536 | 0.12365 | -0.012689 | -0.053897 | -0.068322 | -0.047194 | -0.039111 | 0.086964 | 0.007751 | -0.12294 | 61.4238 | -61.5171 | 61.4009 | 61.3594 | -0.064395 | -61.5643 | -61.4181 | 61.3135 | -61.5809 | 61.3826 | 61.3893 | 0.075745 | -61.4548 | -61.534 | 61.4611 | 61.4139 | 61.5601 | 61.3875 | -61.5544 | 61.3974 | 61.5234 | 61.4442 | 61.3681 | -61.6647
612.6406 | 123.2666 | -61.4639 | 61.5555 | 0.0031287 | -0.0089572 | 0.0013291 | 0.014028 | -0.0030747 | 0.015251 | 0.0081646 | -0.00089301 | -0.00038025 | 0.014738 | 0.013051 | 0.017321 | -0.03558 | -0.044379 | -0.067927 | 0.010922 | -0.017957 | 0.11449 | -0.021847 | -0.058476 | -0.068322 | -0.019721 | -0.039111 | 0.091543 | 0.016908 | -0.1321 | 61.4421 | -61.5446 | 61.4283 | 61.396 | -0.04608 | -61.5734 | -61.441 | 61.3318 | -61.5946 | 61.4055 | 61.4442 | 0.11238 | -61.4639 | -61.5386 | 61.4749 | 61.446 | 61.5784 | 61.4195 | -61.5773 | 61.4248 | 61.5555 | 61.4808 | 61.3956 | -61.6876
613.6406 | 123.2529 | -61.4456 | 61.5097 | -0.0045023 | -0.0087436 | 0.0011155 | 0.013601 | -0.0032883 | 0.015465 | 0.0081646 | -0.00089301 | -0.00080765 | 0.014738 | 0.013479 | 0.017321 | -0.03558 | -0.053537 | -0.077084 | 0.024657 | -0.017957 | 0.12365 | -0.012689 | -0.063054 | -0.068322 | -0.019721 | -0.034533 | 0.077807 | 0.012329 | -0.12752 | 61.4329 | -61.485 | 61.41 | 61.3685 | -0.064395 | -61.5277 | -61.3861 | 61.3181 | -61.5442 | 61.3826 | 61.4259 | 0.1078 | -61.4319 | -61.4974 | 61.4703 | 61.4277 | 61.5693 | 61.3921 | -61.5224 | 61.4111 | 61.5234 | 61.4579 | 61.3773 | -61.6372
614.6406 | 123.2208 | -61.4548 | 61.5234 | -0.0045023 | -0.0089572 | 0.0015427 | 0.013815 | -0.0030747 | 0.014824 | -0.0070964 | -0.00089301 | -0.00038025 | 0.014097 | 0.013051 | 0.017321 | -0.040158 | -0.039801 | -0.077084 | 0.020079 | -0.022536 | 0.11907 | -0.012689 | -0.044739 | -0.063743 | -0.019721 | -0.034533 | 0.096121 | 0.016908 | -0.12752 | 61.4421 | -61.5034 | 61.4146 | 61.3777 | -0.064395 | -61.546 | -61.4044 | 61.3273 | -61.558 | 61.41 | 61.4351 | 0.1078 | -61.4273 | -61.5065 | 61.4749 | 61.4322 | 61.5738 | 61.415 | -61.5361 | 61.4202 | 61.5509 | 61.4717 | 61.391 | -61.651
615.6406 | 123.2529 | -61.4365 | 61.5234 | 0.0031287 | -0.0091708 | 0.00090168 | 0.013815 | -0.0032883 | 0.015038 | -0.0070964 | -0.0013204 | -0.00038025 | 0.014738 | 0.013265 | 0.017321 | -0.031001 | -0.044379 | -0.067927 | 0.020079 | -0.022536 | 0.12365 | -0.012689 | -0.053897 | -0.0729 | -0.028879 | -0.034533 | 0.082386 | 0.012329 | -0.1321 | 61.4238 | -61.5034 | 61.4055 | 61.3685 | -0.055238 | -61.546 | -61.3998 | 61.3044 | -61.558 | 61.3826 | 61.4076 | 0.10322 | -61.4411 | -61.5111 | 61.4565 | 61.4139 | 61.5601 | 61.3921 | -61.5361 | 61.4019 | 61.5188 | 61.4488 | 61.3636 | -61.6555
616.6406 | 123.2437 | -61.4365 | 61.5463 | -0.0045023 | -0.0091708 | 0.0015427 | 0.014028 | -0.0030747 | 0.015251 | -0.014727 | -0.00067941 | -0.00059405 | 0.014738 | 0.013051 | 0.017321 | -0.031001 | -0.048958 | -0.072505 | 0.010922 | -0.022536 | 0.11907 | -0.017268 | -0.063054 | -0.0729 | -0.047194 | -0.039111 | 0.082386 | 0.016908 | -0.1321 | 61.4192 | -61.5354 | 61.4055 | 61.364 | -0.055237 | -61.5689 | -61.4273 | 61.3044 | -61.5854 | 61.3734 | 61.3893 | 0.084903 | -61.4639 | -61.5294 | 61.4474 | 61.4139 | 61.5555 | 61.3875 | -61.5636 | 61.3974 | 61.5188 | 61.4534 | 61.3636 | -61.6784
617.6406 | 123.2941 | -61.441 | 61.528 | -0.012133 | -0.0091708 | 0.0013291 | 0.014028 | -0.0032883 | 0.015251 | -0.0070964 | -0.0011066 | -0.00038025 | 0.014524 | 0.013051 | 0.017321 | -0.031001 | -0.039801 | -0.063349 | 0.020079 | -0.031693 | 0.12365 | -0.012689 | -0.049318 | -0.0729 | -0.019721 | -0.034533 | 0.091543 | 0.016908 | -0.12752 | 61.4284 | -61.5079 | 61.41 | 61.3777 | -0.05066 | -61.5597 | -61.4044 | 61.3135 | -61.5625 | 61.3917 | 61.4213 | 0.1078 | -61.4365 | -61.5111 | 61.4611 | 61.4093 | 61.5647 | 61.4012 | -61.5407 | 61.4065 | 61.5326 | 61.4579 | 61.3681 | -61.6555
618.6406 | 123.2391 | -61.4639 | 61.528 | -0.012133 | -0.0093846 | 0.0011155 | 0.013815 | -0.0028609 | 0.015251 | 0.00053414 | -0.00089301 | -0.00016665 | 0.01431 | 0.013692 | 0.017321 | -0.03558 | -0.048958 | -0.072505 | 0.024657 | -0.017957 | 0.11907 | -0.021847 | -0.044739 | -0.068322 | -0.019721 | -0.04369 | 0.096121 | 0.016908 | -0.1321 | 61.4421 | -61.5034 | 61.4283 | 61.3914 | -0.050658 | -61.546 | -61.4089 | 61.3318 | -61.5717 | 61.4192 | 61.4442 | 0.11238 | -61.4319 | -61.5111 | 61.4886 | 61.446 | 61.583 | 61.415 | -61.5499 | 61.4202 | 61.56 | 61.4808 | 61.3956 | -61.6601
619.6406 | 123.2758 | -61.441 | 61.5189 | -0.012133 | -0.0089572 | 0.0015427 | 0.013601 | -0.0030747 | 0.015038 | 0.00053414 | -0.00089301 | -0.00038025 | 0.014738 | 0.013479 | 0.017321 | -0.026423 | -0.044379 | -0.067927 | 0.020079 | -0.022536 | 0.12365 | -0.012689 | -0.049318 | -0.068322 | -0.015143 | -0.039111 | 0.086964 | 0.021486 | -0.1321 | 61.4284 | -61.4988 | 61.4146 | 61.3731 | -0.055238 | -61.5414 | -61.3952 | 61.3089 | -61.558 | 61.3917 | 61.4259 | 0.11695 | -61.4319 | -61.4974 | 61.4611 | 61.4185 | 61.5647 | 61.3967 | -61.5315 | 61.4019 | 61.528 | 61.4625 | 61.3727 | -61.651
620.6406 | 123.2437 | -61.4639 | 61.5509 | 0.01076 | -0.0091708 | 0.0013291 | 0.014028 | -0.0030747 | 0.015465 | -0.0070964 | -0.0013204 | -0.00038025 | 0.014738 | 0.013051 | 0.017107 | -0.031001 | -0.039801 | -0.072505 | 0.024657 | -0.022536 | 0.11907 | -0.012689 | -0.049318 | -0.0729 | -0.019721 | -0.034533 | 0.077807 | 0.021486 | -0.1321 | 61.4512 | -61.5262 | 61.4329 | 61.3914 | -0.059816 | -61.5734 | -61.4318 | 61.3318 | -61.5854 | 61.4146 | 61.4442 | 0.11238 | -61.4731 | -61.5294 | 61.4886 | 61.4414 | 61.583 | 61.4241 | -61.5636 | 61.4294 | 61.5417 | 61.4854 | 61.391 | -61.683
621.6406 | 123.2803 | -61.4594 | 61.5051 | -0.0045023 | -0.0091708 | 0.0017565 | 0.014028 | -0.0032883 | 0.015251 | -0.0070964 | -0.00089301 | -0.00038025 | 0.014524 | 0.013265 | 0.017321 | -0.031001 | -0.035222 | -0.077084 | 0.015501 | -0.022536 | 0.11907 | -0.012689 | -0.040161 | -0.082058 | -0.019721 | -0.039111 | 0.077807 | 0.021486 | -0.14125 | 61.4467 | -61.4896 | 61.4283 | 61.3823 | -0.064395 | -61.5277 | -61.3861 | 61.3181 | -61.5442 | 61.4192 | 61.4396 | 0.12153 | -61.4273 | -61.4836 | 61.4749 | 61.4368 | 61.5784 | 61.4241 | -61.5178 | 61.4202 | 61.5372 | 61.4808 | 61.3773 | -61.6464
622.6406 | 123.262 | -61.4594 | 61.528 | -0.0045023 | -0.0093846 | 0.0015427 | 0.014028 | -0.0030747 | 0.015038 | 0.0081646 | -0.0011066 | -0.00080765 | 0.014738 | 0.013051 | 0.017321 | -0.03558 | -0.044379 | -0.077084 | 0.024657 | -0.027115 | 0.12365 | -0.021847 | -0.040161 | -0.0729 | -0.010564 | -0.034533 | 0.086964 | 0.012329 | -0.1321 | 61.4375 | -61.5034 | 61.4238 | 61.3823 | -0.055237 | -61.5551 | -61.4044 | 61.3273 | -61.5625 | 61.4192 | 61.4488 | 0.12153 | -61.4411 | -61.5157 | 61.484 | 61.4322 | 61.583 | 61.415 | -61.5499 | 61.4248 | 61.5463 | 61.4717 | 61.3865 | -61.6601
623.6406 | 123.3124 | -61.4639 | 61.5417 | -0.012133 | -0.0091708 | 0.0013291 | 0.013815 | -0.0030747 | 0.015251 | 0.00053414 | -0.00089301 | -0.00016665 | 0.01431 | 0.013265 | 0.017535 | -0.031001 | -0.039801 | -0.072505 | 0.020079 | -0.022536 | 0.11907 | -0.017268 | -0.040161 | -0.068322 | -0.015143 | -0.04369 | 0.086964 | 0.016908 | -0.1321 | 61.4467 | -61.5217 | 61.4329 | 61.3914 | -0.055237 | -61.5643 | -61.4227 | 61.3318 | -61.5854 | 61.4238 | 61.4488 | 0.11695 | -61.4548 | -61.5248 | 61.484 | 61.4414 | 61.583 | 61.4241 | -61.559 | 61.4202 | 61.5509 | 61.4808 | 61.3956 | -61.6738
624.6406 | 123.2574 | -61.4639 | 61.5234 | -0.0045023 | -0.0091708 | 0.0017565 | 0.013601 | -0.0032883 | 0.015465 | 0.00053414 | -0.0011066 | -0.00059405 | 0.014524 | 0.013051 | 0.017321 | -0.026423 | -0.035222 | -0.072505 | 0.024657 | -0.022536 | 0.12365 | -0.012689 | -0.049318 | -0.068322 | -0.019721 | -0.039111 | 0.086964 | 0.012329 | -0.12752 | 61.4512 | -61.4988 | 61.4375 | 61.3914 | -0.059816 | -61.546 | -61.3998 | 61.3364 | -61.5625 | 61.4146 | 61.4442 | 0.1078 | -61.4365 | -61.5111 | 61.4886 | 61.4414 | 61.5876 | 61.4287 | -61.5361 | 61.4248 | 61.5509 | 61.4763 | 61.3956 | -61.651
625.6406 | 123.262 | -61.4639 | 61.5509 | -0.0045023 | -0.0089572 | 0.0013291 | 0.013815 | -0.0035019 | 0.015465 | -0.0070964 | -0.0013204 | -0.00038025 | 0.014524 | 0.013265 | 0.017321 | -0.040158 | -0.035222 | -0.072505 | 0.020079 | -0.022536 | 0.11907 | -0.021847 | -0.040161 | -0.0729 | -0.010564 | -0.039111 | 0.091543 | 0.016908 | -0.12752 | 61.4421 | -61.5308 | 61.4238 | 61.3914 | -0.050658 | -61.5734 | -61.4318 | 61.3364 | -61.59 | 61.4238 | 61.4534 | 0.11695 | -61.4594 | -61.534 | 61.484 | 61.4414 | 61.583 | 61.4287 | -61.5727 | 61.4248 | 61.5555 | 61.4808 | 61.391 | -61.6784
626.6406 | 123.2758 | -61.4822 | 61.5143 | -0.012133 | -0.0093846 | 0.0015427 | 0.014242 | -0.0035019 | 0.015038 | -0.0070964 | -0.0011066 | -0.00059405 | 0.014524 | 0.013479 | 0.017107 | -0.03558 | -0.039801 | -0.072505 | 0.029236 | -0.022536 | 0.11449 | -0.021847 | -0.049318 | -0.068322 | -0.015143 | -0.039111 | 0.086964 | 0.016908 | -0.12294 | 61.4604 | -61.485 | 61.4467 | 61.4097 | -0.050658 | -61.5368 | -61.3998 | 61.3593 | -61.5534 | 61.4329 | 61.4671 | 0.1078 | -61.4273 | -61.4974 | 61.5115 | 61.4597 | 61.5967 | 61.4424 | -61.5361 | 61.4431 | 61.5692 | 61.4991 | 61.4139 | -61.6372
627.6406 | 123.2071 | -61.5005 | 61.5509 | -0.012133 | -0.0091708 | 0.00090168 | 0.013815 | -0.0032883 | 0.014824 | -0.0070964 | -0.00067941 | -0.00038025 | 0.014738 | 0.013265 | 0.017748 | -0.031001 | -0.039801 | -0.077084 | 0.024657 | -0.017957 | 0.11907 | -0.021847 | -0.044739 | -0.068322 | -0.005985 | -0.029954 | 0.086964 | 0.021486 | -0.12752 | 61.4787 | -61.5262 | 61.4695 | 61.4235 | -0.055237 | -61.5689 | -61.4318 | 61.373 | -61.5809 | 61.4558 | 61.4946 | 0.12153 | -61.4639 | -61.5294 | 61.5252 | 61.4826 | 61.6196 | 61.4607 | -61.5727 | 61.4706 | 61.5875 | 61.522 | 61.4322 | -61.6784
628.6406 | 123.3124 | -61.4456 | 61.528 | 0.0031287 | -0.0093846 | 0.0011155 | 0.014028 | -0.0032883 | 0.015251 | 0.00053414 | -0.0011066 | -0.00038025 | 0.014524 | 0.013265 | 0.017535 | -0.026423 | -0.039801 | -0.077084 | 0.024657 | -0.022536 | 0.12365 | -0.021847 | -0.044739 | -0.068322 | -0.015143 | -0.04369 | 0.077807 | 0.012329 | -0.12294 | 61.4238 | -61.5034 | 61.4192 | 61.3685 | -0.055237 | -61.5506 | -61.4044 | 61.3227 | -61.5717 | 61.4009 | 61.4305 | 0.1078 | -61.4502 | -61.5157 | 61.4703 | 61.4231 | 61.5693 | 61.4058 | -61.5499 | 61.4019 | 61.5234 | 61.4579 | 61.3773 | -61.651
629.6406 | 123.2254 | -61.4868 | 61.5646 | -0.0045023 | -0.0091708 | 0.0015427 | 0.014028 | -0.0035019 | 0.015038 | 0.00053414 | -0.00089301 | -0.00038025 | 0.014951 | 0.013479 | 0.017107 | -0.026423 | -0.030644 | -0.067927 | 0.020079 | -0.022536 | 0.12365 | -0.021847 | -0.040161 | -0.068322 | -0.005985 | -0.034533 | 0.082386 | 0.021486 | -0.12752 | 61.465 | -61.5446 | 61.4604 | 61.4189 | -0.04608 | -61.5872 | -61.441 | 61.3593 | -61.5992 | 61.4467 | 61.4808 | 0.12153 | -61.4823 | -61.5431 | 61.5069 | 61.4643 | 61.6105 | 61.4562 | -61.5865 | 61.4523 | 61.5692 | 61.5083 | 61.4185 | -61.6922
630.6406 | 123.2712 | -61.4594 | 61.528 | -0.012133 | -0.0089572 | 0.0011155 | 0.013601 | -0.0035019 | 0.015679 | 0.00053414 | -0.00089301 | -0.00016665 | 0.014738 | 0.013479 | 0.017107 | -0.03558 | -0.039801 | -0.067927 | 0.024657 | -0.022536 | 0.11449 | -0.021847 | -0.044739 | -0.077479 | -0.015143 | -0.034533 | 0.082386 | 0.016908 | -0.12294 | 61.4375 | -61.5034 | 61.4238 | 61.3914 | -0.04608 | -61.5506 | -61.4135 | 61.3364 | -61.5625 | 61.4146 | 61.4442 | 0.1078 | -61.4456 | -61.5111 | 61.484 | 61.4368 | 61.5738 | 61.4196 | -61.5499 | 61.4248 | 61.5417 | 61.4763 | 61.3819 | -61.651
631.6406 | 123.1705 | -61.5051 | 61.5509 | -0.0045023 | -0.0095982 | 0.0013291 | 0.013601 | -0.0030747 | 0.015038 | -0.0070964 | -0.00089301 | -0.00038025 | 0.01431 | 0.013479 | 0.017107 | -0.026423 | -0.039801 | -0.067927 | 0.015501 | -0.017957 | 0.11449 | -0.021847 | -0.035582 | -0.0729 | -0.001407 | -0.039111 | 0.082386 | 0.003172 | -0.12752 | 61.4833 | -61.5354 | 61.4787 | 61.4372 | -0.04608 | -61.5689 | -61.4364 | 61.3776 | -61.59 | 61.4695 | 61.5037 | 0.12611 | -61.4685 | -61.5477 | 61.5206 | 61.4872 | 61.6196 | 61.4653 | -61.5727 | 61.466 | 61.5875 | 61.5083 | 61.4322 | -61.6784
632.6406 | 123.317 | -61.4685 | 61.528 | -0.0045023 | -0.0091708 | 0.0013291 | 0.013601 | -0.0028609 | 0.015251 | -0.0070964 | -0.0011066 | -0.00016665 | 0.014738 | 0.013479 | 0.017321 | -0.031001 | -0.035222 | -0.077084 | 0.015501 | -0.027115 | 0.12365 | -0.031005 | -0.040161 | -0.068322 | -0.005985 | -0.039111 | 0.077807 | 0.016908 | -0.12294 | 61.4375 | -61.5125 | 61.4375 | 61.3914 | -0.046079 | -61.5551 | -61.4044 | 61.3456 | -61.5671 | 61.4283 | 61.4625 | 0.11695 | -61.4502 | -61.5111 | 61.484 | 61.4414 | 61.5922 | 61.4333 | -61.559 | 61.4294 | 61.5463 | 61.4854 | 61.4002 | -61.651
633.6406 | 123.1476 | -61.5234 | 61.6013 | 0.0031287 | -0.0093846 | 0.0017565 | 0.014242 | -0.0030747 | 0.015038 | 0.00053414 | -0.00067941 | -0.00016665 | 0.014738 | 0.013692 | 0.017107 | -0.026423 | -0.039801 | -0.077084 | 0.020079 | -0.022536 | 0.12365 | -0.017268 | -0.044739 | -0.068322 | -0.010564 | -0.039111 | 0.086964 | 0.021486 | -0.12294 | 61.5062 | -61.5812 | 61.497 | 61.4464 | -0.059816 | -61.6238 | -61.4776 | 61.4005 | -61.6404 | 61.4787 | 61.5129 | 0.11238 | -61.5143 | -61.5798 | 61.5435 | 61.5009 | 61.6471 | 61.4836 | -61.6185 | 61.4843 | 61.6104 | 61.5449 | 61.4551 | -61.7242
634.6406 | 123.317 | -61.4365 | 61.5234 | -0.012133 | -0.0093846 | 0.0013291 | 0.013601 | -0.0035019 | 0.015251 | 0.00053414 | -0.0011066 | -0.00038025 | 0.014951 | 0.013479 | 0.017321 | -0.026423 | -0.030644 | -0.067927 | 0.020079 | -0.022536 | 0.11907 | -0.021847 | -0.040161 | -0.0729 | -0.005985 | -0.039111 | 0.082386 | 0.016908 | -0.12294 | 61.4146 | -61.5034 | 61.41 | 61.3685 | -0.04608 | -61.546 | -61.4044 | 61.3135 | -61.5625 | 61.3963 | 61.4305 | 0.11695 | -61.4411 | -61.5065 | 61.4565 | 61.4139 | 61.5555 | 61.4058 | -61.5453 | 61.3974 | 61.5188 | 61.4534 | 61.3636 | -61.6464
635.6406 | 123.1064 | -61.5143 | 61.5646 | -0.0045023 | -0.0093846 | 0.0013291 | 0.014028 | -0.0032883 | 0.015251 | -0.0070964 | -0.00089301 | -0.00016665 | 0.014524 | 0.013479 | 0.017321 | -0.040158 | -0.035222 | -0.072505 | 0.015501 | -0.027115 | 0.12365 | -0.017268 | -0.040161 | -0.0729 | -0.015143 | -0.039111 | 0.086964 | 0.012329 | -0.12294 | 61.497 | -61.5491 | 61.4741 | 61.4418 | -0.055237 | -61.5918 | -61.441 | 61.3913 | -61.6037 | 61.4741 | 61.4991 | 0.1078 | -61.4777 | -61.5523 | 61.5298 | 61.4872 | 61.6379 | 61.4791 | -61.5819 | 61.4752 | 61.6012 | 61.5266 | 61.4414 | -61.6876
636.6406 | 123.2574 | -61.4777 | 61.528 | -0.0045023 | -0.0095982 | 0.0015427 | 0.014028 | -0.0030747 | 0.014824 | -0.0070964 | -0.00089301 | -0.00038025 | 0.01431 | 0.013479 | 0.017535 | -0.031001 | -0.030644 | -0.067927 | 0.024657 | -0.027115 | 0.11907 | -0.012689 | -0.040161 | -0.059164 | -0.005985 | -0.034533 | 0.077807 | 0.007751 | -0.12752 | 61.465 | -61.5034 | 61.4467 | 61.4097 | -0.055238 | -61.5551 | -61.4089 | 61.3501 | -61.5625 | 61.4375 | 61.4717 | 0.12153 | -61.4502 | -61.5203 | 61.5023 | 61.4505 | 61.5967 | 61.447 | -61.5407 | 61.4431 | 61.5555 | 61.4854 | 61.4185 | -61.6555
637.6406 | 123.1567 | -61.5097 | 61.5875 | -0.0045023 | -0.0093846 | 0.0013291 | 0.013387 | -0.0030747 | 0.014824 | 0.00053414 | -0.00067941 | -0.00059405 | 0.01431 | 0.013479 | 0.017107 | -0.031001 | -0.030644 | -0.072505 | 0.015501 | -0.027115 | 0.12823 | -0.035584 | -0.035582 | -0.0729 | -0.005985 | -0.034533 | 0.082386 | 0.021486 | -0.11378 | 61.4741 | -61.572 | 61.4787 | 61.4372 | -0.036921 | -61.6146 | -61.4593 | 61.3959 | -61.6221 | 61.4741 | 61.5037 | 0.1078 | -61.5051 | -61.566 | 61.5252 | 61.4826 | 61.6379 | 61.4791 | -61.6231 | 61.4752 | 61.5921 | 61.5312 | 61.4368 | -61.7013
638.6406 | 123.1842 | -61.5005 | 61.5692 | 0.0031287 | -0.0091708 | 0.0013291 | 0.013815 | -0.0035019 | 0.015251 | -0.0070964 | -0.00089301 | -0.00038025 | 0.01431 | 0.013479 | 0.016894 | -0.03558 | -0.035222 | -0.08624 | 0.020079 | -0.017957 | 0.11907 | -0.035584 | -0.031003 | -0.059164 | -0.015143 | -0.034533 | 0.077807 | -0.001407 | -0.11836 | 61.465 | -61.5491 | 61.465 | 61.4143 | -0.050656 | -61.5872 | -61.4501 | 61.3822 | -61.6037 | 61.4695 | 61.4854 | 0.10322 | -61.4914 | -61.5706 | 61.5206 | 61.4826 | 61.6196 | 61.4653 | -61.6048 | 61.466 | 61.5784 | 61.4991 | 61.4414 | -61.6876
639.6406 | 123.175 | -61.5005 | 61.5601 | 0.0031287 | -0.0091708 | 0.0013291 | 0.013601 | -0.0032883 | 0.015251 | 0.00053414 | -0.00067941 | -0.00016665 | 0.01431 | 0.013479 | 0.017535 | -0.03558 | -0.035222 | -0.081662 | 0.029236 | -0.022536 | 0.11907 | -0.040163 | -0.031003 | -0.068322 | -0.010564 | -0.039111 | 0.082386 | 0.016908 | -0.12294 | 61.4604 | -61.5308 | 61.465 | 61.4189 | -0.041499 | -61.5826 | -61.441 | 61.3776 | -61.5992 | 61.4695 | 61.49 | 0.11238 | -61.4777 | -61.5432 | 61.5298 | 61.478 | 61.6196 | 61.4653 | -61.6002 | 61.4614 | 61.5829 | 61.5175 | 61.4322 | -61.683
640.6406 | 123.2254 | -61.5051 | 61.5601 | -0.0045023 | -0.0089572 | 0.0013291 | 0.013815 | -0.0032883 | 0.015251 | -0.0070964 | -0.00089301 | -0.00059405 | 0.014524 | 0.013906 | 0.017107 | -0.026423 | -0.035222 | -0.067927 | 0.020079 | -0.027115 | 0.12365 | -0.031005 | -0.040161 | -0.0729 | -0.019721 | -0.034533 | 0.082386 | 0.021486 | -0.12294 | 61.4741 | -61.54 | 61.4787 | 61.4372 | -0.036922 | -61.5872 | -61.4364 | 61.3822 | -61.5946 | 61.465 | 61.4854 | 0.10322 | -61.4777 | -61.5386 | 61.5252 | 61.478 | 61.6288 | 61.4699 | -61.5911 | 61.4706 | 61.5875 | 61.5266 | 61.4322 | -61.683
641.6406 | 123.2162 | -61.4777 | 61.5601 | 0.0031287 | -0.0093846 | 0.0011155 | 0.013601 | -0.0030747 | 0.014824 | 0.0081646 | -0.0011066 | 4.695e-05 | 0.014524 | 0.013692 | 0.017321 | -0.031001 | -0.035222 | -0.072505 | 0.020079 | -0.013378 | 0.11449 | -0.035584 | -0.031003 | -0.068322 | -0.010564 | -0.034533 | 0.082386 | 0.016908 | -0.11378 | 61.4421 | -61.54 | 61.4467 | 61.4052 | -0.036921 | -61.5734 | -61.4456 | 61.3639 | -61.5946 | 61.4467 | 61.4671 | 0.10322 | -61.4777 | -61.5432 | 61.4977 | 61.4643 | 61.5922 | 61.4424 | -61.5956 | 61.4431 | 61.56 | 61.4946 | 61.4093 | -61.6738
642.6406 | 123.1796 | -61.496 | 61.5692 | -0.012133 | -0.0095982 | 0.00090168 | 0.014028 | -0.0030747 | 0.015038 | -0.014727 | -0.00067941 | -0.00016665 | 0.01431 | 0.013479 | 0.017107 | -0.03558 | -0.035222 | -0.081662 | 0.029236 | -0.027115 | 0.11449 | -0.031005 | -0.026425 | -0.063743 | -0.015143 | -0.034533 | 0.073228 | 0.016908 | -0.1092 | 61.465 | -61.54 | 61.4604 | 61.4143 | -0.050657 | -61.5963 | -61.4547 | 61.3868 | -61.6037 | 61.4695 | 61.4808 | 0.09406 | -61.496 | -61.5523 | 61.5252 | 61.4689 | 61.6105 | 61.4608 | -61.6002 | 61.4614 | 61.5692 | 61.5129 | 61.4322 | -61.6784
643.6406 | 123.1659 | -61.4822 | 61.5967 | -0.0045023 | -0.0093846 | 0.0015427 | 0.013387 | -0.0030747 | 0.015251 | 0.00053414 | -0.00089301 | -0.00059405 | 0.014524 | 0.013265 | 0.017107 | -0.031001 | -0.035222 | -0.072505 | 0.024657 | -0.031693 | 0.12365 | -0.040163 | -0.026425 | -0.059164 | -0.010564 | -0.039111 | 0.077807 | 0.026065 | -0.11836 | 61.4421 | -61.572 | 61.4512 | 61.4097 | -0.032342 | -61.6284 | -61.473 | 61.3639 | -61.6358 | 61.4558 | 61.4717 | 0.1078 | -61.5189 | -61.5706 | 61.5069 | 61.4505 | 61.6059 | 61.447 | -61.6368 | 61.4431 | 61.56 | 61.5083 | 61.4231 | -61.715
644.6406 | 123.2162 | -61.5143 | 61.5463 | -0.012133 | -0.0091708 | 0.0013291 | 0.013815 | -0.0032883 | 0.015251 | -0.0070964 | -0.00089301 | -0.00038025 | 0.014738 | 0.013692 | 0.017107 | -0.031001 | -0.035222 | -0.072505 | 0.020079 | -0.022536 | 0.12365 | -0.031005 | -0.026425 | -0.063743 | -0.010564 | -0.034533 | 0.091543 | 0.012329 | -0.11378 | 61.4833 | -61.5262 | 61.4833 | 61.4418 | -0.0415 | -61.5689 | -61.4227 | 61.4005 | -61.5809 | 61.4879 | 61.5037 | 0.10322 | -61.4548 | -61.534 | 61.5344 | 61.4917 | 61.6379 | 61.4791 | -61.5773 | 61.4797 | 61.6058 | 61.5266 | 61.4505 | -61.6601
645.6406 | 123.1476 | -61.5005 | 61.5875 | 0.0031287 | -0.0095982 | 0.0013291 | 0.014242 | -0.0030747 | 0.015038 | -0.0070964 | -0.0011066 | -0.00016665 | 0.01431 | 0.013265 | 0.017107 | -0.03558 | -0.035222 | -0.072505 | 0.033814 | -0.059167 | 0.12365 | -0.085952 | -0.021846 | -0.068322 | -0.015143 | -0.029954 | 0.082386 | -0.12045 | -0.11836 | 61.4146 | -61.5537 | 61.465 | 61.428 | 0.013447 | -61.6467 | -61.4639 | 61.3822 | -61.6175 | 61.4787 | 61.4854 | 0.10322 | -61.5051 | -61.708 | 61.5344 | 61.4414 | 61.6242 | 61.4653 | -61.6735 | 61.4706 | 61.5829 | 61.3801 | 61.4322 | -61.7059
646.6406 | 123.1979 | -61.5097 | 61.5601 | -0.019764 | -0.0089572 | 0.0013291 | 0.013815 | -0.0030747 | 0.015038 | -0.014727 | -0.00046581 | 4.695e-05 | 0.014951 | 0.013692 | 0.017321 | -0.031001 | -0.035222 | -0.077084 | 0.020079 | -0.077483 | 0.11907 | 0.12926 | -0.021846 | -0.054586 | -0.010564 | -0.039111 | 0.086964 | -0.14334 | -0.12294 | 61.639 | -61.54 | 61.4787 | 61.4326 | -0.20634 | -61.6375 | -61.441 | 61.3868 | -61.5992 | 61.4879 | 61.4991 | 0.11238 | -61.4731 | -61.7034 | 61.5298 | 61.4322 | 61.6288 | 61.4745 | -61.4308 | 61.4706 | 61.5967 | 61.3664 | 61.4551 | -61.683

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2 | Cable 3
-0.2458 | 20.648 | 19.9442 | 20.0965 | 20.1788
0.7542 | 20.6506 | 19.9417 | 20.0918 | 20.1769
1.7542 | 20.9632 | 19.9401 | 20.0868 | 20.1848
2.7542 | 21.9585 | 19.9364 | 20.0897 | 20.1796
3.7542 | 23.7099 | 19.9438 | 20.0919 | 20.1818
4.7542 | 26.1329 | 19.9469 | 20.0936 | 20.1698
5.7542 | 29.1092 | 19.9382 | 20.0897 | 20.1786
6.7542 | 32.527 | 19.9506 | 20.0945 | 20.1881
7.7542 | 36.3345 | 19.9579 | 20.0998 | 20.1774
8.7542 | 40.4657 | 19.9838 | 20.1124 | 20.1822
9.7542 | 44.854 | 20.0068 | 20.1184 | 20.1884
10.7542 | 49.4559 | 20.0184 | 20.139 | 20.1805
11.7542 | 54.2554 | 20.0591 | 20.1515 | 20.1811
12.7542 | 59.2665 | 20.0954 | 20.1828 | 20.178
13.7542 | 64.4316 | 20.137 | 20.2118 | 20.1785
14.7542 | 69.7219 | 20.2029 | 20.2445 | 20.1802
15.7542 | 75.0951 | 20.2851 | 20.2949 | 20.1786
16.7542 | 80.6172 | 20.356 | 20.3435 | 20.1828
17.7542 | 86.2028 | 20.4521 | 20.4038 | 20.1827
18.7542 | 91.7963 | 20.5586 | 20.4634 | 20.1824
19.7542 | 97.5011 | 20.6814 | 20.5327 | 20.1852
20.7542 | 103.2926 | 20.8039 | 20.6217 | 20.1804
21.7542 | 109.1263 | 20.952 | 20.7098 | 20.1824
22.7542 | 114.9826 | 21.1045 | 20.8101 | 20.177
23.7542 | 120.8666 | 21.289 | 20.9285 | 20.186
24.7542 | 126.7475 | 21.4697 | 21.0586 | 20.185
25.7542 | 132.6688 | 21.6671 | 21.2118 | 20.1881
26.7542 | 138.7144 | 21.8724 | 21.3695 | 20.1849
27.7542 | 144.7212 | 22.1029 | 21.5231 | 20.1958
28.7542 | 150.6845 | 22.352 | 21.7159 | 20.2014
29.7542 | 156.5718 | 22.6063 | 21.9176 | 20.1993
30.7542 | 162.4878 | 22.8729 | 22.1404 | 20.2072
31.7542 | 168.4694 | 23.1842 | 22.3848 | 20.2023
32.7542 | 174.3766 | 23.4826 | 22.6355 | 20.2029
33.7542 | 180.2524 | 23.8205 | 22.9175 | 20.2174
34.7542 | 186.1489 | 24.1728 | 23.2154 | 20.2164
35.7542 | 192.1808 | 24.5347 | 23.5259 | 20.2191
36.7542 | 198.2289 | 24.9239 | 23.8524 | 20.2317
37.7542 | 204.2266 | 25.3216 | 24.1958 | 20.2296
38.7542 | 210.1787 | 25.7417 | 24.5479 | 20.2371
39.7542 | 216.0464 | 26.1951 | 24.9154 | 20.243
40.7542 | 221.8699 | 26.6682 | 25.3166 | 20.2561
41.7542 | 227.8055 | 27.1561 | 25.7307 | 20.2644
42.7542 | 233.6492 | 27.6934 | 26.1746 | 20.269
43.7542 | 239.4289 | 28.2233 | 26.6344 | 20.2841
44.7542 | 245.2962 | 28.7962 | 27.108 | 20.2938
45.7542 | 251.1224 | 29.3847 | 27.5963 | 20.306
46.7542 | 256.8418 | 29.9955 | 28.1065 | 20.3138
47.7542 | 262.4046 | 30.6232 | 28.6416 | 20.3305
48.7542 | 268.0026 | 31.3058 | 29.1863 | 20.3416
49.7542 | 273.7269 | 31.9907 | 29.7574 | 20.3559
50.7542 | 279.4331 | 32.7053 | 30.3593 | 20.3782
51.7542 | 285.1254 | 33.4449 | 30.974 | 20.3866
52.7542 | 290.77 | 34.2087 | 31.6197 | 20.4059
53.7542 | 296.2732 | 34.985 | 32.2872 | 20.4341
54.7542 | 301.8584 | 35.7901 | 32.9769 | 20.4496
55.7542 | 307.4429 | 36.6289 | 33.6957 | 20.4769
56.7542 | 312.9797 | 37.4869 | 34.4228 | 20.4933
57.7542 | 318.4586 | 38.3588 | 35.1728 | 20.5214
58.7542 | 323.7561 | 39.2574 | 35.9619 | 20.5525
59.7542 | 329.0432 | 40.1758 | 36.7622 | 20.5726
60.7542 | 334.3624 | 41.109 | 37.5895 | 20.607
61.7542 | 339.7709 | 42.0947 | 38.4265 | 20.6473
62.7542 | 345.0836 | 43.0719 | 39.2796 | 20.6721
63.7542 | 350.2955 | 44.101 | 40.1614 | 20.704
64.7542 | 355.4859 | 45.1448 | 41.0539 | 20.7479
65.7542 | 360.5883 | 46.204 | 41.9756 | 20.7834
66.7542 | 365.8473 | 47.314 | 42.9277 | 20.8289
67.7542 | 371.1218 | 48.4603 | 43.9073 | 20.8596
68.7542 | 376.3579 | 49.6266 | 44.9243 | 20.9052
69.7542 | 381.5677 | 50.8275 | 45.9766 | 20.9599
70.7542 | 386.7151 | 52.064 | 47.0476 | 21.0019
71.7542 | 391.7758 | 53.3463 | 48.1651 | 21.058
72.7542 | 396.7383 | 54.6616 | 49.296 | 21.1101
73.7542 | 401.6572 | 56.0578 | 50.4621 | 21.1577
74.7542 | 406.4858 | 57.4818 | 51.6646 | 21.2236
75.7542 | 411.1751 | 58.9411 | 52.893 | 21.2871
76.7542 | 415.992 | 60.4525 | 54.1503 | 21.3427
77.7542 | 420.837 | 62.0025 | 55.4544 | 21.4144
78.7542 | 425.217 | 63.6014 | 56.7804 | 21.4773
79.7542 | 429.0997 | 65.245 | 58.1423 | 21.5474
80.7542 | 432.6921 | 66.8974 | 59.5463 | 21.6179
81.7542 | 436.2067 | 68.6394 | 60.9747 | 21.6995
82.7542 | 439.3371 | 70.371 | 62.4525 | 21.7781
83.7542 | 442.3696 | 72.1583 | 63.9587 | 21.8647
84.7542 | 445.1188 | 73.9929 | 65.5055 | 21.9504
85.7542 | 447.9622 | 75.8372 | 67.0687 | 22.0312
86.7542 | 450.6534 | 77.7302 | 68.6668 | 22.1153
87.7542 | 453.5857 | 79.6323 | 70.2736 | 22.2116
88.7542 | 456.21 | 81.571 | 71.9081 | 22.3105
89.7542 | 458.5506 | 83.5694 | 73.5693 | 22.4121
90.7542 | 460.6915 | 85.5933 | 75.2533 | 22.5149
91.7542 | 462.5047 | 87.6429 | 76.9325 | 22.6241
92.7542 | 463.984 | 89.7591 | 78.6275 | 22.7379
93.7542 | 465.296 | 91.8987 | 80.3386 | 22.8445
94.7542 | 466.5542 | 94.0973 | 82.0596 | 22.9619
95.7542 | 467.4805 | 96.3179 | 83.8068 | 23.0819
96.7542 | 468.075 | 98.5518 | 85.5569 | 23.2015
97.7542 | 468.6007 | 100.8106 | 87.3023 | 23.3344
98.7542 | 469.1503 | 103.1079 | 89.0519 | 23.4655
99.7542 | 469.5558 | 105.4073 | 90.8048 | 23.598
100.7542 | 469.5809 | 107.683 | 92.5732 | 23.736
101.7542 | 469.6431 | 109.9698 | 94.3197 | 23.8792
102.7542 | 469.7349 | 112.2614 | 96.0773 | 24.0204
103.7542 | 469.7915 | 114.5043 | 97.8331 | 24.1738
104.7542 | 469.7854 | 116.7515 | 99.5675 | 24.3229
105.7542 | 469.7699 | 118.9815 | 101.296 | 24.4912
106.7542 | 469.7767 | 121.196 | 103.0384 | 24.6413
107.7542 | 469.6409 | 123.3441 | 104.7458 | 24.8098
108.7542 | 469.5695 | 125.4648 | 106.4471 | 24.9743
109.7542 | 469.4827 | 127.5135 | 108.1395 | 25.1423
110.7542 | 469.6029 | 129.466 | 109.8236 | 25.3238
111.7542 | 469.6248 | 131.3539 | 111.5126 | 25.4957
112.7542 | 469.6278 | 133.1366 | 113.185 | 25.6843
113.7542 | 469.7249 | 134.8712 | 114.848 | 25.8663
114.7542 | 469.8398 | 136.5502 | 116.5002 | 26.0596
115.7542 | 469.8896 | 138.1394 | 118.1571 | 26.2449
116.7542 | 469.9176 | 139.6622 | 119.8052 | 26.4388
117.7542 | 469.9702 | 141.1487 | 121.4802 | 26.6408
118.7542 | 470.1707 | 142.553 | 123.1488 | 26.8508
119.7542 | 470.4022 | 143.7862 | 124.8124 | 27.058
120.7542 | 470.6287 | 144.6779 | 126.4962 | 27.268
121.7542 | 470.7442 | 145.4809 | 128.1995 | 27.4903
122.7542 | 471.0258 | 146.2342 | 129.9212 | 27.6858
123.7542 | 471.0963 | 146.9564 | 131.6781 | 27.9104
124.7542 | 471.2284 | 147.8564 | 133.459 | 28.1326
125.7542 | 471.413 | 149.2154 | 135.2843 | 28.3508
126.7542 | 471.5542 | 150.6031 | 137.1571 | 28.5835
127.7542 | 471.7752 | 151.7088 | 139.0659 | 28.8112
128.7542 | 471.9327 | 152.5518 | 141.0403 | 29.0369
129.7542 | 472.2684 | 153.2623 | 143.0532 | 29.2787
130.7542 | 472.5735 | 154.0018 | 145.0911 | 29.5133
131.7542 | 472.7875 | 154.7481 | 147.1841 | 29.7486
132.7542 | 473.0884 | 155.6651 | 149.6522 | 29.9836
133.7542 | 473.0169 | 156.5179 | 153.4921 | 30.2221
134.7542 | 473.1218 | 157.6996 | 157.3272 | 30.4684
135.7542 | 473.1732 | 158.8726 | 160.6508 | 30.7139
136.7542 | 473.2865 | 160.275 | 163.9563 | 30.9567
137.7542 | 473.3545 | 161.6912 | 167.3257 | 31.2149
138.7542 | 473.5222 | 163.18 | 170.8226 | 31.4632
139.7542 | 473.6932 | 164.8558 | 178.3555 | 31.7144
140.7542 | 473.6698 | 166.45 | 184.9311 | 31.963
141.7542 | 473.6246 | 168.042 | 190.1114 | 32.2207
142.7542 | 473.689 | 169.605 | 194.7772 | 32.4783
143.7542 | 473.8323 | 171.5313 | 199.2714 | 32.7349
144.7542 | 473.9703 | 173.2876 | 203.6511 | 33.0008
145.7542 | 473.9912 | 175.4227 | 207.8568 | 33.2655
146.7542 | 473.8746 | 177.0757 | 211.614 | 33.5346
147.7542 | 473.7039 | 178.6542 | 215.2341 | 33.8072
148.7542 | 473.6588 | 180.3008 | 218.7818 | 34.0783
149.7542 | 473.7927 | 181.8585 | 222.2153 | 34.3523
150.7542 | 473.9034 | 183.2339 | 225.4064 | 34.6215
151.7542 | 473.9131 | 184.7602 | 228.4369 | 34.9056
152.7542 | 473.8497 | 186.1995 | 231.2963 | 35.1779
153.7542 | 473.9057 | 187.8295 | 234.2037 | 35.4723
154.7542 | 473.8635 | 189.1977 | 237.0686 | 35.7623
155.7542 | 473.7105 | 190.4376 | 239.7195 | 36.053
156.7542 | 473.7765 | 191.7191 | 242.264 | 36.3421
157.7542 | 473.8364 | 193.1752 | 244.8175 | 36.6529
158.7542 | 473.8482 | 194.3218 | 247.246 | 36.9588
159.7542 | 473.9166 | 195.4764 | 249.6958 | 37.2562
160.7542 | 474.006 | 196.8497 | 252.0681 | 37.5638
161.7542 | 473.8556 | 197.9804 | 254.6605 | 37.8706
162.7542 | 473.7651 | 199.1779 | 256.8744 | 38.1825
163.7542 | 473.6873 | 200.2544 | 259.044 | 38.496
164.7542 | 473.8732 | 201.3253 | 261.1227 | 38.8081
165.7542 | 474.0853 | 202.4505 | 263.1634 | 39.1311
166.7542 | 474.1412 | 203.5627 | 265.4925 | 39.4494
167.7542 | 474.1472 | 204.4237 | 267.8422 | 39.7762
168.7542 | 474.2854 | 205.5575 | 269.7754 | 40.1071
169.7542 | 474.2293 | 206.5969 | 271.776 | 40.4347
170.7542 | 474.1168 | 207.6384 | 273.9738 | 40.7623
171.7542 | 474.1172 | 208.9478 | 276.293 | 41.1029
172.7542 | 473.9815 | 209.9946 | 278.7943 | 41.4393
173.7542 | 473.9691 | 211.0934 | 281.0062 | 41.7757
174.7542 | 474.082 | 211.816 | 283.1051 | 42.1229
175.7542 | 474.038 | 212.7275 | 285.3106 | 42.4549
176.7542 | 473.9971 | 213.6271 | 287.2122 | 42.8164
177.7542 | 474.055 | 214.5979 | 289.0514 | 43.1579
178.7542 | 474.0738 | 215.5803 | 290.7133 | 43.5221
179.7542 | 474.0475 | 216.6519 | 292.3333 | 43.8739
180.7542 | 474.0109 | 217.4913 | 293.8145 | 44.2333
181.7542 | 473.9945 | 218.4648 | 295.4078 | 44.5982
182.7542 | 473.9055 | 219.3487 | 297.3213 | 44.9715
183.7542 | 473.8884 | 220.1529 | 299.1383 | 45.3368
184.7542 | 473.8999 | 220.8363 | 300.8178 | 45.7122
185.7542 | 473.899 | 221.5523 | 302.3609 | 46.1034
186.7542 | 473.7075 | 222.3046 | 303.8287 | 46.4774
187.7542 | 473.6729 | 223.0337 | 305.3081 | 46.8612
188.7542 | 473.5798 | 223.9073 | 306.7737 | 47.245
189.7542 | 473.6422 | 224.3791 | 308.2325 | 47.6199
190.7542 | 473.6063 | 224.8934 | 309.5918 | 48.0173
191.7542 | 473.5336 | 225.6783 | 310.8911 | 48.4112
192.7542 | 473.6183 | 226.2053 | 312.5633 | 48.8055
193.7542 | 473.6585 | 226.5109 | 314.1411 | 49.2036
194.7542 | 473.6303 | 224.7521 | 315.5598 | 49.6113
195.7542 | 473.5077 | 220.329 | 316.8493 | 50.01
196.7542 | 473.3566 | 220.0454 | 318.1037 | 50.4203
197.7542 | 473.305 | 218.408 | 319.3674 | 50.8373
198.7542 | 473.2192 | 218.897 | 320.3547 | 51.2501
199.7542 | 473.0716 | 218.2056 | 321.3704 | 51.6708
200.7542 | 472.9409 | 217.8793 | 322.5052 | 52.0896
201.7542 | 472.855 | 218.6148 | 323.7567 | 52.515
202.7542 | 472.854 | 219.8335 | 324.8917 | 52.9494
203.7542 | 472.8533 | 220.0083 | 325.9615 | 53.3794
204.7542 | 472.7546 | 219.4766 | 326.8535 | 53.8213
205.7542 | 472.6317 | 219.377 | 327.7592 | 54.2757
206.7542 | 472.4508 | 220.3536 | 328.6444 | 54.7289
207.7542 | 472.2281 | 221.1853 | 329.6832 | 55.1924
208.7542 | 471.9696 | 222.4156 | 330.9938 | 55.6616
209.7542 | 471.9349 | 223.1323 | 332.3158 | 56.1205
210.7542 | 471.8825 | 224.2852 | 333.2084 | 56.58
211.7542 | 471.8142 | 225.6192 | 334.175 | 57.0589
212.7542 | 471.6384 | 226.2404 | 335.3224 | 57.5292
213.7542 | 471.532 | 225.9507 | 336.193 | 58.0027
214.7542 | 471.4867 | 226.326 | 337.1995 | 58.4825
215.7542 | 471.459 | 226.4127 | 338.2013 | 58.9619
216.7542 | 471.4399 | 227.2941 | 338.9967 | 59.452
217.7542 | 471.3563 | 228.904 | 340.0203 | 59.933
218.7542 | 471.3313 | 229.897 | 341.2801 | 60.4257
219.7542 | 471.2219 | 230.8205 | 342.5018 | 60.921
220.7542 | 471.1164 | 231.6801 | 343.5129 | 61.4123
221.7542 | 471.0556 | 231.7459 | 344.6252 | 61.9031
222.7542 | 470.9834 | 231.732 | 345.9913 | 62.3969
223.7542 | 470.9251 | 233.4033 | 347.2094 | 62.8788
224.7542 | 470.8538 | 234.5209 | 348.1874 | 63.3712
225.7542 | 470.6436 | 235.3651 | 348.8905 | 63.8715
226.7542 | 470.5225 | 235.9227 | 349.8048 | 64.3667
227.7542 | 470.4493 | 236.1583 | 351.1433 | 64.8611
228.7542 | 470.3572 | 236.6769 | 352.2457 | 65.3638
229.7542 | 470.2825 | 237.3015 | 353.1345 | 65.8616
230.7542 | 470.2103 | 238.7168 | 354.1937 | 66.355
231.7542 | 470.0938 | 239.8288 | 355.4401 | 66.8434
232.7542 | 470.1047 | 241.1582 | 356.6502 | 67.3416
233.7542 | 470.068 | 241.9769 | 357.7239 | 67.8394
234.7542 | 470.1621 | 243.396 | 358.863 | 68.3246
235.7542 | 470.0136 | 244.3818 | 359.8147 | 68.8256
236.7542 | 469.9075 | 245.2289 | 361.1115 | 69.3144
237.7542 | 469.9139 | 246.1462 | 362.6684 | 69.8022
238.7542 | 469.834 | 247.5732 | 363.7555 | 70.3044
239.7542 | 469.7635 | 249.0515 | 364.7704 | 70.8035
240.7542 | 469.8367 | 250.6726 | 365.3803 | 71.3147
241.7542 | 469.8592 | 251.9911 | 366.4406 | 71.7967
242.7542 | 469.7859 | 253.3603 | 367.6473 | 72.2761
243.7542 | 469.5991 | 254.5934 | 368.8561 | 72.7497
244.7542 | 469.4211 | 255.2823 | 369.9782 | 73.2205
245.7542 | 469.308 | 255.6234 | 370.8754 | 73.6871
246.7542 | 469.212 | 255.7732 | 371.2643 | 74.1621
247.7542 | 469.4681 | 266.9924 | 383.5143 | 74.6372
248.7542 | 470.3328 | 281.5798 | 399.3501 | 75.1134
249.7542 | 471.6712 | 299.2663 | 413.5841 | 75.6049
250.7542 | 473.4114 | 310.1465 | 424.8452 | 76.1342
251.7542 | 474.4553 | 318.1979 | 430.7716 | 76.6848
252.7542 | 475.0195 | 320.5601 | 434.6445 | 77.2021
253.7542 | 475.0305 | 320.2781 | 435.5458 | 77.7029
254.7542 | 474.7137 | 321.1016 | 436.2418 | 78.1954
255.7542 | 474.5313 | 322.5943 | 436.9382 | 78.6995
256.7542 | 474.2756 | 322.849 | 437.4414 | 79.2146
257.7542 | 473.7714 | 322.3084 | 437.2461 | 79.722
258.7542 | 473.3021 | 322.9093 | 442.4006 | 80.2502
259.7542 | 473.1878 | 325.8598 | 448.5438 | 80.7943
260.7542 | 473.2318 | 329.8466 | 454.0134 | 81.3329
261.7542 | 473.2787 | 330.9468 | 459.4954 | 81.8712
262.7542 | 473.2232 | 333.4089 | 464.8588 | 82.4145
263.7542 | 472.9118 | 334.4243 | 466.1519 | 82.955
264.7542 | 472.3749 | 336.6309 | 464.7117 | 83.4955
265.7542 | 471.8981 | 338.5046 | 467.7483 | 84.053
266.7542 | 471.4908 | 339.7475 | 473.3223 | 84.5775
267.7542 | 471.1501 | 343.7244 | 479.9212 | 85.1053
268.7542 | 470.8825 | 346.1785 | 483.2297 | 85.6351
269.7542 | 470.6037 | 346.305 | 485.1345 | 86.1653
270.7542 | 470.2328 | 346.4203 | 487.0805 | 86.6997
271.7542 | 469.7788 | 346.832 | 490.3125 | 87.2215
272.7542 | 469.4428 | 347.4739 | 495.9391 | 87.7371
273.7542 | 469.1707 | 349.0797 | 500.2715 | 88.2446
274.7542 | 468.9534 | 352.682 | 505.0971 | 88.782
275.7542 | 468.5548 | 352.2476 | 507.2975 | 89.3119
276.7542 | 468.3444 | 353.779 | 511.3644 | 89.8442
277.7542 | 468.4383 | 354.3465 | 516.479 | 90.3907
278.7542 | 468.3175 | 362.1119 | 521.1602 | 90.9394
279.7542 | 467.949 | 360.3438 | 523.2429 | 91.4713
280.7542 | 467.5019 | 360.2809 | 527.3464 | 92.0125
281.7542 | 467.1722 | 361.1877 | 529.5768 | 92.536
282.7542 | 467.0465 | 362.4842 | 532.5785 | 93.0579
283.7542 | 466.7644 | 366.4117 | 536.8682 | 93.5951
284.7542 | 466.5534 | 365.5268 | 540.7357 | 94.1139
285.7542 | 466.2569 | 365.8689 | 544.2923 | 94.6626
286.7542 | 465.9577 | 369.6955 | 552.2947 | 95.1976
287.7542 | 465.6274 | 376.6175 | 555.2866 | 95.7234
288.7542 | 465.5812 | 387.9365 | 562.4689 | 96.256
289.7542 | 465.5921 | 395.0486 | 567.7736 | 96.8125
290.7542 | 465.8288 | 396.5723 | 573.0275 | 97.3268
291.7542 | 465.7365 | 397.1659 | 578.7244 | 97.8302
292.7542 | 465.7984 | 405.1577 | 581.0692 | 98.3406
293.7542 | 465.6713 | 410.2403 | 580.3517 | 98.7476
294.7542 | 465.5676 | 406.1655 | 586.0213 | 99.2071
295.7542 | 465.4925 | 409.5875 | 594.3669 | 99.6825
296.7542 | 465.5865 | 419.3939 | 597.7276 | 100.1069
297.7542 | 465.4813 | 426.63 | 601.414 | 100.6137
298.7542 | 465.3129 | 425.8877 | 603.3197 | 101.0434
299.7542 | 465.1694 | 427.1622 | 607.1197 | 101.479
300.7542 | 465.256 | 431.1772 | 609.991 | 101.9405
301.7542 | 465.3045 | 435.4815 | 612.8397 | 102.4385
302.7542 | 465.4827 | 433.352 | 616.9789 | 102.982
303.7542 | 465.5745 | 434.0507 | 618.0546 | 103.5532
304.7542 | 465.5173 | 440.5043 | 620.9072 | 104.1272
305.7542 | 465.7072 | 446.9142 | 630.643 | 104.6915
306.7542 | 465.938 | 443.3846 | 640.9743 | 105.311
307.7542 | 466.0527 | 450.5934 | 642.6519 | 105.9528
308.7542 | 466.2884 | 450.2944 | 641.2835 | 106.5234
309.7542 | 467.0512 | 449.1967 | 647.5088 | 107.1273
310.7542 | 466.9853 | 446.0442 | 652.5868 | 107.6971
311.7542 | 467.0386 | 444.3896 | 649.7362 | 108.2208
312.7542 | 466.9013 | 445.2346 | 646.1634 | 108.7713
313.7542 | 466.6981 | 446.911 | 643.554 | 109.3075
314.7542 | 466.5829 | 448.9413 | 645.3484 | 109.8296
315.7542 | 466.8168 | 449.4333 | 650.3827 | 110.4801
316.7542 | 466.8915 | 451.7488 | 645.3037 | 111.0514
317.7542 | 466.8356 | 452.3199 | 645.3379 | 111.6584
318.7542 | 467.073 | 458.0016 | 645.2907 | 112.3309
319.7542 | 467.0896 | 456.2593 | 642.2829 | 112.9865
320.7542 | 466.9206 | 458.4402 | 642.6215 | 113.6055
321.7542 | 466.8136 | 459.0479 | 645.0391 | 114.2345
322.7542 | 466.8774 | 466.8136 | 643.7791 | 114.9562
323.7542 | 466.95 | 469.0362 | 639.2484 | 115.6348
324.7542 | 466.9782 | 477.8605 | 634.8765 | 116.4483
325.7542 | 467.0454 | 480.1198 | 637.7618 | 117.2155
326.7542 | 467.1595 | 482.6827 | 641.4415 | 118.1324
327.7542 | 467.565 | 487.6394 | 634.0601 | 119.027
328.7542 | 467.69 | 491.931 | 630.2941 | 119.9362
329.7542 | 467.9453 | 492.9858 | 627.1894 | 121.0334
330.7542 | 467.9559 | 494.5355 | 622.8523 | 121.8769
331.7542 | 467.943 | 496.3327 | 624.8821 | 122.9178
332.7542 | 467.9427 | 502.3683 | 622.4237 | 123.9117
333.7542 | 467.9687 | 505.2064 | 618.2301 | 124.8365
334.7542 | 468.1741 | 506.4796 | 614.2162 | 126.0108
335.7542 | 468.2675 | 508.9691 | 611.7813 | 127.3989
336.7542 | 468.3003 | 505.3045 | 608.2029 | 128.2246
337.7542 | 468.3111 | 505.5974 | 604.5116 | 129.3479
338.7542 | 468.3435 | 507.3675 | 602.8967 | 130.504
339.7542 | 468.41 | 502.9501 | 600.5447 | 131.7776
340.7542 | 468.3802 | 501.0018 | 597.1533 | 133.3126
341.7542 | 468.3778 | 499.7289 | 593.3086 | 134.6786
342.7542 | 468.4203 | 499.0878 | 589.7505 | 136.1433
343.7542 | 468.4022 | 496.302 | 587.7242 | 137.3983
344.7542 | 468.4117 | 495.1085 | 585.2263 | 138.7929
345.7542 | 468.4177 | 491.0759 | 581.8153 | 140.3271
346.7542 | 468.4611 | 489.5168 | 579.7397 | 141.9427
347.7542 | 468.4898 | 489.6366 | 579.0061 | 143.4731
348.7542 | 468.4697 | 486.3904 | 577.9768 | 145.1991
349.7542 | 468.373 | 484.0952 | 576.9395 | 146.6479
350.7542 | 468.3826 | 481.4588 | 575.6743 | 148.0351
351.7542 | 468.4407 | 479.2631 | 573.2016 | 149.7212
352.7542 | 468.3725 | 477.136 | 571.1194 | 151.3717
353.7542 | 468.2514 | 476.0437 | 570.2992 | 152.6555
354.7542 | 468.2677 | 474.2943 | 568.0354 | 154.1149
355.7542 | 468.2059 | 472.0329 | 564.7649 | 155.9851
356.7542 | 468.1311 | 470.145 | 560.9601 | 157.4023
357.7542 | 468.1278 | 469.2851 | 559.2436 | 158.9517
358.7542 | 468.0606 | 468.3791 | 557.0999 | 160.5318
359.7542 | 467.9687 | 467.3951 | 555.8634 | 162.0266
360.7542 | 467.8775 | 466.1077 | 553.5007 | 163.827
361.7542 | 467.898 | 464.9017 | 550.0493 | 165.1701
362.7542 | 467.9267 | 464.5025 | 548.2236 | 166.4926
363.7542 | 467.9294 | 463.8243 | 546.452 | 168.0835
364.7542 | 467.9828 | 463.4814 | 544.8774 | 169.5255
365.7542 | 467.96 | 462.353 | 542.8579 | 170.9189
366.7542 | 467.9952 | 461.621 | 540.7976 | 172.5359
367.7542 | 468.0459 | 459.9569 | 537.442 | 174.2189
368.7542 | 468.0856 | 458.7608 | 534.5615 | 175.9595
369.7542 | 468.1491 | 458.1411 | 533.2681 | 177.5325
370.7542 | 468.1949 | 457.5607 | 531.687 | 179.2616
371.7542 | 468.2338 | 456.7852 | 529.8155 | 180.8608
372.7542 | 468.1981 | 456.545 | 528.9051 | 182.7852
373.7542 | 468.1634 | 455.9859 | 527.1149 | 184.5202
374.7542 | 468.1743 | 455.4038 | 525.3183 | 186.3007
375.7542 | 468.2481 | 455.1021 | 525.0877 | 188.0411
376.7542 | 468.354 | 453.93 | 522.3846 | 189.5263
377.7542 | 468.4036 | 453.0026 | 520.5511 | 190.8906
378.7542 | 468.4477 | 452.1346 | 518.4678 | 192.4877
379.7542 | 468.5349 | 451.9261 | 517.676 | 194.0566
380.7542 | 468.6369 | 451.0466 | 516.3438 | 195.5936
381.7542 | 468.7029 | 451.2099 | 515.9494 | 197.4469
382.7542 | 468.7539 | 450.8867 | 515.2093 | 199.2411
383.7542 | 468.7223 | 450.4824 | 513.9951 | 200.6101
384.7542 | 468.7398 | 449.9334 | 512.9871 | 202.0807
385.7542 | 468.8037 | 449.2478 | 511.4723 | 203.5225
386.7542 | 468.8985 | 448.763 | 511.2462 | 204.8147
387.7542 | 468.8708 | 448.1742 | 510.0756 | 206.102
388.7542 | 468.8191 | 446.8622 | 508.6155 | 207.7397
389.7542 | 468.7491 | 445.6692 | 507.3171 | 209.4006
390.7542 | 468.7431 | 445.4941 | 506.4636 | 211.2146
391.7542 | 468.7334 | 444.4602 | 505.6182 | 212.723
392.7542 | 468.7981 | 444.2284 | 505.063 | 214.474
393.7542 | 468.922 | 444.1363 | 504.3651 | 216.1999
394.7542 | 468.9839 | 444.0189 | 503.2313 | 217.5974
395.7542 | 469.0138 | 443.7212 | 502.7197 | 219.4952
396.7542 | 469.1116 | 443.2647 | 502.0242 | 220.9776
397.7542 | 469.1591 | 442.287 | 501.4088 | 222.6819
398.7542 | 469.1541 | 441.6307 | 500.8625 | 224.1593
399.7542 | 469.0894 | 440.4613 | 499.9586 | 225.8904
400.7542 | 469.0987 | 439.6253 | 499.2061 | 227.4888
401.7542 | 469.0091 | 438.9538 | 497.6378 | 229.2324
402.7542 | 468.9563 | 439.0193 | 497.141 | 230.602
403.7542 | 468.9009 | 438.4508 | 495.5521 | 232.1135
404.7542 | 468.866 | 438.1727 | 495.1772 | 233.612
405.7542 | 468.7959 | 438.1518 | 494.4967 | 234.9727
406.7542 | 468.7371 | 438.1052 | 493.9753 | 236.4457
407.7542 | 468.7726 | 437.5758 | 492.2858 | 237.8025
408.7542 | 468.8162 | 437.2288 | 491.4041 | 239.0706
409.7542 | 468.8523 | 436.2367 | 489.961 | 240.0857
410.7542 | 468.9435 | 435.4792 | 489.2646 | 241.3268
411.7542 | 468.965 | 435.4168 | 488.4889 | 242.5275
412.7542 | 468.9877 | 435.3518 | 487.4581 | 243.4086
413.7542 | 468.982 | 435.0604 | 486.9987 | 244.7418
414.7542 | 469.0319 | 434.2138 | 486.4036 | 245.9927
415.7542 | 469.1509 | 433.7486 | 486.015 | 246.8088
416.7542 | 469.1373 | 433.2503 | 485.5075 | 247.3659
417.7542 | 469.0882 | 433.5408 | 485.1824 | 248.3026
418.7542 | 469.0832 | 433.4405 | 483.9978 | 249.0032
419.7542 | 469.0495 | 433.6392 | 483.4971 | 249.6578
420.7542 | 469.002 | 433.5668 | 482.4791 | 250.3137
421.7542 | 468.8107 | 433.3025 | 481.6893 | 251.123
422.7542 | 468.6997 | 432.1236 | 481.0162 | 252.0214
423.7542 | 468.6254 | 431.4385 | 480.6736 | 252.6644
424.7542 | 468.496 | 431.3529 | 480.5756 | 253.4327
425.7542 | 468.4454 | 431.3424 | 479.711 | 254.0403
426.7542 | 468.3767 | 431.5003 | 479.2726 | 254.8649
427.7542 | 468.2782 | 430.522 | 478.8976 | 255.7072
428.7542 | 468.0957 | 429.7585 | 478.0364 | 256.3852
429.7542 | 467.9947 | 429.4566 | 478.0422 | 257.4907
430.7542 | 468.1089 | 429.2988 | 477.7408 | 258.1752
431.7542 | 468.0255 | 428.7529 | 477.1149 | 258.7634
432.7542 | 467.9319 | 428.6683 | 476.5371 | 259.6384
433.7542 | 467.8314 | 428.6932 | 476.076 | 260.5288
434.7542 | 467.9006 | 428.6315 | 475.2412 | 261.4068
435.7542 | 467.8771 | 428.8746 | 474.87 | 262.1622
436.7542 | 467.8951 | 428.0163 | 474.2849 | 263.2814
437.7542 | 467.9011 | 427.1858 | 473.5756 | 264.0876
438.7542 | 467.8772 | 426.6402 | 472.5005 | 264.5725
439.7542 | 467.7731 | 425.9948 | 472.2972 | 265.3079
440.7542 | 467.7042 | 425.6841 | 472.3442 | 266.2617
441.7698 | 467.7151 | 426.155 | 471.9522 | 267.057
442.7542 | 467.5707 | 425.4762 | 471.4592 | 268.1421
443.7542 | 467.5269 | 423.9681 | 470.0838 | 269.0257
444.7542 | 467.4583 | 422.6365 | 469.6798 | 269.9182
445.7542 | 467.3321 | 422.0929 | 468.9645 | 270.6866
446.7542 | 467.2957 | 421.7075 | 469.0692 | 271.6938
447.7542 | 467.341 | 421.4168 | 468.2311 | 272.6899
448.7542 | 467.3547 | 421.2843 | 468.3949 | 273.4917
449.7542 | 467.2999 | 420.6167 | 468.327 | 274.3777
450.7542 | 467.3708 | 419.8303 | 467.8115 | 275.313
451.7542 | 467.367 | 420.0649 | 467.6562 | 276.3403
452.7542 | 467.2646 | 420.8951 | 467.6787 | 277.3857
453.7542 | 467.2153 | 421.2622 | 467.2336 | 278.1707
454.7542 | 467.2512 | 421.3476 | 466.9151 | 279.0289
455.7542 | 467.2005 | 421.3518 | 466.5629 | 279.8639
456.7542 | 467.2739 | 421.1571 | 466.4431 | 280.6745
457.7542 | 467.3167 | 421.0826 | 466.2818 | 281.9522
458.7542 | 467.2707 | 420.7385 | 465.6646 | 282.7172
459.7542 | 467.2935 | 420.7921 | 465.0595 | 283.1752
460.7542 | 467.2459 | 420.7556 | 464.6023 | 284.1507
461.7542 | 467.2122 | 421.036 | 463.9851 | 284.8448
462.7542 | 467.2872 | 421.1335 | 463.5253 | 285.3946
463.7542 | 467.2571 | 420.3605 | 461.7165 | 286.0899
464.7542 | 467.1516 | 420.6463 | 461.7898 | 286.7968
465.7542 | 467.069 | 420.861 | 461.2288 | 287.3852
466.7542 | 467.0368 | 420.6984 | 460.7514 | 288.1257
467.7542 | 467.0577 | 420.4686 | 459.6688 | 288.6825
468.7542 | 466.8785 | 419.4105 | 458.8444 | 289.3852
469.7542 | 466.8204 | 418.6266 | 457.7389 | 290.0518
470.7542 | 466.8557 | 418.5206 | 457.858 | 290.7259
471.7542 | 466.8133 | 417.7469 | 457.545 | 291.5209
472.7542 | 466.8092 | 418.0834 | 456.5911 | 292.1703
473.7542 | 466.7958 | 417.1332 | 456.495 | 292.9563
474.7542 | 466.7977 | 416.2885 | 456.2972 | 293.6479
475.7542 | 466.7484 | 416.1919 | 455.1816 | 294.3964
476.7542 | 466.7997 | 416.5986 | 455.1369 | 295.0655
477.7542 | 466.7722 | 416.273 | 455.0597 | 295.7264
478.7542 | 466.7176 | 416.6055 | 454.6145 | 296.3887
479.7542 | 466.753 | 415.9625 | 454.5826 | 297.1611
480.7542 | 466.7175 | 415.7599 | 454.1803 | 297.9219
481.7542 | 466.8017 | 415.0992 | 453.1059 | 298.6883
482.7542 | 466.8775 | 414.9366 | 453.3015 | 299.464
483.7542 | 466.8308 | 415.4251 | 452.6635 | 300.1624
484.7542 | 466.7644 | 414.3585 | 452.3047 | 300.9295
485.7542 | 466.6731 | 413.802 | 451.1547 | 301.7236
486.7542 | 466.6448 | 413.2363 | 450.1181 | 302.5679
487.7542 | 466.6606 | 413.0886 | 449.1752 | 303.3058
488.7542 | 466.8032 | 413.0328 | 449.0417 | 304.0293
489.7542 | 466.8329 | 412.8689 | 448.7204 | 304.7509
490.7542 | 466.7366 | 412.6932 | 448.4555 | 305.4824
491.7542 | 466.6123 | 412.0791 | 448.3389 | 306.2381
492.7542 | 466.6445 | 412.6351 | 448.4316 | 307.0483
493.7542 | 466.627 | 412.1851 | 447.3621 | 307.7965
494.7542 | 466.5023 | 412.1092 | 446.954 | 308.5616
495.7542 | 466.5417 | 411.5467 | 446.0239 | 309.2586
496.7542 | 466.4283 | 412.5591 | 446.3047 | 309.9795
497.7542 | 466.4316 | 412.8705 | 445.972 | 310.7656
498.7542 | 466.4197 | 412.3509 | 445.2565 | 311.5165
499.7542 | 466.3448 | 411.7584 | 444.1653 | 312.2296
500.7542 | 466.3922 | 412.4721 | 444.2598 | 312.9159
501.7542 | 466.3015 | 412.3492 | 444.1351 | 313.5488
502.7542 | 466.2584 | 412.9466 | 444.0936 | 314.1867
503.7542 | 466.237 | 412.5886 | 443.898 | 314.3451
504.7542 | 466.2918 | 412.5894 | 443.7166 | 314.7934
505.7542 | 466.3631 | 412.8167 | 443.7088 | 315.3858
506.7542 | 466.225 | 412.5805 | 443.1251 | 315.7378
507.7542 | 466.1834 | 412.1978 | 442.9929 | 316.2413
508.7542 | 466.2103 | 411.7852 | 442.0099 | 316.5866
509.7542 | 466.185 | 411.7625 | 441.7126 | 317.1927
510.7542 | 466.1537 | 412.3182 | 441.3968 | 317.8132
511.7542 | 466.1168 | 411.5999 | 441.7712 | 318.4824
512.7542 | 466.2533 | 411.7056 | 442.1962 | 319.2029
513.7542 | 466.2926 | 411.7187 | 442.3394 | 320.0592
514.7542 | 466.2327 | 412.3904 | 441.2856 | 321.0236
515.7542 | 466.1882 | 412.2748 | 441.2449 | 321.809
516.7542 | 466.0996 | 412.3701 | 441.6312 | 322.6314
517.7542 | 466.1377 | 412.874 | 441.9802 | 323.3698
518.7542 | 466.1208 | 412.9187 | 441.9601 | 324.0482
519.7542 | 466.1475 | 412.4456 | 441.8475 | 324.6402
520.7542 | 466.1903 | 412.9112 | 442.0475 | 325.0846
521.7542 | 466.195 | 413.1376 | 441.7475 | 325.6227
522.7542 | 466.2718 | 412.7573 | 441.4355 | 326.2677
523.7542 | 466.2474 | 412.1765 | 441.2094 | 326.8089
524.7542 | 466.1428 | 412.72 | 441.2613 | 327.4606
525.7542 | 466.1553 | 411.6703 | 441.2063 | 328.3575
526.7542 | 466.1267 | 411.8753 | 441.1398 | 329.087
527.7542 | 466.0727 | 411.9767 | 440.0053 | 329.5463
528.7542 | 465.9935 | 412.119 | 440.3429 | 330.0335
529.7542 | 466.0887 | 412.0606 | 440.548 | 330.5449
530.7542 | 466.2208 | 412.4983 | 440.2332 | 331.0377
531.7542 | 466.2161 | 412.6914 | 439.9409 | 331.7137
532.7542 | 466.2202 | 412.5556 | 440.1519 | 332.4571
533.7542 | 466.1612 | 412.4253 | 440.1537 | 333.0358
534.7542 | 466.0579 | 412.7891 | 439.8339 | 333.3347
535.7542 | 466.0036 | 413.2719 | 439.9549 | 333.9592
536.7542 | 466.0296 | 412.6931 | 440.1426 | 334.2567
537.7542 | 466.1089 | 412.0953 | 439.4635 | 334.777
538.7542 | 466.168 | 412.1694 | 439.2494 | 335.4565
539.7542 | 466.1355 | 412.8674 | 439.2501 | 336.18
540.7542 | 466.0699 | 412.5279 | 438.9421 | 336.8589
541.7542 | 466.0917 | 412.5886 | 438.5066 | 337.5613
542.7542 | 466.0369 | 413.021 | 438.1398 | 338.2616
543.7542 | 466.1292 | 413.3036 | 438.5782 | 338.8542
544.7542 | 466.1552 | 412.8939 | 438.5149 | 339.2702
545.7542 | 466.238 | 412.9981 | 438.9259 | 339.9354
546.7542 | 466.1522 | 412.8494 | 438.7959 | 340.4813
547.7542 | 466.087 | 413.148 | 439.0014 | 341.045
548.7542 | 465.9772 | 413.7356 | 438.776 | 341.3906
549.7542 | 465.9632 | 413.8771 | 439.0847 | 341.657
550.7542 | 466.0247 | 414.2027 | 439.1353 | 341.8185
551.7542 | 466.1757 | 414.5899 | 439.4343 | 342.3357
552.7542 | 466.2735 | 414.2561 | 439.0892 | 342.8055
553.7542 | 466.2585 | 413.6718 | 438.7447 | 343.2856
554.7542 | 466.3165 | 413.6262 | 438.7204 | 343.8621
555.7542 | 466.3302 | 413.6383 | 438.4677 | 344.2936
556.7542 | 466.2215 | 414.0403 | 438.6547 | 344.3053
557.7542 | 466.2284 | 413.8556 | 437.533 | 344.5699
558.7542 | 466.217 | 414.0608 | 437.2458 | 344.9937
559.7542 | 466.2211 | 414.3502 | 437.0891 | 345.5245
560.7542 | 466.2191 | 414.1734 | 436.3098 | 345.9031
561.7542 | 466.2385 | 413.5069 | 435.7872 | 346.3446
562.7542 | 466.1795 | 412.9112 | 435.1973 | 346.7626
563.7542 | 466.1825 | 412.5464 | 434.0726 | 347.2072
564.7542 | 466.2492 | 413.0787 | 434.4449 | 347.7731
565.7542 | 466.1815 | 412.8532 | 434.0273 | 348.3784
566.7542 | 466.2687 | 413.4101 | 434.2771 | 348.9603
567.7542 | 466.2797 | 413.8919 | 434.966 | 349.719
568.7542 | 466.2302 | 414.2558 | 434.9945 | 350.5099
569.7542 | 466.1233 | 414.86 | 434.9743 | 351.1847
570.7542 | 465.9743 | 414.5486 | 433.7114 | 351.632
571.7542 | 465.9411 | 414.763 | 434.5513 | 353.2859
572.7542 | 465.8975 | 415.0975 | 434.9131 | 354.02
573.7542 | 465.8917 | 416.0371 | 435.4418 | 354.6932
574.7542 | 465.9619 | 416.9732 | 435.7518 | 354.2576
575.7542 | 466.0228 | 416.6411 | 435.5537 | 354.7134
576.7542 | 466.126 | 416.4052 | 435.5142 | 355.0247
577.7542 | 466.1699 | 417.635 | 435.7852 | 355.1692
578.7542 | 466.1615 | 417.8969 | 436.0474 | 355.9152
579.7542 | 466.1306 | 417.3718 | 435.919 | 356.5591
580.7542 | 466.037 | 418.3973 | 436.3196 | 357.0909
581.7542 | 466.1153 | 417.9721 | 435.3252 | 357.5576
582.7542 | 466.0892 | 417.3117 | 435.6723 | 357.8334
583.7542 | 466.0545 | 417.4112 | 435.2244 | 358.4026
584.7542 | 466.0309 | 418.2387 | 435.9727 | 360.3908
585.7542 | 466.1108 | 418.8412 | 436.2455 | 360.4776
586.7542 | 466.1343 | 418.9563 | 435.8783 | 361.1287
587.7542 | 466.09 | 419.458 | 436.2869 | 361.5056
588.7542 | 466.0797 | 419.7731 | 435.9761 | 362.3407
589.7542 | 466.1154 | 420.2819 | 436.7022 | 362.2467
590.7542 | 466.1116 | 420.6115 | 436.3781 | 362.6913
591.7542 | 466.003 | 420.267 | 436.1974 | 363.1991
592.7542 | 466.0877 | 420.486 | 436.4192 | 363.3898
593.7542 | 466.0407 | 421.2328 | 436.4877 | 363.7149
594.7542 | 465.9008 | 421.2068 | 436.966 | 364.0788
595.7542 | 465.8071 | 420.4931 | 437.3027 | 364.5353
596.7542 | 465.7728 | 420.937 | 437.6592 | 365.223
597.7542 | 465.8827 | 420.3391 | 436.8678 | 365.8914
598.7542 | 465.9018 | 420.5503 | 436.4735 | 366.4336
599.7542 | 465.8846 | 420.3134 | 436.5062 | 366.93
600.7542 | 465.846 | 420.3672 | 436.1138 | 367.6567
601.7542 | 465.765 | 420.3836 | 435.9422 | 368.5405
602.7542 | 465.6393 | 419.9442 | 435.9338 | 368.9046
603.7542 | 465.5524 | 419.9169 | 435.322 | 369.6197
604.7542 | 465.4628 | 420.7355 | 435.9517 | 370.1208
605.7542 | 465.3748 | 420.4436 | 436.2599 | 370.7338
606.7542 | 465.3402 | 420.0467 | 436.5244 | 371.8363
607.7542 | 465.4114 | 419.9255 | 436.3374 | 371.9256
608.7542 | 465.5195 | 420.7411 | 436.3786 | 372.2881
609.7542 | 465.4672 | 419.777 | 435.9713 | 372.941
610.7542 | 465.3923 | 420.8879 | 436.5922 | 372.8532
611.7542 | 465.3779 | 421.8833 | 436.9017 | 374.1082
612.7542 | 465.3468 | 422.1636 | 437.34 | 374.8399
613.7542 | 465.3825 | 422.9426 | 437.8634 | 375.3301
614.7542 | 465.4226 | 422.3646 | 437.8472 | 375.8067
615.7542 | 465.4168 | 422.3231 | 438.1351 | 377.1184
616.7542 | 465.4588 | 422.3671 | 438.7068 | 377.8113
617.7542 | 465.424 | 421.7389 | 438.4659 | 379.1082
618.7542 | 465.4321 | 422.2808 | 438.8144 | 380.9723
619.7542 | 465.3984 | 422.2807 | 438.5811 | 381.6183
620.7542 | 465.3431 | 421.7041 | 437.9031 | 381.7841
621.7542 | 465.3498 | 422.0487 | 437.9513 | 383.5928
622.7542 | 465.2629 | 421.4996 | 437.5671 | 384.2642
623.7542 | 465.1621 | 420.6301 | 436.7919 | 384.4188
624.7542 | 465.2311 | 421.2998 | 436.6364 | 384.9411
625.7542 | 465.2172 | 421.1162 | 437.0329 | 385.9136
626.7542 | 465.2554 | 421.3183 | 437.1991 | 386.6191
627.7542 | 465.2208 | 422.0886 | 437.2006 | 387.8267
628.7542 | 465.2358 | 421.605 | 436.9849 | 387.5678
629.7542 | 465.1457 | 422.0863 | 436.8899 | 389.9774
630.7542 | 465.0921 | 421.9369 | 436.6063 | 390.1684
631.7542 | 465.0748 | 421.9164 | 436.3841 | 391.3244
632.7542 | 465.1147 | 421.5572 | 436.3994 | 393.1652
633.7542 | 465.2009 | 422.4243 | 435.9769 | 395.2259
634.7542 | 465.3129 | 421.939 | 435.5457 | 400.2846
635.7542 | 465.3871 | 422.3053 | 435.692 | 402.8243
636.7542 | 465.5612 | 421.7803 | 435.9368 | 404.98
637.7542 | 465.6402 | 420.8038 | 435.3936 | 404.9448
638.7542 | 465.6835 | 421.7235 | 435.8643 | 403.9122
639.7542 | 465.6965 | 422.1294 | 436.9897 | 405.7407
640.7542 | 465.6793 | 421.6221 | 437.131 | 404.4417
641.7542 | 465.6066 | 421.1497 | 437.0499 | 406.4726
642.7542 | 465.5704 | 421.7925 | 435.487 | 408.5717
643.7542 | 465.5123 | 421.4114 | 435.0066 | 407.8076
644.7542 | 465.4825 | 420.8879 | 434.6387 | 408.6523
645.7542 | 465.4863 | 421.931 | 435.0204 | 411.4302
646.7542 | 465.4998 | 422.4004 | 435.4756 | 411.1438